## Templates
Templates combine standards and prototype data to create space types and construction sets, templates for each building type are exported to OSM format
0 | 1
Name | Notes
DOE Ref Pre-1980 | Numbers taken from the DOE Pre-1980 reference buildings, with values mapped back to the original data source (standards, etc) where possible. The infiltration numbers were taken from the reference buildings but converted to cfm/ft^2 of exterior surface area. Color scheme is based on redder for more public spaces, bluer for more private spaces. Occupancy from ventilation standards was not used by reference buildings because numbers were generally found to be too high for modeling, representing very conservative design scenarios.
DOE Ref 1980-2004 | Numbers taken from the DOE 1980-2004 reference buildings, with values mapped back to the original data source (standards, etc) where possible. The infiltration numbers were taken from the reference buildings but converted to cfm/ft^2 of exterior surface area. Color scheme is based on redder for more public spaces, bluer for more private spaces. Occupancy from ventilation standards was not used by reference buildings because numbers were generally found to be too high for modeling, representing very conservative design scenarios.
DOE Ref 2004 | Numbers taken from the DOE 2004 reference buildings, with values mapped back to the original data source (standards, etc) where possible. The infiltration numbers were taken from the reference buildings but converted to cfm/ft^2 of exterior surface area. Color scheme is based on redder for more public spaces, bluer for more private spaces. Occupancy from ventilation standards was not used by reference buildings because numbers were generally found to be too high for modeling, representing very conservative design scenarios.
189.1-2009 | Lighting, equipment, infiltration, and ventilation taken from the EnergyPlus example file generator low-energy case. Schedules and occupancy taken from DOE Ref 2004 template.
90.1-2007 | Lighting and ventilation taken from 90.1-2007. Equipment and infiltration taken from 189.1-2009 template. Schedules and occupancy taken from DOE Ref 2004 template.

## Standards
Standards are actual standards documents issued by a standards organization
Name
AIA 2001
ASHRAE 169-2006
ASHRAE 189.1-2009
ASHRAE 62.1-1999
ASHRAE 62.1-2004
ASHRAE 62.1-2007
ASHRAE 90.1-1999
ASHRAE 90.1-2001
ASHRAE 90.1-2004
ASHRAE 90.1-2007
ASHRAE 90.1-2010
GGHC v2.2
CEC Title24-2005
CEC Title24-2008

## ClimateZones
A climate zone is a geographic area defined in a standards document
0 | 1 | 2 | 3
Name | Standard | Representative City | BCL Weather Component ID
ASHRAE 169-2006-1A | ASHRAE 169-2006
ASHRAE 169-2006-1B | ASHRAE 169-2006
ASHRAE 169-2006-2A | ASHRAE 169-2006
ASHRAE 169-2006-2B | ASHRAE 169-2006
ASHRAE 169-2006-3A | ASHRAE 169-2006
ASHRAE 169-2006-3B | ASHRAE 169-2006
ASHRAE 169-2006-3C | ASHRAE 169-2006
ASHRAE 169-2006-4A | ASHRAE 169-2006
ASHRAE 169-2006-4B | ASHRAE 169-2006
ASHRAE 169-2006-4C | ASHRAE 169-2006
ASHRAE 169-2006-5A | ASHRAE 169-2006
ASHRAE 169-2006-5B | ASHRAE 169-2006
ASHRAE 169-2006-5C | ASHRAE 169-2006
ASHRAE 169-2006-6A | ASHRAE 169-2006
ASHRAE 169-2006-6B | ASHRAE 169-2006
ASHRAE 169-2006-7A | ASHRAE 169-2006
ASHRAE 169-2006-7B | ASHRAE 169-2006
ASHRAE 169-2006-8A | ASHRAE 169-2006
ASHRAE 169-2006-8B | ASHRAE 169-2006
CEC 2005-1 | CEC Title24-2005
CEC 2005-2 | CEC Title24-2005
CEC 2005-3 | CEC Title24-2005
CEC 2005-4 | CEC Title24-2005
CEC 2005-5 | CEC Title24-2005
CEC 2005-6 | CEC Title24-2005
CEC 2005-7 | CEC Title24-2005
CEC 2005-8 | CEC Title24-2005
CEC 2005-9 | CEC Title24-2005
CEC 2005-10 | CEC Title24-2005
CEC 2008-1 | CEC Title24-2008
CEC 2008-2 | CEC Title24-2008
CEC 2008-3 | CEC Title24-2008
CEC 2008-4 | CEC Title24-2008
CEC 2008-5 | CEC Title24-2008
CEC 2008-6 | CEC Title24-2008
CEC 2008-7 | CEC Title24-2008
CEC 2008-8 | CEC Title24-2008
CEC 2008-9 | CEC Title24-2008
CEC 2008-10 | CEC Title24-2008

## ClimateZoneSets
A climate zone set is a group of climate zones
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39
Name | Climate Zone | Climate Zone2 | Climate Zone3 | Climate Zone4 | Climate Zone5 | Climate Zone6 | Climate Zone7 | Climate Zone8 | Climate Zone9 | Climate Zone10 | Climate Zone11 | Climate Zone12 | Climate Zone13 | Climate Zone14 | Climate Zone15 | Climate Zone16 | Climate Zone17 | Climate Zone18 | Climate Zone19 | Climate Zone20 | Climate Zone21 | Climate Zone22 | Climate Zone23 | Climate Zone24 | Climate Zone25 | Climate Zone26 | Climate Zone27 | Climate Zone28 | Climate Zone29 | Climate Zone30 | Climate Zone31 | Climate Zone32 | Climate Zone33 | Climate Zone34 | Climate Zone35 | Climate Zone36 | Climate Zone37 | Climate Zone38 | Climate Zone39
All Climates | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B | CEC 2005-1 | CEC 2005-2 | CEC 2005-3 | CEC 2005-4 | CEC 2005-5 | CEC 2005-6 | CEC 2005-7 | CEC 2005-8 | CEC 2005-9 | CEC 2005-10 | CEC 2008-1 | CEC 2008-2 | CEC 2008-3 | CEC 2008-4 | CEC 2008-5 | CEC 2008-6 | CEC 2008-7 | CEC 2008-8 | CEC 2008-9 | CEC 2008-10
ClimateZone 1 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B
ClimateZone 1-2 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B
ClimateZone 1-3 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C
ClimateZone 1-3b | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B
ClimateZone 1-4 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C
ClimateZone 1-5 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C
ClimateZone 1-6 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B
ClimateZone 1-7 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B
ClimateZone 1-8 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 1a | ASHRAE 169-2006-1A
ClimateZone 1b | ASHRAE 169-2006-1B
ClimateZone 2 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B
ClimateZone 2-4 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C
ClimateZone 2-5 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C
ClimateZone 2-6 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B
ClimateZone 2-7 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B
ClimateZone 2-8 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 2a | ASHRAE 169-2006-2A
ClimateZone 2b | ASHRAE 169-2006-2B
ClimateZone 3 | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C
ClimateZone 3-4 | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C
ClimateZone 3-5 | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C
ClimateZone 3-7 | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B
ClimateZone 3a | ASHRAE 169-2006-3A
ClimateZone 3a-3b | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B
ClimateZone 3b | ASHRAE 169-2006-3B
ClimateZone 3c | ASHRAE 169-2006-3C
ClimateZone 4 | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C
ClimateZone 4-5 | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C
ClimateZone 4-6 | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B
ClimateZone 4-8 | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 4a | ASHRAE 169-2006-4A
ClimateZone 4b | ASHRAE 169-2006-4B
ClimateZone 4c | ASHRAE 169-2006-4C
ClimateZone 4c-5a | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A
ClimateZone 5 | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C
ClimateZone 5-6 | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B
ClimateZone 5-8 | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 5a | ASHRAE 169-2006-5A
ClimateZone 5b | ASHRAE 169-2006-5B
ClimateZone 5c | ASHRAE 169-2006-5C
ClimateZone 6 | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B
ClimateZone 6-7 | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B
ClimateZone 6-8 | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 6a | ASHRAE 169-2006-6A
ClimateZone 6b | ASHRAE 169-2006-6B
ClimateZone 7 | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B
ClimateZone 7-8 | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 7a | ASHRAE 169-2006-7A
ClimateZone 7b | ASHRAE 169-2006-7B
ClimateZone 8 | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 8a | ASHRAE 169-2006-8A
ClimateZone 8b | ASHRAE 169-2006-8B

## SpaceTypes
|  | 0 | 1 | 2 | 3 | 4 | 11 | 12 | 13 | 14 | 17 | 18 | 19 | 20 | 21 |  |  |  | 25 | 26 | 27 | 28 | 29 | 34 | 35 | 36 | 41 | 43 | 44 | 46 | 47 | 48 |  |  |  | 50 | 51 |  |  |  | 53 | 54 | 55
A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49
|  | COLUMN KEY |  |  |  | Color | Lighting | [12 empty] | Ventilation | [6 empty] | Occupancy |  |  | Infiltration |  | Gas Equipment |  |  |  |  | Electric Plug Loads |  |  |  |  | Thermostats - not currently part of a space type |  | Service Hot Water - not currently part of a space type | [6 empty] | Exhaust - Not currently part of a space type
Full Space Type Name | ImportOrder | Template | Climate Zone Set | BuildingType | SpaceType | R_G_B | Lighting Standard | Lighting Primary Space Type | Lighting Secondary Space Type | LookupColumn | Lighting (W/person) | OSM Lighting (W/ft) | STD Lighting (W/ft^2) | STD Lighting (W/person) | STD Lighting (W/ft) | Fraction to Return Air | Fraction Radiant | Fraction Visible | Lighting Sch | Ventilation Standard | Ventilation Primary Space Type | Ventilation Secondary Space Type | Lookup | STD Ventilation (ft^3/min*ft^2) | STD Ventilation (ft^3/min*person) | STD Ventilation (ach) | OSM Occupancy (people/1000 ft^2)2 | Occupancy Sch | Activity Sch | Infiltration (ft^3/min*ft^2 ext) | Infiltration Sch | OSM Gas Equipment (Btu/hr*ft^2) | Gas Equipment Fraction Latent | Gas Equipment Fraction Radiant | Gas Equipment Fraction Lost | Gas Equipment Sch | OSM Electric Equipment (W/ft^2) | Fraction Latent | Fraction Radiant2 | Fraction Lost | Electric Equipment Sch | Heating Setpoint Schedule | Cooling Setpoint Schedule | Peak Flow Rate (gal/h) | area (ft^2) | calculated (gal/h*ft^2) | Target Temperature Schedule (c) | Sensible Fraction Schedule (c) | Latent Fraction Schedule (c) | Flow Rate Fraction Schedule | 62.1-2004 Exhaust (cfm/ft2) | Total Exhaust (cfm) | Exhaust Fan total eff. | Exhaust Fan DP (in.w.g.) | Exhaust Fan Elec. Power (W) | Elec Power w/sf | Exhaust Sch
CBECS_1980-2004_Outpatient_Anesthesia | 509 | DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Anesthesia | 204_120_230 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
ASHRAE_90.1-2004_Outpatient_Anesthesia | 257 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 90.1-2004 | Hospital | Operating Room | ASHRAE 90.1-2004HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Anesthesia | 300 | 189.1-2009 | ClimateZone 1-3 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Anesthesia | 462 | 189.1-2009 | ClimateZone 4-8 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
CBECS_Before-1980_Outpatient_Anesthesia | 402 | DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Anesthesia | 204_120_230 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 90.1-2007 | Hospital | Operating Room | ASHRAE 90.1-2007HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 90.1-2010 | Hospital | Operating Room | ASHRAE 90.1-2010HospitalOperating Room |  |  | 1.89 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
|  | 90.1-2007 | ClimateZone 1-8 | MidriseApartment | Apartment | 78_167_222 | ASHRAE 90.1-2007 | Dormitory | Living Quarters | ASHRAE 90.1-2007DormitoryLiving Quarters |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Apartment Light | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2004Hotels, Motels, Resorts, Dormitories Bedroom/living Room | 0 | 0 | 0 | 2.63 | MidriseApartment Apartment Occ | MidriseApartment Activity | 0.0446 | MidriseApartment Infil | [5 empty] | 0.36 | 0 | 0.5 | 0 | MidriseApartment Apartment Equip | MidriseApartment Apartment HtgSetp | MidriseApartment Apartment ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | MidriseApartment DHW
CBECS_1980-2004_MidriseApartment Apartment | 473 | DOE Ref 1980-2004 | ClimateZone 1-8 | MidriseApartment | Apartment | 78_167_222 | [6 empty] | 0.36 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Apartment Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 0 | 0 | 2.63 | MidriseApartment Apartment Occ | MidriseApartment Activity | 0.2232 | MidriseApartment Infil | [5 empty] | 0.5 | 0 | 0.5 | 0 | MidriseApartment Apartment Equip | MidriseApartment Apartment HtgSetp | MidriseApartment Apartment ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | MidriseApartment DHW
ASHRAE_90.1-2004_MidriseApartment Apartment | 151 | DOE Ref 2004 | ClimateZone 1-8 | MidriseApartment | Apartment | 78_167_222 | ASHRAE 90.1-2004 | Dormitory | Living Quarters | ASHRAE 90.1-2004DormitoryLiving Quarters |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Apartment Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 0 | 0 | 2.63 | MidriseApartment Apartment Occ | MidriseApartment Activity | 0.0595 | MidriseApartment Infil | [5 empty] | 0.5 | 0 | 0.5 | 0 | MidriseApartment Apartment Equip | MidriseApartment Apartment HtgSetp | MidriseApartment Apartment ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | MidriseApartment DHW
ASHRAE_189.1-2009_ClimateZone 1-3_MidriseApartment Apartment | 310 | 189.1-2009 | ClimateZone 1-3 | MidriseApartment | Apartment | 78_167_222 | ASHRAE 189.1-2009 | Dormitory | Living Quarters | ASHRAE 189.1-2009DormitoryLiving Quarters |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Apartment Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 0 | 0 | 2.63 | MidriseApartment Apartment Occ | MidriseApartment Activity | 0.0595 | MidriseApartment Infil | [5 empty] | 0.36 | 0 | 0.5 | 0 | MidriseApartment Apartment Equip | MidriseApartment Apartment HtgSetp | MidriseApartment Apartment ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | MidriseApartment DHW
ASHRAE_189.1-2009_ClimateZone 4-8_MidriseApartment Apartment | 466 | 189.1-2009 | ClimateZone 4-8 | MidriseApartment | Apartment | 78_167_222 | ASHRAE 189.1-2009 | Dormitory | Living Quarters | ASHRAE 189.1-2009DormitoryLiving Quarters |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Apartment Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 0 | 0 | 2.63 | MidriseApartment Apartment Occ | MidriseApartment Activity | 0.0446 | MidriseApartment Infil | [5 empty] | 0.36 | 0 | 0.5 | 0 | MidriseApartment Apartment Equip | MidriseApartment Apartment HtgSetp | MidriseApartment Apartment ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | MidriseApartment DHW
CBECS_Before-1980_MidriseApartment Apartment | 362 | DOE Ref Pre-1980 | ClimateZone 1-8 | MidriseApartment | Apartment | 78_167_222 | [6 empty] | 0.36 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Apartment Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 0 | 0 | 2.63 | MidriseApartment Apartment Occ | MidriseApartment Activity | 0.2232 | MidriseApartment Infil | [5 empty] | 0.5 | 0 | 0.5 | 0 | MidriseApartment Apartment Equip | MidriseApartment Apartment HtgSetp | MidriseApartment Apartment ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | MidriseApartment DHW
|  | 90.1-2010 | ClimateZone 1-8 | MidriseApartment | Apartment | 78_167_222 | ASHRAE 90.1-2010 | Dormitory | Living Quarters | ASHRAE 90.1-2010DormitoryLiving Quarters |  |  | 0.38 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Apartment Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 | 0 | 2.63 | MidriseApartment Apartment Occ | MidriseApartment Activity | 0.0446 | MidriseApartment Infil | [5 empty] | 0.36 | 0 | 0.5 | 0 | MidriseApartment Apartment Equip | MidriseApartment Apartment HtgSetp | MidriseApartment Apartment ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | MidriseApartment DHW
|  | 90.1-2007 | ClimateZone 1-8 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 90.1-2007 | Audience/Seating Area | General | ASHRAE 90.1-2007Audience/Seating AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2004 | Educational Facilities | Music/theater/dance | ASHRAE 62.1-2004Educational FacilitiesMusic/theater/dance | 0.06 | 10 | 0 | 92.94 | SecondarySchool Auditorium Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
CBECS_1980-2004_SecondarySchool_Auditorium | 534 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Auditorium; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_196_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.12; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Auditorium; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationAuditorium; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 92.94; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Auditorium Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.46; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp
ASHRAE_90.1-2004_SecondarySchool_Auditorium | 454 | DOE Ref 2004 | ClimateZone 1-8 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 90.1-2004 | Audience/Seating Area | General | ASHRAE 90.1-2004Audience/Seating AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Auditorium | ASHRAE 62.1-1999EducationAuditorium | 0 | 15 | 0 | 92.94 | SecondarySchool Auditorium Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Auditorium | 273 | 189.1-2009 | ClimateZone 1-3 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 189.1-2009 | Audience/Seating Area | General | ASHRAE 189.1-2009Audience/Seating AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Auditorium | ASHRAE 62.1-1999EducationAuditorium | 0 | 15 | 0 | 92.94 | SecondarySchool Auditorium Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Auditorium | 253 | 189.1-2009 | ClimateZone 4-8 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 189.1-2009 | Audience/Seating Area | General | ASHRAE 189.1-2009Audience/Seating AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Auditorium | ASHRAE 62.1-1999EducationAuditorium | 0 | 15 | 0 | 92.94 | SecondarySchool Auditorium Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
CBECS_Before-1980_SecondarySchool_Auditorium | 511 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Auditorium; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_196_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.45; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Auditorium; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationAuditorium; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 92.94; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Auditorium Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.46; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 90.1-2010 | Audience/Seating Area | For Auditorium | ASHRAE 90.1-2010Audience/Seating AreaFor Auditorium |  |  | 0.79 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2007 | Educational Facilities | Music/theater/dance | ASHRAE 62.1-2007Educational FacilitiesMusic/theater/dance | 0.06 | 10 | 0 | 92.94 | SecondarySchool Auditorium Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Retail | Back_Space | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 3.33 | Retail Bldg Occ | Retail Activity | 0.0446 | Retail Infil Half On | [5 empty] | 0.546 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
CBECS_1980-2004_Retail_Back_Space | 384 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Retail; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Back_Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_149_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.17; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Retail Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Storage rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 3.33; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Retail Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Retail Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Retail Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.75; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Retail Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Retail HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Retail ClgSetp
ASHRAE_90.1-2004_Retail_Back_Space | 488 | DOE Ref 2004 | ClimateZone 1-8 | Retail | Back_Space | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 3.33 | Retail Bldg Occ | Retail Activity | 0.0595 | Retail Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Retail_Back_Space | 145 | 189.1-2009 | ClimateZone 1-3 | Retail | Back_Space | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 3.33 | Retail Bldg Occ | Retail Activity | 0.0595 | Retail Infil Half On | [5 empty] | 0.546 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Retail_Back_Space | 328 | 189.1-2009 | ClimateZone 4-8 | Retail | Back_Space | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 3.33 | Retail Bldg Occ | Retail Activity | 0.0446 | Retail Infil Half On | [5 empty] | 0.546 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
CBECS_Before-1980_Retail_Back_Space | 434 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Retail; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Back_Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_149_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.77; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Retail Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Storage rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 3.33; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Retail Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Retail Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Retail Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.75; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Retail Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Retail HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Retail ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Retail | Back_Space | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 3.33 | Retail Bldg Occ | Retail Activity | 0.0446 | Retail Infil Half On | [5 empty] | 0.546 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | LargeHotel | Banquet | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | 0.06 | 5 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
CBECS_1980-2004_LargeHotel_Banquet | 501 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: LargeHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Banquet; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_196_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.56; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: LargeHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Conference rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 67; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: LargeHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: LargeHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: LargeHotel Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 6.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: LargeHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: LargeHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: LargeHotel ClgSetp
ASHRAE_90.1-2004_LargeHotel_Banquet | 369 | DOE Ref 2004 | ClimateZone 1-8 | LargeHotel | Banquet | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 6.3 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Banquet | 25 | 189.1-2009 | ClimateZone 1-3 | LargeHotel | Banquet | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Banquet | 229 | 189.1-2009 | ClimateZone 4-8 | LargeHotel | Banquet | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
CBECS_Before-1980_LargeHotel_Banquet | 142 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: LargeHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Banquet; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_196_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.77; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: LargeHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Conference rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 67; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: LargeHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: LargeHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: LargeHotel Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 6.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: LargeHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: LargeHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: LargeHotel ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | LargeHotel | Banquet | 230_196_120 | ASHRAE 90.1-2010 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2010Conference/Meeting/MultipurposeGeneral |  |  | 1.23 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | 0.06 | 5 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
CBECS_1980-2004_Outpatient_BioHazard | 1 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: BioHazard; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 204_120_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: GGHC v2.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Health Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Bedpan Room; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: GGHC v2.2Health CareBedpan Room; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_BioHazard | 9 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | BioHazard | 204_120_230 | ASHRAE 90.1-2004 | Active Storage | For Hospital | ASHRAE 90.1-2004Active StorageFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_BioHazard | 542 | 189.1-2009 | ClimateZone 1-3 | Outpatient | BioHazard | 204_120_230 | ASHRAE 189.1-2009 | Active Storage | For Hospital | ASHRAE 189.1-2009Active StorageFor Hospital |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_BioHazard | 337 | 189.1-2009 | ClimateZone 4-8 | Outpatient | BioHazard | 204_120_230 | ASHRAE 189.1-2009 | Active Storage | For Hospital | ASHRAE 189.1-2009Active StorageFor Hospital |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_BioHazard | 36 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: BioHazard; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 204_120_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: GGHC v2.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Health Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Bedpan Room; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: GGHC v2.2Health CareBedpan Room; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | BioHazard | 204_120_230 | ASHRAE 90.1-2007 | Active Storage | For Hospital | ASHRAE 90.1-2007Active StorageFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | BioHazard | 204_120_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Office | BreakRoom | 230_157_120 | ASHRAE 90.1-2007 | Lounge/Recreation | General | ASHRAE 90.1-2007Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2004 | General | Conference/meeting | ASHRAE 62.1-2004GeneralConference/meeting | 0.06 | 5 | 0 | 50 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 4.46 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | BreakRoom | 230_157_120 | [6 empty] | 1.884 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 50 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 5.63 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 1-3 | Office | BreakRoom | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 50 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 4.46 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 4-8 | Office | BreakRoom | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 50 | Office Misc Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 4.46 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | BreakRoom | 230_157_120 | ASHRAE 90.1-2004 | Lounge/Recreation | General | ASHRAE 90.1-2004Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 50 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 5.58 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | BreakRoom | 230_157_120 | [6 empty] | 2.28 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 50 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 5.63 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Office | BreakRoom | 230_157_120 | ASHRAE 90.1-2010 | Lounge/Recreation | General | ASHRAE 90.1-2010Lounge/RecreationGeneral |  |  | 0.73 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 | 0 | 50 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 4.46 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Warehouse | Bulk | 41_31_169 | ASHRAE 90.1-2007 | Warehouse | Medium/Bulky Material Storage | ASHRAE 90.1-2007WarehouseMedium/Bulky Material Storage |  |  | 0.9 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-2004 | Miscellaneous Spaces | Warehouses | ASHRAE 62.1-2004Miscellaneous SpacesWarehouses | 0.06 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0446 | Always On | [5 empty] | 0.17 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp BulkStorage | Warehouse ClgSetp
CBECS_1980-2004_Warehouse_Bulk | 185 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Warehouse; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Bulk; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 41_31_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Warehouse Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Warehouses; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Warehouse Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Warehouse Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Always On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.25; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Warehouse Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Warehouse HtgSetp BulkStorage; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Warehouse ClgSetp
ASHRAE_90.1-2004_Warehouse_Bulk | 449 | DOE Ref 2004 | ClimateZone 1-8 | Warehouse | Bulk | 41_31_169 | ASHRAE 90.1-2004 | Warehouse | Medium/Bulky Material Storage | ASHRAE 90.1-2004WarehouseMedium/Bulky Material Storage |  |  | 0.9 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0595 | Always On | [5 empty] | 0.25 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp BulkStorage | Warehouse ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Warehouse_Bulk | 158 | 189.1-2009 | ClimateZone 1-3 | Warehouse | Bulk | 41_31_169 | ASHRAE 189.1-2009 | Warehouse | Medium/Bulky Material Storage | ASHRAE 189.1-2009WarehouseMedium/Bulky Material Storage |  |  | 0.81 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0595 | Always On | [5 empty] | 0.17 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp BulkStorage | Warehouse ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Warehouse_Bulk | 123 | 189.1-2009 | ClimateZone 4-8 | Warehouse | Bulk | 41_31_169 | ASHRAE 189.1-2009 | Warehouse | Medium/Bulky Material Storage | ASHRAE 189.1-2009WarehouseMedium/Bulky Material Storage |  |  | 0.81 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0446 | Always On | [5 empty] | 0.17 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp BulkStorage | Warehouse ClgSetp
CBECS_Before-1980_Warehouse_Bulk | 331 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Warehouse; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Bulk; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 41_31_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.62; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Warehouse Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Warehouses; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Warehouse Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Warehouse Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Always On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.25; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Warehouse Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Warehouse HtgSetp BulkStorage; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Warehouse ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Warehouse | Bulk | 41_31_169 | ASHRAE 90.1-2010 | Warehouse | Medium/Bulky Material Storage | ASHRAE 90.1-2010WarehouseMedium/Bulky Material Storage |  |  | 0.58 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses | ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | 0.06 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0446 | Always On | [5 empty] | 0.17 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp BulkStorage | Warehouse ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | LargeHotel | Cafe | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | For Hotel | ASHRAE 90.1-2007Dining AreaFor Hotel |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
CBECS_1980-2004_LargeHotel_Cafe | 389 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: LargeHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Cafe; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.46; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: LargeHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Food and Beverage Service; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Cafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 67; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: LargeHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: LargeHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: LargeHotel Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: LargeHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: LargeHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: LargeHotel ClgSetp
ASHRAE_90.1-2004_LargeHotel_Cafe | 62 | DOE Ref 2004 | ClimateZone 1-8 | LargeHotel | Cafe | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | For Hotel | ASHRAE 90.1-2004Dining AreaFor Hotel |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 0.5 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Cafe | 225 | 189.1-2009 | ClimateZone 1-3 | LargeHotel | Cafe | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Hotel | ASHRAE 189.1-2009Dining AreaFor Hotel |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Cafe | 510 | 189.1-2009 | ClimateZone 4-8 | LargeHotel | Cafe | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Hotel | ASHRAE 189.1-2009Dining AreaFor Hotel |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
CBECS_Before-1980_LargeHotel_Cafe | 291 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: LargeHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Cafe; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 3.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: LargeHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Food and Beverage Service; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Cafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 67; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: LargeHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: LargeHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: LargeHotel Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: LargeHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: LargeHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: LargeHotel ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | Cafe | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 92.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_1980-2004_Outpatient_Cafe | 29 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Cafe; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Food and Beverage Service; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Cafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 92.94; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_Cafe | 333 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | Cafe | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 92.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Cafe | 201 | 189.1-2009 | ClimateZone 1-3 | Outpatient | Cafe | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 92.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Cafe | 91 | 189.1-2009 | ClimateZone 4-8 | Outpatient | Cafe | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 92.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_Cafe | 378 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Cafe; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Food and Beverage Service; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Cafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 92.94; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | LargeHotel | Cafe | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | For Hotel | ASHRAE 90.1-2010Dining AreaFor Hotel |  |  | 0.82 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | Cafe | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | General | ASHRAE 90.1-2010Dining AreaGeneral |  |  | 0.65 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 92.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 66.67 | PrimarySchool Cafeteria Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 1.72 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
CBECS_1980-2004_PrimarySchool_Cafeteria | 192 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Cafeteria; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.4; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Food and Beverage Service; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Cafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 66.67; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Cafeteria Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 2.36; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Cafeteria | 87 | DOE Ref 2004 | ClimateZone 1-8 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 66.67 | PrimarySchool Cafeteria Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 2.36 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Cafeteria | 321 | 189.1-2009 | ClimateZone 1-3 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 66.67 | PrimarySchool Cafeteria Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 1.72 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Cafeteria | 457 | 189.1-2009 | ClimateZone 4-8 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 66.67 | PrimarySchool Cafeteria Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 1.72 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
CBECS_Before-1980_PrimarySchool_Cafeteria | 136 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Cafeteria; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 3.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Food and Beverage Service; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Cafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 66.67; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Cafeteria Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 2.36; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 66.84 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
CBECS_1980-2004_SecondarySchool_Cafeteria | 79 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Cafeteria; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Food and Beverage Service; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Cafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 66.84; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.79; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp
ASHRAE_90.1-2004_SecondarySchool_Cafeteria | 459 | DOE Ref 2004 | ClimateZone 1-8 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 66.84 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 1.79 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Cafeteria | 69 | 189.1-2009 | ClimateZone 1-3 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 66.84 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Cafeteria | 424 | 189.1-2009 | ClimateZone 4-8 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 66.84 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
CBECS_Before-1980_SecondarySchool_Cafeteria | 426 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Cafeteria; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 3.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Food and Beverage Service; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Cafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 66.84; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.79; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | General | ASHRAE 90.1-2010Dining AreaGeneral |  |  | 0.65 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 66.67 | PrimarySchool Cafeteria Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 1.72 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | General | ASHRAE 90.1-2010Dining AreaGeneral |  |  | 0.65 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 66.84 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2007 | Classroom/Lecture/Training | General | ASHRAE 90.1-2007Classroom/Lecture/TrainingGeneral |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (ages 5-8) | ASHRAE 62.1-2004Educational FacilitiesClassrooms (ages 5-8) | 0.12 | 10 | 0 | 23.22 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
CBECS_1980-2004_PrimarySchool_Classroom | 444 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Classroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Classroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationClassroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 23.22; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.39; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Classroom | 411 | DOE Ref 2004 | ClimateZone 1-8 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2004 | Classroom/Lecture/Training | General | ASHRAE 90.1-2004Classroom/Lecture/TrainingGeneral |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 15 | 0 | 23.22 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 1.39 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Classroom | 135 | 189.1-2009 | ClimateZone 1-3 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 15 | 0 | 23.22 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Classroom | 344 | 189.1-2009 | ClimateZone 4-8 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 15 | 0 | 23.22 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
CBECS_Before-1980_PrimarySchool_Classroom | 68 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Classroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Classroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationClassroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 23.22; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.39; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2007 | Classroom/Lecture/Training | General | ASHRAE 90.1-2007Classroom/Lecture/TrainingGeneral |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (age 9 plus) | ASHRAE 62.1-2004Educational FacilitiesClassrooms (age 9 plus) | 0.12 | 10 | 0 | 23.22 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
CBECS_1980-2004_SecondarySchool_Classroom | 197 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Classroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Classroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationClassroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 23.22; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.93; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp
ASHRAE_90.1-2004_SecondarySchool_Classroom | 419 | DOE Ref 2004 | ClimateZone 1-8 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2004 | Classroom/Lecture/Training | General | ASHRAE 90.1-2004Classroom/Lecture/TrainingGeneral |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 15 | 0 | 23.22 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.93 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Classroom | 120 | 189.1-2009 | ClimateZone 1-3 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 15 | 0 | 23.22 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Classroom | 382 | 189.1-2009 | ClimateZone 4-8 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 15 | 0 | 23.22 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
CBECS_Before-1980_SecondarySchool_Classroom | 358 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Classroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Classroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationClassroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 23.22; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.93; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2010 | Classroom/Lecture/Training | General | ASHRAE 90.1-2010Classroom/Lecture/TrainingGeneral |  |  | 1.24 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (ages 5-8) | ASHRAE 62.1-2007Educational FacilitiesClassrooms (ages 5-8) | 0.12 | 10 | 0 | 23.22 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2010 | Classroom/Lecture/Training | General | ASHRAE 90.1-2010Classroom/Lecture/TrainingGeneral |  |  | 1.24 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (age 9 plus) | ASHRAE 62.1-2007Educational FacilitiesClassrooms (age 9 plus) | 0.12 | 10 | 0 | 23.22 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
CBECS_1980-2004_Outpatient_CleanWork | 352 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: CleanWork; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 204_120_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: GGHC v2.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Health Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Clean Utility / Workroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: GGHC v2.2Health CareClean Utility / Workroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 18.58; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_CleanWork | 31 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | CleanWork | 204_120_230 | ASHRAE 90.1-2004 | Hospital | Medical Supply | ASHRAE 90.1-2004HospitalMedical Supply |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_CleanWork | 393 | 189.1-2009 | ClimateZone 1-3 | Outpatient | CleanWork | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Medical Supply | ASHRAE 189.1-2009HospitalMedical Supply |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_CleanWork | 178 | 189.1-2009 | ClimateZone 4-8 | Outpatient | CleanWork | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Medical Supply | ASHRAE 189.1-2009HospitalMedical Supply |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_CleanWork | 314 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: CleanWork; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 204_120_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: GGHC v2.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Health Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Clean Utility / Workroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: GGHC v2.2Health CareClean Utility / Workroom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 18.58; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | CleanWork | 204_120_230 | ASHRAE 90.1-2007 | Hospital | Medical Supply | ASHRAE 90.1-2007HospitalMedical Supply |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | CleanWork | 204_120_230 | ASHRAE 90.1-2010 | Hospital | Medical Supply | ASHRAE 90.1-2010HospitalMedical Supply |  |  | 1.27 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Office | ClosedOffice | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 4.75 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0.64 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | ClosedOffice | 120_230_199 | [6 empty] | 1.727 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.75 | Office Work Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.87 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 1-3 | Office | ClosedOffice | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.75 | Office Work Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.64 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 4-8 | Office | ClosedOffice | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.75 | Office Work Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0.64 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | ClosedOffice | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.75 | Office Work Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.87 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | ClosedOffice | 120_230_199 | [6 empty] | 2.09 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.75 | Office Work Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.87 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Office | ClosedOffice | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 4.75 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0.64 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Office | Conference | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2004 | General | Conference/meeting | ASHRAE 62.1-2004GeneralConference/meeting | 0.06 | 5 | 0 | 50 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0.37 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Conference | 230_196_120 | [6 empty] | 1.84 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 | 0 | 50 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 1-3 | Office | Conference | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 | 0 | 50 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.37 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 4-8 | Office | Conference | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 | 0 | 50 | Office Misc Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0.37 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | Conference | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 | 0 | 50 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Conference | 230_196_120 | [6 empty] | 2.47 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 | 0 | 50 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | Conference | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2004 | General | Conference/meeting | ASHRAE 62.1-2004GeneralConference/meeting | 0.06 | 5 | 0 | 46.45 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_1980-2004_Outpatient_Conference | 285 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Conference; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_196_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Conference rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 46.45; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_Conference | 507 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | Conference | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 46.45 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Conference | 4 | 189.1-2009 | ClimateZone 1-3 | Outpatient | Conference | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 46.45 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Conference | 111 | 189.1-2009 | ClimateZone 4-8 | Outpatient | Conference | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 46.45 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_Conference | 371 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Conference; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_196_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Conference rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 46.45; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Office | Conference | 230_196_120 | ASHRAE 90.1-2010 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2010Conference/Meeting/MultipurposeGeneral |  |  | 1.23 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 | 0 | 50 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0.37 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | Conference | 230_196_120 | ASHRAE 90.1-2010 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2010Conference/Meeting/MultipurposeGeneral |  |  | 1.23 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 | 0 | 46.45 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_1980-2004_Hospital_Corridor | 49 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Corridor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.36; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Critical Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Bldg HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Bldg ClgSetp
ASHRAE_90.1-2004_Hospital_Corridor | 470 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | ASHRAE 90.1-2004Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_Corridor | 37 | 189.1-2009 | ClimateZone 1-3 | Hospital | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_Corridor | 296 | 189.1-2009 | ClimateZone 4-8 | Hospital | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
CBECS_Before-1980_Hospital_Corridor | 96 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Corridor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.32; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Critical Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Bldg HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Bldg ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | ASHRAE 90.1-2007Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
CBECS_1980-2004_LargeHotel_Corridor | 222 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: LargeHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Corridor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.22; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: LargeHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: LargeHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: LargeHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: LargeHotel Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: LargeHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: LargeHotel Corridor HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: LargeHotel Corridor ClgSetp
ASHRAE_90.1-2004_LargeHotel_Corridor | 440 | DOE Ref 2004 | ClimateZone 1-8 | LargeHotel | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel Corridor HtgSetp | LargeHotel Corridor ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Corridor | 54 | 189.1-2009 | ClimateZone 1-3 | LargeHotel | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel Corridor HtgSetp | LargeHotel Corridor ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Corridor | 388 | 189.1-2009 | ClimateZone 4-8 | LargeHotel | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel Corridor HtgSetp | LargeHotel Corridor ClgSetp
CBECS_Before-1980_LargeHotel_Corridor | 212 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: LargeHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Corridor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.6; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: LargeHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: LargeHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: LargeHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: LargeHotel Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: LargeHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: LargeHotel Corridor HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: LargeHotel Corridor ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | LargeHotel | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 1 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel Corridor HtgSetp | LargeHotel Corridor ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | MidriseApartment | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Corridor Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 |  |  | 0.0446 | MidriseApartment Infil | [5 empty] | 0 | 0 | 0.5 | 0 |  | MidriseApartment Corridor HtgSetp | MidriseApartment Corridor ClgSetp
CBECS_1980-2004_MidriseApartment_Corridor | 41 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: MidriseApartment; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Corridor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.92; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: MidriseApartment Corridor Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: MidriseApartment Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: MidriseApartment Corridor HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: MidriseApartment Corridor ClgSetp
ASHRAE_90.1-2004_MidriseApartment_Corridor | 559 | DOE Ref 2004 | ClimateZone 1-8 | MidriseApartment | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Corridor Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  |  | 0.0595 | MidriseApartment Infil | [5 empty] | 0 | 0 | 0.5 | 0 |  | MidriseApartment Corridor HtgSetp | MidriseApartment Corridor ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_MidriseApartment_Corridor | 45 | 189.1-2009 | ClimateZone 1-3 | MidriseApartment | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Corridor Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  |  | 0.0595 | MidriseApartment Infil | [5 empty] | 0 | 0 | 0.5 | 0 |  | MidriseApartment Corridor HtgSetp | MidriseApartment Corridor ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_MidriseApartment_Corridor | 363 | 189.1-2009 | ClimateZone 4-8 | MidriseApartment | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Corridor Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  |  | 0.0446 | MidriseApartment Infil | [5 empty] | 0 | 0 | 0.5 | 0 |  | MidriseApartment Corridor HtgSetp | MidriseApartment Corridor ClgSetp
CBECS_Before-1980_MidriseApartment_Corridor | 146 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: MidriseApartment; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Corridor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.92; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: MidriseApartment Corridor Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: MidriseApartment Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: MidriseApartment Corridor HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: MidriseApartment Corridor ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Office | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 1 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0.16 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Corridor | 169_31_31 | [6 empty] | 0.785 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Work Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.29 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 1-3 | Office | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Work Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.16 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 4-8 | Office | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Work Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0.16 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Work Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.29 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Corridor | 169_31_31 | [6 empty] | 0.95 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Work Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.29 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
CBECS_1980-2004_PrimarySchool_Corridor | 438 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Corridor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationCorridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 9.29; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool BathCorrMechKitchen HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool BathCorrMechKitchen ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Corridor | 280 | DOE Ref 2004 | ClimateZone 1-8 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Corridor | 223 | 189.1-2009 | ClimateZone 1-3 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Corridor | 11 | 189.1-2009 | ClimateZone 4-8 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
CBECS_Before-1980_PrimarySchool_Corridor | 155 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Corridor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationCorridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 9.29; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool BathCorrMechKitchen HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool BathCorrMechKitchen ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 9.31 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
CBECS_1980-2004_SecondarySchool_Corridor | 555 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Corridor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.86; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationCorridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 9.31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp BathCorrMechKitchen; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp BathCorrMechKitchen
ASHRAE_90.1-2004_SecondarySchool_Corridor | 284 | DOE Ref 2004 | ClimateZone 1-8 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.31 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Corridor | 211 | 189.1-2009 | ClimateZone 1-3 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.31 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Corridor | 112 | 189.1-2009 | ClimateZone 4-8 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.31 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
CBECS_Before-1980_SecondarySchool_Corridor | 124 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Corridor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationCorridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 9.31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp BathCorrMechKitchen; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp BathCorrMechKitchen
|  | 90.1-2007 | ClimateZone 1-8 | SmallHotel | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_1980-2004_SmallHotel_Corridor | 234 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Corridor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.88; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
ASHRAE_90.1-2004_SmallHotel_Corridor | 259 | DOE Ref 2004 | ClimateZone 1-8 | SmallHotel | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Corridor | 3 | 189.1-2009 | ClimateZone 1-3 | SmallHotel | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Corridor | 261 | 189.1-2009 | ClimateZone 4-8 | SmallHotel | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_Before-1980_SmallHotel_Corridor | 35 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Corridor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.88; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | For Hospital | ASHRAE 90.1-2010Corridor/TransitionFor Hospital |  |  | 0.89 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | LargeHotel | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral |  |  | 0.66 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 1 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel Corridor HtgSetp | LargeHotel Corridor ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | MidriseApartment | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral |  |  | 0.66 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Corridor Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 |  |  | 0.0446 | MidriseApartment Infil | [5 empty] | 0 | 0 | 0.5 | 0 |  | MidriseApartment Corridor HtgSetp | MidriseApartment Corridor ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Office | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral |  |  | 0.66 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 1 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0.16 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral |  |  | 0.66 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral |  |  | 0.66 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 9.31 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
|  | 90.1-2010 | ClimateZone 1-8 | SmallHotel | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral |  |  | 0.66 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2004 | Retail | Supermarket | ASHRAE 62.1-2004RetailSupermarket | 0.06 | 7.5 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 | SuperMarket Infil Half On | 6.25 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 3.64 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
CBECS_1980-2004_SuperMarket_Deli/Bakery | 536 | DOE Ref 1980-2004 | ClimateZone 1-8 | SuperMarket | Deli/Bakery | 31_169_34 | [6 empty] | 2.78 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.2232 | SuperMarket Infil Half On | 8.53 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
ASHRAE_90.1-2004_SuperMarket_Deli/Bakery | 545 | DOE Ref 2004 | ClimateZone 1-8 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 | SuperMarket Infil Half On | 8.53 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_SuperMarket_Deli/Bakery | 172 | 189.1-2009 | ClimateZone 1-3 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 | SuperMarket Infil Half On | 6.25 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 3.64 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_SuperMarket_Deli/Bakery | 561 | 189.1-2009 | ClimateZone 4-8 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 | SuperMarket Infil Half On | 6.25 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 3.64 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
CBECS_Before-1980_SuperMarket_Deli/Bakery | 301 | DOE Ref Pre-1980 | ClimateZone 1-8 | SuperMarket | Deli/Bakery | 31_169_34 | [6 empty] | 5.04 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.2232 | SuperMarket Infil Half On | 8.53 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
|  | 90.1-2010 | ClimateZone 1-8 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 90.1-2010 | Sales Area | General | ASHRAE 90.1-2010Sales AreaGeneral |  |  | 1.68 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | Retail | Supermarket | ASHRAE 62.1-2007RetailSupermarket | 0.06 | 7.5 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 | SuperMarket Infil Half On | 6.25 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 3.64 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
CBECS_1980-2004_FullServiceRestaurant_Dining | 20 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: FullServiceRestaurant; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Dining; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.54; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: FullServiceRestaurant Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Food and Beverage Service; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Dining Rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 67; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: FullServiceRestaurant Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: FullServiceRestaurant Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: FullServiceRestaurant Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 5.6; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0.25; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: FullServiceRestaurant Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: FullServiceRestaurant HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: FullServiceRestaurant ClgSetp
ASHRAE_90.1-2004_FullServiceRestaurant_Dining | 418 | DOE Ref 2004 | ClimateZone 1-8 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | For Family Dining | ASHRAE 90.1-2004Dining AreaFor Family Dining |  |  | 2.1 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 67 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0595 | FullServiceRestaurant Infil Half On | [5 empty] | 5.6 | 0.25 | 0.3 | 0 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_FullServiceRestaurant_Dining | 122 | 189.1-2009 | ClimateZone 1-3 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Family Dining | ASHRAE 189.1-2009Dining AreaFor Family Dining |  |  | 1.89 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 67 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0595 | FullServiceRestaurant Infil Half On | [5 empty] | 4.08 | 0.25 | 0.3 | 0 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_FullServiceRestaurant_Dining | 554 | 189.1-2009 | ClimateZone 4-8 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Family Dining | ASHRAE 189.1-2009Dining AreaFor Family Dining |  |  | 1.89 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 67 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0446 | FullServiceRestaurant Infil Half On | [5 empty] | 4.08 | 0.25 | 0.3 | 0 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp
CBECS_Before-1980_FullServiceRestaurant_Dining | 107 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: FullServiceRestaurant; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Dining; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.77; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: FullServiceRestaurant Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Food and Beverage Service; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Dining Rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 67; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: FullServiceRestaurant Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: FullServiceRestaurant Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: FullServiceRestaurant Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 5.6; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0.25; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: FullServiceRestaurant Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: FullServiceRestaurant HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: FullServiceRestaurant ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | For Family Dining | ASHRAE 90.1-2007Dining AreaFor Family Dining |  |  | 2.1 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-2004 | Food and Beverage Service | Restaurant dining rooms | ASHRAE 62.1-2004Food and Beverage ServiceRestaurant dining rooms | 0.18 | 7.5 | 0 | 67 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0446 | FullServiceRestaurant Infil Half On | [5 empty] | 4.08 | 0.25 | 0.3 | 0 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp
CBECS_1980-2004_Hospital_Dining | 538 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Dining; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.58; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Food and Beverage Service; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Dining Rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 10; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Critical Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Bldg HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Bldg ClgSetp
ASHRAE_90.1-2004_Hospital_Dining | 51 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | Dining | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 10 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_Dining | 376 | 189.1-2009 | ClimateZone 1-3 | Hospital | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 10 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_Dining | 558 | 189.1-2009 | ClimateZone 4-8 | Hospital | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 10 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
CBECS_Before-1980_Hospital_Dining | 400 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Dining; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.77; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Food and Beverage Service; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Dining Rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 10; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Critical Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Bldg HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Bldg ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | Dining | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 10 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | For Family Dining | ASHRAE 90.1-2007Dining AreaFor Family Dining |  |  | 2.1 |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 67 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0446 | QuickServiceRestaurant Infil Half On | [5 empty] | 8.74 | 0.25 | 0.3 | 0 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp
CBECS_1980-2004_QuickServiceRestaurant_Dining | 100 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: QuickServiceRestaurant; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Dining; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.44; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: QuickServiceRestaurant Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Food and Beverage Service; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Cafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 67; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: QuickServiceRestaurant Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: QuickServiceRestaurant Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: QuickServiceRestaurant Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 12; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0.25; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: QuickServiceRestaurant Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: QuickServiceRestaurant HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: QuickServiceRestaurant ClgSetp
ASHRAE_90.1-2004_QuickServiceRestaurant_Dining | 370 | DOE Ref 2004 | ClimateZone 1-8 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | For Family Dining | ASHRAE 90.1-2004Dining AreaFor Family Dining |  |  | 2.1 |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 67 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0595 | QuickServiceRestaurant Infil Half On | [5 empty] | 12 | 0.25 | 0.3 | 0 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_QuickServiceRestaurant_Dining | 502 | 189.1-2009 | ClimateZone 1-3 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Family Dining | ASHRAE 189.1-2009Dining AreaFor Family Dining |  |  | 1.89 |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 67 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0595 | QuickServiceRestaurant Infil Half On | [5 empty] | 8.74 | 0.25 | 0.3 | 0 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_QuickServiceRestaurant_Dining | 359 | 189.1-2009 | ClimateZone 4-8 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Family Dining | ASHRAE 189.1-2009Dining AreaFor Family Dining |  |  | 1.89 |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 67 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0446 | QuickServiceRestaurant Infil Half On | [5 empty] | 8.74 | 0.25 | 0.3 | 0 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp
CBECS_Before-1980_QuickServiceRestaurant_Dining | 290 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: QuickServiceRestaurant; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Dining; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 3.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: QuickServiceRestaurant Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Food and Beverage Service; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Cafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 67; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: QuickServiceRestaurant Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: QuickServiceRestaurant Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: QuickServiceRestaurant Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 12; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0.25; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: QuickServiceRestaurant Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: QuickServiceRestaurant HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: QuickServiceRestaurant ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | For Family Dining | ASHRAE 90.1-2010Dining AreaFor Family Dining |  |  | 0.89 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-2007 | Food and Beverage Service | Restaurant dining rooms | ASHRAE 62.1-2007Food and Beverage ServiceRestaurant dining rooms | 0.18 | 7.5 | 0 | 67 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0446 | FullServiceRestaurant Infil Half On | [5 empty] | 4.08 | 0.25 | 0.3 | 0 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | Dining | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | General | ASHRAE 90.1-2010Dining AreaGeneral |  |  | 0.65 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 10 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | For Family Dining | ASHRAE 90.1-2010Dining AreaFor Family Dining |  |  | 0.89 |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 67 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0446 | QuickServiceRestaurant Infil Half On | [5 empty] | 8.74 | 0.25 | 0.3 | 0 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 90.1-2007 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2007Dressing/Locker/Fitting RoomGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Patient rooms | ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPatient rooms | 0 | 25 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_1980-2004_Outpatient_DressingRoom | 325 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: DressingRoom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 136_78_222; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Dormitory sleeping areas; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 4.65; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_DressingRoom | 484 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 90.1-2004 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2004Dressing/Locker/Fitting RoomGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_DressingRoom | 24 | 189.1-2009 | ClimateZone 1-3 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_DressingRoom | 302 | 189.1-2009 | ClimateZone 4-8 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_DressingRoom | 547 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: DressingRoom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 136_78_222; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Dormitory sleeping areas; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 4.65; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 90.1-2010 | Dressing/Fitting Room | For Retail | ASHRAE 90.1-2010Dressing/Fitting RoomFor Retail |  |  | 0.87 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Patient rooms | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPatient rooms | 0 | 25 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
CBECS_1980-2004_SuperMarket_DryStorage | 245 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SuperMarket; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: DryStorage; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_149_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SuperMarket Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Shipping and receiving; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 3.33; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SuperMarket Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SuperMarket Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SuperMarket Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.75; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SuperMarket Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SuperMarket HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SuperMarket ClgSetp
ASHRAE_90.1-2004_SuperMarket_DryStorage | 465 | DOE Ref 2004 | ClimateZone 1-8 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 | SuperMarket Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SuperMarket_DryStorage | 217 | 189.1-2009 | ClimateZone 1-3 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SuperMarket_DryStorage | 492 | 189.1-2009 | ClimateZone 4-8 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
CBECS_Before-1980_SuperMarket_DryStorage | 195 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SuperMarket; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: DryStorage; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_149_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.77; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SuperMarket Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Shipping and receiving; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 3.33; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SuperMarket Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SuperMarket Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SuperMarket Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.75; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SuperMarket Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SuperMarket HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SuperMarket ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Elec/MechRoom | 41_31_169 | [6 empty] | 2.355 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 0 |  | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 1-3 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 0 |  | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 4-8 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 0 |  | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 0 |  | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Elec/MechRoom | 41_31_169 | [6 empty] | 2.85 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 0 |  | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
CBECS_1980-2004_Outpatient_Elec/MechRoom | 535 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Elec/MechRoom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 41_31_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: GGHC v2.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Health Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Mechanical Equipment Room; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: GGHC v2.2Health CareMechanical Equipment Room; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_Elec/MechRoom | 86 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 5 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Elec/MechRoom | 226 | 189.1-2009 | ClimateZone 1-3 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 3.64 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Elec/MechRoom | 368 | 189.1-2009 | ClimateZone 4-8 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 3.64 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_Elec/MechRoom | 193 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Elec/MechRoom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 41_31_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: GGHC v2.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Health Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Mechanical Equipment Room; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: GGHC v2.2Health CareMechanical Equipment Room; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 3.64 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral |  |  | 0.95 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral |  |  | 0.95 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 3.64 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Retail | Entry | 169_31_31 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Mall Concourse | ASHRAE 90.1-2007Retail (not including accent lighting)Mall Concourse |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-2004 | Retail | General Sales | ASHRAE 62.1-2004RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0446 | Retail Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
CBECS_1980-2004_Retail_Entry | 335 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Retail; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Entry; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 3.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Retail Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Basement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Retail Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Retail Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Retail Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Retail Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Retail HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Retail ClgSetp
ASHRAE_90.1-2004_Retail_Entry | 105 | DOE Ref 2004 | ClimateZone 1-8 | Retail | Entry | 169_31_31 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Mall Concourse | ASHRAE 90.1-2004Retail (not including accent lighting)Mall Concourse |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0595 | Retail Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Retail_Entry | 160 | 189.1-2009 | ClimateZone 1-3 | Retail | Entry | 169_31_31 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Mall Concourse | ASHRAE 189.1-2009Retail (not including accent lighting)Mall Concourse |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0595 | Retail Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
|  | 189.1-2009 | ClimateZone 4-8 | Retail | Entry | 169_31_31 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Mall Concourse | ASHRAE 189.1-2009Retail (not including accent lighting)Mall Concourse |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0446 | Retail Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
CBECS_Before-1980_Retail_Entry | 156 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Retail; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Entry; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 5.04; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Retail Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Basement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Retail Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Retail Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Retail Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Retail Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Retail HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Retail ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Retail | Entry | 169_31_31 | ASHRAE 90.1-2010 | Retail | Mall Concourse | ASHRAE 90.1-2010RetailMall Concourse |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0446 | Retail Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
CBECS_1980-2004_Hospital_ER_Exam | 50 | DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | ER_Exam | 169_31_159 | [6 empty] | 3.84 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
ASHRAE_90.1-2004_Hospital_ER_Exam | 204 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | ER_Exam | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_ER_Exam | 56 | 189.1-2009 | ClimateZone 1-3 | Hospital | ER_Exam | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_ER_Exam | 121 | 189.1-2009 | ClimateZone 4-8 | Hospital | ER_Exam | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
CBECS_Before-1980_Hospital_ER_Exam | 508 | DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | ER_Exam | 169_31_159 | [6 empty] | 5 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | ER_Exam | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | ER_Exam | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Emergency | ASHRAE 90.1-2010HospitalEmergency |  |  | 2.26 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
CBECS_1980-2004_Hospital_ER_NurseStn | 450 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: ER_NurseStn; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_162_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.66; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: AIA 2001; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Surgery and Critical Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: ER Waiting Room; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: AIA 2001Surgery and Critical CareER Waiting Room; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 6.25; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Critical Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.36; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Critical HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Critical HtgSetp
ASHRAE_90.1-2004_Hospital_ER_NurseStn | 30 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 1.36 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_ER_NurseStn | 150 | 189.1-2009 | ClimateZone 1-3 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 0.99 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_ER_NurseStn | 166 | 189.1-2009 | ClimateZone 4-8 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0.99 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
CBECS_Before-1980_Hospital_ER_NurseStn | 527 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: ER_NurseStn; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_162_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.64; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: AIA 2001; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Surgery and Critical Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: ER Waiting Room; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: AIA 2001Surgery and Critical CareER Waiting Room; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 6.25; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Critical Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.36; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Critical HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Critical HtgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0.99 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 90.1-2010 | Hospital | Nurse Station | ASHRAE 90.1-2010HospitalNurse Station |  |  | 0.87 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0.99 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
CBECS_1980-2004_Hospital_ER_Trauma | 34 | DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | ER_Trauma | 169_31_159 | [6 empty] | 3.84 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
ASHRAE_90.1-2004_Hospital_ER_Trauma | 177 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | ER_Trauma | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_ER_Trauma | 330 | 189.1-2009 | ClimateZone 1-3 | Hospital | ER_Trauma | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_ER_Trauma | 213 | 189.1-2009 | ClimateZone 4-8 | Hospital | ER_Trauma | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
CBECS_Before-1980_Hospital_ER_Trauma | 243 | DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | ER_Trauma | 169_31_159 | [6 empty] | 5 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | ER_Trauma | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | ER_Trauma | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Emergency | ASHRAE 90.1-2010HospitalEmergency |  |  | 2.26 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
CBECS_1980-2004_Hospital_ER_Triage | 293 | DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | ER_Triage | 169_31_159 | [6 empty] | 3.84 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
ASHRAE_90.1-2004_Hospital_ER_Triage | 90 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | ER_Triage | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_ER_Triage | 530 | 189.1-2009 | ClimateZone 1-3 | Hospital | ER_Triage | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 1.97 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_ER_Triage | 74 | 189.1-2009 | ClimateZone 4-8 | Hospital | ER_Triage | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 1.97 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
CBECS_Before-1980_Hospital_ER_Triage | 237 | DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | ER_Triage | 169_31_159 | [6 empty] | 5 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | ER_Triage | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 1.97 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | ER_Triage | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Emergency | ASHRAE 90.1-2010HospitalEmergency |  |  | 2.26 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 1.97 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
CBECS_1980-2004_Outpatient_Exam | 75 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Exam; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 136_78_222; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.6; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: GGHC v2.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Health Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Special Procedure Room, Diagnostic; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: GGHC v2.2Health CareSpecial Procedure Room, Diagnostic; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 18.58; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_Exam | 517 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | Exam | 136_78_222 | ASHRAE 90.1-2004 | Hospital | Exam/Treatment | ASHRAE 90.1-2004HospitalExam/Treatment |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Exam | 329 | 189.1-2009 | ClimateZone 1-3 | Outpatient | Exam | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Exam/Treatment | ASHRAE 189.1-2009HospitalExam/Treatment |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Exam | 208 | 189.1-2009 | ClimateZone 4-8 | Outpatient | Exam | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Exam/Treatment | ASHRAE 189.1-2009HospitalExam/Treatment |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_Exam | 516 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Exam; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 136_78_222; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.6; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: GGHC v2.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Health Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Special Procedure Room, Diagnostic; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: GGHC v2.2Health CareSpecial Procedure Room, Diagnostic; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 18.58; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | Exam | 136_78_222 | ASHRAE 90.1-2007 | Hospital | Exam/Treatment | ASHRAE 90.1-2007HospitalExam/Treatment |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | Exam | 136_78_222 | ASHRAE 90.1-2010 | Hospital | Exam/Treatment | ASHRAE 90.1-2010HospitalExam/Treatment |  |  | 1.66 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SmallHotel | Exercise | 154_230_120 | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 90.1-2007Gymnasium/Exercise CenterExercise Area |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | SmallHotel Exercise Light | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/weight rooms | ASHRAE 62.1-2004Sports and EntertainmentHealth club/weight rooms | 0.06 | 20 | 0 | 30 | SmallHotel Exercise Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.55 | 0 | 0.5 | 0 | SmallHotel Exercise Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_1980-2004_SmallHotel_Exercise | 269 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Exercise; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 154_230_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel Exercise Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Sports and Amusement; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Playing floors (gymnasium); A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium); A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 30; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel Exercise Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.07; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel Exercise Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
ASHRAE_90.1-2004_SmallHotel_Exercise | 399 | DOE Ref 2004 | ClimateZone 1-8 | SmallHotel | Exercise | 154_230_120 | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 90.1-2004Gymnasium/Exercise CenterExercise Area |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | SmallHotel Exercise Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 30 | SmallHotel Exercise Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 1.07 | 0 | 0.5 | 0 | SmallHotel Exercise Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Exercise | 89 | 189.1-2009 | ClimateZone 1-3 | SmallHotel | Exercise | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterExercise Area |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | SmallHotel Exercise Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 30 | SmallHotel Exercise Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 0.55 | 0 | 0.5 | 0 | SmallHotel Exercise Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Exercise | 167 | 189.1-2009 | ClimateZone 4-8 | SmallHotel | Exercise | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterExercise Area |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | SmallHotel Exercise Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 30 | SmallHotel Exercise Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.55 | 0 | 0.5 | 0 | SmallHotel Exercise Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_Before-1980_SmallHotel_Exercise | 500 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Exercise; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 154_230_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel Exercise Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Sports and Amusement; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Playing floors (gymnasium); A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium); A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 30; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel Exercise Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.07; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel Exercise Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SmallHotel | Exercise | 154_230_120 | ASHRAE 90.1-2010 | Gymnasium/Fitness Center | Fitness Area | ASHRAE 90.1-2010Gymnasium/Fitness CenterFitness Area |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | SmallHotel Exercise Light | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/weight rooms | ASHRAE 62.1-2007Sports and EntertainmentHealth club/weight rooms | 0.06 | 20 | 0 | 30 | SmallHotel Exercise Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.55 | 0 | 0.5 | 0 | SmallHotel Exercise Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Warehouse | Fine | 120_149_230 | ASHRAE 90.1-2007 | Warehouse | Fine Material Storage | ASHRAE 90.1-2007WarehouseFine Material Storage |  |  | 1.4 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-2004 | Miscellaneous Spaces | Warehouses | ASHRAE 62.1-2004Miscellaneous SpacesWarehouses | 0.06 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0446 | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp FineStorage | Warehouse ClgSetp FineStorage
CBECS_1980-2004_Warehouse_Fine | 405 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Warehouse; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Fine; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_149_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.08; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Warehouse Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Warehouses; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Warehouse Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Warehouse Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Always On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Warehouse Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Warehouse HtgSetp FineStorage; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Warehouse ClgSetp FineStorage
ASHRAE_90.1-2004_Warehouse_Fine | 55 | DOE Ref 2004 | ClimateZone 1-8 | Warehouse | Fine | 120_149_230 | ASHRAE 90.1-2004 | Warehouse | Fine Material Storage | ASHRAE 90.1-2004WarehouseFine Material Storage |  |  | 1.4 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0595 | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp FineStorage | Warehouse ClgSetp FineStorage
ASHRAE_189.1-2009_ClimateZone 1-3_Warehouse_Fine | 65 | 189.1-2009 | ClimateZone 1-3 | Warehouse | Fine | 120_149_230 | ASHRAE 189.1-2009 | Warehouse | Fine Material Storage | ASHRAE 189.1-2009WarehouseFine Material Storage |  |  | 1.26 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0595 | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp FineStorage | Warehouse ClgSetp FineStorage
ASHRAE_189.1-2009_ClimateZone 4-8_Warehouse_Fine | 206 | 189.1-2009 | ClimateZone 4-8 | Warehouse | Fine | 120_149_230 | ASHRAE 189.1-2009 | Warehouse | Fine Material Storage | ASHRAE 189.1-2009WarehouseFine Material Storage |  |  | 1.26 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0446 | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp FineStorage | Warehouse ClgSetp FineStorage
CBECS_Before-1980_Warehouse_Fine | 209 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Warehouse; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Fine; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_149_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.08; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Warehouse Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Warehouses; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Warehouse Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Warehouse Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Always On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Warehouse Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Warehouse HtgSetp FineStorage; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Warehouse ClgSetp FineStorage
|  | 90.1-2010 | ClimateZone 1-8 | Warehouse | Fine | 120_149_230 | ASHRAE 90.1-2010 | Warehouse | Fine Material Storage | ASHRAE 90.1-2010WarehouseFine Material Storage |  |  | 0.95 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses | ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | 0.06 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0446 | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp FineStorage | Warehouse ClgSetp FineStorage
|  | 90.1-2007 | ClimateZone 1-8 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 90.1-2007 | Lounge/Recreation | General | ASHRAE 90.1-2007Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 | 0 | 30 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.73 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_1980-2004_SmallHotel_GuestLounge | 262 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: GuestLounge; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Lobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 30; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.43; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
ASHRAE_90.1-2004_SmallHotel_GuestLounge | 180 | DOE Ref 2004 | ClimateZone 1-8 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 90.1-2004 | Lounge/Recreation | General | ASHRAE 90.1-2004Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 1.43 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_GuestLounge | 557 | 189.1-2009 | ClimateZone 1-3 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 0.73 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_GuestLounge | 540 | 189.1-2009 | ClimateZone 4-8 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.73 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_Before-1980_SmallHotel_GuestLounge | 387 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: GuestLounge; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Lobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 30; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.43; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 90.1-2010 | Lounge/Recreation | General | ASHRAE 90.1-2010Lounge/RecreationGeneral |  |  | 0.73 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 | 0 | 30 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.73 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_1980-2004_LargeHotel_GuestRoom | 417 | DOE Ref 1980-2004 | ClimateZone 1-8 | LargeHotel | GuestRoom | 78_167_222 | [6 empty] | 1.77 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
ASHRAE_90.1-2004_LargeHotel_GuestRoom | 101 | DOE Ref 2004 | ClimateZone 1-8 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2004 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2004Hotel/MotelGuest Rooms |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_GuestRoom | 396 | 189.1-2009 | ClimateZone 1-3 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | ASHRAE 189.1-2009Hotel/MotelGuest Rooms |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 0.68 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_GuestRoom | 71 | 189.1-2009 | ClimateZone 4-8 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | ASHRAE 189.1-2009Hotel/MotelGuest Rooms |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.68 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
CBECS_Before-1980_LargeHotel_GuestRoom | 464 | DOE Ref Pre-1980 | ClimateZone 1-8 | LargeHotel | GuestRoom | 78_167_222 | [6 empty] | 1.4 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
|  | 90.1-2007 | ClimateZone 1-8 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2007 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2007Hotel/MotelGuest Rooms |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 | 0 | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.68 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
|  | 90.1-2007 | ClimateZone 1-8 | SmallHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2007 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2007Hotel/MotelGuest Rooms |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 | 0 | 4.27 | SmallHotel GuestRoom Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.68 | 0 | 0.5 | 0 | SmallHotel GuestRoom Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel SWH GuestRoom
CBECS_1980-2004_SmallHotel_GuestRoom | 250 | DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | GuestRoom | 78_167_222 | [6 empty] | 1.92 |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 4.27 | SmallHotel GuestRoom Occ | SmallHotel Activity | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1.33 | 0 | 0.5 | 0 | SmallHotel GuestRoom Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel SWH GuestRoom
ASHRAE_90.1-2004_SmallHotel_GuestRoom | 528 | DOE Ref 2004 | ClimateZone 1-8 | SmallHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2004 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2004Hotel/MotelGuest Rooms |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 4.27 | SmallHotel GuestRoom Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 1.33 | 0 | 0.5 | 0 | SmallHotel GuestRoom Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel SWH GuestRoom
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_GuestRoom | 254 | 189.1-2009 | ClimateZone 1-3 | SmallHotel | GuestRoom | 78_167_222 | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | ASHRAE 189.1-2009Hotel/MotelGuest Rooms |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 4.27 | SmallHotel GuestRoom Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 0.68 | 0 | 0.5 | 0 | SmallHotel GuestRoom Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel SWH GuestRoom
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_GuestRoom | 372 | 189.1-2009 | ClimateZone 4-8 | SmallHotel | GuestRoom | 78_167_222 | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | ASHRAE 189.1-2009Hotel/MotelGuest Rooms |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 4.27 | SmallHotel GuestRoom Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.68 | 0 | 0.5 | 0 | SmallHotel GuestRoom Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel SWH GuestRoom
CBECS_Before-1980_SmallHotel_GuestRoom | 520 | DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | GuestRoom | 78_167_222 | [6 empty] | 1.92 |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 4.27 | SmallHotel GuestRoom Occ | SmallHotel Activity | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1.33 | 0 | 0.5 | 0 | SmallHotel GuestRoom Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel SWH GuestRoom
|  | 90.1-2010 | ClimateZone 1-8 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Hotel | ASHRAE 90.1-2010Guest RoomFor Hotel |  |  | 1.11 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 | 0 | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.68 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
|  | 90.1-2010 | ClimateZone 1-8 | SmallHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Highway Lodging | ASHRAE 90.1-2010Guest RoomFor Highway Lodging |  |  | 0.75 |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 | 0 | 4.27 | SmallHotel GuestRoom Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.68 | 0 | 0.5 | 0 | SmallHotel GuestRoom Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel SWH GuestRoom
|  | 90.1-2007 | ClimateZone 1-8 | PrimarySchool | Gym | 154_230_120 | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Playing Area | ASHRAE 90.1-2007Gymnasium/Exercise CenterPlaying Area |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2004 | Sports and Entertainment | Gym, stadium (play area) | ASHRAE 62.1-2004Sports and EntertainmentGym, stadium (play area) | 0.3 | 0 | 0 | 27.9 | PrimarySchool Gym Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
CBECS_1980-2004_PrimarySchool_Gym | 347 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Gym; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 154_230_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.07; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Sports and Amusement; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Playing floors (gymnasium); A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium); A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 27.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Gym Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.46; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Gym | 60 | DOE Ref 2004 | ClimateZone 1-8 | PrimarySchool | Gym | 154_230_120 | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Playing Area | ASHRAE 90.1-2004Gymnasium/Exercise CenterPlaying Area |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 27.9 | PrimarySchool Gym Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Gym | 523 | 189.1-2009 | ClimateZone 1-3 | PrimarySchool | Gym | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 27.9 | PrimarySchool Gym Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Gym | 480 | 189.1-2009 | ClimateZone 4-8 | PrimarySchool | Gym | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 27.9 | PrimarySchool Gym Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
CBECS_Before-1980_PrimarySchool_Gym | 169 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Gym; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 154_230_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Sports and Amusement; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Playing floors (gymnasium); A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium); A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 27.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Gym Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.46; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SecondarySchool | Gym | 154_230_120 | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Playing Area | ASHRAE 90.1-2007Gymnasium/Exercise CenterPlaying Area |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2004 | Sports and Entertainment | Gym, stadium (play area) | ASHRAE 62.1-2004Sports and EntertainmentGym, stadium (play area) | 0.3 | 0 | 0 | 92.94 | SecondarySchool Gym Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
CBECS_1980-2004_SecondarySchool_Gym | 522 | DOE Ref 1980-2004 | ClimateZone 1-8 | SecondarySchool | Gym | 154_230_120 | [6 empty] | 1.06 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 92.94 | SecondarySchool Gym Occ | SecondarySchool Activity | 0.2232 | SecondarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
ASHRAE_90.1-2004_SecondarySchool_Gym | 283 | DOE Ref 2004 | ClimateZone 1-8 | SecondarySchool | Gym | 154_230_120 | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Playing Area | ASHRAE 90.1-2004Gymnasium/Exercise CenterPlaying Area |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 92.94 | SecondarySchool Gym Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Gym | 174 | 189.1-2009 | ClimateZone 1-3 | SecondarySchool | Gym | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 92.94 | SecondarySchool Gym Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Gym | 233 | 189.1-2009 | ClimateZone 4-8 | SecondarySchool | Gym | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 92.94 | SecondarySchool Gym Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
CBECS_Before-1980_SecondarySchool_Gym | 343 | DOE Ref Pre-1980 | ClimateZone 1-8 | SecondarySchool | Gym | 154_230_120 | [6 empty] | 0.8 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 92.94 | SecondarySchool Gym Occ | SecondarySchool Activity | 0.2232 | SecondarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
|  | 90.1-2010 | ClimateZone 1-8 | PrimarySchool | Gym | 154_230_120 | ASHRAE 90.1-2010 | Gymnasium/Fitness Center | Playing Area | ASHRAE 90.1-2010Gymnasium/Fitness CenterPlaying Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) | ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | 0.3 | 0 | 0 | 27.9 | PrimarySchool Gym Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SecondarySchool | Gym | 154_230_120 | ASHRAE 90.1-2010 | Gymnasium/Fitness Center | Playing Area | ASHRAE 90.1-2010Gymnasium/Fitness CenterPlaying Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) | ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | 0.3 | 0 | 0 | 92.94 | SecondarySchool Gym Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | Hall | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | ASHRAE 90.1-2007Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.29 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_1980-2004_Outpatient_Hall | 82 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Hall; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.4; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_Hall | 490 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | Hall | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | ASHRAE 90.1-2004Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.4 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Hall | 99 | 189.1-2009 | ClimateZone 1-3 | Outpatient | Hall | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.29 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Hall | 453 | 189.1-2009 | ClimateZone 4-8 | Outpatient | Hall | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.29 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_Hall | 88 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Hall; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.4; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | Hall | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | For Hospital | ASHRAE 90.1-2010Corridor/TransitionFor Hospital |  |  | 0.89 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.29 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_1980-2004_Hospital_ICU_NurseStn | 248 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: ICU_NurseStn; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_162_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.71; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: AIA 2001; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Surgery and Critical Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Critical and Intensive Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: AIA 2001Surgery and Critical CareCritical and Intensive Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Critical Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Critical HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Critical HtgSetp
ASHRAE_90.1-2004_Hospital_ICU_NurseStn | 102 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_ICU_NurseStn | 560 | 189.1-2009 | ClimateZone 1-3 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_ICU_NurseStn | 110 | 189.1-2009 | ClimateZone 4-8 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
CBECS_Before-1980_Hospital_ICU_NurseStn | 143 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: ICU_NurseStn; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_162_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.64; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: AIA 2001; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Surgery and Critical Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Critical and Intensive Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: AIA 2001Surgery and Critical CareCritical and Intensive Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Critical Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Critical HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Critical HtgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 90.1-2010 | Hospital | Nurse Station | ASHRAE 90.1-2010HospitalNurse Station |  |  | 0.87 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
CBECS_1980-2004_Hospital_ICU_Open | 415 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: ICU_Open; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 78_167_222; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 3.84; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: AIA 2001; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Surgery and Critical Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Critical and Intensive Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: AIA 2001Surgery and Critical CareCritical and Intensive Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Critical Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Critical HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Critical HtgSetp
ASHRAE_90.1-2004_Hospital_ICU_Open | 409 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | ICU_Open | 78_167_222 | ASHRAE 90.1-2004 | Hospital | Recovery | ASHRAE 90.1-2004HospitalRecovery |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_ICU_Open | 27 | 189.1-2009 | ClimateZone 1-3 | Hospital | ICU_Open | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Recovery | ASHRAE 189.1-2009HospitalRecovery |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_ICU_Open | 210 | 189.1-2009 | ClimateZone 4-8 | Hospital | ICU_Open | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Recovery | ASHRAE 189.1-2009HospitalRecovery |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
CBECS_Before-1980_Hospital_ICU_Open | 407 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: ICU_Open; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 78_167_222; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 4.22; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: AIA 2001; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Surgery and Critical Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Critical and Intensive Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: AIA 2001Surgery and Critical CareCritical and Intensive Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Critical Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Critical HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Critical HtgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | ICU_Open | 78_167_222 | ASHRAE 90.1-2007 | Hospital | Recovery | ASHRAE 90.1-2007HospitalRecovery |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | ICU_Open | 78_167_222 | ASHRAE 90.1-2010 | Hospital | Recovery | ASHRAE 90.1-2010HospitalRecovery |  |  | 1.15 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
CBECS_1980-2004_Hospital_ICU_PatRm | 52 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: ICU_PatRm; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 78_167_222; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 3.84; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: AIA 2001; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Surgery and Critical Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Critical and Intensive Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: AIA 2001Surgery and Critical CareCritical and Intensive Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Critical Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Critical HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Critical HtgSetp
ASHRAE_90.1-2004_Hospital_ICU_PatRm | 386 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 90.1-2004 | Hospital | Patient Room | ASHRAE 90.1-2004HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_ICU_PatRm | 476 | 189.1-2009 | ClimateZone 1-3 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_ICU_PatRm | 433 | 189.1-2009 | ClimateZone 4-8 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
CBECS_Before-1980_Hospital_ICU_PatRm | 76 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: ICU_PatRm; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 78_167_222; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 4.22; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: AIA 2001; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Surgery and Critical Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Critical and Intensive Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: AIA 2001Surgery and Critical CareCritical and Intensive Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Critical Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Critical HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Critical HtgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 90.1-2007 | Hospital | Patient Room | ASHRAE 90.1-2007HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 90.1-2010 | Hospital | Patient Room | ASHRAE 90.1-2010HospitalPatient Room |  |  | 0.62 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | IT_Room | 41_31_169 | [6 empty] | 1.55 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 5 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 1-3 | Office | IT_Room | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 5 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 1.56 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 4-8 | Office | IT_Room | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 5 | Office Misc Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 1.56 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | IT_Room | 41_31_169 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 5 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | IT_Room | 41_31_169 | [6 empty] | 2.09 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 5 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Office | IT_Room | 41_31_169 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Telephone/data entry | ASHRAE 62.1-2004Office BuildingsTelephone/data entry | 0.06 | 5 | 0 | 5 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 1.56 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | IT_Room | 41_31_169 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Telephone/data entry | ASHRAE 62.1-2004Office BuildingsTelephone/data entry | 0.06 | 5 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_1980-2004_Outpatient_IT_Room | 59 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: IT_Room; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 41_31_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Telecommunication centers and data entry areas; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 4.65; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_IT_Room | 479 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | IT_Room | 41_31_169 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | 0 | 20 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_IT_Room | 274 | 189.1-2009 | ClimateZone 1-3 | Outpatient | IT_Room | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | 0 | 20 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_IT_Room | 200 | 189.1-2009 | ClimateZone 4-8 | Outpatient | IT_Room | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | 0 | 20 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_IT_Room | 519 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: IT_Room; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 41_31_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Telecommunication centers and data entry areas; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 4.65; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Office | IT_Room | 41_31_169 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | ASHRAE 62.1-2007Office BuildingsTelephone/data entry | 0.06 | 5 | 0 | 5 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 1.56 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | IT_Room | 41_31_169 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | ASHRAE 62.1-2007Office BuildingsTelephone/data entry | 0.06 | 5 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_1980-2004_Outpatient_Janitor | 338 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Janitor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_149_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: GGHC v2.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Health Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Janitors Closet / Utility; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: GGHC v2.2Health CareJanitors Closet / Utility; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 1.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_Janitor | 271 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | Janitor | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Janitor | 220 | 189.1-2009 | ClimateZone 1-3 | Outpatient | Janitor | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Janitor | 175 | 189.1-2009 | ClimateZone 4-8 | Outpatient | Janitor | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_Janitor | 264 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Janitor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_149_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: GGHC v2.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Health Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Janitors Closet / Utility; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: GGHC v2.2Health CareJanitors Closet / Utility; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 1.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | Janitor | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | Janitor | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_1980-2004_FullServiceRestaurant_Kitchen | 242 | DOE Ref 1980-2004 | ClimateZone 1-8 | FullServiceRestaurant | Kitchen | 78_222_133 | [6 empty] | 1.52 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.2232 | FullServiceRestaurant Infil Half On | 378.75 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant Gas Equip | 35 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp Kitchen | FullServiceRestaurant ClgSetp Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant Kitchen Exhaust
ASHRAE_90.1-2004_FullServiceRestaurant_Kitchen | 12 | DOE Ref 2004 | ClimateZone 1-8 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0595 | FullServiceRestaurant Infil Half On | 378.75 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant Gas Equip | 35 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp Kitchen | FullServiceRestaurant ClgSetp Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant Kitchen Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_FullServiceRestaurant_Kitchen | 44 | 189.1-2009 | ClimateZone 1-3 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0595 | FullServiceRestaurant Infil Half On | 276.72 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant Gas Equip | 25.5 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp Kitchen | FullServiceRestaurant ClgSetp Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant Kitchen Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_FullServiceRestaurant_Kitchen | 448 | 189.1-2009 | ClimateZone 4-8 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0446 | FullServiceRestaurant Infil Half On | 276.72 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant Gas Equip | 25.5 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp Kitchen | FullServiceRestaurant ClgSetp Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant Kitchen Exhaust
CBECS_Before-1980_FullServiceRestaurant_Kitchen | 128 | DOE Ref Pre-1980 | ClimateZone 1-8 | FullServiceRestaurant | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.2232 | FullServiceRestaurant Infil Half On | 378.75 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant Gas Equip | 35 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp Kitchen | FullServiceRestaurant ClgSetp Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant Kitchen Exhaust
|  | 90.1-2007 | ClimateZone 1-8 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0446 | FullServiceRestaurant Infil Half On | 276.72 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant Gas Equip | 25.5 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp Kitchen | FullServiceRestaurant ClgSetp Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant Kitchen Exhaust
CBECS_1980-2004_Hospital_Kitchen | 373 | DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | Kitchen | 78_222_133 | [6 empty] | 1.42 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | 96.7 | 0.1 | 0.2 | 0.7 | Hospital Kitchen Gas | 7.5 | 0.2 | 0.5 | 0.1 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital SWH Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital Kitchen Exhaust
ASHRAE_90.1-2004_Hospital_Kitchen | 423 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | 96.7 | 0.1 | 0.2 | 0.7 | Hospital Kitchen Gas | 7.5 | 0.2 | 0.5 | 0.1 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital SWH Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital Kitchen Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_Kitchen | 162 | 189.1-2009 | ClimateZone 1-3 | Hospital | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | 70.46 | 0.1 | 0.2 | 0.7 | Hospital Kitchen Gas | 5.47 | 0.2 | 0.5 | 0.1 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital SWH Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital Kitchen Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_Kitchen | 451 | 189.1-2009 | ClimateZone 4-8 | Hospital | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | 70.46 | 0.1 | 0.2 | 0.7 | Hospital Kitchen Gas | 5.47 | 0.2 | 0.5 | 0.1 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital SWH Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital Kitchen Exhaust
CBECS_Before-1980_Hospital_Kitchen | 126 | DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | 96.7 | 0.1 | 0.2 | 0.7 | Hospital Kitchen Gas | 7.5 | 0.2 | 0.5 | 0.1 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital SWH Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital Kitchen Exhaust
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | 70.46 | 0.1 | 0.2 | 0.7 | Hospital Kitchen Gas | 5.47 | 0.2 | 0.5 | 0.1 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital SWH Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital Kitchen Exhaust
CBECS_1980-2004_LargeHotel_Kitchen | 218 | DOE Ref 1980-2004 | ClimateZone 1-8 | LargeHotel | Kitchen | 78_222_133 | [6 empty] | 1.56 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | LargeHotel Bldg Occ | LargeHotel Activity | 0.2232 | LargeHotel Infil Quarter On | 511 | 0.1 | 0.2 | 0.7 | LargeHotel Kitchen Gas | 47.22 | 0.2 | 0.5 | 0.1 | LargeHotel Kitchen Equip | LargeHotel Kitchen HtgSetp | LargeHotel Kitchen ClgSetp | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel SWH Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel Kitchen Exhaust
ASHRAE_90.1-2004_LargeHotel_Kitchen | 398 | DOE Ref 2004 | ClimateZone 1-8 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | 511 | 0.1 | 0.2 | 0.7 | LargeHotel Kitchen Gas | 47.22 | 0.2 | 0.5 | 0.1 | LargeHotel Kitchen Equip | LargeHotel Kitchen HtgSetp | LargeHotel Kitchen ClgSetp | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel SWH Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel Kitchen Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Kitchen | 173 | 189.1-2009 | ClimateZone 1-3 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | 373.8 | 0.1 | 0.2 | 0.7 | LargeHotel Kitchen Gas | 24.16 | 0.2 | 0.5 | 0.1 | LargeHotel Kitchen Equip | LargeHotel Kitchen HtgSetp | LargeHotel Kitchen ClgSetp | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel SWH Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel Kitchen Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Kitchen | 287 | 189.1-2009 | ClimateZone 4-8 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | 373.8 | 0.1 | 0.2 | 0.7 | LargeHotel Kitchen Gas | 24.16 | 0.2 | 0.5 | 0.1 | LargeHotel Kitchen Equip | LargeHotel Kitchen HtgSetp | LargeHotel Kitchen ClgSetp | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel SWH Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel Kitchen Exhaust
CBECS_Before-1980_LargeHotel_Kitchen | 282 | DOE Ref Pre-1980 | ClimateZone 1-8 | LargeHotel | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | LargeHotel Bldg Occ | LargeHotel Activity | 0.2232 | LargeHotel Infil Quarter On | 511 | 0.1 | 0.2 | 0.7 | LargeHotel Kitchen Gas | 47.22 | 0.2 | 0.5 | 0.1 | LargeHotel Kitchen Equip | LargeHotel Kitchen HtgSetp | LargeHotel Kitchen ClgSetp | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel SWH Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel Kitchen Exhaust
|  | 90.1-2007 | ClimateZone 1-8 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | 373.8 | 0.1 | 0.2 | 0.7 | LargeHotel Kitchen Gas | 24.16 | 0.2 | 0.5 | 0.1 | LargeHotel Kitchen Equip | LargeHotel Kitchen HtgSetp | LargeHotel Kitchen ClgSetp | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel SWH Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel Kitchen Exhaust
|  | 90.1-2007 | ClimateZone 1-8 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 13.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | 220.5 | 0.1 | 0.2 | 0.7 | PrimarySchool Kitchen Gas | 13.13 | 0.25 | 0.3 | 0.2 | PrimarySchool Kitchen Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool Kitchen Exhaust
CBECS_1980-2004_PrimarySchool_Kitchen | 106 | DOE Ref 1980-2004 | ClimateZone 1-8 | PrimarySchool | Kitchen | 78_222_133 | [6 empty] | 1.6 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 13.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.2232 | PrimarySchool Infil | 302.6 | 0.1 | 0.2 | 0.7 | PrimarySchool Kitchen Gas | 17.7 | 0.25 | 0.3 | 0.2 | PrimarySchool Kitchen Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool Kitchen Exhaust
ASHRAE_90.1-2004_PrimarySchool_Kitchen | 231 | DOE Ref 2004 | ClimateZone 1-8 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 13.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | 302.6 | 0.1 | 0.2 | 0.7 | PrimarySchool Kitchen Gas | 17.7 | 0.25 | 0.3 | 0.2 | PrimarySchool Kitchen Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool Kitchen Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Kitchen | 463 | 189.1-2009 | ClimateZone 1-3 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 13.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | 220.5 | 0.1 | 0.2 | 0.7 | PrimarySchool Kitchen Gas | 13.13 | 0.25 | 0.3 | 0.2 | PrimarySchool Kitchen Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool Kitchen Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Kitchen | 456 | 189.1-2009 | ClimateZone 4-8 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 13.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | 220.5 | 0.1 | 0.2 | 0.7 | PrimarySchool Kitchen Gas | 13.13 | 0.25 | 0.3 | 0.2 | PrimarySchool Kitchen Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool Kitchen Exhaust
CBECS_Before-1980_PrimarySchool_Kitchen | 305 | DOE Ref Pre-1980 | ClimateZone 1-8 | PrimarySchool | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 13.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.2232 | PrimarySchool Infil | 302.6 | 0.1 | 0.2 | 0.7 | PrimarySchool Kitchen Gas | 17.7 | 0.25 | 0.3 | 0.2 | PrimarySchool Kitchen Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool Kitchen Exhaust
|  | 90.1-2007 | ClimateZone 1-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0446 | QuickServiceRestaurant Infil Half On | 298.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant Gas Equip | 20.4 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp Kitchen | QuickServiceRestaurant ClgSetp Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant Kitchen Exhaust
CBECS_1980-2004_QuickServiceRestaurant_Kitchen | 303 | DOE Ref 1980-2004 | ClimateZone 1-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | [6 empty] | 1.55 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.2232 | QuickServiceRestaurant Infil Half On | 409.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant Gas Equip | 28 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp Kitchen | QuickServiceRestaurant ClgSetp Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant Kitchen Exhaust
ASHRAE_90.1-2004_QuickServiceRestaurant_Kitchen | 141 | DOE Ref 2004 | ClimateZone 1-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0595 | QuickServiceRestaurant Infil Half On | 409.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant Gas Equip | 28 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp Kitchen | QuickServiceRestaurant ClgSetp Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant Kitchen Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_QuickServiceRestaurant_Kitchen | 64 | 189.1-2009 | ClimateZone 1-3 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0595 | QuickServiceRestaurant Infil Half On | 298.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant Gas Equip | 20.4 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp Kitchen | QuickServiceRestaurant ClgSetp Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant Kitchen Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_QuickServiceRestaurant_Kitchen | 187 | 189.1-2009 | ClimateZone 4-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0446 | QuickServiceRestaurant Infil Half On | 298.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant Gas Equip | 20.4 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp Kitchen | QuickServiceRestaurant ClgSetp Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant Kitchen Exhaust
CBECS_Before-1980_QuickServiceRestaurant_Kitchen | 153 | DOE Ref Pre-1980 | ClimateZone 1-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.2232 | QuickServiceRestaurant Infil Half On | 409.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant Gas Equip | 28 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp Kitchen | QuickServiceRestaurant ClgSetp Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant Kitchen Exhaust
|  | 90.1-2007 | ClimateZone 1-8 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 15.48 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | 258.6 | 0.1 | 0.2 | 0.7 | SecondarySchool Kitchen Gas | 15.05 | 0.25 | 0.3 | 0.2 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool Kitchen Exhaust
CBECS_1980-2004_SecondarySchool_Kitchen | 439 | DOE Ref 1980-2004 | ClimateZone 1-8 | SecondarySchool | Kitchen | 78_222_133 | [6 empty] | 1.56 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 15.48 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.2232 | SecondarySchool Infil | 354.9 | 0.1 | 0.2 | 0.7 | SecondarySchool Kitchen Gas | 20.65 | 0.25 | 0.3 | 0.2 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool Kitchen Exhaust
ASHRAE_90.1-2004_SecondarySchool_Kitchen | 385 | DOE Ref 2004 | ClimateZone 1-8 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 15.48 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | 354.9 | 0.1 | 0.2 | 0.7 | SecondarySchool Kitchen Gas | 20.65 | 0.25 | 0.3 | 0.2 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool Kitchen Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Kitchen | 349 | 189.1-2009 | ClimateZone 1-3 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 15.48 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | 258.6 | 0.1 | 0.2 | 0.7 | SecondarySchool Kitchen Gas | 15.05 | 0.25 | 0.3 | 0.2 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool Kitchen Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Kitchen | 531 | 189.1-2009 | ClimateZone 4-8 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 15.48 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | 258.6 | 0.1 | 0.2 | 0.7 | SecondarySchool Kitchen Gas | 15.05 | 0.25 | 0.3 | 0.2 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool Kitchen Exhaust
CBECS_Before-1980_SecondarySchool_Kitchen | 278 | DOE Ref Pre-1980 | ClimateZone 1-8 | SecondarySchool | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 15.48 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.2232 | SecondarySchool Infil | 354.9 | 0.1 | 0.2 | 0.7 | SecondarySchool Kitchen Gas | 20.65 | 0.25 | 0.3 | 0.2 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool Kitchen Exhaust
|  | 90.1-2010 | ClimateZone 1-8 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0446 | FullServiceRestaurant Infil Half On | 276.72 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant Gas Equip | 25.5 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp Kitchen | FullServiceRestaurant ClgSetp Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant Kitchen Exhaust
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | 70.46 | 0.1 | 0.2 | 0.7 | Hospital Kitchen Gas | 5.47 | 0.2 | 0.5 | 0.1 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital SWH Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital Kitchen Exhaust
|  | 90.1-2010 | ClimateZone 1-8 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | 373.8 | 0.1 | 0.2 | 0.7 | LargeHotel Kitchen Gas | 24.16 | 0.2 | 0.5 | 0.1 | LargeHotel Kitchen Equip | LargeHotel Kitchen HtgSetp | LargeHotel Kitchen ClgSetp | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel SWH Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel Kitchen Exhaust
|  | 90.1-2010 | ClimateZone 1-8 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 13.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | 220.5 | 0.1 | 0.2 | 0.7 | PrimarySchool Kitchen Gas | 13.13 | 0.25 | 0.3 | 0.2 | PrimarySchool Kitchen Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool Kitchen Exhaust
|  | 90.1-2010 | ClimateZone 1-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0446 | QuickServiceRestaurant Infil Half On | 298.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant Gas Equip | 20.4 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp Kitchen | QuickServiceRestaurant ClgSetp Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant Kitchen Exhaust
|  | 90.1-2010 | ClimateZone 1-8 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 15.48 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | 258.6 | 0.1 | 0.2 | 0.7 | SecondarySchool Kitchen Gas | 15.05 | 0.25 | 0.3 | 0.2 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool Kitchen Exhaust
CBECS_1980-2004_Hospital_Lab | 154 | DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | Lab | 204_120_230 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital SWH
ASHRAE_90.1-2004_Hospital_Lab | 475 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | Lab | 204_120_230 | ASHRAE 90.1-2004 | Laboratory | General | ASHRAE 90.1-2004LaboratoryGeneral |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_Lab | 85 | 189.1-2009 | ClimateZone 1-3 | Hospital | Lab | 204_120_230 | ASHRAE 189.1-2009 | Laboratory | General | ASHRAE 189.1-2009LaboratoryGeneral |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 3.22 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_Lab | 22 | 189.1-2009 | ClimateZone 4-8 | Hospital | Lab | 204_120_230 | ASHRAE 189.1-2009 | Laboratory | General | ASHRAE 189.1-2009LaboratoryGeneral |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 3.22 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital SWH
CBECS_Before-1980_Hospital_Lab | 482 | DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | Lab | 204_120_230 | [6 empty] | 1.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital SWH
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | Lab | 204_120_230 | ASHRAE 90.1-2007 | Laboratory | General | ASHRAE 90.1-2007LaboratoryGeneral |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2004 | Educational Facilities | Science laboratories | ASHRAE 62.1-2004Educational FacilitiesScience laboratories | 0.18 | 10 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 3.22 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital SWH
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | Lab | 204_120_230 | ASHRAE 90.1-2010 | Laboratory | For Medical/Industrial/Research | ASHRAE 90.1-2010LaboratoryFor Medical/Industrial/Research |  |  | 1.81 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2007 | Educational Facilities | Science laboratories | ASHRAE 62.1-2007Educational FacilitiesScience laboratories | 0.18 | 10 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 3.22 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital SWH
CBECS_1980-2004_LargeHotel_Laundry | 67 | DOE Ref 1980-2004 | ClimateZone 1-8 | LargeHotel | Laundry | 120_149_230 | [6 empty] | 1.14 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 4 | LargeHotel Bldg Occ | LargeHotel Activity | 0.2232 | LargeHotel Infil Quarter On | 170 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Gas | 5.73 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Equip | LargeHotel HtgSetp | LargeHotel ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel SWH Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel Laundry Exhaust_Always On
ASHRAE_90.1-2004_LargeHotel_Laundry | 288 | DOE Ref 2004 | ClimateZone 1-8 | LargeHotel | Laundry | 120_149_230 | ASHRAE 90.1-2004 | Hospital | Laundry-Washing | ASHRAE 90.1-2004HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 4 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | 170 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Gas | 5.73 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Equip | LargeHotel HtgSetp | LargeHotel ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel SWH Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel Laundry Exhaust_Always On
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Laundry | 203 | 189.1-2009 | ClimateZone 1-3 | LargeHotel | Laundry | 120_149_230 | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | ASHRAE 189.1-2009HospitalLaundry-Washing |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 4 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | 123.8 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Gas | 2.93 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Equip | LargeHotel HtgSetp | LargeHotel ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel SWH Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel Laundry Exhaust_Always On
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Laundry | 252 | 189.1-2009 | ClimateZone 4-8 | LargeHotel | Laundry | 120_149_230 | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | ASHRAE 189.1-2009HospitalLaundry-Washing |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 4 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | 123.8 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Gas | 2.93 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Equip | LargeHotel HtgSetp | LargeHotel ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel SWH Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel Laundry Exhaust_Always On
CBECS_Before-1980_LargeHotel_Laundry | 78 | DOE Ref Pre-1980 | ClimateZone 1-8 | LargeHotel | Laundry | 120_149_230 | [6 empty] | 0.7 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 4 | LargeHotel Bldg Occ | LargeHotel Activity | 0.2232 | LargeHotel Infil Quarter On | 170 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Gas | 5.73 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Equip | LargeHotel HtgSetp | LargeHotel ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel SWH Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel Laundry Exhaust_Always On
|  | 90.1-2007 | ClimateZone 1-8 | LargeHotel | Laundry | 120_149_230 | ASHRAE 90.1-2007 | Hospital | Laundry-Washing | ASHRAE 90.1-2007HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2004 | Retail | Coinoperated laundries | ASHRAE 62.1-2004RetailCoinoperated laundries | 0.06 | 7.5 | 0 | 4 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | 123.8 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Gas | 2.93 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Equip | LargeHotel HtgSetp | LargeHotel ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel SWH Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel Laundry Exhaust_Always On
|  | 90.1-2007 | ClimateZone 1-8 | SmallHotel | Laundry | 120_149_230 | ASHRAE 90.1-2007 | Hospital | Laundry-Washing | ASHRAE 90.1-2007HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | SmallHotel Laundry Light | ASHRAE 62.1-2004 | Retail | Coinoperated laundries | ASHRAE 62.1-2004RetailCoinoperated laundries | 0.06 | 7.5 | 0 | 10 | SmallHotel Laundry Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | 42.6 |  |  |  | SmallHotel Laundry Gas | 1.04 | 0 | 0.5 | 0 | SmallHotel Laundry Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel SWH Laundry
CBECS_1980-2004_SmallHotel_Laundry | 132 | DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | Laundry | 120_149_230 | [6 empty] | 1.04 |  |  | 0 | 0.7 | 0.2 | SmallHotel Laundry Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 10 | SmallHotel Laundry Occ | SmallHotel Activity | 0.2232 | SmallHotel Infil Half On | 58.4 |  |  |  | SmallHotel Laundry Gas | 2.03 | 0 | 0.5 | 0 | SmallHotel Laundry Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel SWH Laundry
ASHRAE_90.1-2004_SmallHotel_Laundry | 489 | DOE Ref 2004 | ClimateZone 1-8 | SmallHotel | Laundry | 120_149_230 | ASHRAE 90.1-2004 | Hospital | Laundry-Washing | ASHRAE 90.1-2004HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | SmallHotel Laundry Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 10 | SmallHotel Laundry Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | 58.4 |  |  |  | SmallHotel Laundry Gas | 2.03 | 0 | 0.5 | 0 | SmallHotel Laundry Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel SWH Laundry
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Laundry | 340 | 189.1-2009 | ClimateZone 1-3 | SmallHotel | Laundry | 120_149_230 | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | ASHRAE 189.1-2009HospitalLaundry-Washing |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | SmallHotel Laundry Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 10 | SmallHotel Laundry Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | 42.6 |  |  |  | SmallHotel Laundry Gas | 1.04 | 0 | 0.5 | 0 | SmallHotel Laundry Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel SWH Laundry
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Laundry | 312 | 189.1-2009 | ClimateZone 4-8 | SmallHotel | Laundry | 120_149_230 | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | ASHRAE 189.1-2009HospitalLaundry-Washing |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | SmallHotel Laundry Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 10 | SmallHotel Laundry Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | 42.6 |  |  |  | SmallHotel Laundry Gas | 1.04 | 0 | 0.5 | 0 | SmallHotel Laundry Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel SWH Laundry
CBECS_Before-1980_SmallHotel_Laundry | 427 | DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | Laundry | 120_149_230 | [6 empty] | 1.04 |  |  | 0 | 0.7 | 0.2 | SmallHotel Laundry Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 10 | SmallHotel Laundry Occ | SmallHotel Activity | 0.2232 | SmallHotel Infil Half On | 58.4 |  |  |  | SmallHotel Laundry Gas | 2.03 | 0 | 0.5 | 0 | SmallHotel Laundry Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel SWH Laundry
|  | 90.1-2010 | ClimateZone 1-8 | LargeHotel | Laundry | 120_149_230 | ASHRAE 90.1-2010 | Hospital | Laundry-Washing | ASHRAE 90.1-2010HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | ASHRAE 62.1-2007RetailCoinoperated laundries | 0.06 | 7.5 | 0 | 4 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | 123.8 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Gas | 2.93 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Equip | LargeHotel HtgSetp | LargeHotel ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel SWH Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel Laundry Exhaust_Always On
|  | 90.1-2010 | ClimateZone 1-8 | SmallHotel | Laundry | 120_149_230 | ASHRAE 90.1-2010 | Hospital | Laundry-Washing | ASHRAE 90.1-2010HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | SmallHotel Laundry Light | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | ASHRAE 62.1-2007RetailCoinoperated laundries | 0.06 | 7.5 | 0 | 10 | SmallHotel Laundry Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | 42.6 |  |  |  | SmallHotel Laundry Gas | 1.04 | 0 | 0.5 | 0 | SmallHotel Laundry Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel SWH Laundry
|  | 90.1-2007 | ClimateZone 1-8 | PrimarySchool | Library | 230_196_120 | ASHRAE 90.1-2007 | Library | Reading Area | ASHRAE 90.1-2007LibraryReading Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2004 | Educational Facilities | Media center | ASHRAE 62.1-2004Educational FacilitiesMedia center | 0.12 | 10 | 0 | 21.36 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
CBECS_1980-2004_PrimarySchool_Library | 348 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Library; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_196_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.11; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Libraries; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationLibraries; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 21.36; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.39; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Library | 28 | DOE Ref 2004 | ClimateZone 1-8 | PrimarySchool | Library | 230_196_120 | ASHRAE 90.1-2004 | Library | Reading Area | ASHRAE 90.1-2004LibraryReading Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 15 | 0 | 21.36 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | 0 |  |  |  |  | 1.39 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Library | 552 | 189.1-2009 | ClimateZone 1-3 | PrimarySchool | Library | 230_196_120 | ASHRAE 189.1-2009 | Library | Reading Area | ASHRAE 189.1-2009LibraryReading Area |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 15 | 0 | 21.36 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Library | 361 | 189.1-2009 | ClimateZone 4-8 | PrimarySchool | Library | 230_196_120 | ASHRAE 189.1-2009 | Library | Reading Area | ASHRAE 189.1-2009LibraryReading Area |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 15 | 0 | 21.36 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
CBECS_Before-1980_PrimarySchool_Library | 190 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Library; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_196_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Libraries; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationLibraries; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 21.36; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.39; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SecondarySchool | Library | 230_196_120 | ASHRAE 90.1-2007 | Library | Reading Area | ASHRAE 90.1-2007LibraryReading Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2004 | Educational Facilities | Media center | ASHRAE 62.1-2004Educational FacilitiesMedia center | 0.12 | 10 | 0 | 21.34 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
CBECS_1980-2004_SecondarySchool_Library | 549 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Library; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_196_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.52; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Libraries; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationLibraries; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 21.34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.93; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp
ASHRAE_90.1-2004_SecondarySchool_Library | 159 | DOE Ref 2004 | ClimateZone 1-8 | SecondarySchool | Library | 230_196_120 | ASHRAE 90.1-2004 | Library | Reading Area | ASHRAE 90.1-2004LibraryReading Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 15 | 0 | 21.34 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.93 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Library | 513 | 189.1-2009 | ClimateZone 1-3 | SecondarySchool | Library | 230_196_120 | ASHRAE 189.1-2009 | Library | Reading Area | ASHRAE 189.1-2009LibraryReading Area |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 15 | 0 | 21.34 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Library | 256 | 189.1-2009 | ClimateZone 4-8 | SecondarySchool | Library | 230_196_120 | ASHRAE 189.1-2009 | Library | Reading Area | ASHRAE 189.1-2009LibraryReading Area |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 15 | 0 | 21.34 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
CBECS_Before-1980_SecondarySchool_Library | 414 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Library; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_196_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Libraries; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationLibraries; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 21.34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.93; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | PrimarySchool | Library | 230_196_120 | ASHRAE 90.1-2010 | Library | Reading Area | ASHRAE 90.1-2010LibraryReading Area |  |  | 0.93 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2007 | Educational Facilities | Media center | ASHRAE 62.1-2007Educational FacilitiesMedia center | 0.12 | 10 | 0 | 21.36 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SecondarySchool | Library | 230_196_120 | ASHRAE 90.1-2010 | Library | Reading Area | ASHRAE 90.1-2010LibraryReading Area |  |  | 0.93 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2007 | Educational Facilities | Media center | ASHRAE 62.1-2007Educational FacilitiesMedia center | 0.12 | 10 | 0 | 21.34 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
CBECS_1980-2004_Hospital_Lobby/Records | 33 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Lobby; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_162_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.46; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Lobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 7.14; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Bldg HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Bldg ClgSetp
ASHRAE_90.1-2004_Hospital_Lobby/Records | 228 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | Lobby | 31_162_169 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 0.1 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_Lobby/Records | 365 | 189.1-2009 | ClimateZone 1-3 | Hospital | Lobby | 31_162_169 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_Lobby/Records | 486 | 189.1-2009 | ClimateZone 4-8 | Hospital | Lobby | 31_162_169 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
CBECS_Before-1980_Hospital_Lobby/Records | 323 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Lobby; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_162_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.49; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Lobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 7.14; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Bldg HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Bldg ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | Lobby | 31_162_169 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2004Office BuildingsMain entry lobbies | 0.06 | 5 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
CBECS_1980-2004_LargeHotel_Lobby | 313 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: LargeHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Lobby; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.88; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: LargeHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Lobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 30; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: LargeHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: LargeHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: LargeHotel Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.75; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: LargeHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: LargeHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: LargeHotel ClgSetp
ASHRAE_90.1-2004_LargeHotel_Lobby | 171 | DOE Ref 2004 | ClimateZone 1-8 | LargeHotel | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | For Hotel | ASHRAE 90.1-2004LobbyFor Hotel |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 0.75 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Lobby | 164 | 189.1-2009 | ClimateZone 1-3 | LargeHotel | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | For Hotel | ASHRAE 189.1-2009LobbyFor Hotel |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 0.38 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Lobby | 39 | 189.1-2009 | ClimateZone 4-8 | LargeHotel | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | For Hotel | ASHRAE 189.1-2009LobbyFor Hotel |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.38 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
CBECS_Before-1980_LargeHotel_Lobby | 298 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: LargeHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Lobby; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.45; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: LargeHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Lobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 30; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: LargeHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: LargeHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: LargeHotel Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.75; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: LargeHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: LargeHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: LargeHotel ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | LargeHotel | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | For Hotel | ASHRAE 90.1-2007LobbyFor Hotel |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 | 0 | 30 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.38 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Lobby | 230_157_120 | [6 empty] | 2.04 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 10 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 1-3 | Office | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 10 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 4-8 | Office | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 10 | Office Misc Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral |  |  | 1.3 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 10 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Lobby | 230_157_120 | [6 empty] | 2.47 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 10 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Office | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral |  |  | 1.3 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2004Office BuildingsMain entry lobbies | 0.06 | 5 | 0 | 10 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
CBECS_1980-2004_Outpatient_Lobby | 114 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Lobby; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Lobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 27.87; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_Lobby | 289 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 27.87 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Lobby | 446 | 189.1-2009 | ClimateZone 1-3 | Outpatient | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 27.87 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Lobby | 194 | 189.1-2009 | ClimateZone 4-8 | Outpatient | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 27.87 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_Lobby | 277 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Lobby; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Lobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 27.87; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2004Office BuildingsMain entry lobbies | 0.06 | 5 | 0 | 27.87 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
CBECS_1980-2004_PrimarySchool_Lobby | 391 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Lobby; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.14; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationCorridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Lobby | 72 | DOE Ref 2004 | ClimateZone 1-8 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Lobby | 416 | 189.1-2009 | ClimateZone 1-3 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Lobby | 364 | 189.1-2009 | ClimateZone 4-8 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
CBECS_Before-1980_PrimarySchool_Lobby | 295 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Lobby; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.32; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationCorridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
CBECS_1980-2004_SecondarySchool_Lobby | 497 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Lobby; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.12; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationCorridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp
ASHRAE_90.1-2004_SecondarySchool_Lobby | 58 | DOE Ref 2004 | ClimateZone 1-8 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Lobby | 505 | 189.1-2009 | ClimateZone 1-3 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Lobby | 332 | 189.1-2009 | ClimateZone 4-8 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
CBECS_Before-1980_SecondarySchool_Lobby | 241 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Lobby; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.32; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Education; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999EducationCorridors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | Lobby | 31_162_169 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2007Office BuildingsMain entry lobbies | 0.06 | 5 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | LargeHotel | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | For Hotel | ASHRAE 90.1-2010LobbyFor Hotel |  |  | 1.06 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 | 0 | 30 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.38 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Office | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2007Office BuildingsMain entry lobbies | 0.06 | 5 | 0 | 10 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2007Office BuildingsMain entry lobbies | 0.06 | 5 | 0 | 27.87 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
CBECS_1980-2004_Outpatient_LockerRoom | 487 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: LockerRoom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_169_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: GGHC v2.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Health Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Lockers; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: GGHC v2.2Health CareLockers; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 13.94; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_LockerRoom | 304 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 90.1-2004 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2004Dressing/Locker/Fitting RoomGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_LockerRoom | 18 | 189.1-2009 | ClimateZone 1-3 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_LockerRoom | 115 | 189.1-2009 | ClimateZone 4-8 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_LockerRoom | 235 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: LockerRoom; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_169_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: GGHC v2.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Health Care; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Lockers; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: GGHC v2.2Health CareLockers; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 13.94; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 90.1-2007 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2007Dressing/Locker/Fitting RoomGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 90.1-2010 | Locker Room | General | ASHRAE 90.1-2010Locker RoomGeneral |  |  | 0.75 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_1980-2004_Outpatient_Lounge | 499 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Lounge; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Lobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 13.94; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_Lounge | 165 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | Lounge | 230_157_120 | ASHRAE 90.1-2004 | Lounge/Recreation | For Hospital | ASHRAE 90.1-2004Lounge/RecreationFor Hospital |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Lounge | 468 | 189.1-2009 | ClimateZone 1-3 | Outpatient | Lounge | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | For Hospital | ASHRAE 189.1-2009Lounge/RecreationFor Hospital |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Lounge | 441 | 189.1-2009 | ClimateZone 4-8 | Outpatient | Lounge | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | For Hospital | ASHRAE 189.1-2009Lounge/RecreationFor Hospital |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_Lounge | 319 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Lounge; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Lobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 13.94; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | Lounge | 230_157_120 | ASHRAE 90.1-2007 | Lounge/Recreation | For Hospital | ASHRAE 90.1-2007Lounge/RecreationFor Hospital |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | Lounge | 230_157_120 | ASHRAE 90.1-2010 | Lounge/Recreation | For Hospital | ASHRAE 90.1-2010Lounge/RecreationFor Hospital |  |  | 1.07 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_1980-2004_LargeHotel_Mechanical | 224 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: LargeHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Mechanical; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 41_31_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: LargeHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: LargeHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: LargeHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: LargeHotel Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: LargeHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: LargeHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: LargeHotel ClgSetp
ASHRAE_90.1-2004_LargeHotel_Mechanical | 14 | DOE Ref 2004 | ClimateZone 1-8 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 0.5 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Mechanical | 412 | 189.1-2009 | ClimateZone 1-3 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Mechanical | 551 | 189.1-2009 | ClimateZone 4-8 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
CBECS_Before-1980_LargeHotel_Mechanical | 255 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: LargeHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Mechanical; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 41_31_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.6; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: LargeHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: LargeHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: LargeHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: LargeHotel Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: LargeHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: LargeHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: LargeHotel ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
CBECS_1980-2004_PrimarySchool_Mechanical | 395 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Mechanical; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 41_31_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.77; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0.93; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool BathCorrMechKitchen HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool BathCorrMechKitchen ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Mechanical | 357 | DOE Ref 2004 | ClimateZone 1-8 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Mechanical | 525 | 189.1-2009 | ClimateZone 1-3 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Mechanical | 294 | 189.1-2009 | ClimateZone 4-8 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
CBECS_Before-1980_PrimarySchool_Mechanical | 379 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Mechanical; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 41_31_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.6; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0.93; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool BathCorrMechKitchen HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool BathCorrMechKitchen ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0.93 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
CBECS_1980-2004_SecondarySchool_Mechanical | 326 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Mechanical; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 41_31_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.75; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0.93; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp BathCorrMechKitchen; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp BathCorrMechKitchen
ASHRAE_90.1-2004_SecondarySchool_Mechanical | 494 | DOE Ref 2004 | ClimateZone 1-8 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Mechanical | 98 | 189.1-2009 | ClimateZone 1-3 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | SecondarySchool BathCorrMechKitchen HtgSetp |  | #VALUE!
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Mechanical | 263 | 189.1-2009 | ClimateZone 4-8 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
CBECS_Before-1980_SecondarySchool_Mechanical | 232 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Mechanical; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 41_31_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.6; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0.93; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp BathCorrMechKitchen; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp BathCorrMechKitchen
|  | 90.1-2007 | ClimateZone 1-8 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_1980-2004_SmallHotel_Mechanical | 309 | DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | Mechanical | 41_31_169 | [6 empty] | 0.96 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.2232 | SmallHotel Infil Half On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_90.1-2004_SmallHotel_Mechanical | 432 | DOE Ref 2004 | ClimateZone 1-8 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Mechanical | 394 | 189.1-2009 | ClimateZone 1-3 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Mechanical | 404 | 189.1-2009 | ClimateZone 4-8 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_Before-1980_SmallHotel_Mechanical | 316 | DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | Mechanical | 41_31_169 | [6 empty] | 0.96 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.2232 | SmallHotel Infil Half On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral |  |  | 0.95 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral |  |  | 0.95 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral |  |  | 0.95 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0.93 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
|  | 90.1-2010 | ClimateZone 1-8 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral |  |  | 0.95 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_1980-2004_Outpatient_MedGas | 249 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: MedGas; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 204_120_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Storage rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_MedGas | 13 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | MedGas | 204_120_230 | ASHRAE 90.1-2004 | Active Storage | For Hospital | ASHRAE 90.1-2004Active StorageFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_MedGas | 144 | 189.1-2009 | ClimateZone 1-3 | Outpatient | MedGas | 204_120_230 | ASHRAE 189.1-2009 | Active Storage | For Hospital | ASHRAE 189.1-2009Active StorageFor Hospital |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_MedGas | 550 | 189.1-2009 | ClimateZone 4-8 | Outpatient | MedGas | 204_120_230 | ASHRAE 189.1-2009 | Active Storage | For Hospital | ASHRAE 189.1-2009Active StorageFor Hospital |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_MedGas | 157 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: MedGas; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 204_120_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Storage rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | MedGas | 204_120_230 | ASHRAE 90.1-2007 | Active Storage | For Hospital | ASHRAE 90.1-2007Active StorageFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | MedGas | 204_120_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SmallHotel | Meeting | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | SmallHotel Meeting Light | ASHRAE 62.1-2004 | General | Conference/meeting | ASHRAE 62.1-2004GeneralConference/meeting | 0.06 | 5 | 0 | 50 | SmallHotel Meeting Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel Meeting Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_1980-2004_SmallHotel_Meeting | 40 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Meeting; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_196_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.13; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel Meeting Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Conference rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 50; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel Meeting Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel Meeting Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
ASHRAE_90.1-2004_SmallHotel_Meeting | 198 | DOE Ref 2004 | ClimateZone 1-8 | SmallHotel | Meeting | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | SmallHotel Meeting Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 50 | SmallHotel Meeting Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 1.2 | 0 | 0.5 | 0 | SmallHotel Meeting Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Meeting | 356 | 189.1-2009 | ClimateZone 1-3 | SmallHotel | Meeting | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | SmallHotel Meeting Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 50 | SmallHotel Meeting Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel Meeting Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Meeting | 406 | 189.1-2009 | ClimateZone 4-8 | SmallHotel | Meeting | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | SmallHotel Meeting Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 50 | SmallHotel Meeting Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel Meeting Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_Before-1980_SmallHotel_Meeting | 267 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Meeting; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_196_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.13; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel Meeting Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Conference rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 50; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel Meeting Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel Meeting Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SmallHotel | Meeting | 230_196_120 | ASHRAE 90.1-2010 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2010Conference/Meeting/MultipurposeGeneral |  |  | 1.23 |  |  | 0 | 0.7 | 0.2 | SmallHotel Meeting Light | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 | 0 | 50 | SmallHotel Meeting Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel Meeting Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_1980-2004_Outpatient_MRI | 518 | DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | MRI | 169_31_159 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 53.06 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
ASHRAE_90.1-2004_Outpatient_MRI | 168 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | MRI | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 53.06 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_MRI | 354 | 189.1-2009 | ClimateZone 1-3 | Outpatient | MRI | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 38.63 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_MRI | 138 | 189.1-2009 | ClimateZone 4-8 | Outpatient | MRI | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 38.63 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
CBECS_Before-1980_Outpatient_MRI | 207 | DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | MRI | 169_31_159 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 53.06 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | MRI | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 38.63 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | MRI | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Radiology/Imaging | ASHRAE 90.1-2010HospitalRadiology/Imaging |  |  | 1.32 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 38.63 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
CBECS_1980-2004_Outpatient_MRI_Control | 481 | DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | MRI_Control | 136_78_222 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
ASHRAE_90.1-2004_Outpatient_MRI_Control | 541 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_MRI_Control | 553 | 189.1-2009 | ClimateZone 1-3 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_MRI_Control | 214 | 189.1-2009 | ClimateZone 4-8 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
CBECS_Before-1980_Outpatient_MRI_Control | 189 | DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | MRI_Control | 136_78_222 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 90.1-2010 | Hospital | Radiology/Imaging | ASHRAE 90.1-2010HospitalRadiology/Imaging |  |  | 1.32 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
CBECS_1980-2004_Outpatient_NurseStation | 515 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: NurseStation; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_162_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 18.58; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_NurseStation | 127 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | NurseStation | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_NurseStation | 77 | 189.1-2009 | ClimateZone 1-3 | Outpatient | NurseStation | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_NurseStation | 161 | 189.1-2009 | ClimateZone 4-8 | Outpatient | NurseStation | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_NurseStation | 125 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: NurseStation; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_162_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 18.58; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | NurseStation | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | NurseStation | 31_162_169 | ASHRAE 90.1-2010 | Hospital | Nurse Station | ASHRAE 90.1-2010HospitalNurse Station |  |  | 0.87 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_1980-2004_Hospital_NurseStn | 258 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: NurseStn; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_162_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.46; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Reception Areas; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesReception Areas; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 7.14; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.04; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Bldg HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Bldg ClgSetp
ASHRAE_90.1-2004_Hospital_NurseStn | 367 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | NurseStn | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 1.04 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_NurseStn | 244 | 189.1-2009 | ClimateZone 1-3 | Hospital | NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 0.76 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_NurseStn | 109 | 189.1-2009 | ClimateZone 4-8 | Hospital | NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0.76 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
CBECS_Before-1980_Hospital_NurseStn | 183 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: NurseStn; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_162_169; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.53; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Reception Areas; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesReception Areas; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 7.14; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.04; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Bldg HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Bldg ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | NurseStn | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0.76 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | NurseStn | 31_162_169 | ASHRAE 90.1-2010 | Hospital | Nurse Station | ASHRAE 90.1-2010HospitalNurse Station |  |  | 0.87 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0.76 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
CBECS_1980-2004_Hospital_Office | 108 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.4; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 6.99; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Bldg HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Bldg ClgSetp
ASHRAE_90.1-2004_Hospital_Office | 239 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 6.99 | Hospital Bldg Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_Office | 48 | 189.1-2009 | ClimateZone 1-3 | Hospital | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 6.99 | Hospital Bldg Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_Office | 318 | 189.1-2009 | ClimateZone 4-8 | Hospital | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 6.99 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
CBECS_Before-1980_Hospital_Office | 152 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 6.99; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Bldg HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Bldg ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 6.99 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
CBECS_1980-2004_MidriseApartment_Office | 496 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: MidriseApartment; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.04; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: MidriseApartment Office Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 2.11; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: MidriseApartment Office Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: MidriseApartment Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: MidriseApartment Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: MidriseApartment Office Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: MidriseApartment Office HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: MidriseApartment Office ClgSetp
ASHRAE_90.1-2004_MidriseApartment_Office | 345 | DOE Ref 2004 | ClimateZone 1-8 | MidriseApartment | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 2.11 | MidriseApartment Office Occ | MidriseApartment Activity | 0.0595 | MidriseApartment Infil | [5 empty] | 1.2 | 0 | 0.5 | 0 | MidriseApartment Office Equip | MidriseApartment Office HtgSetp | MidriseApartment Office ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_MidriseApartment_Office | 308 | 189.1-2009 | ClimateZone 1-3 | MidriseApartment | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 2.11 | MidriseApartment Office Occ | MidriseApartment Activity | 0.0595 | MidriseApartment Infil | [5 empty] | 0.87 | 0 | 0.5 | 0 | MidriseApartment Office Equip | MidriseApartment Office HtgSetp | MidriseApartment Office ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_MidriseApartment_Office | 270 | 189.1-2009 | ClimateZone 4-8 | MidriseApartment | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 2.11 | MidriseApartment Office Occ | MidriseApartment Activity | 0.0446 | MidriseApartment Infil | [5 empty] | 0.87 | 0 | 0.5 | 0 | MidriseApartment Office Equip | MidriseApartment Office HtgSetp | MidriseApartment Office ClgSetp
CBECS_Before-1980_MidriseApartment_Office | 341 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: MidriseApartment; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.04; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: MidriseApartment Office Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 2.11; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: MidriseApartment Office Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: MidriseApartment Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: MidriseApartment Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: MidriseApartment Office Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: MidriseApartment Office HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: MidriseApartment Office ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | MidriseApartment | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Office Light | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 2.11 | MidriseApartment Office Occ | MidriseApartment Activity | 0.0446 | MidriseApartment Infil | [5 empty] | 0.87 | 0 | 0.5 | 0 | MidriseApartment Office Equip | MidriseApartment Office HtgSetp | MidriseApartment Office ClgSetp
CBECS_1980-2004_Outpatient_Office | 139 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 4.65; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_Office | 184 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Office | 43 | 189.1-2009 | ClimateZone 1-3 | Outpatient | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Office | 320 | 189.1-2009 | ClimateZone 4-8 | Outpatient | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_Office | 221 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 4.65; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_1980-2004_PrimarySchool_Office | 474 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.89; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 4.65; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Office | 342 | DOE Ref 2004 | ClimateZone 1-8 | PrimarySchool | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 1 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Office | 524 | 189.1-2009 | ClimateZone 1-3 | PrimarySchool | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Office | 408 | 189.1-2009 | ClimateZone 4-8 | PrimarySchool | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
CBECS_Before-1980_PrimarySchool_Office | 8 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: PrimarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: PrimarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 4.65; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: PrimarySchool Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: PrimarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: PrimarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: PrimarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: PrimarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: PrimarySchool ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | PrimarySchool | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 4.65 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SecondarySchool | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 4.65 | SecondarySchool Office Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
CBECS_1980-2004_SecondarySchool_Office | 443 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.87; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 4.65; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Office Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp
ASHRAE_90.1-2004_SecondarySchool_Office | 521 | DOE Ref 2004 | ClimateZone 1-8 | SecondarySchool | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | SecondarySchool Office Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 1 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Office | 334 | 189.1-2009 | ClimateZone 1-3 | SecondarySchool | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | SecondarySchool Office Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Office | 469 | 189.1-2009 | ClimateZone 4-8 | SecondarySchool | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | SecondarySchool Office Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
CBECS_Before-1980_SecondarySchool_Office | 336 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SecondarySchool; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SecondarySchool Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 4.65; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SecondarySchool Office Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SecondarySchool Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SecondarySchool Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SecondarySchool Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SecondarySchool HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SecondarySchool ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SmallHotel | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | SmallHotel Office Light | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 7.14 | SmallHotel Office Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel Office Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_1980-2004_SmallHotel_Office | 21 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.01; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel Office Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 7.14; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel Office Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel Office Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
ASHRAE_90.1-2004_SmallHotel_Office | 93 | DOE Ref 2004 | ClimateZone 1-8 | SmallHotel | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | SmallHotel Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 7.14 | SmallHotel Office Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 1.2 | 0 | 0.5 | 0 | SmallHotel Office Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Office | 381 | 189.1-2009 | ClimateZone 1-3 | SmallHotel | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SmallHotel Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 7.14 | SmallHotel Office Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel Office Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Office | 491 | 189.1-2009 | ClimateZone 4-8 | SmallHotel | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SmallHotel Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 7.14 | SmallHotel Office Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel Office Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_Before-1980_SmallHotel_Office | 186 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.01; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel Office Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 7.14; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel Office Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel Office Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SuperMarket | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 5 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
CBECS_1980-2004_SuperMarket_Office | 23 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SuperMarket; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.98; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SuperMarket Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SuperMarket Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SuperMarket Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SuperMarket Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.75; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SuperMarket Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SuperMarket HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SuperMarket ClgSetp
ASHRAE_90.1-2004_SuperMarket_Office | 421 | DOE Ref 2004 | ClimateZone 1-8 | SuperMarket | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 | SuperMarket Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SuperMarket_Office | 179 | 189.1-2009 | ClimateZone 1-3 | SuperMarket | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SuperMarket_Office | 539 | 189.1-2009 | ClimateZone 4-8 | SuperMarket | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
CBECS_Before-1980_SuperMarket_Office | 292 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SuperMarket; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SuperMarket Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SuperMarket Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SuperMarket Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SuperMarket Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.75; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SuperMarket Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SuperMarket HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SuperMarket ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Warehouse | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 1.96 | Warehouse Bldg Occ | Warehouse Activity | 0.0446 | Always On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp | Warehouse ClgSetp
CBECS_1980-2004_Warehouse_Office | 460 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Warehouse; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.02; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Warehouse Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 1.96; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Warehouse Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Warehouse Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Always On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.75; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Warehouse Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Warehouse HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Warehouse ClgSetp
ASHRAE_90.1-2004_Warehouse_Office | 113 | DOE Ref 2004 | ClimateZone 1-8 | Warehouse | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 1.96 | Warehouse Bldg Occ | Warehouse Activity | 0.0595 | Always On | [5 empty] | 0.75 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp | Warehouse ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Warehouse_Office | 315 | 189.1-2009 | ClimateZone 1-3 | Warehouse | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 1.96 | Warehouse Bldg Occ | Warehouse Activity | 0.0595 | Always On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp | Warehouse ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Warehouse_Office | 196 | 189.1-2009 | ClimateZone 4-8 | Warehouse | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 1.96 | Warehouse Bldg Occ | Warehouse Activity | 0.0446 | Always On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp | Warehouse ClgSetp
CBECS_Before-1980_Warehouse_Office | 95 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Warehouse; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Office; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_230_199; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.9; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Warehouse Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Offices; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Office Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999OfficesOffice Space; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 20; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 1.96; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Warehouse Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Warehouse Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Always On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.75; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Warehouse Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Warehouse HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Warehouse ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 6.99 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | MidriseApartment | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Office Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 2.11 | MidriseApartment Office Occ | MidriseApartment Activity | 0.0446 | MidriseApartment Infil | [5 empty] | 0.87 | 0 | 0.5 | 0 | MidriseApartment Office Equip | MidriseApartment Office HtgSetp | MidriseApartment Office ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | PrimarySchool | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 4.65 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SecondarySchool | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 4.65 | SecondarySchool Office Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SmallHotel | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.7 | 0.2 | SmallHotel Office Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 7.14 | SmallHotel Office Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel Office Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SuperMarket | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 5 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Warehouse | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 1.96 | Warehouse Bldg Occ | Warehouse Activity | 0.0446 | Always On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp | Warehouse ClgSetp
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | OpenOffice | 120_230_199 | [6 empty] | 1.73 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5.25 | Office Work Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.96 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 1-3 | Office | OpenOffice | 120_230_199 | ASHRAE 189.1-2009 | Office-Open Plan | General | ASHRAE 189.1-2009Office-Open PlanGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5.25 | Office Work Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.71 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 4-8 | Office | OpenOffice | 120_230_199 | ASHRAE 189.1-2009 | Office-Open Plan | General | ASHRAE 189.1-2009Office-Open PlanGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5.25 | Office Work Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0.71 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | OpenOffice | 120_230_199 | ASHRAE 90.1-2004 | Office-Open Plan | General | ASHRAE 90.1-2004Office-Open PlanGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5.25 | Office Work Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.96 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | OpenOffice | 120_230_199 | [6 empty] | 2.09 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5.25 | Office Work Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.96 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
C |  | 90.1-2007 | ClimateZone 1-8 | Office | OpenOffice | 120_230_199 | ASHRAE 90.1-2007 | Office-Open Plan | General | ASHRAE 90.1-2007Office-Open PlanGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 5.25 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0.71 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Office | OpenOffice | 120_230_199 | ASHRAE 90.1-2010 | Office-Open Plan | General | ASHRAE 90.1-2010Office-Open PlanGeneral |  |  | 0.98 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 5.25 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0.71 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
CBECS_1980-2004_Hospital_OR | 265 | DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | OR | 169_31_159 | [6 empty] | 9.75 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital Critical Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH
ASHRAE_90.1-2004_Hospital_OR | 97 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | OR | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Operating Room | ASHRAE 90.1-2004HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_OR | 327 | 189.1-2009 | ClimateZone 1-3 | Hospital | OR | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_OR | 26 | 189.1-2009 | ClimateZone 4-8 | Hospital | OR | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH
CBECS_Before-1980_Hospital_OR | 493 | DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | OR | 169_31_159 | [6 empty] | 10 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital Critical Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | OR | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Operating Room | ASHRAE 90.1-2007HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH
CBECS_1980-2004_Outpatient_OR | 458 | DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | OR | 169_31_159 | [6 empty] | 7 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | 23.9 | 0 | 0 | 0.5 | Outpatient Bldg Equip | 4 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient OR HtgSetp | Outpatient OR ClgSetp | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_90.1-2004_Outpatient_OR | 147 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | OR | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Operating Room | ASHRAE 90.1-2004HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | 23.9 | 0 | 0 | 0.5 | Outpatient Bldg Equip | 4 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient OR HtgSetp | Outpatient OR ClgSetp | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_OR | 311 | 189.1-2009 | ClimateZone 1-3 | Outpatient | OR | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | 17.4 | 0 | 0 | 0.5 | Outpatient Bldg Equip | 2.92 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient OR HtgSetp | Outpatient OR ClgSetp | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_OR | 346 | 189.1-2009 | ClimateZone 4-8 | Outpatient | OR | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | 17.4 | 0 | 0 | 0.5 | Outpatient Bldg Equip | 2.92 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient OR HtgSetp | Outpatient OR ClgSetp | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient SWH
CBECS_Before-1980_Outpatient_OR | 435 | DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | OR | 169_31_159 | [6 empty] | 7 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | 23.9 | 0 | 0 | 0.5 | Outpatient Bldg Equip | 4 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient OR HtgSetp | Outpatient OR ClgSetp | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient SWH
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | OR | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Operating Room | ASHRAE 90.1-2007HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | 17.4 | 0 | 0 | 0.5 | Outpatient Bldg Equip | 2.92 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient OR HtgSetp | Outpatient OR ClgSetp | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient SWH
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | OR | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Operating Room | ASHRAE 90.1-2010HospitalOperating Room |  |  | 1.89 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | OR | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Operating Room | ASHRAE 90.1-2010HospitalOperating Room |  |  | 1.89 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | 17.4 | 0 | 0 | 0.5 | Outpatient Bldg Equip | 2.92 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient OR HtgSetp | Outpatient OR ClgSetp | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient SWH
CBECS_1980-2004_Outpatient_PACU | 236 | DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | PACU | 169_31_159 | [6 empty] | 2.3 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_90.1-2004_Outpatient_PACU | 251 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | PACU | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Recovery | ASHRAE 90.1-2004HospitalRecovery |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_PACU | 247 | 189.1-2009 | ClimateZone 1-3 | Outpatient | PACU | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Recovery | ASHRAE 189.1-2009HospitalRecovery |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_PACU | 546 | 189.1-2009 | ClimateZone 4-8 | Outpatient | PACU | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Recovery | ASHRAE 189.1-2009HospitalRecovery |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH
CBECS_Before-1980_Outpatient_PACU | 42 | DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | PACU | 169_31_159 | [6 empty] | 2.3 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | PACU | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Recovery | ASHRAE 90.1-2007HospitalRecovery |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | PACU | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Recovery | ASHRAE 90.1-2010HospitalRecovery |  |  | 1.15 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH
CBECS_1980-2004_Hospital_PatCorridor | 324 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: PatCorridor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.36; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Critical Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Critical HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Critical ClgSetp
ASHRAE_90.1-2004_Hospital_PatCorridor | 512 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | PatCorridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | ASHRAE 90.1-2004Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_PatCorridor | 73 | 189.1-2009 | ClimateZone 1-3 | Hospital | PatCorridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_PatCorridor | 397 | 189.1-2009 | ClimateZone 4-8 | Hospital | PatCorridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp
CBECS_Before-1980_Hospital_PatCorridor | 529 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Hospital; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: PatCorridor; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 169_31_31; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.32; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Hospital Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Hospital Critical Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Hospital Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Hospital Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Hospital Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Hospital Critical HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Hospital Critical ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | PatCorridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | ASHRAE 90.1-2007Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | PatCorridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | For Hospital | ASHRAE 90.1-2010Corridor/TransitionFor Hospital |  |  | 0.89 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp
CBECS_1980-2004_Hospital_PatRoom | 286 | DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | PatRoom | 78_167_222 | [6 empty] | 2.19 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital SWH Extd
ASHRAE_90.1-2004_Hospital_PatRoom | 134 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | PatRoom | 78_167_222 | ASHRAE 90.1-2004 | Hospital | Patient Room | ASHRAE 90.1-2004HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital SWH Extd
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_PatRoom | 246 | 189.1-2009 | ClimateZone 1-3 | Hospital | PatRoom | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital SWH Extd
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_PatRoom | 103 | 189.1-2009 | ClimateZone 4-8 | Hospital | PatRoom | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital SWH Extd
CBECS_Before-1980_Hospital_PatRoom | 380 | DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | PatRoom | 78_167_222 | [6 empty] | 1.85 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital SWH Extd
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | PatRoom | 78_167_222 | ASHRAE 90.1-2007 | Hospital | Patient Room | ASHRAE 90.1-2007HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital SWH Extd
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | PatRoom | 78_167_222 | ASHRAE 90.1-2010 | Hospital | Patient Room | ASHRAE 90.1-2010HospitalPatient Room |  |  | 0.62 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital SWH Extd
CBECS_1980-2004_Outpatient_PhysicalTherapy | 15 | DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | PhysicalTherapy | 154_230_120 | [6 empty] | 1.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 1.5 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_90.1-2004_Outpatient_PhysicalTherapy | 80 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 90.1-2004 | Hospital | Physical Therapy | ASHRAE 90.1-2004HospitalPhysical Therapy |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1.5 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_PhysicalTherapy | 281 | 189.1-2009 | ClimateZone 1-3 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 189.1-2009 | Hospital | Physical Therapy | ASHRAE 189.1-2009HospitalPhysical Therapy |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1.09 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_PhysicalTherapy | 428 | 189.1-2009 | ClimateZone 4-8 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 189.1-2009 | Hospital | Physical Therapy | ASHRAE 189.1-2009HospitalPhysical Therapy |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.09 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient SWH
CBECS_Before-1980_Outpatient_PhysicalTherapy | 351 | DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | PhysicalTherapy | 154_230_120 | [6 empty] | 1.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 1.5 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient SWH
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 90.1-2007 | Hospital | Physical Therapy | ASHRAE 90.1-2007HospitalPhysical Therapy |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.09 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient SWH
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 90.1-2010 | Hospital | Physical Therapy | ASHRAE 90.1-2010HospitalPhysical Therapy |  |  | 0.91 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.09 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient SWH
CBECS_1980-2004_Hospital_PhysTherapy | 137 | DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | PhysTherapy | 154_230_120 | [6 empty] | 2.5 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital SWH
ASHRAE_90.1-2004_Hospital_PhysTherapy | 306 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 90.1-2004 | Hospital | Physical Therapy | ASHRAE 90.1-2004HospitalPhysical Therapy |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_PhysTherapy | 66 | 189.1-2009 | ClimateZone 1-3 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 189.1-2009 | Hospital | Physical Therapy | ASHRAE 189.1-2009HospitalPhysical Therapy |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_PhysTherapy | 38 | 189.1-2009 | ClimateZone 4-8 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 189.1-2009 | Hospital | Physical Therapy | ASHRAE 189.1-2009HospitalPhysical Therapy |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital SWH
CBECS_Before-1980_Hospital_PhysTherapy | 163 | DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | PhysTherapy | 154_230_120 | [6 empty] | 2.51 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital SWH
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 90.1-2007 | Hospital | Physical Therapy | ASHRAE 90.1-2007HospitalPhysical Therapy |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital SWH
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 90.1-2010 | Hospital | Physical Therapy | ASHRAE 90.1-2010HospitalPhysical Therapy |  |  | 0.91 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital SWH
CBECS_1980-2004_Retail_Point_of_Sale | 81 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Retail; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Point_of_Sale; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 171_222_78; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 3.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Retail Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Basement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Retail Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Retail Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Retail Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Retail Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Retail HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Retail ClgSetp
ASHRAE_90.1-2004_Retail_Point_of_Sale | 63 | DOE Ref 2004 | ClimateZone 1-8 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0595 | Retail Infil Half On | [5 empty] | 2 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Retail_Point_of_Sale | 350 | 189.1-2009 | ClimateZone 1-3 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0595 | Retail Infil Half On | [5 empty] | 1.45 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Retail_Point_of_Sale | 353 | 189.1-2009 | ClimateZone 4-8 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0446 | Retail Infil Half On | [5 empty] | 1.45 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
CBECS_Before-1980_Retail_Point_of_Sale | 317 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Retail; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Point_of_Sale; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 171_222_78; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 5.04; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Retail Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Basement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Retail Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Retail Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Retail Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Retail Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Retail HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Retail ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-2004 | Retail | General Sales | ASHRAE 62.1-2004RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0446 | Retail Infil Half On | [5 empty] | 1.45 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 90.1-2010 | Sales Area | General | ASHRAE 90.1-2010Sales AreaGeneral |  |  | 1.68 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0446 | Retail Infil Half On | [5 empty] | 1.45 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
CBECS_1980-2004_Outpatient_PreOp | 420 | DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | PreOp | 169_31_159 | [6 empty] | 1.4 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_90.1-2004_Outpatient_PreOp | 455 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | PreOp | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Patient Room | ASHRAE 90.1-2004HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_PreOp | 133 | 189.1-2009 | ClimateZone 1-3 | Outpatient | PreOp | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_PreOp | 92 | 189.1-2009 | ClimateZone 4-8 | Outpatient | PreOp | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient SWH
CBECS_Before-1980_Outpatient_PreOp | 32 | DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | PreOp | 169_31_159 | [6 empty] | 1.4 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient SWH
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | PreOp | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Patient Room | ASHRAE 90.1-2007HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient SWH
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | PreOp | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Patient Room | ASHRAE 90.1-2010HospitalPatient Room |  |  | 0.62 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient SWH
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | PrintRoom | 41_31_169 | [6 empty] | 1.55 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 5.4 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | PrintRoom | 41_31_169 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 5.4 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 1-3 | Office | PrintRoom | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 2.79 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 4-8 | Office | PrintRoom | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 2.79 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | PrintRoom | 41_31_169 | [6 empty] | 1.881 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 5.4 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Office | PrintRoom | 41_31_169 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 10 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 2.79 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Office | PrintRoom | 41_31_169 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 10 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 2.79 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
CBECS_1980-2004_Outpatient_ProcedureRoom | 215 | DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | ProcedureRoom | 169_31_159 | [6 empty] | 1.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_90.1-2004_Outpatient_ProcedureRoom | 104 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_ProcedureRoom | 46 | 189.1-2009 | ClimateZone 1-3 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_ProcedureRoom | 544 | 189.1-2009 | ClimateZone 4-8 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient SWH
CBECS_Before-1980_Outpatient_ProcedureRoom | 205 | DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | ProcedureRoom | 169_31_159 | [6 empty] | 1.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient SWH
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient SWH
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Emergency | ASHRAE 90.1-2010HospitalEmergency |  |  | 2.26 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient SWH
|  | 90.1-2007 | ClimateZone 1-8 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 2.85 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.51 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
CBECS_1980-2004_SmallHotel_PublicRestroom | 377 | DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | PublicRestroom | 169_169_31 | [6 empty] | 1.1 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 2.85 | SmallHotel Bldg Occ | SmallHotel Activity | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
ASHRAE_90.1-2004_SmallHotel_PublicRestroom | 366 | DOE Ref 2004 | ClimateZone 1-8 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 2.85 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 1 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_PublicRestroom | 2 | 189.1-2009 | ClimateZone 1-3 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 2.85 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 0.51 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_PublicRestroom | 430 | 189.1-2009 | ClimateZone 4-8 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 2.85 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.51 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
CBECS_Before-1980_SmallHotel_PublicRestroom | 202 | DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | PublicRestroom | 169_169_31 | [6 empty] | 1.1 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 2.85 | SmallHotel Bldg Occ | SmallHotel Activity | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
|  | 90.1-2010 | ClimateZone 1-8 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 90.1-2010 | Restrooms | General | ASHRAE 90.1-2010RestroomsGeneral |  |  | 0.98 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 2.85 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0.51 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
CBECS_1980-2004_Hospital_Radiology | 452 | DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | Radiology | 136_78_222 | [6 empty] | 2.21 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 10 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital SWH Extd
ASHRAE_90.1-2004_Hospital_Radiology | 57 | DOE Ref 2004 | ClimateZone 1-8 | Hospital | Radiology | 136_78_222 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 10 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital SWH Extd
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_Radiology | 299 | 189.1-2009 | ClimateZone 1-3 | Hospital | Radiology | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0595 | Hospital Infil Quarter On | [5 empty] | 7.28 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital SWH Extd
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_Radiology | 5 | 189.1-2009 | ClimateZone 4-8 | Hospital | Radiology | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 7.28 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital SWH Extd
CBECS_Before-1980_Hospital_Radiology | 260 | DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | Radiology | 136_78_222 | [6 empty] | 3.3 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.2232 | Hospital Infil Quarter On | [5 empty] | 10 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital SWH Extd
|  | 90.1-2007 | ClimateZone 1-8 | Hospital | Radiology | 136_78_222 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 7.28 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital SWH Extd
|  | 90.1-2010 | ClimateZone 1-8 | Hospital | Radiology | 136_78_222 | ASHRAE 90.1-2010 | Hospital | Radiology/Imaging | ASHRAE 90.1-2010HospitalRadiology/Imaging |  |  | 1.32 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 | Hospital Infil Quarter On | [5 empty] | 7.28 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital SWH Extd
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Restroom | 169_169_31 | [6 empty] | 1.41 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office Bldg Occ
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | Restroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office Bldg Occ
|  | 189.1-2009 | ClimateZone 1-3 | Office | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office Bldg Occ
|  | 189.1-2009 | ClimateZone 4-8 | Office | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office Bldg Occ
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Restroom | 169_169_31 | [6 empty] | 1.71 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office Bldg Occ
|  | 90.1-2007 | ClimateZone 1-8 | Office | Restroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 10 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office Bldg Occ
CBECS_1980-2004_PrimarySchool_Restroom | 129 | DOE Ref 1980-2004 | ClimateZone 1-8 | PrimarySchool | Restroom | 169_169_31 | [6 empty] | 0.9 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.2232 | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
ASHRAE_90.1-2004_PrimarySchool_Restroom | 10 | DOE Ref 2004 | ClimateZone 1-8 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Restroom | 170 | 189.1-2009 | ClimateZone 1-3 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Restroom | 390 | 189.1-2009 | ClimateZone 4-8 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
CBECS_Before-1980_PrimarySchool_Restroom | 148 | DOE Ref Pre-1980 | ClimateZone 1-8 | PrimarySchool | Restroom | 169_169_31 | [6 empty] | 1.08 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.2232 | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
|  | 90.1-2007 | ClimateZone 1-8 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
CBECS_1980-2004_SecondarySchool_Restroom | 436 | DOE Ref 1980-2004 | ClimateZone 1-8 | SecondarySchool | Restroom | 169_169_31 | [6 empty] | 0.89 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.2232 | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
ASHRAE_90.1-2004_SecondarySchool_Restroom | 275 | DOE Ref 2004 | ClimateZone 1-8 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Restroom | 504 | 189.1-2009 | ClimateZone 1-3 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Restroom | 94 | 189.1-2009 | ClimateZone 4-8 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
CBECS_Before-1980_SecondarySchool_Restroom | 181 | DOE Ref Pre-1980 | ClimateZone 1-8 | SecondarySchool | Restroom | 169_169_31 | [6 empty] | 1.08 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.2232 | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
|  | 90.1-2007 | ClimateZone 1-8 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 9.29 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
|  | 90.1-2010 | ClimateZone 1-8 | Office | Restroom | 169_169_31 | ASHRAE 90.1-2010 | Restrooms | General | ASHRAE 90.1-2010RestroomsGeneral |  |  | 0.98 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 10 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office Bldg Occ
|  | 90.1-2010 | ClimateZone 1-8 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2010 | Restrooms | General | ASHRAE 90.1-2010RestroomsGeneral |  |  | 0.98 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
|  | 90.1-2010 | ClimateZone 1-8 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2010 | Restrooms | General | ASHRAE 90.1-2010RestroomsGeneral |  |  | 0.98 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 9.29 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
CBECS_1980-2004_LargeHotel_Retail | 219 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: LargeHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Retail; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 171_222_78; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 3.54; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: LargeHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Basement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: LargeHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: LargeHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: LargeHotel Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: LargeHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: LargeHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: LargeHotel ClgSetp
ASHRAE_90.1-2004_LargeHotel_Retail | 526 | DOE Ref 2004 | ClimateZone 1-8 | LargeHotel | Retail | 171_222_78 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Retail | 272 | 189.1-2009 | ClimateZone 1-3 | LargeHotel | Retail | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 0.51 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Retail | 437 | 189.1-2009 | ClimateZone 4-8 | LargeHotel | Retail | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.51 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
CBECS_Before-1980_LargeHotel_Retail | 339 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: LargeHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Retail; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 171_222_78; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 5.04; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: LargeHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Basement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: LargeHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: LargeHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: LargeHotel Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 1; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: LargeHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: LargeHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: LargeHotel ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | LargeHotel | Retail | 171_222_78 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2004 | Retail | General Sales | ASHRAE 62.1-2004RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.51 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
CBECS_1980-2004_Retail_Core | 495 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Retail; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Retail; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 171_222_78; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 3.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Retail Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Specialty Shops; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Clothiers, furniture; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Specialty ShopsClothiers, furniture; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Retail Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Retail Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Retail Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Retail Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Retail HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Retail ClgSetp
ASHRAE_90.1-2004_Retail_Core | 556 | DOE Ref 2004 | ClimateZone 1-8 | Retail | Retail | 171_222_78 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0595 | Retail Infil Half On | [5 empty] | 0.3 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Retail_Core | 413 | 189.1-2009 | ClimateZone 1-3 | Retail | Retail | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0595 | Retail Infil Half On | [5 empty] | 0.22 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Retail_Core | 506 | 189.1-2009 | ClimateZone 4-8 | Retail | Retail | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0446 | Retail Infil Half On | [5 empty] | 0.22 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
CBECS_Before-1980_Retail_Core | 445 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Retail; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Retail; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 171_222_78; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 5.04; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Retail Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Specialty Shops; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Clothiers, furniture; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Specialty ShopsClothiers, furniture; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Retail Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Retail Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Retail Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Retail Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Retail HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Retail ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Retail | Retail | 171_222_78 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-2004 | Retail | General Sales | ASHRAE 62.1-2004RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0446 | Retail Infil Half On | [5 empty] | 0.22 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | LargeHotel | Retail | 171_222_78 | ASHRAE 90.1-2010 | Sales Area | General | ASHRAE 90.1-2010Sales AreaGeneral |  |  | 1.68 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.51 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Retail | Retail | 171_222_78 | ASHRAE 90.1-2010 | Sales Area | General | ASHRAE 90.1-2010Sales AreaGeneral |  |  | 1.68 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0446 | Retail Infil Half On | [5 empty] | 0.22 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2004 | Retail | Supermarket | ASHRAE 62.1-2004RetailSupermarket | 0.06 | 7.5 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 | SuperMarket Infil Half On | [5 empty] | 0.36 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
CBECS_1980-2004_SuperMarket_Sales/Produce | 472 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SuperMarket; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Sales/Produce; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_196_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 2.78; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SuperMarket Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Specialty Shops; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Supermarket; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Specialty ShopsSupermarket; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SuperMarket Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SuperMarket Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SuperMarket Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SuperMarket Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SuperMarket HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SuperMarket ClgSetp
ASHRAE_90.1-2004_SuperMarket_Sales/Produce | 401 | DOE Ref 2004 | ClimateZone 1-8 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 | SuperMarket Infil Half On | [5 empty] | 0.5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SuperMarket_Sales/Produce | 116 | 189.1-2009 | ClimateZone 1-3 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 | SuperMarket Infil Half On | [5 empty] | 0.36 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SuperMarket_Sales/Produce | 7 | 189.1-2009 | ClimateZone 4-8 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 | SuperMarket Infil Half On | [5 empty] | 0.36 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
CBECS_Before-1980_SuperMarket_Sales/Produce | 17 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SuperMarket; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Sales/Produce; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_196_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 5.04; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SuperMarket Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Specialty Shops; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Supermarket; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Specialty ShopsSupermarket; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SuperMarket Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SuperMarket Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SuperMarket Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SuperMarket Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SuperMarket HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SuperMarket ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 90.1-2010 | Sales Area | General | ASHRAE 90.1-2010Sales AreaGeneral |  |  | 1.68 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | Retail | Supermarket | ASHRAE 62.1-2007RetailSupermarket | 0.06 | 7.5 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 | SuperMarket Infil Half On | [5 empty] | 0.36 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
CBECS_1980-2004_Outpatient_Soil Work | 532 | DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Soil Work | 204_120_230 | [6 empty] | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
ASHRAE_90.1-2004_Outpatient_Soil Work | 191 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | Soil Work | 204_120_230 | ASHRAE 90.1-2004 | Hospital | Medical Supply | ASHRAE 90.1-2004HospitalMedical Supply |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Soil Work | 182 | 189.1-2009 | ClimateZone 1-3 | Outpatient | Soil Work | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Medical Supply | ASHRAE 189.1-2009HospitalMedical Supply |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Soil Work | 514 | 189.1-2009 | ClimateZone 4-8 | Outpatient | Soil Work | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Medical Supply | ASHRAE 189.1-2009HospitalMedical Supply |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
CBECS_Before-1980_Outpatient_Soil Work | 238 | DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Soil Work | 204_120_230 | [6 empty] | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | Soil Work | 204_120_230 | ASHRAE 90.1-2007 | Hospital | Medical Supply | ASHRAE 90.1-2007HospitalMedical Supply |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | Soil Work | 204_120_230 | ASHRAE 90.1-2010 | Hospital | Medical Supply | ASHRAE 90.1-2010HospitalMedical Supply |  |  | 1.27 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
CBECS_1980-2004_SmallHotel_StaffLounge | 498 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: StaffLounge; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.65; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel StaffLounge Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Lobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 30; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel StaffLounge Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 7.17; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel StaffLounge Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
ASHRAE_90.1-2004_SmallHotel_StaffLounge | 442 | DOE Ref 2004 | ClimateZone 1-8 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 90.1-2004 | Lounge/Recreation | General | ASHRAE 90.1-2004Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel StaffLounge Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 7.17 | 0 | 0.5 | 0 | SmallHotel StaffLounge Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_StaffLounge | 176 | 189.1-2009 | ClimateZone 1-3 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel StaffLounge Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 3.67 | 0 | 0.5 | 0 | SmallHotel StaffLounge Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_StaffLounge | 199 | 189.1-2009 | ClimateZone 4-8 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel StaffLounge Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 3.67 | 0 | 0.5 | 0 | SmallHotel StaffLounge Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_Before-1980_SmallHotel_StaffLounge | 130 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: StaffLounge; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 31_169_34; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 1.65; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel StaffLounge Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Hotels, Motels, Resorts, Dormitories; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Lobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 30; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel StaffLounge Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 7.17; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel StaffLounge Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 90.1-2007 | Lounge/Recreation | General | ASHRAE 90.1-2007Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-2004 | General | Conference/meeting | ASHRAE 62.1-2004GeneralConference/meeting | 0.06 | 5 | 0 | 30 | SmallHotel StaffLounge Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 3.67 | 0 | 0.5 | 0 | SmallHotel StaffLounge Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 90.1-2010 | Lounge/Recreation | General | ASHRAE 90.1-2010Lounge/RecreationGeneral |  |  | 0.73 |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 | 0 | 30 | SmallHotel StaffLounge Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 3.67 | 0 | 0.5 | 0 | SmallHotel StaffLounge Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Stair | 230_157_120 | [6 empty] | 0.942 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | Stair | 230_157_120 | ASHRAE 90.1-2004 | Stairs-Active | General | ASHRAE 90.1-2004Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 1-3 | Office | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 4-8 | Office | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Stair | 230_157_120 | [6 empty] | 1.14 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Office | Stair | 230_157_120 | ASHRAE 90.1-2007 | Stairs-Active | General | ASHRAE 90.1-2007Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
CBECS_1980-2004_Outpatient_Stair | 19 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Stair; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
ASHRAE_90.1-2004_Outpatient_Stair | 537 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | Stair | 230_157_120 | ASHRAE 90.1-2004 | Stairs-Active | General | ASHRAE 90.1-2004Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Stair | 467 | 189.1-2009 | ClimateZone 1-3 | Outpatient | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Stair | 422 | 189.1-2009 | ClimateZone 4-8 | Outpatient | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_Before-1980_Outpatient_Stair | 131 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: Outpatient; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Stair; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: Outpatient Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: Outpatient Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: Outpatient Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: Outpatient Infil; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: Outpatient Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: Outpatient HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: Outpatient ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | Stair | 230_157_120 | ASHRAE 90.1-2007 | Stairs-Active | General | ASHRAE 90.1-2007Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
CBECS_1980-2004_SmallHotel_Stair | 61 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Stair; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.82; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
ASHRAE_90.1-2004_SmallHotel_Stair | 533 | DOE Ref 2004 | ClimateZone 1-8 | SmallHotel | Stair | 230_157_120 | ASHRAE 90.1-2004 | Stairs-Active | General | ASHRAE 90.1-2004Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Stair | 227 | 189.1-2009 | ClimateZone 1-3 | SmallHotel | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Stair | 485 | 189.1-2009 | ClimateZone 4-8 | SmallHotel | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_Before-1980_SmallHotel_Stair | 119 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Stair; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 230_157_120; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.82; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Public Spaces; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Corridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.05; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SmallHotel | Stair | 230_157_120 | ASHRAE 90.1-2007 | Stairs-Active | General | ASHRAE 90.1-2007Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Office | Stair | 230_157_120 | ASHRAE 90.1-2010 | Stairway | General | ASHRAE 90.1-2010StairwayGeneral |  |  | 0.69 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | Stair | 230_157_120 | ASHRAE 90.1-2010 | Stairway | General | ASHRAE 90.1-2010StairwayGeneral |  |  | 0.69 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SmallHotel | Stair | 230_157_120 | ASHRAE 90.1-2010 | Stairway | General | ASHRAE 90.1-2010StairwayGeneral |  |  | 0.69 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_1980-2004_LargeHotel_Storage | 83 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: LargeHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Storage; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_149_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.37; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: LargeHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Shipping and receiving; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: LargeHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: LargeHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: LargeHotel Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.25; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: LargeHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: LargeHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: LargeHotel ClgSetp
ASHRAE_90.1-2004_LargeHotel_Storage | 355 | DOE Ref 2004 | ClimateZone 1-8 | LargeHotel | Storage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 2 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 0.25 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Storage | 471 | 189.1-2009 | ClimateZone 1-3 | LargeHotel | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 2 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 | LargeHotel Infil Quarter On | [5 empty] | 0.13 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Storage | 478 | 189.1-2009 | ClimateZone 4-8 | LargeHotel | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 2 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.13 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
CBECS_Before-1980_LargeHotel_Storage | 149 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: LargeHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Storage; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_149_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.62; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: LargeHotel Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Shipping and receiving; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: LargeHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: LargeHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: LargeHotel Infil Quarter On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.25; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: LargeHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: LargeHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: LargeHotel ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | LargeHotel | Storage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 2 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.13 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Storage | 120_149_230 | [6 empty] | 1.27 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | Storage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 1-3 | Office | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 4-8 | Office | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Storage | 120_149_230 | [6 empty] | 1.539 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Office | Storage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
CBECS_1980-2004_SmallHotel_Storage | 383 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Storage; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_149_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.45; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel Storage Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Shipping and receiving; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
ASHRAE_90.1-2004_SmallHotel_Storage | 374 | DOE Ref 2004 | ClimateZone 1-8 | SmallHotel | Storage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Storage | 483 | 189.1-2009 | ClimateZone 1-3 | SmallHotel | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Storage | 477 | 189.1-2009 | ClimateZone 4-8 | SmallHotel | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_Before-1980_SmallHotel_Storage | 447 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: SmallHotel; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: Storage; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 120_149_230; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 0.45; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: SmallHotel Storage Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Shipping and receiving; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: SmallHotel Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: SmallHotel Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: SmallHotel Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: SmallHotel Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: SmallHotel HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: SmallHotel ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | SmallHotel | Storage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | LargeHotel | Storage | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 2 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 | LargeHotel Infil Quarter On | [5 empty] | 0.13 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Office | Storage | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | SmallHotel | Storage | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
CBECS_1980-2004_Outpatient_Toilet | 84 | DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Toilet | 169_169_31 | [6 empty] | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 0.4 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
ASHRAE_90.1-2004_Outpatient_Toilet | 375 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | Toilet | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.4 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Toilet | 268 | 189.1-2009 | ClimateZone 1-3 | Outpatient | Toilet | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.29 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Toilet | 279 | 189.1-2009 | ClimateZone 4-8 | Outpatient | Toilet | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.29 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
CBECS_Before-1980_Outpatient_Toilet | 425 | DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Toilet | 169_169_31 | [6 empty] | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 0.4 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | Toilet | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.29 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | Toilet | 169_169_31 | ASHRAE 90.1-2010 | Restrooms | General | ASHRAE 90.1-2010RestroomsGeneral |  |  | 0.98 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.29 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Vending | 230_157_120 | [6 empty] | 1.57 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 3.85 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | Vending | 230_157_120 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 3.85 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 1-3 | Office | Vending | 230_157_120 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 3.85 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 189.1-2009 | ClimateZone 4-8 | Office | Vending | 230_157_120 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Misc Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 3.85 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Vending | 230_157_120 | [6 empty] | 0.95 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 3.85 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2007 | ClimateZone 1-8 | Office | Vending | 230_157_120 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 1 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 3.85 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
|  | 90.1-2010 | ClimateZone 1-8 | Office | Vending | 230_157_120 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral |  |  | 0.66 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 1 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 3.85 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
CBECS_1980-2004_StripMall | 230 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref 1980-2004; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: StripMall; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: WholeBuilding; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 171_222_78; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 3.58; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: StripMall Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Basement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: StripMall Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: StripMall Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: StripMall Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.4; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: StripMall Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: StripMall HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: StripMall ClgSetp
ASHRAE_90.1-2004_StripMall | 297 | DOE Ref 2004 | ClimateZone 1-8 | StripMall | WholeBuilding | 171_222_78 | ASHRAE 90.1-2004 | Whole Building | Retail | ASHRAE 90.1-2004Whole BuildingRetail |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | StripMall Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | StripMall Bldg Occ | StripMall Activity | 0.0595 | StripMall Infil Half On | [5 empty] | 0.4 | 0 | 0.5 | 0 | StripMall Bldg Equip | StripMall HtgSetp | StripMall ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_StripMall | 543 | 189.1-2009 | ClimateZone 1-3 | StripMall | WholeBuilding | 171_222_78 | ASHRAE 189.1-2009 | Whole Building | Retail | ASHRAE 189.1-2009Whole BuildingRetail |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | StripMall Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | StripMall Bldg Occ | StripMall Activity | 0.0595 | StripMall Infil Half On | [5 empty] | 0.29 | 0 | 0.5 | 0 | StripMall Bldg Equip | StripMall HtgSetp | StripMall ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_StripMall | 188 | 189.1-2009 | ClimateZone 4-8 | StripMall | WholeBuilding | 171_222_78 | ASHRAE 189.1-2009 | Whole Building | Retail | ASHRAE 189.1-2009Whole BuildingRetail |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | StripMall Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | StripMall Bldg Occ | StripMall Activity | 0.0446 | StripMall Infil Half On | [5 empty] | 0.29 | 0 | 0.5 | 0 | StripMall Bldg Equip | StripMall HtgSetp | StripMall ClgSetp
CBECS_Before-1980_StripMall | 240 | A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 0: DOE Ref Pre-1980; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 1: ClimateZone 1-8; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 2: StripMall; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 3: WholeBuilding; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 4: 171_222_78; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 11: 4.81; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 14: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 15: 0.7; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 16: 0.2; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 17: StripMall Bldg Light; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 18: ASHRAE 62.1-1999; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 19: Retail Stores, Sales Floors, and Show Room Floors; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 20: Basement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 22: 0.3; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 23: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 24: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 25: 15; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 26: StripMall Bldg Occ; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 27: StripMall Activity; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 28: 0.2232; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 29: StripMall Infil Half On; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 35: 0.4; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 36: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 37: 0.5; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 38: 0; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 39: StripMall Bldg Equip; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 40: StripMall HtgSetp; A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building 41: StripMall ClgSetp
CBECS_1980-2004_LargeOffice | 140 | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | WholeBuilding - Lg Office | 120_230_199 | [6 empty] | 1.5 |  |  | 0 | 0.7 | 0.2 | Large Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Large Office Bldg Occ | Large Office Activity | 0.2232 | Large Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Large Office Bldg Equip | Large Office HtgSetp | Large Office ClgSetp | 63.9 | 498588 | 0.00012816 | 43.3 | 0.2 | 0.05 | Office SWH
ASHRAE_189.1-2009_ClimateZone 1-3_LargeOffice | 307 | 189.1-2009 | ClimateZone 1-3 | Office | WholeBuilding - Lg Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Large Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Large Office Bldg Occ | Large Office Activity | 0.0595 | Large Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Large Office Bldg Equip | Large Office HtgSetp | Large Office ClgSetp | 63.9 | 498588 | 0.00012816 | 43.3 | 0.2 | 0.05 | Office SWH
ASHRAE_189.1-2009_ClimateZone 4-8_LargeOffice | 410 | 189.1-2009 | ClimateZone 4-8 | Office | WholeBuilding - Lg Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Large Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Large Office Bldg Occ | Large Office Activity | 0.0446 | Large Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Large Office Bldg Equip | Large Office HtgSetp | Large Office ClgSetp | 63.9 | 498588 | 0.00012816 | 43.3 | 0.2 | 0.05 | Office SWH
CBECS_Before-1980_LargeOffice | 266 | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | WholeBuilding - Lg Office | 120_230_199 | [6 empty] | 1.9 |  |  | 0 | 0.7 | 0.2 | Large Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Large Office Bldg Occ | Large Office Activity | 0.2232 | Large Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Large Office Bldg Equip | Large Office HtgSetp | Large Office ClgSetp | 63.9 | 498588 | 0.00012816 | 43.3 | 0.2 | 0.05 | Office SWH
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | WholeBuilding - Lg Office | 120_230_199 | ASHRAE 90.1-2004 | Whole Building | Office | ASHRAE 90.1-2004Whole BuildingOffice |  |  | 1 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Medium Office Bldg Occ | Medium Office Activity | 0.0595 | Medium Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | Office SWH
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | WholeBuilding - Md Office | 120_230_199 | [6 empty] | 1.57 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Medium Office Bldg Occ | Medium Office Activity | 0.2232 | Medium Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | Office SWH
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | WholeBuilding - Md Office | 120_230_199 | ASHRAE 90.1-2004 | Whole Building | Office | ASHRAE 90.1-2004Whole BuildingOffice |  |  | 1 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Medium Office Bldg Occ | Medium Office Activity | 0.0595 | Medium Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | Office SWH
|  | 189.1-2009 | ClimateZone 1-3 | Office | WholeBuilding - Md Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Medium Office Bldg Occ | Medium Office Activity | 0.0595 | Medium Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | Office SWH
|  | 189.1-2009 | ClimateZone 4-8 | Office | WholeBuilding - Md Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 | Medium Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | Office SWH
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | WholeBuilding - Md Office | 120_230_199 | [6 empty] | 1.9 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Medium Office Bldg Occ | Medium Office Activity | 0.2232 | Medium Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | Office SWH
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | WholeBuilding - Sm Office | 120_230_199 | [6 empty] | 1.81 |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Small Office Bldg Occ | Small Office Activity | 0.2232 | Small Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Small Office Bldg Equip | Small Office HtgSetp | Small Office ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | Office SWH
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 90.1-2004 | Whole Building | Office | ASHRAE 90.1-2004Whole BuildingOffice |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Small Office Bldg Occ | Small Office Activity | 0.0595 | Small Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Small Office Bldg Equip | Small Office HtgSetp | Small Office ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | Office SWH
|  | 189.1-2009 | ClimateZone 1-3 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Small Office Bldg Occ | Small Office Activity | 0.0595 | Small Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Small Office Bldg Equip | Small Office HtgSetp | Small Office ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | Office SWH
|  | 189.1-2009 | ClimateZone 4-8 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Small Office Bldg Occ | Small Office Activity | 0.0446 | Small Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Small Office Bldg Equip | Small Office HtgSetp | Small Office ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | Office SWH
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | WholeBuilding - Sm Office | 120_230_199 | [6 empty] | 1.81 |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Small Office Bldg Occ | Small Office Activity | 0.2232 | Small Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Small Office Bldg Equip | Small Office HtgSetp | Small Office ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | Office SWH
CBECS_1980-2004_Outpatient_Xray | 16 | DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Xray | 169_31_159 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_90.1-2004_Outpatient_Xray | 216 | DOE Ref 2004 | ClimateZone 1-8 | Outpatient | Xray | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Xray | 117 | 189.1-2009 | ClimateZone 1-3 | Outpatient | Xray | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 | Outpatient Infil | [5 empty] | 0.95 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Xray | 461 | 189.1-2009 | ClimateZone 4-8 | Outpatient | Xray | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.95 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient SWH
CBECS_Before-1980_Outpatient_Xray | 392 | DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Xray | 169_31_159 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.2232 | Outpatient Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient SWH
|  | 90.1-2007 | ClimateZone 1-8 | Outpatient | Xray | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.95 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient SWH
|  | 90.1-2010 | ClimateZone 1-8 | Outpatient | Xray | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Radiology/Imaging | ASHRAE 90.1-2010HospitalRadiology/Imaging |  |  | 1.32 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 | Outpatient Infil | [5 empty] | 0.95 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient SWH
|  | 90.1-2010 | ClimateZone 1-8 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 90.1-2010 | Whole Building | Office | ASHRAE 90.1-2010Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 5 | Small Office Bldg Occ | Small Office Activity | 0.112 | Small Office Infil Quarter On | [5 empty] | 0.63 | 0 | 0.5 | 0 | Small Office Bldg Equip | Small Office HtgSetp | Small Office ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | Office SWH
|  | DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Attic | 120_149_230 | [23 empty] | 0.2232 | Small Office Infil Quarter On
|  | DOE Ref 2004 | ClimateZone 1-8 | Office | Attic | 120_149_230 | [23 empty] | 0.0595 | Small Office Infil Quarter On
|  | 189.1-2009 | ClimateZone 1-3 | Office | Attic | 120_149_230 | [23 empty] | 0.0595 | Small Office Infil Quarter On
|  | 189.1-2009 | ClimateZone 4-8 | Office | Attic | 120_149_230 | [23 empty] | 0.0446 | Small Office Infil Quarter On
|  | DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Attic | 120_149_230 | [23 empty] | 0.2232 | Small Office Infil Quarter On
|  | 90.1-2010 | ClimateZone 1-8 | Office | Attic | 120_149_230 | [23 empty] | 0.112 | Small Office Infil Quarter On
Note on BF8: NREL: Typical - ref has different schedule for 2nd and 3rd floor than first
Note on F92: NREL: Not adjusted for special computer classrroom with slightly higher plug loads
Note on AZ181: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AZ182: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AZ183: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AZ184: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AZ185: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AZ186: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AZ187: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AT383: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AT384: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AT385: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AT386: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AT387: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AT388: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AT414: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AT643: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AT644: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AT645: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AT646: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AT647: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AT648: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AT655: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on F658: NREL: Step down and Recovery same as this
Note on AT671: NREL: average size across 8 rooms
Note on AT672: NREL: average size across 8 rooms
Note on AT673: NREL: average size across 8 rooms
Note on AT674: NREL: average size across 8 rooms
Note on AT675: NREL: average size across 8 rooms
Note on AT676: NREL: average size across 8 rooms
Note on AT677: NREL: average size across 8 rooms
Note on BF723: NREL: Don’t see an elec object for this in ref building model like I do for other exhaust fans
Note on BF742: NREL: Don’t see an elec object for this in ref building model like I do for other exhaust fans
Note on BF748: NREL: Don’t see an elec object for this in ref building model like I do for other exhaust fans

## Ventilation
Each row represents ventilation requirements for a particular space type in a particular standard. Values are referenced on Space Types tab.
|  |  |  | ventilation | ventilation | ventilation
VlookupColumn | Ventilation Standard | Primary Space Type | Secondary Space Type | ft^3/min*person | ft^3/min*ft^2 | ach | Notes
AIA 2001AncillaryX-Ray (Surgical/Critical Care and Catheterization) | AIA 2001 | Ancillary | X-Ray (Surgical/Critical Care and Catheterization) |  |  | 3
ASHRAE 62.1-1999Correctional FacilitiesCell | ASHRAE 62.1-1999 | Correctional Facilities | Cell | 20 | 0
ASHRAE 62.1-1999Correctional FacilitiesDining halls | ASHRAE 62.1-1999 | Correctional Facilities | Dining halls | 15 | 0
ASHRAE 62.1-1999Correctional FacilitiesGuard stations | ASHRAE 62.1-1999 | Correctional Facilities | Guard stations | 15 | 0
ASHRAE 62.1-2004Correctional FacilitiesDay room | ASHRAE 62.1-2004 | Correctional Facilities | Day room | 5 | 0.06
ASHRAE 62.1-2004Correctional FacilitiesGuard stations | ASHRAE 62.1-2004 | Correctional Facilities | Guard stations | 5 | 0.06
ASHRAE 62.1-2004Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2004 | Correctional Facilities | Booking/waiting | 7.5 | 0.06
ASHRAE 62.1-2007Correctional FacilitiesDay room | ASHRAE 62.1-2007 | Correctional Facilities | Day room | 5 | 0.06
ASHRAE 62.1-2007Correctional FacilitiesGuard stations | ASHRAE 62.1-2007 | Correctional Facilities | Guard stations | 5 | 0.06
ASHRAE 62.1-2007Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2007 | Correctional Facilities | Booking/waiting | 7.5 | 0.06
ASHRAE 62.1-2004Correctional FacilitiesCell | ASHRAE 62.1-2004 | Correctional Facilities | Cell | 5 | 0.12
ASHRAE 62.1-2007Correctional FacilitiesCell | ASHRAE 62.1-2007 | Correctional Facilities | Cell | 5 | 0.12
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial laundry | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial laundry | 25 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial dry cleaner | 30 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesStorage, pick up | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Storage, pick up | 35 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated laundries | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated laundries | 15 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated dry cleaner | 15 | 0
ASHRAE 62.1-1999EducationClassroom | ASHRAE 62.1-1999 | Education | Classroom | 15 | 0
ASHRAE 62.1-1999EducationLaboratories | ASHRAE 62.1-1999 | Education | Laboratories | 20 | 0
ASHRAE 62.1-1999EducationTraining shop | ASHRAE 62.1-1999 | Education | Training shop | 20 | 0
ASHRAE 62.1-1999EducationMusic rooms | ASHRAE 62.1-1999 | Education | Music rooms | 15 | 0
ASHRAE 62.1-1999EducationLibraries | ASHRAE 62.1-1999 | Education | Libraries | 15 | 0
ASHRAE 62.1-1999EducationAuditorium | ASHRAE 62.1-1999 | Education | Auditorium | 15 | 0
ASHRAE 62.1-1999EducationSmoking lounges | ASHRAE 62.1-1999 | Education | Smoking lounges | 60 | 0
ASHRAE 62.1-1999EducationCorridors | ASHRAE 62.1-1999 | Education | Corridors | 0 | 0.1
ASHRAE 62.1-1999EducationLocker rooms | ASHRAE 62.1-1999 | Education | Locker rooms | 0 | 0.5
ASHRAE 62.1-2004Educational FacilitiesLecture classroom | ASHRAE 62.1-2004 | Educational Facilities | Lecture classroom | 7.5 | 0.06
ASHRAE 62.1-2004Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2004 | Educational Facilities | Lecture hall (fixed seats) | 7.5 | 0.06
ASHRAE 62.1-2004Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2004 | Educational Facilities | Music/theater/dance | 10 | 0.06
ASHRAE 62.1-2004Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2004 | Educational Facilities | Multiuse assembly | 7.5 | 0.06
ASHRAE 62.1-2007Educational FacilitiesLecture classroom | ASHRAE 62.1-2007 | Educational Facilities | Lecture classroom | 7.5 | 0.06
ASHRAE 62.1-2007Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2007 | Educational Facilities | Lecture hall (fixed seats) | 7.5 | 0.06
ASHRAE 62.1-2007Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2007 | Educational Facilities | Music/theater/dance | 10 | 0.06
ASHRAE 62.1-2007Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2007 | Educational Facilities | Multiuse assembly | 7.5 | 0.06
ASHRAE 62.1-2004Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (ages 5-8) | 10 | 0.12
ASHRAE 62.1-2004Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (age 9 plus) | 10 | 0.12
ASHRAE 62.1-2004Educational FacilitiesComputer lab | ASHRAE 62.1-2004 | Educational Facilities | Computer lab | 10 | 0.12
ASHRAE 62.1-2004Educational FacilitiesMedia center | ASHRAE 62.1-2004 | Educational Facilities | Media center | 10 | 0.12 |  | A
ASHRAE 62.1-2007Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (ages 5-8) | 10 | 0.12
ASHRAE 62.1-2007Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (age 9 plus) | 10 | 0.12
ASHRAE 62.1-2007Educational FacilitiesComputer lab | ASHRAE 62.1-2007 | Educational Facilities | Computer lab | 10 | 0.12
ASHRAE 62.1-2007Educational FacilitiesMedia center | ASHRAE 62.1-2007 | Educational Facilities | Media center | 10 | 0.12 |  | A
ASHRAE 62.1-2004Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2004 | Educational Facilities | Daycare (through age 4) | 10 | 0.18
ASHRAE 62.1-2004Educational FacilitiesArt classroom | ASHRAE 62.1-2004 | Educational Facilities | Art classroom | 10 | 0.18
ASHRAE 62.1-2004Educational FacilitiesScience laboratories | ASHRAE 62.1-2004 | Educational Facilities | Science laboratories | 10 | 0.18 |  | E
ASHRAE 62.1-2004Educational FacilitiesWood/metal shop | ASHRAE 62.1-2004 | Educational Facilities | Wood/metal shop | 10 | 0.18
ASHRAE 62.1-2007Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2007 | Educational Facilities | Daycare (through age 4) | 10 | 0.18
ASHRAE 62.1-2007Educational FacilitiesArt classroom | ASHRAE 62.1-2007 | Educational Facilities | Art classroom | 10 | 0.18
ASHRAE 62.1-2007Educational FacilitiesScience laboratories | ASHRAE 62.1-2007 | Educational Facilities | Science laboratories | 10 | 0.18 |  | E
ASHRAE 62.1-2007Educational FacilitiesWood/metal shop | ASHRAE 62.1-2007 | Educational Facilities | Wood/metal shop | 10 | 0.18
ASHRAE 62.1-1999Food and Beverage ServiceDining rooms | ASHRAE 62.1-1999 | Food and Beverage Service | Dining rooms | 20 | 0
ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | 20 | 0
ASHRAE 62.1-1999Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-1999 | Food and Beverage Service | Bars, cocktail lounges | 30 | 0
ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | 15 | 0 |  | Exhaust >= 1.5 cfm/ft2, 7.5 L/s m2
ASHRAE 62.1-2004Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2004 | Food and Beverage Service | Restaurant dining rooms | 7.5 | 0.18
ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | 7.5 | 0.18
ASHRAE 62.1-2004Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2004 | Food and Beverage Service | Bars, cocktail lounges | 7.5 | 0.18
ASHRAE 62.1-2007Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2007 | Food and Beverage Service | Restaurant dining rooms | 7.5 | 0.18
ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | 7.5 | 0.18
ASHRAE 62.1-2007Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2007 | Food and Beverage Service | Bars, cocktail lounges | 7.5 | 0.18
ASHRAE 62.1-1999Garages, Repair, Service StationsEnclosed parking garage | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Enclosed parking garage | 0 | 1.5
ASHRAE 62.1-1999Garages, Repair, Service StationsAuto repair rooms | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Auto repair rooms | 0 | 1.5
ASHRAE 62.1-2004GeneralConference/meeting | ASHRAE 62.1-2004 | General | Conference/meeting | 5 | 0.06
ASHRAE 62.1-2004GeneralCorridors | ASHRAE 62.1-2004 | General | Corridors |  | 0.06
ASHRAE 62.1-2007GeneralConference/meeting | ASHRAE 62.1-2007 | General | Conference/meeting | 5 | 0.06
ASHRAE 62.1-2007GeneralCorridors | ASHRAE 62.1-2007 | General | Corridors |  | 0.06
ASHRAE 62.1-2004GeneralStorage rooms | ASHRAE 62.1-2004 | General | Storage rooms |  | 0.12 |  | B
ASHRAE 62.1-2007GeneralStorage rooms | ASHRAE 62.1-2007 | General | Storage rooms |  | 0.12 |  | B
GGHC v2.2Health CareBathroom/ Public | GGHC v2.2 | Health Care | Bathroom/ Public |  | 0.15
GGHC v2.2Health CareBedpan Room | GGHC v2.2 | Health Care | Bedpan Room |  | 0.15
GGHC v2.2Health CareLobby | GGHC v2.2 | Health Care | Lobby |  | 0.15
GGHC v2.2Health CareLockers | GGHC v2.2 | Health Care | Lockers |  | 0.15
GGHC v2.2Health CareMechanical Equipment Room | GGHC v2.2 | Health Care | Mechanical Equipment Room |  | 0.15
GGHC v2.2Health CareMedical Records | GGHC v2.2 | Health Care | Medical Records |  | 0.15
GGHC v2.2Health CareNursing Stations- General | GGHC v2.2 | Health Care | Nursing Stations- General |  | 0.15
GGHC v2.2Health CareStairways | GGHC v2.2 | Health Care | Stairways |  | 0.15
GGHC v2.2Health CareWaiting Areas/Lounges | GGHC v2.2 | Health Care | Waiting Areas/Lounges |  | 0.15
GGHC v2.2Health CareAngiographic-All Other Types | GGHC v2.2 | Health Care | Angiographic-All Other Types |  | 0.3
GGHC v2.2Health CareAutopsy | GGHC v2.2 | Health Care | Autopsy |  | 0.3
GGHC v2.2Health CareCast Room | GGHC v2.2 | Health Care | Cast Room |  | 0.3
GGHC v2.2Health CareClean Linen Storage | GGHC v2.2 | Health Care | Clean Linen Storage |  | 0.3
GGHC v2.2Health CareClean Utility / Workroom | GGHC v2.2 | Health Care | Clean Utility / Workroom |  | 0.3
GGHC v2.2Health CareCorridors | GGHC v2.2 | Health Care | Corridors |  | 0.3
GGHC v2.2Health CareDarkroom | GGHC v2.2 | Health Care | Darkroom |  | 0.3
GGHC v2.2Health CareDecontamination | GGHC v2.2 | Health Care | Decontamination |  | 0.3
GGHC v2.2Health CareDietary Day Storage | GGHC v2.2 | Health Care | Dietary Day Storage |  | 0.3
GGHC v2.2Health CareDishwashing | GGHC v2.2 | Health Care | Dishwashing |  | 0.3
GGHC v2.2Health CareEndoscopy | GGHC v2.2 | Health Care | Endoscopy |  | 0.3
GGHC v2.2Health CareHistology | GGHC v2.2 | Health Care | Histology |  | 0.3
GGHC v2.2Health CareIsolation | GGHC v2.2 | Health Care | Isolation |  | 0.3
GGHC v2.2Health CareKitchen, Food Preparation | GGHC v2.2 | Health Care | Kitchen, Food Preparation |  | 0.3
GGHC v2.2Health CareLabor/ Delivery/Recovery | GGHC v2.2 | Health Care | Labor/ Delivery/Recovery |  | 0.3
GGHC v2.2Health CareL / D / R / Post Partum | GGHC v2.2 | Health Care | L / D / R / Post Partum |  | 0.3
GGHC v2.2Health CareLaboratory | GGHC v2.2 | Health Care | Laboratory |  | 0.3
GGHC v2.2Health CareLinen Storage, Clean | GGHC v2.2 | Health Care | Linen Storage, Clean |  | 0.3
GGHC v2.2Health CareMammography | GGHC v2.2 | Health Care | Mammography |  | 0.3
GGHC v2.2Health CareNuclear Medicine, Hot Lab | GGHC v2.2 | Health Care | Nuclear Medicine, Hot Lab |  | 0.3
GGHC v2.2Health CarePathology | GGHC v2.2 | Health Care | Pathology |  | 0.3
GGHC v2.2Health CarePatient Room | GGHC v2.2 | Health Care | Patient Room |  | 0.3
GGHC v2.2Health CarePharmacy / Medicine Room | GGHC v2.2 | Health Care | Pharmacy / Medicine Room |  | 0.3
GGHC v2.2Health CarePhysical Therapy and Hydrotherapy | GGHC v2.2 | Health Care | Physical Therapy and Hydrotherapy |  | 0.3
GGHC v2.2Health CareRecovery | GGHC v2.2 | Health Care | Recovery |  | 0.3
GGHC v2.2Health CareScrub Up Area, Surgical Corridor | GGHC v2.2 | Health Care | Scrub Up Area, Surgical Corridor |  | 0.3
GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic |  | 0.3
GGHC v2.2Health CareSub-Sterile | GGHC v2.2 | Health Care | Sub-Sterile |  | 0.3
GGHC v2.2Health CareSurgical Supply | GGHC v2.2 | Health Care | Surgical Supply |  | 0.3
GGHC v2.2Health CareTreatment / Examination | GGHC v2.2 | Health Care | Treatment / Examination |  | 0.3
GGHC v2.2Health CareUnsterile Supply | GGHC v2.2 | Health Care | Unsterile Supply |  | 0.3
GGHC v2.2Health CareX-ray, Diagnostic and Treatment | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment |  | 0.3
GGHC v2.2Health CareNursery, General | GGHC v2.2 | Health Care | Nursery, General |  | 0.45
GGHC v2.2Health CareNursery, Exam | GGHC v2.2 | Health Care | Nursery, Exam |  | 0.45
GGHC v2.2Health CareConference Rooms | GGHC v2.2 | Health Care | Conference Rooms |  | 0.5
GGHC v2.2Health CareAngiographic-Heart Only | GGHC v2.2 | Health Care | Angiographic-Heart Only |  | 0.75
GGHC v2.2Health CareCystoscopy | GGHC v2.2 | Health Care | Cystoscopy |  | 0.75
GGHC v2.2Health CareDelivery Room | GGHC v2.2 | Health Care | Delivery Room |  | 0.75
GGHC v2.2Health CareOperating Room | GGHC v2.2 | Health Care | Operating Room |  | 0.75
GGHC v2.2Health CareSpecial Procedure Room, Invasive | GGHC v2.2 | Health Care | Special Procedure Room, Invasive |  | 0.75
GGHC v2.2Health CareTrauma | GGHC v2.2 | Health Care | Trauma |  | 0.75
GGHC v2.2Health CareAnesthesia Storage | GGHC v2.2 | Health Care | Anesthesia Storage |  | 1.2
GGHC v2.2Health CareDining Room | GGHC v2.2 | Health Care | Dining Room |  | 1.5
GGHC v2.2Health CareJanitors Closet / Utility | GGHC v2.2 | Health Care | Janitors Closet / Utility |  | 1.5
GGHC v2.2Health CareSoiled Linen, Sorting | GGHC v2.2 | Health Care | Soiled Linen, Sorting |  | 1.5
GGHC v2.2Health CareSterilizer Room | GGHC v2.2 | Health Care | Sterilizer Room |  | 1.5
GGHC v2.2Health CareTrash Chute Room | GGHC v2.2 | Health Care | Trash Chute Room |  | 1.5
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 25 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 15 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 30 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 15 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 15 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 0 | 0.5
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 25 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 30 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms |  | 0.5 |  | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 15
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 25 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 30 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms |  | 0.5 |  | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 15
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBedrooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Bedrooms | 0 | -9999 |  | 30 cfm/room, 15 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLiving rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Living rooms | 0 | -9999 |  | 30 cfm/room, 15 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBaths | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Baths | 0 | -9999 |  | 35 cfm/room, 18 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | 15 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | 20 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesAssembly rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Assembly rooms | 15 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | 15 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesGambling casinos | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Gambling casinos | 30 | 0
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 5 | 0.06
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 5 | 0.06
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 7.5 | 0.06
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 5 | 0.06
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 5 | 0.06
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 5 | 0.06
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 7.5 | 0.06
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2004 | Miscellaneous Spaces | Bank vaults/safe deposit | 5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Computer (not printing) | 5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2004 | Miscellaneous Spaces | Transportation waiting | 7.5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesWarehouses | ASHRAE 62.1-2004 | Miscellaneous Spaces | Warehouses |  | 0.06 |  | B
ASHRAE 62.1-2007Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2007 | Miscellaneous Spaces | Bank vaults/safe deposit | 5 | 0.06
ASHRAE 62.1-2007Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Computer (not printing) | 5 | 0.06
ASHRAE 62.1-2007Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2007 | Miscellaneous Spaces | Transportation waiting | 7.5 | 0.06
ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses |  | 0.06 |  | B
ASHRAE 62.1-2004Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2004 | Miscellaneous Spaces | Photo studios | 5 | 0.12
ASHRAE 62.1-2004Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2004 | Miscellaneous Spaces | Shipping/receiving |  | 0.12 |  | B
ASHRAE 62.1-2007Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2007 | Miscellaneous Spaces | Photo studios | 5 | 0.12
ASHRAE 62.1-2007Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2007 | Miscellaneous Spaces | Shipping/receiving |  | 0.12 |  | B
ASHRAE 62.1-2004Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Pharmacy (prep. area) | 5 | 0.18
ASHRAE 62.1-2007Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Pharmacy (prep. area) | 5 | 0.18
AIA 2001NursingPatient Room | AIA 2001 | Nursing | Patient Room |  |  | 2
AIA 2001NursingNewborn Nursery Suite | AIA 2001 | Nursing | Newborn Nursery Suite |  |  | 2
AIA 2001NursingProtective Environment Room | AIA 2001 | Nursing | Protective Environment Room |  |  | 2
AIA 2001NursingAirborne Infection Isolation Room | AIA 2001 | Nursing | Airborne Infection Isolation Room |  |  | 2
AIA 2001NursingLabor/Delivery/Recovery | AIA 2001 | Nursing | Labor/Delivery/Recovery |  |  | 2
AIA 2001NursingLabor/Delivery/Recovery/Postpartum | AIA 2001 | Nursing | Labor/Delivery/Recovery/Postpartum |  |  | 2
ASHRAE 62.1-2004Office BuildingsOffice space | ASHRAE 62.1-2004 | Office Buildings | Office space | 5 | 0.06
ASHRAE 62.1-2004Office BuildingsReception areas | ASHRAE 62.1-2004 | Office Buildings | Reception areas | 5 | 0.06
ASHRAE 62.1-2004Office BuildingsTelephone/data entry | ASHRAE 62.1-2004 | Office Buildings | Telephone/data entry | 5 | 0.06
ASHRAE 62.1-2004Office BuildingsMain entry lobbies | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsOffice space | ASHRAE 62.1-2007 | Office Buildings | Office space | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsReception areas | ASHRAE 62.1-2007 | Office Buildings | Reception areas | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsTelephone/data entry | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsMain entry lobbies | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | 5 | 0.06
ASHRAE 62.1-1999OfficesOffice space | ASHRAE 62.1-1999 | Offices | Office space | 20 | 0
ASHRAE 62.1-1999OfficesReception areas | ASHRAE 62.1-1999 | Offices | Reception areas | 15 | 0
ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | 20 | 0
ASHRAE 62.1-1999OfficesConference rooms | ASHRAE 62.1-1999 | Offices | Conference rooms | 20 | 0
ASHRAE 62.1-2004Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2004 | Public Assembly Spaces | Auditorium seating area | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2004 | Public Assembly Spaces | Places of religious worship | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesCourtrooms | ASHRAE 62.1-2004 | Public Assembly Spaces | Courtrooms | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2004 | Public Assembly Spaces | Legislative chambers | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesLobbies | ASHRAE 62.1-2004 | Public Assembly Spaces | Lobbies | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums/galleries | 7.5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2007 | Public Assembly Spaces | Auditorium seating area | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2007 | Public Assembly Spaces | Places of religious worship | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesCourtrooms | ASHRAE 62.1-2007 | Public Assembly Spaces | Courtrooms | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2007 | Public Assembly Spaces | Legislative chambers | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesLobbies | ASHRAE 62.1-2007 | Public Assembly Spaces | Lobbies | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums/galleries | 7.5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesLibraries | ASHRAE 62.1-2004 | Public Assembly Spaces | Libraries | 5 | 0.12
ASHRAE 62.1-2004Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums (children’s) | 7.5 | 0.12
ASHRAE 62.1-2007Public Assembly SpacesLibraries | ASHRAE 62.1-2007 | Public Assembly Spaces | Libraries | 5 | 0.12
ASHRAE 62.1-2007Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums (children’s) | 7.5 | 0.12
ASHRAE 62.1-1999Public SpacesSmoking lounge | ASHRAE 62.1-1999 | Public Spaces | Smoking lounge | 60 | 0
ASHRAE 62.1-1999Public SpacesCorridors and utilities | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | 0 | 0.05
ASHRAE 62.1-1999Public SpacesLocker and dressing rooms | ASHRAE 62.1-1999 | Public Spaces | Locker and dressing rooms | 0 | 0.5
ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | 0 | 0.96 |  | 50 cfm/wc or urinal, 25 L/s wc or urinal
ASHRAE 62.1-1999Public SpacesElevators | ASHRAE 62.1-1999 | Public Spaces | Elevators | 0 | 1
ASHRAE 62.1-2004RetailMall common areas | ASHRAE 62.1-2004 | Retail | Mall common areas | 7.5 | 0.06
ASHRAE 62.1-2004RetailBarber shop | ASHRAE 62.1-2004 | Retail | Barber shop | 7.5 | 0.06
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 7.5 | 0.06
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 7.5 | 0.06
ASHRAE 62.1-2004RetailCoinoperated laundries | ASHRAE 62.1-2004 | Retail | Coinoperated laundries | 7.5 | 0.06
ASHRAE 62.1-2007RetailMall common areas | ASHRAE 62.1-2007 | Retail | Mall common areas | 7.5 | 0.06
ASHRAE 62.1-2007RetailBarber shop | ASHRAE 62.1-2007 | Retail | Barber shop | 7.5 | 0.06
ASHRAE 62.1-2007RetailSupermarket | ASHRAE 62.1-2007 | Retail | Supermarket | 7.5 | 0.06
ASHRAE 62.1-2007RetailCoinoperated laundries | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | 7.5 | 0.06
ASHRAE 62.1-2004RetailGeneral Sales | ASHRAE 62.1-2004 | Retail | General Sales | 7.5 | 0.12
ASHRAE 62.1-2004RetailBeauty and nail salons | ASHRAE 62.1-2004 | Retail | Beauty and nail salons | 20 | 0.12
ASHRAE 62.1-2007RetailGeneral Sales | ASHRAE 62.1-2007 | Retail | General Sales | 7.5 | 0.12
ASHRAE 62.1-2007RetailBeauty and nail salons | ASHRAE 62.1-2007 | Retail | Beauty and nail salons | 20 | 0.12
ASHRAE 62.1-2004RetailPet shops (animal areas) | ASHRAE 62.1-2004 | Retail | Pet shops (animal areas) | 7.5 | 0.18
ASHRAE 62.1-2007RetailPet shops (animal areas) | ASHRAE 62.1-2007 | Retail | Pet shops (animal areas) | 7.5 | 0.18
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsSmoking lounge | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Smoking lounge | 60 | 0
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | 0 | 0.05
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | 0 | 0.15
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | 0 | 0.15
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsUpper floors | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Upper floors | 0 | 0.2
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsDressing rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Dressing rooms | 0 | 0.2
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsMalls and arcades | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Malls and arcades | 0 | 0.2
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | 0 | 0.3
ASHRAE 62.1-1999Specialty ShopsBarber | ASHRAE 62.1-1999 | Specialty Shops | Barber | 15 | 0
ASHRAE 62.1-1999Specialty ShopsBeauty | ASHRAE 62.1-1999 | Specialty Shops | Beauty | 25 | 0
ASHRAE 62.1-1999Specialty ShopsReducing salons | ASHRAE 62.1-1999 | Specialty Shops | Reducing salons | 15 | 0
ASHRAE 62.1-1999Specialty ShopsFlorists | ASHRAE 62.1-1999 | Specialty Shops | Florists | 15 | 0
ASHRAE 62.1-1999Specialty ShopsHardware, drugs, fabric | ASHRAE 62.1-1999 | Specialty Shops | Hardware, drugs, fabric | 15 | 0
ASHRAE 62.1-1999Specialty ShopsSupermarket | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | 15 | 0
ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | 0 | 0.3
ASHRAE 62.1-1999Specialty ShopsPet shops | ASHRAE 62.1-1999 | Specialty Shops | Pet shops | 0 | 1
ASHRAE 62.1-1999Sports and AmusementSpectator areas | ASHRAE 62.1-1999 | Sports and Amusement | Spectator areas | 15 | 0
ASHRAE 62.1-1999Sports and AmusementGame rooms | ASHRAE 62.1-1999 | Sports and Amusement | Game rooms | 25 | 0
ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | 20 | 0
ASHRAE 62.1-1999Sports and AmusementBallrooms and discos | ASHRAE 62.1-1999 | Sports and Amusement | Ballrooms and discos | 25 | 0
ASHRAE 62.1-1999Sports and AmusementBowling alleys (seating areas) | ASHRAE 62.1-1999 | Sports and Amusement | Bowling alleys (seating areas) | 25 | 0
ASHRAE 62.1-1999Sports and AmusementIce arenas (playing areas) | ASHRAE 62.1-1999 | Sports and Amusement | Ice arenas (playing areas) | 0 | 0.5 |  | Higher may be needed if internal combustion engines are operated for maintenance
ASHRAE 62.1-1999Sports and AmusementSwimming pools (pool and deck areas) | ASHRAE 62.1-1999 | Sports and Amusement | Swimming pools (pool and deck areas) | 0 | 0.5 |  | Higher may be needed for humidity control
ASHRAE 62.1-2004Sports and EntertainmentSpectator areas | ASHRAE 62.1-2004 | Sports and Entertainment | Spectator areas | 7.5 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2004 | Sports and Entertainment | Disco/dance floors | 20 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/aerobics room | 20 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/weight rooms | 20 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentStages, studios | ASHRAE 62.1-2004 | Sports and Entertainment | Stages, studios | 10 | 0.06 |  | D
ASHRAE 62.1-2007Sports and EntertainmentSpectator areas | ASHRAE 62.1-2007 | Sports and Entertainment | Spectator areas | 7.5 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2007 | Sports and Entertainment | Disco/dance floors | 20 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/aerobics room | 20 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/weight rooms | 20 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentStages, studios | ASHRAE 62.1-2007 | Sports and Entertainment | Stages, studios | 10 | 0.06 |  | D
ASHRAE 62.1-2004Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2004 | Sports and Entertainment | Bowling alley (seating) | 10 | 0.12
ASHRAE 62.1-2007Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2007 | Sports and Entertainment | Bowling alley (seating) | 10 | 0.12
ASHRAE 62.1-2004Sports and EntertainmentGambling casinos | ASHRAE 62.1-2004 | Sports and Entertainment | Gambling casinos | 7.5 | 0.18
ASHRAE 62.1-2004Sports and EntertainmentGame arcades | ASHRAE 62.1-2004 | Sports and Entertainment | Game arcades | 7.5 | 0.18
ASHRAE 62.1-2007Sports and EntertainmentGambling casinos | ASHRAE 62.1-2007 | Sports and Entertainment | Gambling casinos | 7.5 | 0.18
ASHRAE 62.1-2007Sports and EntertainmentGame arcades | ASHRAE 62.1-2007 | Sports and Entertainment | Game arcades | 7.5 | 0.18
ASHRAE 62.1-2004Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Sports arena (play area) |  | 0.3
ASHRAE 62.1-2004Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Gym, stadium (play area) |  | 0.3
ASHRAE 62.1-2007Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Sports arena (play area) |  | 0.3
ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) |  | 0.3
ASHRAE 62.1-2004Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2004 | Sports and Entertainment | Swimming (pool & deck) |  | 0.48 |  | C
ASHRAE 62.1-2007Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2007 | Sports and Entertainment | Swimming (pool & deck) |  | 0.48 |  | C
AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms |  |  | 3
AIA 2001Surgery and Critical CareDelivery Room | AIA 2001 | Surgery and Critical Care | Delivery Room |  |  | 3
AIA 2001Surgery and Critical CareRecovery Room | AIA 2001 | Surgery and Critical Care | Recovery Room |  |  | 2
AIA 2001Surgery and Critical CareCritical and Intensive Care | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care |  |  | 2
AIA 2001Surgery and Critical CareNewborn Intensive Care | AIA 2001 | Surgery and Critical Care | Newborn Intensive Care |  |  | 2
AIA 2001Surgery and Critical CareTrauma Room | AIA 2001 | Surgery and Critical Care | Trauma Room |  |  | 3
AIA 2001Surgery and Critical CareEndoscopy | AIA 2001 | Surgery and Critical Care | Endoscopy |  |  | 2
AIA 2001Surgery and Critical CareBronchoscopy | AIA 2001 | Surgery and Critical Care | Bronchoscopy |  |  | 2
AIA 2001Surgery and Critical CareER Waiting Room | AIA 2001 | Surgery and Critical Care | ER Waiting Room |  |  | 2
AIA 2001Surgery and Critical CareTriage | AIA 2001 | Surgery and Critical Care | Triage |  |  | 2
AIA 2001Surgery and Critical CareRadiology Waiting Rooms | AIA 2001 | Surgery and Critical Care | Radiology Waiting Rooms |  |  | 2
AIA 2001Surgery and Critical CareProcedure Room | AIA 2001 | Surgery and Critical Care | Procedure Room |  |  | 3
ASHRAE 62.1-1999TheatersTicket booths | ASHRAE 62.1-1999 | Theaters | Ticket booths | 20 | 0
ASHRAE 62.1-1999TheatersLobbies | ASHRAE 62.1-1999 | Theaters | Lobbies | 20 | 0
ASHRAE 62.1-1999TheatersAuditorium | ASHRAE 62.1-1999 | Theaters | Auditorium | 15 | 0
ASHRAE 62.1-1999TheatersStages, studios | ASHRAE 62.1-1999 | Theaters | Stages, studios | 15 | 0
ASHRAE 62.1-1999TransportationWaiting rooms | ASHRAE 62.1-1999 | Transportation | Waiting rooms | 15 | 0
ASHRAE 62.1-1999TransportationPlatforms | ASHRAE 62.1-1999 | Transportation | Platforms | 15 | 0
ASHRAE 62.1-1999TransportationVehicles | ASHRAE 62.1-1999 | Transportation | Vehicles | 15 | 0
ASHRAE 62.1-1999WorkroomsMeat processing | ASHRAE 62.1-1999 | Workrooms | Meat processing | 15 | 0
ASHRAE 62.1-1999WorkroomsPhoto studios | ASHRAE 62.1-1999 | Workrooms | Photo studios | 15 | 0
ASHRAE 62.1-1999WorkroomsPharmacy | ASHRAE 62.1-1999 | Workrooms | Pharmacy | 15 | 0
ASHRAE 62.1-1999WorkroomsBank vaults | ASHRAE 62.1-1999 | Workrooms | Bank vaults | 15 | 0
ASHRAE 62.1-1999WorkroomsDarkrooms | ASHRAE 62.1-1999 | Workrooms | Darkrooms | 0 | 0.5
ASHRAE 62.1-1999WorkroomsDuplicating, printing | ASHRAE 62.1-1999 | Workrooms | Duplicating, printing | 0 | 0.5

## Occupancy
Each row represents typical design occupancy for a particular space type in a particular standard. Values may be referenced on Space Types tab.
occupancy
VlookupColumn | Ventilation Standard | Primary Space Type | Secondary Space Type | people/1000 ft^2 | Notes
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial laundry | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial laundry | 10
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial dry cleaner | 30
ASHRAE 62.1-1999Dry Cleaners, LaundriesStorage, pick up | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Storage, pick up | 30
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated laundries | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated laundries | 20
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated dry cleaner | 20
ASHRAE 62.1-1999Food and Beverage ServiceDining rooms | ASHRAE 62.1-1999 | Food and Beverage Service | Dining rooms | 70
ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | 100
ASHRAE 62.1-1999Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-1999 | Food and Beverage Service | Bars, cocktail lounges | 100
ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | 20 | Exhaust >= 1.5 cfm/ft2, 7.5 L/s m2
ASHRAE 62.1-1999Garages, Repair, Service StationsEnclosed parking garage | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Enclosed parking garage | 0
ASHRAE 62.1-1999Garages, Repair, Service StationsAuto repair rooms | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Auto repair rooms | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBedrooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Bedrooms | 0 | 30 cfm/room, 15 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLiving rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Living rooms | 0 | 30 cfm/room, 15 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBaths | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Baths | 0 | 35 cfm/room, 18 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | 30
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | 50
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesAssembly rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Assembly rooms | 120
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | 20
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesGambling casinos | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Gambling casinos | 120
ASHRAE 62.1-1999OfficesOffice space | ASHRAE 62.1-1999 | Offices | Office space | 7
ASHRAE 62.1-1999OfficesReception areas | ASHRAE 62.1-1999 | Offices | Reception areas | 60
ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | 60
ASHRAE 62.1-1999OfficesConference rooms | ASHRAE 62.1-1999 | Offices | Conference rooms | 50
ASHRAE 62.1-1999Public SpacesCorridors and utilities | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | 0
ASHRAE 62.1-1999Public SpacesPublic restrooms | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | 0 | (Assume 12 toilet/625 ft^2) 50 cfm/wc or urinal, 25 L/s wc or urinal
ASHRAE 62.1-1999Public SpacesLocker and dressing rooms | ASHRAE 62.1-1999 | Public Spaces | Locker and dressing rooms | 0
ASHRAE 62.1-1999Public SpacesSmoking lounge | ASHRAE 62.1-1999 | Public Spaces | Smoking lounge | 70
ASHRAE 62.1-1999Public SpacesElevators | ASHRAE 62.1-1999 | Public Spaces | Elevators | 0
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | 30
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsUpper floors | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Upper floors | 20
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | 15
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsDressing rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Dressing rooms | 0
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsMalls and arcades | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Malls and arcades | 20
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | 10
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | 5
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsSmoking lounge | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Smoking lounge | 70
ASHRAE 62.1-1999Specialty ShopsBarber | ASHRAE 62.1-1999 | Specialty Shops | Barber | 25
ASHRAE 62.1-1999Specialty ShopsBeauty | ASHRAE 62.1-1999 | Specialty Shops | Beauty | 25
ASHRAE 62.1-1999Specialty ShopsReducing salons | ASHRAE 62.1-1999 | Specialty Shops | Reducing salons | 20
ASHRAE 62.1-1999Specialty ShopsFlorists | ASHRAE 62.1-1999 | Specialty Shops | Florists | 8
ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | 0
ASHRAE 62.1-1999Specialty ShopsHardware, drugs, fabric | ASHRAE 62.1-1999 | Specialty Shops | Hardware, drugs, fabric | 8
ASHRAE 62.1-1999Specialty ShopsSupermarket | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | 8
ASHRAE 62.1-1999Specialty ShopsPet shops | ASHRAE 62.1-1999 | Specialty Shops | Pet shops | 0
ASHRAE 62.1-1999Sports and AmusementSpectator areas | ASHRAE 62.1-1999 | Sports and Amusement | Spectator areas | 150
ASHRAE 62.1-1999Sports and AmusementGame rooms | ASHRAE 62.1-1999 | Sports and Amusement | Game rooms | 70
ASHRAE 62.1-1999Sports and AmusementIce arenas (playing areas) | ASHRAE 62.1-1999 | Sports and Amusement | Ice arenas (playing areas) | 0 | Higher may be needed if internal combustion engines are operated for maintenance
ASHRAE 62.1-1999Sports and AmusementSwimming pools (pool and deck areas) | ASHRAE 62.1-1999 | Sports and Amusement | Swimming pools (pool and deck areas) | 0 | Higher may be needed for humidity control
ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | 30
ASHRAE 62.1-1999Sports and AmusementBallrooms and discos | ASHRAE 62.1-1999 | Sports and Amusement | Ballrooms and discos | 100
ASHRAE 62.1-1999Sports and AmusementBowling alleys (seating areas) | ASHRAE 62.1-1999 | Sports and Amusement | Bowling alleys (seating areas) | 70
ASHRAE 62.1-1999TheatersTicket booths | ASHRAE 62.1-1999 | Theaters | Ticket booths | 60
ASHRAE 62.1-1999TheatersLobbies | ASHRAE 62.1-1999 | Theaters | Lobbies | 150
ASHRAE 62.1-1999TheatersAuditorium | ASHRAE 62.1-1999 | Theaters | Auditorium | 150
ASHRAE 62.1-1999TheatersStages, studios | ASHRAE 62.1-1999 | Theaters | Stages, studios | 70
ASHRAE 62.1-1999TransportationWaiting rooms | ASHRAE 62.1-1999 | Transportation | Waiting rooms | 100
ASHRAE 62.1-1999TransportationPlatforms | ASHRAE 62.1-1999 | Transportation | Platforms | 100
ASHRAE 62.1-1999TransportationVehicles | ASHRAE 62.1-1999 | Transportation | Vehicles | 150
ASHRAE 62.1-1999WorkroomsMeat processing | ASHRAE 62.1-1999 | Workrooms | Meat processing | 10
ASHRAE 62.1-1999WorkroomsPhoto studios | ASHRAE 62.1-1999 | Workrooms | Photo studios | 10
ASHRAE 62.1-1999WorkroomsDarkrooms | ASHRAE 62.1-1999 | Workrooms | Darkrooms | 10
ASHRAE 62.1-1999WorkroomsPharmacy | ASHRAE 62.1-1999 | Workrooms | Pharmacy | 20
ASHRAE 62.1-1999WorkroomsBank vaults | ASHRAE 62.1-1999 | Workrooms | Bank vaults | 5
ASHRAE 62.1-1999WorkroomsDuplicating, printing | ASHRAE 62.1-1999 | Workrooms | Duplicating, printing | 0
ASHRAE 62.1-1999EducationClassroom | ASHRAE 62.1-1999 | Education | Classroom | 50
ASHRAE 62.1-1999EducationLaboratories | ASHRAE 62.1-1999 | Education | Laboratories | 30
ASHRAE 62.1-1999EducationTraining shop | ASHRAE 62.1-1999 | Education | Training shop | 30
ASHRAE 62.1-1999EducationMusic rooms | ASHRAE 62.1-1999 | Education | Music rooms | 50
ASHRAE 62.1-1999EducationLibraries | ASHRAE 62.1-1999 | Education | Libraries | 20
ASHRAE 62.1-1999EducationLocker rooms | ASHRAE 62.1-1999 | Education | Locker rooms | 0
ASHRAE 62.1-1999EducationCorridors | ASHRAE 62.1-1999 | Education | Corridors | 0
ASHRAE 62.1-1999EducationAuditorium | ASHRAE 62.1-1999 | Education | Auditorium | 150
ASHRAE 62.1-1999EducationSmoking lounges | ASHRAE 62.1-1999 | Education | Smoking lounges | 70
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 10
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 20
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 20
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 20
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 20
ASHRAE 62.1-1999Correctional FacilitiesCell | ASHRAE 62.1-1999 | Correctional Facilities | Cell | 20
ASHRAE 62.1-1999Correctional FacilitiesDining halls | ASHRAE 62.1-1999 | Correctional Facilities | Dining halls | 100
ASHRAE 62.1-1999Correctional FacilitiesGuard stations | ASHRAE 62.1-1999 | Correctional Facilities | Guard stations | 40
ASHRAE 62.1-2004Correctional FacilitiesCell | ASHRAE 62.1-2004 | Correctional Facilities | Cell | 25
ASHRAE 62.1-2004Correctional FacilitiesDay room | ASHRAE 62.1-2004 | Correctional Facilities | Day room | 30
ASHRAE 62.1-2004Correctional FacilitiesGuard stations | ASHRAE 62.1-2004 | Correctional Facilities | Guard stations | 15
ASHRAE 62.1-2004Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2004 | Correctional Facilities | Booking/waiting | 50
ASHRAE 62.1-2004Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2004 | Educational Facilities | Daycare (through age 4) | 25
ASHRAE 62.1-2004Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (ages 5-8) | 25
ASHRAE 62.1-2004Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (age 9 plus) | 35
ASHRAE 62.1-2004Educational FacilitiesLecture classroom | ASHRAE 62.1-2004 | Educational Facilities | Lecture classroom | 65
ASHRAE 62.1-2004Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2004 | Educational Facilities | Lecture hall (fixed seats) | 150
ASHRAE 62.1-2004Educational FacilitiesArt classroom | ASHRAE 62.1-2004 | Educational Facilities | Art classroom | 20
ASHRAE 62.1-2004Educational FacilitiesScience laboratories | ASHRAE 62.1-2004 | Educational Facilities | Science laboratories | 25 | E
ASHRAE 62.1-2004Educational FacilitiesWood/metal shop | ASHRAE 62.1-2004 | Educational Facilities | Wood/metal shop | 20
ASHRAE 62.1-2004Educational FacilitiesComputer lab | ASHRAE 62.1-2004 | Educational Facilities | Computer lab | 25
ASHRAE 62.1-2004Educational FacilitiesMedia center | ASHRAE 62.1-2004 | Educational Facilities | Media center | 25 | A
ASHRAE 62.1-2004Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2004 | Educational Facilities | Music/theater/dance | 35
ASHRAE 62.1-2004Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2004 | Educational Facilities | Multiuse assembly | 100
ASHRAE 62.1-2004Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2004 | Food and Beverage Service | Restaurant dining rooms | 70
ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | 100
ASHRAE 62.1-2004Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2004 | Food and Beverage Service | Bars, cocktail lounges | 100
ASHRAE 62.1-2004GeneralConference/meeting | ASHRAE 62.1-2004 | General | Conference/meeting | 50
ASHRAE 62.1-2004GeneralCorridors | ASHRAE 62.1-2004 | General | Corridors | 0
ASHRAE 62.1-2004GeneralStorage rooms | ASHRAE 62.1-2004 | General | Storage rooms | 0 | B
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 10
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 20
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 30
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 120
ASHRAE 62.1-2004Office BuildingsOffice space | ASHRAE 62.1-2004 | Office Buildings | Office space | 5
ASHRAE 62.1-2004Office BuildingsReception areas | ASHRAE 62.1-2004 | Office Buildings | Reception areas | 30
ASHRAE 62.1-2004Office BuildingsTelephone/data entry | ASHRAE 62.1-2004 | Office Buildings | Telephone/data entry | 60
ASHRAE 62.1-2004Office BuildingsMain entry lobbies | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | 10
ASHRAE 62.1-2004Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2004 | Miscellaneous Spaces | Bank vaults/safe deposit | 5
ASHRAE 62.1-2004Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Computer (not printing) | 4
ASHRAE 62.1-2004Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Pharmacy (prep. area) | 10
ASHRAE 62.1-2004Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2004 | Miscellaneous Spaces | Photo studios | 10
ASHRAE 62.1-2004Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2004 | Miscellaneous Spaces | Shipping/receiving | 0 | B
ASHRAE 62.1-2004Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2004 | Miscellaneous Spaces | Transportation waiting | 100
ASHRAE 62.1-2004Miscellaneous SpacesWarehouses | ASHRAE 62.1-2004 | Miscellaneous Spaces | Warehouses | 0 | B
ASHRAE 62.1-2004Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2004 | Public Assembly Spaces | Auditorium seating area | 150
ASHRAE 62.1-2004Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2004 | Public Assembly Spaces | Places of religious worship | 120
ASHRAE 62.1-2004Public Assembly SpacesCourtrooms | ASHRAE 62.1-2004 | Public Assembly Spaces | Courtrooms | 70
ASHRAE 62.1-2004Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2004 | Public Assembly Spaces | Legislative chambers | 50
ASHRAE 62.1-2004Public Assembly SpacesLibraries | ASHRAE 62.1-2004 | Public Assembly Spaces | Libraries | 10
ASHRAE 62.1-2004Public Assembly SpacesLobbies | ASHRAE 62.1-2004 | Public Assembly Spaces | Lobbies | 150
ASHRAE 62.1-2004Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums (children’s) | 40
ASHRAE 62.1-2004Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums/galleries | 40
ASHRAE 62.1-2004RetailGeneral Sales | ASHRAE 62.1-2004 | Retail | General Sales | 15
ASHRAE 62.1-2004RetailMall common areas | ASHRAE 62.1-2004 | Retail | Mall common areas | 40
ASHRAE 62.1-2004RetailBarber shop | ASHRAE 62.1-2004 | Retail | Barber shop | 25
ASHRAE 62.1-2004RetailBeauty and nail salons | ASHRAE 62.1-2004 | Retail | Beauty and nail salons | 25
ASHRAE 62.1-2004RetailPet shops (animal areas) | ASHRAE 62.1-2004 | Retail | Pet shops (animal areas) | 10
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 8
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 8
ASHRAE 62.1-2004RetailCoinoperated laundries | ASHRAE 62.1-2004 | Retail | Coinoperated laundries | 20
ASHRAE 62.1-2004Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Sports arena (play area) | 0
ASHRAE 62.1-2004Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Gym, stadium (play area) | 30
ASHRAE 62.1-2004Sports and EntertainmentSpectator areas | ASHRAE 62.1-2004 | Sports and Entertainment | Spectator areas | 150
ASHRAE 62.1-2004Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2004 | Sports and Entertainment | Swimming (pool & deck) | 0 | C
ASHRAE 62.1-2004Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2004 | Sports and Entertainment | Disco/dance floors | 100
ASHRAE 62.1-2004Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/aerobics room | 40
ASHRAE 62.1-2004Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/weight rooms | 10
ASHRAE 62.1-2004Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2004 | Sports and Entertainment | Bowling alley (seating) | 40
ASHRAE 62.1-2004Sports and EntertainmentGambling casinos | ASHRAE 62.1-2004 | Sports and Entertainment | Gambling casinos | 120
ASHRAE 62.1-2004Sports and EntertainmentGame arcades | ASHRAE 62.1-2004 | Sports and Entertainment | Game arcades | 20
ASHRAE 62.1-2004Sports and EntertainmentStages, studios | ASHRAE 62.1-2004 | Sports and Entertainment | Stages, studios | 70 | D
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 10 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 20 | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 20
ASHRAE 62.1-2007Correctional FacilitiesCell | ASHRAE 62.1-2007 | Correctional Facilities | Cell | 25
ASHRAE 62.1-2007Correctional FacilitiesDay room | ASHRAE 62.1-2007 | Correctional Facilities | Day room | 30
ASHRAE 62.1-2007Correctional FacilitiesGuard stations | ASHRAE 62.1-2007 | Correctional Facilities | Guard stations | 15
ASHRAE 62.1-2007Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2007 | Correctional Facilities | Booking/waiting | 50
ASHRAE 62.1-2007Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2007 | Educational Facilities | Daycare (through age 4) | 25
ASHRAE 62.1-2007Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (ages 5-8) | 25
ASHRAE 62.1-2007Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (age 9 plus) | 35
ASHRAE 62.1-2007Educational FacilitiesLecture classroom | ASHRAE 62.1-2007 | Educational Facilities | Lecture classroom | 65
ASHRAE 62.1-2007Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2007 | Educational Facilities | Lecture hall (fixed seats) | 150
ASHRAE 62.1-2007Educational FacilitiesArt classroom | ASHRAE 62.1-2007 | Educational Facilities | Art classroom | 20
ASHRAE 62.1-2007Educational FacilitiesScience laboratories | ASHRAE 62.1-2007 | Educational Facilities | Science laboratories | 25 | E
ASHRAE 62.1-2007Educational FacilitiesWood/metal shop | ASHRAE 62.1-2007 | Educational Facilities | Wood/metal shop | 20
ASHRAE 62.1-2007Educational FacilitiesComputer lab | ASHRAE 62.1-2007 | Educational Facilities | Computer lab | 25
ASHRAE 62.1-2007Educational FacilitiesMedia center | ASHRAE 62.1-2007 | Educational Facilities | Media center | 25 | A
ASHRAE 62.1-2007Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2007 | Educational Facilities | Music/theater/dance | 35
ASHRAE 62.1-2007Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2007 | Educational Facilities | Multiuse assembly | 100
ASHRAE 62.1-2007Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2007 | Food and Beverage Service | Restaurant dining rooms | 70
ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | 100
ASHRAE 62.1-2007Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2007 | Food and Beverage Service | Bars, cocktail lounges | 100
ASHRAE 62.1-2007GeneralConference/meeting | ASHRAE 62.1-2007 | General | Conference/meeting | 50
ASHRAE 62.1-2007GeneralCorridors | ASHRAE 62.1-2007 | General | Corridors | 0
ASHRAE 62.1-2007GeneralStorage rooms | ASHRAE 62.1-2007 | General | Storage rooms | 0 | B
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 10
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 20
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 30
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 120
ASHRAE 62.1-2007Office BuildingsOffice space | ASHRAE 62.1-2007 | Office Buildings | Office space | 5
ASHRAE 62.1-2007Office BuildingsReception areas | ASHRAE 62.1-2007 | Office Buildings | Reception areas | 30
ASHRAE 62.1-2007Office BuildingsTelephone/data entry | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | 60
ASHRAE 62.1-2007Office BuildingsMain entry lobbies | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | 10
ASHRAE 62.1-2007Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2007 | Miscellaneous Spaces | Bank vaults/safe deposit | 5
ASHRAE 62.1-2007Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Computer (not printing) | 4
ASHRAE 62.1-2007Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Pharmacy (prep. area) | 10
ASHRAE 62.1-2007Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2007 | Miscellaneous Spaces | Photo studios | 10
ASHRAE 62.1-2007Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2007 | Miscellaneous Spaces | Shipping/receiving | 0 | B
ASHRAE 62.1-2007Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2007 | Miscellaneous Spaces | Transportation waiting | 100
ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses | 0 | B
ASHRAE 62.1-2007Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2007 | Public Assembly Spaces | Auditorium seating area | 150
ASHRAE 62.1-2007Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2007 | Public Assembly Spaces | Places of religious worship | 120
ASHRAE 62.1-2007Public Assembly SpacesCourtrooms | ASHRAE 62.1-2007 | Public Assembly Spaces | Courtrooms | 70
ASHRAE 62.1-2007Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2007 | Public Assembly Spaces | Legislative chambers | 50
ASHRAE 62.1-2007Public Assembly SpacesLibraries | ASHRAE 62.1-2007 | Public Assembly Spaces | Libraries | 10
ASHRAE 62.1-2007Public Assembly SpacesLobbies | ASHRAE 62.1-2007 | Public Assembly Spaces | Lobbies | 150
ASHRAE 62.1-2007Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums (children’s) | 40
ASHRAE 62.1-2007Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums/galleries | 40
ASHRAE 62.1-2007RetailGeneral Sales | ASHRAE 62.1-2007 | Retail | General Sales | 15
ASHRAE 62.1-2007RetailMall common areas | ASHRAE 62.1-2007 | Retail | Mall common areas | 40
ASHRAE 62.1-2007RetailBarber shop | ASHRAE 62.1-2007 | Retail | Barber shop | 25
ASHRAE 62.1-2007RetailBeauty and nail salons | ASHRAE 62.1-2007 | Retail | Beauty and nail salons | 25
ASHRAE 62.1-2007RetailPet shops (animal areas) | ASHRAE 62.1-2007 | Retail | Pet shops (animal areas) | 10
ASHRAE 62.1-2007RetailSupermarket | ASHRAE 62.1-2007 | Retail | Supermarket | 8
ASHRAE 62.1-2007RetailCoinoperated laundries | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | 20
ASHRAE 62.1-2007Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Sports arena (play area) | 0
ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) | 30
ASHRAE 62.1-2007Sports and EntertainmentSpectator areas | ASHRAE 62.1-2007 | Sports and Entertainment | Spectator areas | 150
ASHRAE 62.1-2007Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2007 | Sports and Entertainment | Swimming (pool & deck) | 0 | C
ASHRAE 62.1-2007Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2007 | Sports and Entertainment | Disco/dance floors | 100
ASHRAE 62.1-2007Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/aerobics room | 40
ASHRAE 62.1-2007Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/weight rooms | 10
ASHRAE 62.1-2007Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2007 | Sports and Entertainment | Bowling alley (seating) | 40
ASHRAE 62.1-2007Sports and EntertainmentGambling casinos | ASHRAE 62.1-2007 | Sports and Entertainment | Gambling casinos | 120
ASHRAE 62.1-2007Sports and EntertainmentGame arcades | ASHRAE 62.1-2007 | Sports and Entertainment | Game arcades | 20
ASHRAE 62.1-2007Sports and EntertainmentStages, studios | ASHRAE 62.1-2007 | Sports and Entertainment | Stages, studios | 70 | D
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 10 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 20 | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 20
GGHC v2.2Health CareAnesthesia Storage | GGHC v2.2 | Health Care | Anesthesia Storage | 5
GGHC v2.2Health CareAngiographic-All Other Types | GGHC v2.2 | Health Care | Angiographic-All Other Types | 5
GGHC v2.2Health CareAngiographic-Heart Only | GGHC v2.2 | Health Care | Angiographic-Heart Only | 5
GGHC v2.2Health CareAutopsy | GGHC v2.2 | Health Care | Autopsy | 5
GGHC v2.2Health CareBathroom/ Public | GGHC v2.2 | Health Care | Bathroom/ Public | 3.3
GGHC v2.2Health CareBedpan Room | GGHC v2.2 | Health Care | Bedpan Room | 5
GGHC v2.2Health CareCast Room | GGHC v2.2 | Health Care | Cast Room | 5
GGHC v2.2Health CareClean Linen Storage | GGHC v2.2 | Health Care | Clean Linen Storage | 1
GGHC v2.2Health CareClean Utility / Workroom | GGHC v2.2 | Health Care | Clean Utility / Workroom | 5
GGHC v2.2Health CareConference Rooms | GGHC v2.2 | Health Care | Conference Rooms | 20
GGHC v2.2Health CareCorridors | GGHC v2.2 | Health Care | Corridors | 10
GGHC v2.2Health CareCystoscopy | GGHC v2.2 | Health Care | Cystoscopy | 5
GGHC v2.2Health CareDarkroom | GGHC v2.2 | Health Care | Darkroom | 5
GGHC v2.2Health CareDecontamination | GGHC v2.2 | Health Care | Decontamination | 5
GGHC v2.2Health CareDelivery Room | GGHC v2.2 | Health Care | Delivery Room | 5
GGHC v2.2Health CareDietary Day Storage | GGHC v2.2 | Health Care | Dietary Day Storage | 2
GGHC v2.2Health CareDining Room | GGHC v2.2 | Health Care | Dining Room | 10
GGHC v2.2Health CareDishwashing | GGHC v2.2 | Health Care | Dishwashing | 5
GGHC v2.2Health CareEndoscopy | GGHC v2.2 | Health Care | Endoscopy | 5
GGHC v2.2Health CareHistology | GGHC v2.2 | Health Care | Histology | 5
GGHC v2.2Health CareIsolation | GGHC v2.2 | Health Care | Isolation | 5
GGHC v2.2Health CareJanitors Closet / Utility | GGHC v2.2 | Health Care | Janitors Closet / Utility | 1
GGHC v2.2Health CareKitchen, Food Preparation | GGHC v2.2 | Health Care | Kitchen, Food Preparation | 5
GGHC v2.2Health CareLabor/ Delivery/Recovery | GGHC v2.2 | Health Care | Labor/ Delivery/Recovery | 5
GGHC v2.2Health CareL / D / R / Post Partum | GGHC v2.2 | Health Care | L / D / R / Post Partum | 5
GGHC v2.2Health CareLaboratory | GGHC v2.2 | Health Care | Laboratory | 5
GGHC v2.2Health CareLinen Storage, Clean | GGHC v2.2 | Health Care | Linen Storage, Clean | 2
GGHC v2.2Health CareLobby | GGHC v2.2 | Health Care | Lobby | 10
GGHC v2.2Health CareLockers | GGHC v2.2 | Health Care | Lockers | 10
GGHC v2.2Health CareMammography | GGHC v2.2 | Health Care | Mammography | 5
GGHC v2.2Health CareMechanical Equipment Room | GGHC v2.2 | Health Care | Mechanical Equipment Room | 0.5
GGHC v2.2Health CareMedical Records | GGHC v2.2 | Health Care | Medical Records | 2
GGHC v2.2Health CareNuclear Medicine, Hot Lab | GGHC v2.2 | Health Care | Nuclear Medicine, Hot Lab | 5
GGHC v2.2Health CareNursery, General | GGHC v2.2 | Health Care | Nursery, General | 5
GGHC v2.2Health CareNursery, Exam | GGHC v2.2 | Health Care | Nursery, Exam | 5
GGHC v2.2Health CareNursing Stations- General | GGHC v2.2 | Health Care | Nursing Stations- General | 5
GGHC v2.2Health CareOperating Room | GGHC v2.2 | Health Care | Operating Room | 5
GGHC v2.2Health CarePathology | GGHC v2.2 | Health Care | Pathology | 5
GGHC v2.2Health CarePatient Room | GGHC v2.2 | Health Care | Patient Room | 5
GGHC v2.2Health CarePharmacy / Medicine Room | GGHC v2.2 | Health Care | Pharmacy / Medicine Room | 5
GGHC v2.2Health CarePhysical Therapy and Hydrotherapy | GGHC v2.2 | Health Care | Physical Therapy and Hydrotherapy | 5
GGHC v2.2Health CareRecovery | GGHC v2.2 | Health Care | Recovery | 5
GGHC v2.2Health CareScrub Up Area, Surgical Corridor | GGHC v2.2 | Health Care | Scrub Up Area, Surgical Corridor | 5
GGHC v2.2Health CareSoiled Linen, Sorting | GGHC v2.2 | Health Care | Soiled Linen, Sorting | 5
GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | 5
GGHC v2.2Health CareSpecial Procedure Room, Invasive | GGHC v2.2 | Health Care | Special Procedure Room, Invasive | 5
GGHC v2.2Health CareStairways | GGHC v2.2 | Health Care | Stairways | 1
GGHC v2.2Health CareSterilizer Room | GGHC v2.2 | Health Care | Sterilizer Room | 5
GGHC v2.2Health CareSub-Sterile | GGHC v2.2 | Health Care | Sub-Sterile | 5
GGHC v2.2Health CareSurgical Supply | GGHC v2.2 | Health Care | Surgical Supply | 5
GGHC v2.2Health CareTrash Chute Room | GGHC v2.2 | Health Care | Trash Chute Room | 0.5
GGHC v2.2Health CareTrauma | GGHC v2.2 | Health Care | Trauma | 5
GGHC v2.2Health CareTreatment / Examination | GGHC v2.2 | Health Care | Treatment / Examination | 5
GGHC v2.2Health CareUnsterile Supply | GGHC v2.2 | Health Care | Unsterile Supply | 2
GGHC v2.2Health CareWaiting Areas/Lounges | GGHC v2.2 | Health Care | Waiting Areas/Lounges | 10
GGHC v2.2Health CareX-ray, Diagnostic and Treatment | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | 5

## InteriorLighting
Each row represents interior lighting power limits for a particular space type in a particular standard. Values are referenced on Space Types tab.
VLookupColumn | Lighting Standard | Primary Space Type | Secondary Space Type | W/ft^2 | W/ft | Import Order
ASHRAE 90.1-1999Whole BuildingAutomotive Facility | ASHRAE 90.1-1999 | Whole Building | Automotive Facility | 1.5 |  | 1
ASHRAE 90.1-1999Whole BuildingConvention Center | ASHRAE 90.1-1999 | Whole Building | Convention Center | 1.4 |  | 2
ASHRAE 90.1-1999Whole BuildingCourt House | ASHRAE 90.1-1999 | Whole Building | Court House | 1.4 |  | 3
ASHRAE 90.1-1999Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-1999 | Whole Building | Dining: Bar Lounge/Leisure | 1.5 |  | 4
ASHRAE 90.1-1999Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-1999 | Whole Building | Dining: Cafeteria/Fast Food | 1.8 |  | 5
ASHRAE 90.1-1999Whole BuildingDining: Family | ASHRAE 90.1-1999 | Whole Building | Dining: Family | 1.9 |  | 6
ASHRAE 90.1-1999Whole BuildingDormitory | ASHRAE 90.1-1999 | Whole Building | Dormitory | 1.5 |  | 7
ASHRAE 90.1-1999Whole BuildingExercise Center | ASHRAE 90.1-1999 | Whole Building | Exercise Center | 1.4 |  | 8
ASHRAE 90.1-1999Whole BuildingGymnasium | ASHRAE 90.1-1999 | Whole Building | Gymnasium | 1.7 |  | 9
ASHRAE 90.1-1999Whole BuildingHealth Care-Clinic | ASHRAE 90.1-1999 | Whole Building | Health Care-Clinic | 1.6 |  | 10
ASHRAE 90.1-1999Whole BuildingHospital | ASHRAE 90.1-1999 | Whole Building | Hospital | 1.6 |  | 11
ASHRAE 90.1-1999Whole BuildingHotel | ASHRAE 90.1-1999 | Whole Building | Hotel | 1.7 |  | 12
ASHRAE 90.1-1999Whole BuildingLibrary | ASHRAE 90.1-1999 | Whole Building | Library | 1.5 |  | 13
ASHRAE 90.1-1999Whole BuildingManufacturing Facility | ASHRAE 90.1-1999 | Whole Building | Manufacturing Facility | 2.2 |  | 14
ASHRAE 90.1-1999Whole BuildingMotel | ASHRAE 90.1-1999 | Whole Building | Motel | 2 |  | 15
ASHRAE 90.1-1999Whole BuildingMotion Picture Theater | ASHRAE 90.1-1999 | Whole Building | Motion Picture Theater | 1.6 |  | 16
ASHRAE 90.1-1999Whole BuildingMulti-Family | ASHRAE 90.1-1999 | Whole Building | Multi-Family | 1 |  | 17
ASHRAE 90.1-1999Whole BuildingMuseum | ASHRAE 90.1-1999 | Whole Building | Museum | 1.6 |  | 18
ASHRAE 90.1-1999Whole BuildingOffice | ASHRAE 90.1-1999 | Whole Building | Office | 1.3 |  | 19
ASHRAE 90.1-1999Whole BuildingParking Garage | ASHRAE 90.1-1999 | Whole Building | Parking Garage | 0.3 |  | 20
ASHRAE 90.1-1999Whole BuildingPenitentiary | ASHRAE 90.1-1999 | Whole Building | Penitentiary | 1.2 |  | 21
ASHRAE 90.1-1999Whole BuildingPerforming Arts Theater | ASHRAE 90.1-1999 | Whole Building | Performing Arts Theater | 1.5 |  | 22
ASHRAE 90.1-1999Whole BuildingPolice/Fire Station | ASHRAE 90.1-1999 | Whole Building | Police/Fire Station | 1.3 |  | 23
ASHRAE 90.1-1999Whole BuildingPost Office | ASHRAE 90.1-1999 | Whole Building | Post Office | 1.6 |  | 24
ASHRAE 90.1-1999Whole BuildingReligious Building | ASHRAE 90.1-1999 | Whole Building | Religious Building | 2.2 |  | 25
ASHRAE 90.1-1999Whole BuildingRetail | ASHRAE 90.1-1999 | Whole Building | Retail | 1.9 |  | 26
ASHRAE 90.1-1999Whole BuildingSchool/University | ASHRAE 90.1-1999 | Whole Building | School/University | 1.5 |  | 27
ASHRAE 90.1-1999Whole BuildingSports Arena | ASHRAE 90.1-1999 | Whole Building | Sports Arena | 1.5 |  | 28
ASHRAE 90.1-1999Whole BuildingTown Hall | ASHRAE 90.1-1999 | Whole Building | Town Hall | 1.4 |  | 29
ASHRAE 90.1-1999Whole BuildingTransportation | ASHRAE 90.1-1999 | Whole Building | Transportation | 1.2 |  | 30
ASHRAE 90.1-1999Whole BuildingWarehouse | ASHRAE 90.1-1999 | Whole Building | Warehouse | 1.2 |  | 31
ASHRAE 90.1-1999Whole BuildingWorkshop | ASHRAE 90.1-1999 | Whole Building | Workshop | 1.7 |  | 32
ASHRAE 90.1-1999Office-EnclosedGeneral | ASHRAE 90.1-1999 | Office-Enclosed | General | 1.5 |  | 33
ASHRAE 90.1-1999Office-Open PlanGeneral | ASHRAE 90.1-1999 | Office-Open Plan | General | 1.3 |  | 34
ASHRAE 90.1-1999Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-1999 | Conference/Meeting/Multipurpose | General | 1.5 |  | 35
ASHRAE 90.1-1999Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-1999 | Classroom/Lecture/Training | General | 1.6 |  | 36
ASHRAE 90.1-1999Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-1999 | Classroom/Lecture/Training | For Penitentiary | 1.4 |  | 37
ASHRAE 90.1-1999LobbyGeneral | ASHRAE 90.1-1999 | Lobby | General | 1.8 |  | 38
ASHRAE 90.1-1999LobbyFor Hotel | ASHRAE 90.1-1999 | Lobby | For Hotel | 1.8 |  | 39
ASHRAE 90.1-1999LobbyFor Performing Arts Theater | ASHRAE 90.1-1999 | Lobby | For Performing Arts Theater | 1.2 |  | 40
ASHRAE 90.1-1999LobbyFor Motion Picture Theater | ASHRAE 90.1-1999 | Lobby | For Motion Picture Theater | 0.8 |  | 41
ASHRAE 90.1-1999Audience/Seating AreaGeneral | ASHRAE 90.1-1999 | Audience/Seating Area | General | 0.5 |  | 42
ASHRAE 90.1-1999Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-1999 | Audience/Seating Area | For Gymnasium | 0.5 |  | 43
ASHRAE 90.1-1999Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-1999 | Audience/Seating Area | For Exercise Center | 0.5 |  | 44
ASHRAE 90.1-1999Audience/Seating AreaFor Convention Center | ASHRAE 90.1-1999 | Audience/Seating Area | For Convention Center | 0.5 |  | 45
ASHRAE 90.1-1999Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-1999 | Audience/Seating Area | For Penitentiary | 1.9 |  | 46
ASHRAE 90.1-1999Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-1999 | Audience/Seating Area | For Religious Buildings | 3.2 |  | 47
ASHRAE 90.1-1999Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-1999 | Audience/Seating Area | For Sports Arena | 0.5 |  | 48
ASHRAE 90.1-1999Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-1999 | Audience/Seating Area | For Performing Arts Theater | 1.8 |  | 49
ASHRAE 90.1-1999Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-1999 | Audience/Seating Area | For Motion Picture Theater | 1.3 |  | 50
ASHRAE 90.1-1999Audience/Seating AreaFor Transportation | ASHRAE 90.1-1999 | Audience/Seating Area | For Transportation | 1 |  | 51
ASHRAE 90.1-1999AtriumFirst Three Floors | ASHRAE 90.1-1999 | Atrium | First Three Floors | 1.3 |  | 52
ASHRAE 90.1-1999AtriumEach Floor over First Three Floors | ASHRAE 90.1-1999 | Atrium | Each Floor over First Three Floors | 0.2 |  | 53
ASHRAE 90.1-1999Lounge/RecreationGeneral | ASHRAE 90.1-1999 | Lounge/Recreation | General | 1.4 |  | 54
ASHRAE 90.1-1999Lounge/RecreationFor Hospital | ASHRAE 90.1-1999 | Lounge/Recreation | For Hospital | 1.4 |  | 55
ASHRAE 90.1-1999Dining AreaGeneral | ASHRAE 90.1-1999 | Dining Area | General | 1.4 |  | 56
ASHRAE 90.1-1999Dining AreaFor Penitentiary | ASHRAE 90.1-1999 | Dining Area | For Penitentiary | 1.4 |  | 57
ASHRAE 90.1-1999Dining AreaFor Hotel | ASHRAE 90.1-1999 | Dining Area | For Hotel | 1 |  | 58
ASHRAE 90.1-1999Dining AreaFor Motel | ASHRAE 90.1-1999 | Dining Area | For Motel | 1.2 |  | 59
ASHRAE 90.1-1999Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-1999 | Dining Area | For Bar Lounge/Leisure Dining | 1.2 |  | 60
ASHRAE 90.1-1999Dining AreaFor Family Dining | ASHRAE 90.1-1999 | Dining Area | For Family Dining | 2.2 |  | 61
ASHRAE 90.1-1999Food PreparationGeneral | ASHRAE 90.1-1999 | Food Preparation | General | 2.2 |  | 62
ASHRAE 90.1-1999LaboratoryGeneral | ASHRAE 90.1-1999 | Laboratory | General | 1.8 |  | 63
ASHRAE 90.1-1999RestroomsGeneral | ASHRAE 90.1-1999 | Restrooms | General | 1 |  | 64
ASHRAE 90.1-1999Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-1999 | Dressing/Locker/Fitting Room | General | 0.8 |  | 65
ASHRAE 90.1-1999Corridor/TransitionGeneral | ASHRAE 90.1-1999 | Corridor/Transition | General | 0.7 |  | 66
ASHRAE 90.1-1999Corridor/TransitionFor Hospital | ASHRAE 90.1-1999 | Corridor/Transition | For Hospital | 1.6 |  | 67
ASHRAE 90.1-1999Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-1999 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 68
ASHRAE 90.1-1999Stairs—ActiveGeneral | ASHRAE 90.1-1999 | Stairs—Active | General | 0.9 |  | 69
ASHRAE 90.1-1999Active StorageGeneral | ASHRAE 90.1-1999 | Active Storage | General | 1.1 |  | 70
ASHRAE 90.1-1999Active StorageFor Hospital | ASHRAE 90.1-1999 | Active Storage | For Hospital | 2.9 |  | 71
ASHRAE 90.1-1999Inactive storageGeneral | ASHRAE 90.1-1999 | Inactive storage | General | 0.3 |  | 72
ASHRAE 90.1-1999Inactive storageFor Museum | ASHRAE 90.1-1999 | Inactive storage | For Museum | 1.4 |  | 73
ASHRAE 90.1-1999Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-1999 | Gymnasium/Exercise Center | Playing Area | 1.9 |  | 74
ASHRAE 90.1-1999Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-1999 | Gymnasium/Exercise Center | Exercise Area | 1.1 |  | 75
ASHRAE 90.1-1999Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-1999 | Courthouse/Police Station/Penitentiary | Courtroom | 2.1 |  | 76
ASHRAE 90.1-1999Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-1999 | Courthouse/Police Station/Penitentiary | Confinement Cells | 1.1 |  | 77
ASHRAE 90.1-1999Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-1999 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.1 |  | 78
ASHRAE 90.1-1999Fire StationsFire Station Engine Room | ASHRAE 90.1-1999 | Fire Stations | Fire Station Engine Room | 0.9 |  | 79
ASHRAE 90.1-1999Fire StationsSleeping Quarters | ASHRAE 90.1-1999 | Fire Stations | Sleeping Quarters | 1.1 |  | 80
ASHRAE 90.1-1999Post OfficeSorting Area | ASHRAE 90.1-1999 | Post Office | Sorting Area | 1.7 |  | 81
ASHRAE 90.1-1999Convention CenterExhibit Space | ASHRAE 90.1-1999 | Convention Center | Exhibit Space | 3.3 |  | 82
ASHRAE 90.1-1999LibraryCard File and Cataloging | ASHRAE 90.1-1999 | Library | Card File and Cataloging | 1.4 |  | 83
ASHRAE 90.1-1999LibraryStacks | ASHRAE 90.1-1999 | Library | Stacks | 1.9 |  | 84
ASHRAE 90.1-1999LibraryReading Area | ASHRAE 90.1-1999 | Library | Reading Area | 1.8 |  | 85
ASHRAE 90.1-1999HospitalEmergency | ASHRAE 90.1-1999 | Hospital | Emergency | 2.8 |  | 86
ASHRAE 90.1-1999HospitalRecovery | ASHRAE 90.1-1999 | Hospital | Recovery | 2.6 |  | 87
ASHRAE 90.1-1999HospitalNurse Station | ASHRAE 90.1-1999 | Hospital | Nurse Station | 1.8 |  | 88
ASHRAE 90.1-1999HospitalExam/Treatment | ASHRAE 90.1-1999 | Hospital | Exam/Treatment | 1.6 |  | 89
ASHRAE 90.1-1999HospitalPharmacy | ASHRAE 90.1-1999 | Hospital | Pharmacy | 2.3 |  | 90
ASHRAE 90.1-1999HospitalPatient Room | ASHRAE 90.1-1999 | Hospital | Patient Room | 1.2 |  | 91
ASHRAE 90.1-1999HospitalOperating Room | ASHRAE 90.1-1999 | Hospital | Operating Room | 7.6 |  | 92
ASHRAE 90.1-1999HospitalNursery | ASHRAE 90.1-1999 | Hospital | Nursery | 1 |  | 93
ASHRAE 90.1-1999HospitalMedical Supply | ASHRAE 90.1-1999 | Hospital | Medical Supply | 3 |  | 94
ASHRAE 90.1-1999HospitalPhysical Therapy | ASHRAE 90.1-1999 | Hospital | Physical Therapy | 1.9 |  | 95
ASHRAE 90.1-1999HospitalRadiology | ASHRAE 90.1-1999 | Hospital | Radiology | 0.4 |  | 96
ASHRAE 90.1-1999HospitalLaundry—Washing | ASHRAE 90.1-1999 | Hospital | Laundry—Washing | 0.7 |  | 97
ASHRAE 90.1-1999AutomotiveService/Repair | ASHRAE 90.1-1999 | Automotive | Service/Repair | 1.4 |  | 98
ASHRAE 90.1-1999ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-1999 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 2.1 |  | 99
ASHRAE 90.1-1999ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-1999 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 3 |  | 100
ASHRAE 90.1-1999ManufacturingDetailed Manufacturing | ASHRAE 90.1-1999 | Manufacturing | Detailed Manufacturing | 6.2 |  | 101
ASHRAE 90.1-1999ManufacturingEquipment Room | ASHRAE 90.1-1999 | Manufacturing | Equipment Room | 0.8 |  | 102
ASHRAE 90.1-1999ManufacturingControl Room | ASHRAE 90.1-1999 | Manufacturing | Control Room | 0.5 |  | 103
ASHRAE 90.1-1999Hotel/MotelGuest Rooms | ASHRAE 90.1-1999 | Hotel/Motel | Guest Rooms | 2.5 |  | 104
ASHRAE 90.1-1999DormitoryLiving Quarters | ASHRAE 90.1-1999 | Dormitory | Living Quarters | 1.9 |  | 105
ASHRAE 90.1-1999MuseumGeneral Exhibition | ASHRAE 90.1-1999 | Museum | General Exhibition | 1.6 |  | 106
ASHRAE 90.1-1999MuseumRestoration | ASHRAE 90.1-1999 | Museum | Restoration | 2.5 |  | 107
ASHRAE 90.1-1999Electrical/MechanicalGeneral | ASHRAE 90.1-1999 | Electrical/Mechanical | General | 1.3 |  | 108
ASHRAE 90.1-1999WorkshopGeneral | ASHRAE 90.1-1999 | Workshop | General | 2.5 |  | 109
ASHRAE 90.1-1999Bank/OfficeBanking Activity Area | ASHRAE 90.1-1999 | Bank/Office | Banking Activity Area | 2.4 |  | 110
ASHRAE 90.1-1999Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-1999 | Religious Buildings | Worship Pulpit, Choir | 5.2 |  | 111
ASHRAE 90.1-1999Religious BuildingsFellowship Hall | ASHRAE 90.1-1999 | Religious Buildings | Fellowship Hall | 2.3 |  | 112
ASHRAE 90.1-1999Retail (not including accent lighting)Sales Area | ASHRAE 90.1-1999 | Retail (not including accent lighting) | Sales Area | 2.1 |  | 113
ASHRAE 90.1-1999Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-1999 | Retail (not including accent lighting) | Mall Concourse | 1.8 |  | 114
ASHRAE 90.1-1999Sports ArenaRing Sports Area | ASHRAE 90.1-1999 | Sports Arena | Ring Sports Area | 3.8 |  | 115
ASHRAE 90.1-1999Sports ArenaCourt Sports Area | ASHRAE 90.1-1999 | Sports Arena | Court Sports Area | 4.3 |  | 116
ASHRAE 90.1-1999Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-1999 | Sports Arena | Indoor Playing Field Area | 1.9 |  | 117
ASHRAE 90.1-1999WarehouseFine Material Storage | ASHRAE 90.1-1999 | Warehouse | Fine Material Storage | 1.6 |  | 118
ASHRAE 90.1-1999WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-1999 | Warehouse | Medium/Bulky Material Storage | 1.1 |  | 119
ASHRAE 90.1-1999Parking GarageGarage Area | ASHRAE 90.1-1999 | Parking Garage | Garage Area | 0.2 |  | 120
ASHRAE 90.1-1999TransportationAirport—Concourse | ASHRAE 90.1-1999 | Transportation | Airport—Concourse | 0.7 |  | 121
ASHRAE 90.1-1999TransportationAir/Train/Bus—Baggage Area | ASHRAE 90.1-1999 | Transportation | Air/Train/Bus—Baggage Area | 1.3 |  | 122
ASHRAE 90.1-1999TransportationTerminal—Ticket Counter | ASHRAE 90.1-1999 | Transportation | Terminal—Ticket Counter | 1.8 |  | 123
ASHRAE 90.1-1999Exterior SpacesGeneral | ASHRAE 90.1-1999 | Exterior Spaces | General | 0 |  | 124
ASHRAE 90.1-1999AtticsGeneral | ASHRAE 90.1-1999 | Attics | General | 0 |  | 125
ASHRAE 90.1-2001Whole BuildingAutomotive Facility | ASHRAE 90.1-2001 | Whole Building | Automotive Facility | 0.9 |  | 126
ASHRAE 90.1-2001Whole BuildingConvention Center | ASHRAE 90.1-2001 | Whole Building | Convention Center | 1.2 |  | 127
ASHRAE 90.1-2001Whole BuildingCourt House | ASHRAE 90.1-2001 | Whole Building | Court House | 1.2 |  | 128
ASHRAE 90.1-2001Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2001 | Whole Building | Dining: Bar Lounge/Leisure | 1.3 |  | 129
ASHRAE 90.1-2001Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2001 | Whole Building | Dining: Cafeteria/Fast Food | 1.4 |  | 130
ASHRAE 90.1-2001Whole BuildingDining: Family | ASHRAE 90.1-2001 | Whole Building | Dining: Family | 1.6 |  | 131
ASHRAE 90.1-2001Whole BuildingDormitory | ASHRAE 90.1-2001 | Whole Building | Dormitory | 1 |  | 132
ASHRAE 90.1-2001Whole BuildingExercise Center | ASHRAE 90.1-2001 | Whole Building | Exercise Center | 1 |  | 133
ASHRAE 90.1-2001Whole BuildingGymnasium | ASHRAE 90.1-2001 | Whole Building | Gymnasium | 1.1 |  | 134
ASHRAE 90.1-2001Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2001 | Whole Building | Health Care-Clinic | 1 |  | 135
ASHRAE 90.1-2001Whole BuildingHospital | ASHRAE 90.1-2001 | Whole Building | Hospital | 1.2 |  | 136
ASHRAE 90.1-2001Whole BuildingHotel | ASHRAE 90.1-2001 | Whole Building | Hotel | 1 |  | 137
ASHRAE 90.1-2001Whole BuildingLibrary | ASHRAE 90.1-2001 | Whole Building | Library | 1.3 |  | 138
ASHRAE 90.1-2001Whole BuildingManufacturing Facility | ASHRAE 90.1-2001 | Whole Building | Manufacturing Facility | 1.3 |  | 139
ASHRAE 90.1-2001Whole BuildingMotel | ASHRAE 90.1-2001 | Whole Building | Motel | 1 |  | 140
ASHRAE 90.1-2001Whole BuildingMotion Picture Theater | ASHRAE 90.1-2001 | Whole Building | Motion Picture Theater | 1.2 |  | 141
ASHRAE 90.1-2001Whole BuildingMulti-Family | ASHRAE 90.1-2001 | Whole Building | Multi-Family | 0.7 |  | 142
ASHRAE 90.1-2001Whole BuildingMuseum | ASHRAE 90.1-2001 | Whole Building | Museum | 1.1 |  | 143
ASHRAE 90.1-2001Whole BuildingOffice | ASHRAE 90.1-2001 | Whole Building | Office | 1 |  | 144
ASHRAE 90.1-2001Whole BuildingParking Garage | ASHRAE 90.1-2001 | Whole Building | Parking Garage | 0.3 |  | 145
ASHRAE 90.1-2001Whole BuildingPenitentiary | ASHRAE 90.1-2001 | Whole Building | Penitentiary | 1 |  | 146
ASHRAE 90.1-2001Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2001 | Whole Building | Performing Arts Theater | 1.6 |  | 147
ASHRAE 90.1-2001Whole BuildingPolice/Fire Station | ASHRAE 90.1-2001 | Whole Building | Police/Fire Station | 1 |  | 148
ASHRAE 90.1-2001Whole BuildingPost Office | ASHRAE 90.1-2001 | Whole Building | Post Office | 1.1 |  | 149
ASHRAE 90.1-2001Whole BuildingReligious Building | ASHRAE 90.1-2001 | Whole Building | Religious Building | 1.3 |  | 150
ASHRAE 90.1-2001Whole BuildingRetail | ASHRAE 90.1-2001 | Whole Building | Retail | 1.5 |  | 151
ASHRAE 90.1-2001Whole BuildingSchool/University | ASHRAE 90.1-2001 | Whole Building | School/University | 1.2 |  | 152
ASHRAE 90.1-2001Whole BuildingSports Arena | ASHRAE 90.1-2001 | Whole Building | Sports Arena | 1.1 |  | 153
ASHRAE 90.1-2001Whole BuildingTown Hall | ASHRAE 90.1-2001 | Whole Building | Town Hall | 1.1 |  | 154
ASHRAE 90.1-2001Whole BuildingTransportation | ASHRAE 90.1-2001 | Whole Building | Transportation | 1 |  | 155
ASHRAE 90.1-2001Whole BuildingWarehouse | ASHRAE 90.1-2001 | Whole Building | Warehouse | 0.8 |  | 156
ASHRAE 90.1-2001Whole BuildingWorkshop | ASHRAE 90.1-2001 | Whole Building | Workshop | 1.4 |  | 157
ASHRAE 90.1-2001Office-EnclosedGeneral | ASHRAE 90.1-2001 | Office-Enclosed | General | 1.1 |  | 158
ASHRAE 90.1-2001Office-Open PlanGeneral | ASHRAE 90.1-2001 | Office-Open Plan | General | 1.1 |  | 159
ASHRAE 90.1-2001Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2001 | Conference/Meeting/Multipurpose | General | 1.3 |  | 160
ASHRAE 90.1-2001Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2001 | Classroom/Lecture/Training | General | 1.4 |  | 161
ASHRAE 90.1-2001Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2001 | Classroom/Lecture/Training | For Penitentiary | 1.3 |  | 162
ASHRAE 90.1-2001LobbyGeneral | ASHRAE 90.1-2001 | Lobby | General | 1.3 |  | 163
ASHRAE 90.1-2001LobbyFor Hotel | ASHRAE 90.1-2001 | Lobby | For Hotel | 1.1 |  | 164
ASHRAE 90.1-2001LobbyFor Performing Arts Theater | ASHRAE 90.1-2001 | Lobby | For Performing Arts Theater | 3.3 |  | 165
ASHRAE 90.1-2001LobbyFor Motion Picture Theater | ASHRAE 90.1-2001 | Lobby | For Motion Picture Theater | 1.1 |  | 166
ASHRAE 90.1-2001Audience/Seating AreaGeneral | ASHRAE 90.1-2001 | Audience/Seating Area | General | 0.9 |  | 167
ASHRAE 90.1-2001Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2001 | Audience/Seating Area | For Gymnasium | 0.4 |  | 168
ASHRAE 90.1-2001Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-2001 | Audience/Seating Area | For Exercise Center | 0.3 |  | 169
ASHRAE 90.1-2001Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2001 | Audience/Seating Area | For Convention Center | 0.7 |  | 170
ASHRAE 90.1-2001Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2001 | Audience/Seating Area | For Penitentiary | 0.7 |  | 171
ASHRAE 90.1-2001Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2001 | Audience/Seating Area | For Religious Buildings | 1.7 |  | 172
ASHRAE 90.1-2001Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-2001 | Audience/Seating Area | For Sports Arena | 0.4 |  | 173
ASHRAE 90.1-2001Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-2001 | Audience/Seating Area | For Performing Arts Theater | 2.6 |  | 174
ASHRAE 90.1-2001Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2001 | Audience/Seating Area | For Motion Picture Theater | 1.2 |  | 175
ASHRAE 90.1-2001Audience/Seating AreaFor Transportation | ASHRAE 90.1-2001 | Audience/Seating Area | For Transportation | 0.5 |  | 176
ASHRAE 90.1-2001AtriumFirst Three Floors | ASHRAE 90.1-2001 | Atrium | First Three Floors | 0.6 |  | 177
ASHRAE 90.1-2001AtriumEach Floor over First Three Floors | ASHRAE 90.1-2001 | Atrium | Each Floor over First Three Floors | 0.2 |  | 178
ASHRAE 90.1-2001Lounge/RecreationGeneral | ASHRAE 90.1-2001 | Lounge/Recreation | General | 1.2 |  | 179
ASHRAE 90.1-2001Lounge/RecreationFor Hospital | ASHRAE 90.1-2001 | Lounge/Recreation | For Hospital | 0.8 |  | 180
ASHRAE 90.1-2001Dining AreaGeneral | ASHRAE 90.1-2001 | Dining Area | General | 0.9 |  | 181
ASHRAE 90.1-2001Dining AreaFor Penitentiary | ASHRAE 90.1-2001 | Dining Area | For Penitentiary | 1.3 |  | 182
ASHRAE 90.1-2001Dining AreaFor Hotel | ASHRAE 90.1-2001 | Dining Area | For Hotel | 1.3 |  | 183
ASHRAE 90.1-2001Dining AreaFor Motel | ASHRAE 90.1-2001 | Dining Area | For Motel | 1.2 |  | 184
ASHRAE 90.1-2001Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2001 | Dining Area | For Bar Lounge/Leisure Dining | 1.4 |  | 185
ASHRAE 90.1-2001Dining AreaFor Family Dining | ASHRAE 90.1-2001 | Dining Area | For Family Dining | 2.1 |  | 186
ASHRAE 90.1-2001Food PreparationGeneral | ASHRAE 90.1-2001 | Food Preparation | General | 1.2 |  | 187
ASHRAE 90.1-2001LaboratoryGeneral | ASHRAE 90.1-2001 | Laboratory | General | 1.4 |  | 188
ASHRAE 90.1-2001RestroomsGeneral | ASHRAE 90.1-2001 | Restrooms | General | 0.9 |  | 189
ASHRAE 90.1-2001Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-2001 | Dressing/Locker/Fitting Room | General | 0.6 |  | 190
ASHRAE 90.1-2001Corridor/TransitionGeneral | ASHRAE 90.1-2001 | Corridor/Transition | General | 0.5 |  | 191
ASHRAE 90.1-2001Corridor/TransitionFor Hospital | ASHRAE 90.1-2001 | Corridor/Transition | For Hospital | 1 |  | 192
ASHRAE 90.1-2001Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-2001 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 193
ASHRAE 90.1-2001Stairs—ActiveGeneral | ASHRAE 90.1-2001 | Stairs—Active | General | 0.6 |  | 194
ASHRAE 90.1-2001Active StorageGeneral | ASHRAE 90.1-2001 | Active Storage | General | 0.8 |  | 195
ASHRAE 90.1-2001Active StorageFor Hospital | ASHRAE 90.1-2001 | Active Storage | For Hospital | 0.9 |  | 196
ASHRAE 90.1-2001Inactive storageGeneral | ASHRAE 90.1-2001 | Inactive storage | General | 0.3 |  | 197
ASHRAE 90.1-2001Inactive storageFor Museum | ASHRAE 90.1-2001 | Inactive storage | For Museum | 0.8 |  | 198
ASHRAE 90.1-2001Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-2001 | Gymnasium/Exercise Center | Playing Area | 1.4 |  | 199
ASHRAE 90.1-2001Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-2001 | Gymnasium/Exercise Center | Exercise Area | 0.9 |  | 200
ASHRAE 90.1-2001Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-2001 | Courthouse/Police Station/Penitentiary | Courtroom | 1.9 |  | 201
ASHRAE 90.1-2001Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-2001 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.9 |  | 202
ASHRAE 90.1-2001Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-2001 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.3 |  | 203
ASHRAE 90.1-2001Fire StationsFire Station Engine Room | ASHRAE 90.1-2001 | Fire Stations | Fire Station Engine Room | 0.8 |  | 204
ASHRAE 90.1-2001Fire StationsSleeping Quarters | ASHRAE 90.1-2001 | Fire Stations | Sleeping Quarters | 0.3 |  | 205
ASHRAE 90.1-2001Post OfficeSorting Area | ASHRAE 90.1-2001 | Post Office | Sorting Area | 1.2 |  | 206
ASHRAE 90.1-2001Convention CenterExhibit Space | ASHRAE 90.1-2001 | Convention Center | Exhibit Space | 1.3 |  | 207
ASHRAE 90.1-2001LibraryCard File and Cataloging | ASHRAE 90.1-2001 | Library | Card File and Cataloging | 1.1 |  | 208
ASHRAE 90.1-2001LibraryStacks | ASHRAE 90.1-2001 | Library | Stacks | 1.7 |  | 209
ASHRAE 90.1-2001LibraryReading Area | ASHRAE 90.1-2001 | Library | Reading Area | 1.2 |  | 210
ASHRAE 90.1-2001HospitalEmergency | ASHRAE 90.1-2001 | Hospital | Emergency | 2.7 |  | 211
ASHRAE 90.1-2001HospitalRecovery | ASHRAE 90.1-2001 | Hospital | Recovery | 0.8 |  | 212
ASHRAE 90.1-2001HospitalNurse Station | ASHRAE 90.1-2001 | Hospital | Nurse Station | 1 |  | 213
ASHRAE 90.1-2001HospitalExam/Treatment | ASHRAE 90.1-2001 | Hospital | Exam/Treatment | 1.5 |  | 214
ASHRAE 90.1-2001HospitalPharmacy | ASHRAE 90.1-2001 | Hospital | Pharmacy | 1.2 |  | 215
ASHRAE 90.1-2001HospitalPatient Room | ASHRAE 90.1-2001 | Hospital | Patient Room | 0.7 |  | 216
ASHRAE 90.1-2001HospitalOperating Room | ASHRAE 90.1-2001 | Hospital | Operating Room | 2.2 |  | 217
ASHRAE 90.1-2001HospitalNursery | ASHRAE 90.1-2001 | Hospital | Nursery | 0.6 |  | 218
ASHRAE 90.1-2001HospitalMedical Supply | ASHRAE 90.1-2001 | Hospital | Medical Supply | 1.4 |  | 219
ASHRAE 90.1-2001HospitalPhysical Therapy | ASHRAE 90.1-2001 | Hospital | Physical Therapy | 0.9 |  | 220
ASHRAE 90.1-2001HospitalRadiology | ASHRAE 90.1-2001 | Hospital | Radiology | 0.4 |  | 221
ASHRAE 90.1-2001HospitalLaundry—Washing | ASHRAE 90.1-2001 | Hospital | Laundry—Washing | 0.6 |  | 222
ASHRAE 90.1-2001AutomotiveService/Repair | ASHRAE 90.1-2001 | Automotive | Service/Repair | 0.7 |  | 223
ASHRAE 90.1-2001ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2001 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.2 |  | 224
ASHRAE 90.1-2001ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-2001 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.7 |  | 225
ASHRAE 90.1-2001ManufacturingDetailed Manufacturing | ASHRAE 90.1-2001 | Manufacturing | Detailed Manufacturing | 2.1 |  | 226
ASHRAE 90.1-2001ManufacturingEquipment Room | ASHRAE 90.1-2001 | Manufacturing | Equipment Room | 1.2 |  | 227
ASHRAE 90.1-2001ManufacturingControl Room | ASHRAE 90.1-2001 | Manufacturing | Control Room | 0.5 |  | 228
ASHRAE 90.1-2001Hotel/MotelGuest Rooms | ASHRAE 90.1-2001 | Hotel/Motel | Guest Rooms | 1.1 |  | 229
ASHRAE 90.1-2001DormitoryLiving Quarters | ASHRAE 90.1-2001 | Dormitory | Living Quarters | 1.1 |  | 230
ASHRAE 90.1-2001MuseumGeneral Exhibition | ASHRAE 90.1-2001 | Museum | General Exhibition | 1 |  | 231
ASHRAE 90.1-2001MuseumRestoration | ASHRAE 90.1-2001 | Museum | Restoration | 1.7 |  | 232
ASHRAE 90.1-2001Electrical/MechanicalGeneral | ASHRAE 90.1-2001 | Electrical/Mechanical | General | 1.5 |  | 233
ASHRAE 90.1-2001WorkshopGeneral | ASHRAE 90.1-2001 | Workshop | General | 1.9 |  | 234
ASHRAE 90.1-2001Bank/OfficeBanking Activity Area | ASHRAE 90.1-2001 | Bank/Office | Banking Activity Area | 1.5 |  | 235
ASHRAE 90.1-2001Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2001 | Religious Buildings | Worship Pulpit, Choir | 2.4 |  | 236
ASHRAE 90.1-2001Religious BuildingsFellowship Hall | ASHRAE 90.1-2001 | Religious Buildings | Fellowship Hall | 0.9 |  | 237
ASHRAE 90.1-2001Retail (not including accent lighting)Sales Area | ASHRAE 90.1-2001 | Retail (not including accent lighting) | Sales Area | 2.1 |  | 238
ASHRAE 90.1-2001Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-2001 | Retail (not including accent lighting) | Mall Concourse | 1.7 |  | 239
ASHRAE 90.1-2001Sports ArenaRing Sports Area | ASHRAE 90.1-2001 | Sports Arena | Ring Sports Area | 2.7 |  | 240
ASHRAE 90.1-2001Sports ArenaCourt Sports Area | ASHRAE 90.1-2001 | Sports Arena | Court Sports Area | 2.3 |  | 241
ASHRAE 90.1-2001Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-2001 | Sports Arena | Indoor Playing Field Area | 1.4 |  | 242
ASHRAE 90.1-2001WarehouseFine Material Storage | ASHRAE 90.1-2001 | Warehouse | Fine Material Storage | 1.4 |  | 243
ASHRAE 90.1-2001WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2001 | Warehouse | Medium/Bulky Material Storage | 0.9 |  | 244
ASHRAE 90.1-2001Parking GarageGarage Area | ASHRAE 90.1-2001 | Parking Garage | Garage Area | 0.2 |  | 245
ASHRAE 90.1-2001TransportationAirport—Concourse | ASHRAE 90.1-2001 | Transportation | Airport—Concourse | 0.6 |  | 246
ASHRAE 90.1-2001TransportationAir/Train/Bus—Baggage Area | ASHRAE 90.1-2001 | Transportation | Air/Train/Bus—Baggage Area | 1 |  | 247
ASHRAE 90.1-2001TransportationTerminal—Ticket Counter | ASHRAE 90.1-2001 | Transportation | Terminal—Ticket Counter | 1.5 |  | 248
ASHRAE 90.1-2001Exterior SpacesGeneral | ASHRAE 90.1-2001 | Exterior Spaces | General | 0 |  | 249
ASHRAE 90.1-2001AtticsGeneral | ASHRAE 90.1-2001 | Attics | General | 0 |  | 250
ASHRAE 90.1-2004Active StorageFor Hospital | ASHRAE 90.1-2004 | Active Storage | For Hospital | 0.9 |  | 321
ASHRAE 90.1-2004Active StorageGeneral | ASHRAE 90.1-2004 | Active Storage | General | 0.8 |  | 320
ASHRAE 90.1-2004AtriumEach Floor over First Three Floors | ASHRAE 90.1-2004 | Atrium | Each Floor over First Three Floors | 0.2 |  | 303
ASHRAE 90.1-2004AtriumFirst Three Floors | ASHRAE 90.1-2004 | Atrium | First Three Floors | 0.6 |  | 302
ASHRAE 90.1-2004AtticsGeneral | ASHRAE 90.1-2004 | Attics | General | 0 |  | 375
ASHRAE 90.1-2004Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2004 | Audience/Seating Area | For Convention Center | 0.7 |  | 295
ASHRAE 90.1-2004Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-2004 | Audience/Seating Area | For Exercise Center | 0.3 |  | 294
ASHRAE 90.1-2004Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2004 | Audience/Seating Area | For Gymnasium | 0.4 |  | 293
ASHRAE 90.1-2004Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2004 | Audience/Seating Area | For Motion Picture Theater | 1.2 |  | 300
ASHRAE 90.1-2004Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2004 | Audience/Seating Area | For Penitentiary | 0.7 |  | 296
ASHRAE 90.1-2004Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-2004 | Audience/Seating Area | For Performing Arts Theater | 2.6 |  | 299
ASHRAE 90.1-2004Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2004 | Audience/Seating Area | For Religious Buildings | 1.7 |  | 297
ASHRAE 90.1-2004Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-2004 | Audience/Seating Area | For Sports Arena | 0.4 |  | 298
ASHRAE 90.1-2004Audience/Seating AreaFor Transportation | ASHRAE 90.1-2004 | Audience/Seating Area | For Transportation | 0.5 |  | 301
ASHRAE 90.1-2004Audience/Seating AreaGeneral | ASHRAE 90.1-2004 | Audience/Seating Area | General | 0.9 |  | 292
ASHRAE 90.1-2004AutomotiveService/Repair | ASHRAE 90.1-2004 | Automotive | Service/Repair | 0.7 |  | 348
ASHRAE 90.1-2004Bank/OfficeBanking Activity Area | ASHRAE 90.1-2004 | Bank/Office | Banking Activity Area | 1.5 |  | 360
ASHRAE 90.1-2004Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2004 | Classroom/Lecture/Training | For Penitentiary | 1.3 |  | 287
ASHRAE 90.1-2004Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2004 | Classroom/Lecture/Training | General | 1.4 |  | 286
ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | 1.3 |  | 285
ASHRAE 90.1-2004Convention CenterExhibit Space | ASHRAE 90.1-2004 | Convention Center | Exhibit Space | 1.3 |  | 332
ASHRAE 90.1-2004Corridor/TransitionFor Hospital | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | 1 |  | 317
ASHRAE 90.1-2004Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-2004 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 318
ASHRAE 90.1-2004Corridor/TransitionGeneral | ASHRAE 90.1-2004 | Corridor/Transition | General | 0.5 |  | 316
ASHRAE 90.1-2004Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-2004 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.9 |  | 327
ASHRAE 90.1-2004Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-2004 | Courthouse/Police Station/Penitentiary | Courtroom | 1.9 |  | 326
ASHRAE 90.1-2004Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-2004 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.3 |  | 328
ASHRAE 90.1-2004Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2004 | Dining Area | For Bar Lounge/Leisure Dining | 1.4 |  | 310
ASHRAE 90.1-2004Dining AreaFor Family Dining | ASHRAE 90.1-2004 | Dining Area | For Family Dining | 2.1 |  | 311
ASHRAE 90.1-2004Dining AreaFor Hotel | ASHRAE 90.1-2004 | Dining Area | For Hotel | 1.3 |  | 308
ASHRAE 90.1-2004Dining AreaFor Motel | ASHRAE 90.1-2004 | Dining Area | For Motel | 1.2 |  | 309
ASHRAE 90.1-2004Dining AreaFor Penitentiary | ASHRAE 90.1-2004 | Dining Area | For Penitentiary | 1.3 |  | 307
ASHRAE 90.1-2004Dining AreaGeneral | ASHRAE 90.1-2004 | Dining Area | General | 0.9 |  | 306
ASHRAE 90.1-2004DormitoryLiving Quarters | ASHRAE 90.1-2004 | Dormitory | Living Quarters | 1.1 |  | 355
ASHRAE 90.1-2004Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-2004 | Dressing/Locker/Fitting Room | General | 0.6 |  | 315
ASHRAE 90.1-2004Electrical/MechanicalGeneral | ASHRAE 90.1-2004 | Electrical/Mechanical | General | 1.5 |  | 358
ASHRAE 90.1-2004Exterior SpacesGeneral | ASHRAE 90.1-2004 | Exterior Spaces | General | 0 |  | 374
ASHRAE 90.1-2004Fire StationsFire Station Engine Room | ASHRAE 90.1-2004 | Fire Stations | Fire Station Engine Room | 0.8 |  | 329
ASHRAE 90.1-2004Fire StationsSleeping Quarters | ASHRAE 90.1-2004 | Fire Stations | Sleeping Quarters | 0.3 |  | 330
ASHRAE 90.1-2004Food PreparationGeneral | ASHRAE 90.1-2004 | Food Preparation | General | 1.2 |  | 312
ASHRAE 90.1-2004Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Exercise Area | 0.9 |  | 325
ASHRAE 90.1-2004Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Playing Area | 1.4 |  | 324
ASHRAE 90.1-2004HospitalEmergency | ASHRAE 90.1-2004 | Hospital | Emergency | 2.7 |  | 336
ASHRAE 90.1-2004HospitalExam/Treatment | ASHRAE 90.1-2004 | Hospital | Exam/Treatment | 1.5 |  | 339
ASHRAE 90.1-2004HospitalLaundry-Washing | ASHRAE 90.1-2004 | Hospital | Laundry-Washing | 0.6 |  | 347
ASHRAE 90.1-2004HospitalMedical Supply | ASHRAE 90.1-2004 | Hospital | Medical Supply | 1.4 |  | 344
ASHRAE 90.1-2004HospitalNurse Station | ASHRAE 90.1-2004 | Hospital | Nurse Station | 1 |  | 338
ASHRAE 90.1-2004HospitalNursery | ASHRAE 90.1-2004 | Hospital | Nursery | 0.6 |  | 343
ASHRAE 90.1-2004HospitalOperating Room | ASHRAE 90.1-2004 | Hospital | Operating Room | 2.2 |  | 342
ASHRAE 90.1-2004HospitalPatient Room | ASHRAE 90.1-2004 | Hospital | Patient Room | 0.7 |  | 341
ASHRAE 90.1-2004HospitalPharmacy | ASHRAE 90.1-2004 | Hospital | Pharmacy | 1.2 |  | 340
ASHRAE 90.1-2004HospitalPhysical Therapy | ASHRAE 90.1-2004 | Hospital | Physical Therapy | 0.9 |  | 345
ASHRAE 90.1-2004HospitalRadiology | ASHRAE 90.1-2004 | Hospital | Radiology | 0.4 |  | 346
ASHRAE 90.1-2004HospitalRecovery | ASHRAE 90.1-2004 | Hospital | Recovery | 0.8 |  | 337
ASHRAE 90.1-2004Hotel/MotelGuest Rooms | ASHRAE 90.1-2004 | Hotel/Motel | Guest Rooms | 1.1 |  | 354
ASHRAE 90.1-2004Inactive storageFor Museum | ASHRAE 90.1-2004 | Inactive storage | For Museum | 0.8 |  | 323
ASHRAE 90.1-2004Inactive storageGeneral | ASHRAE 90.1-2004 | Inactive storage | General | 0.3 |  | 322
ASHRAE 90.1-2004LaboratoryGeneral | ASHRAE 90.1-2004 | Laboratory | General | 1.4 |  | 313
ASHRAE 90.1-2004LibraryCard File and Cataloging | ASHRAE 90.1-2004 | Library | Card File and Cataloging | 1.1 |  | 333
ASHRAE 90.1-2004LibraryReading Area | ASHRAE 90.1-2004 | Library | Reading Area | 1.2 |  | 335
ASHRAE 90.1-2004LibraryStacks | ASHRAE 90.1-2004 | Library | Stacks | 1.7 |  | 334
ASHRAE 90.1-2004LobbyFor Hotel | ASHRAE 90.1-2004 | Lobby | For Hotel | 1.1 |  | 289
ASHRAE 90.1-2004LobbyFor Motion Picture Theater | ASHRAE 90.1-2004 | Lobby | For Motion Picture Theater | 1.1 |  | 291
ASHRAE 90.1-2004LobbyFor Performing Arts Theater | ASHRAE 90.1-2004 | Lobby | For Performing Arts Theater | 3.3 |  | 290
ASHRAE 90.1-2004LobbyGeneral | ASHRAE 90.1-2004 | Lobby | General | 1.3 |  | 288
ASHRAE 90.1-2004Lounge/RecreationFor Hospital | ASHRAE 90.1-2004 | Lounge/Recreation | For Hospital | 0.8 |  | 305
ASHRAE 90.1-2004Lounge/RecreationGeneral | ASHRAE 90.1-2004 | Lounge/Recreation | General | 1.2 |  | 304
ASHRAE 90.1-2004ManufacturingDetailed Manufacturing | ASHRAE 90.1-2004 | Manufacturing | Detailed Manufacturing | 2.1 |  | 351
ASHRAE 90.1-2004ManufacturingGeneral | ASHRAE 90.1-2004 | Manufacturing | General | 0.5 |  | 353
ASHRAE 90.1-2004ManufacturingGeneral | ASHRAE 90.1-2004 | Manufacturing | General | 1.2 |  | 352
ASHRAE 90.1-2004ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-2004 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.7 |  | 350
ASHRAE 90.1-2004ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2004 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.2 |  | 349
ASHRAE 90.1-2004MuseumGeneral Exhibition | ASHRAE 90.1-2004 | Museum | General Exhibition | 1 |  | 356
ASHRAE 90.1-2004MuseumRestoration | ASHRAE 90.1-2004 | Museum | Restoration | 1.7 |  | 357
ASHRAE 90.1-2004Office-EnclosedGeneral | ASHRAE 90.1-2004 | Office-Enclosed | General | 1.1 |  | 283
ASHRAE 90.1-2004Office-Open PlanGeneral | ASHRAE 90.1-2004 | Office-Open Plan | General | 1.1 |  | 284
ASHRAE 90.1-2004Parking GarageGarage Area | ASHRAE 90.1-2004 | Parking Garage | Garage Area | 0.2 |  | 370
ASHRAE 90.1-2004Post OfficeSorting Area | ASHRAE 90.1-2004 | Post Office | Sorting Area | 1.2 |  | 331
ASHRAE 90.1-2004Religious BuildingsFellowship Hall | ASHRAE 90.1-2004 | Religious Buildings | Fellowship Hall | 0.9 |  | 362
ASHRAE 90.1-2004Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2004 | Religious Buildings | Worship Pulpit, Choir | 2.4 |  | 361
ASHRAE 90.1-2004RestroomsGeneral | ASHRAE 90.1-2004 | Restrooms | General | 0.9 |  | 314
ASHRAE 90.1-2004Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Mall Concourse | 1.7 |  | 364
ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | 1.7 |  | 363
ASHRAE 90.1-2004Sports ArenaCourt Sports Area | ASHRAE 90.1-2004 | Sports Arena | Court Sports Area | 2.3 |  | 366
ASHRAE 90.1-2004Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-2004 | Sports Arena | Indoor Playing Field Area | 1.4 |  | 367
ASHRAE 90.1-2004Sports ArenaRing Sports Area | ASHRAE 90.1-2004 | Sports Arena | Ring Sports Area | 2.7 |  | 365
ASHRAE 90.1-2004Stairs-ActiveGeneral | ASHRAE 90.1-2004 | Stairs-Active | General | 0.6 |  | 319
ASHRAE 90.1-2004TransportationAir/Train/Bus—Baggage Area | ASHRAE 90.1-2004 | Transportation | Air/Train/Bus—Baggage Area | 1 |  | 372
ASHRAE 90.1-2004TransportationAirport—Concourse | ASHRAE 90.1-2004 | Transportation | Airport—Concourse | 0.6 |  | 371
ASHRAE 90.1-2004TransportationTerminal—Ticket Counter | ASHRAE 90.1-2004 | Transportation | Terminal—Ticket Counter | 1.5 |  | 373
ASHRAE 90.1-2004WarehouseFine Material Storage | ASHRAE 90.1-2004 | Warehouse | Fine Material Storage | 1.4 |  | 368
ASHRAE 90.1-2004WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2004 | Warehouse | Medium/Bulky Material Storage | 0.9 |  | 369
ASHRAE 90.1-2004Whole BuildingAutomotive Facility | ASHRAE 90.1-2004 | Whole Building | Automotive Facility | 0.9 |  | 251
ASHRAE 90.1-2004Whole BuildingConvention Center | ASHRAE 90.1-2004 | Whole Building | Convention Center | 1.2 |  | 252
ASHRAE 90.1-2004Whole BuildingCourt House | ASHRAE 90.1-2004 | Whole Building | Court House | 1.2 |  | 253
ASHRAE 90.1-2004Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2004 | Whole Building | Dining: Bar Lounge/Leisure | 1.3 |  | 254
ASHRAE 90.1-2004Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2004 | Whole Building | Dining: Cafeteria/Fast Food | 1.4 |  | 255
ASHRAE 90.1-2004Whole BuildingDining: Family | ASHRAE 90.1-2004 | Whole Building | Dining: Family | 1.6 |  | 256
ASHRAE 90.1-2004Whole BuildingDormitory | ASHRAE 90.1-2004 | Whole Building | Dormitory | 1 |  | 257
ASHRAE 90.1-2004Whole BuildingExercise Center | ASHRAE 90.1-2004 | Whole Building | Exercise Center | 1 |  | 258
ASHRAE 90.1-2004Whole BuildingGymnasium | ASHRAE 90.1-2004 | Whole Building | Gymnasium | 1.1 |  | 259
ASHRAE 90.1-2004Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2004 | Whole Building | Health Care-Clinic | 1 |  | 260
ASHRAE 90.1-2004Whole BuildingHospital | ASHRAE 90.1-2004 | Whole Building | Hospital | 1.2 |  | 261
ASHRAE 90.1-2004Whole BuildingHotel | ASHRAE 90.1-2004 | Whole Building | Hotel | 1 |  | 262
ASHRAE 90.1-2004Whole BuildingLibrary | ASHRAE 90.1-2004 | Whole Building | Library | 1.3 |  | 263
ASHRAE 90.1-2004Whole BuildingManufacturing Facility | ASHRAE 90.1-2004 | Whole Building | Manufacturing Facility | 1.3 |  | 264
ASHRAE 90.1-2004Whole BuildingMotel | ASHRAE 90.1-2004 | Whole Building | Motel | 1 |  | 265
ASHRAE 90.1-2004Whole BuildingMotion Picture Theater | ASHRAE 90.1-2004 | Whole Building | Motion Picture Theater | 1.2 |  | 266
ASHRAE 90.1-2004Whole BuildingMulti-Family | ASHRAE 90.1-2004 | Whole Building | Multi-Family | 0.7 |  | 267
ASHRAE 90.1-2004Whole BuildingMuseum | ASHRAE 90.1-2004 | Whole Building | Museum | 1.1 |  | 268
ASHRAE 90.1-2004Whole BuildingOffice | ASHRAE 90.1-2004 | Whole Building | Office | 1 |  | 269
ASHRAE 90.1-2004Whole BuildingParking Garage | ASHRAE 90.1-2004 | Whole Building | Parking Garage | 0.3 |  | 270
ASHRAE 90.1-2004Whole BuildingPenitentiary | ASHRAE 90.1-2004 | Whole Building | Penitentiary | 1 |  | 271
ASHRAE 90.1-2004Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2004 | Whole Building | Performing Arts Theater | 1.6 |  | 272
ASHRAE 90.1-2004Whole BuildingPolice/Fire Station | ASHRAE 90.1-2004 | Whole Building | Police/Fire Station | 1 |  | 273
ASHRAE 90.1-2004Whole BuildingPost Office | ASHRAE 90.1-2004 | Whole Building | Post Office | 1.1 |  | 274
ASHRAE 90.1-2004Whole BuildingReligious Building | ASHRAE 90.1-2004 | Whole Building | Religious Building | 1.3 |  | 275
ASHRAE 90.1-2004Whole BuildingRetail | ASHRAE 90.1-2004 | Whole Building | Retail | 1.5 |  | 276
ASHRAE 90.1-2004Whole BuildingSchool/University | ASHRAE 90.1-2004 | Whole Building | School/University | 1.2 |  | 277
ASHRAE 90.1-2004Whole BuildingSports Arena | ASHRAE 90.1-2004 | Whole Building | Sports Arena | 1.1 |  | 278
ASHRAE 90.1-2004Whole BuildingTown Hall | ASHRAE 90.1-2004 | Whole Building | Town Hall | 1.1 |  | 279
ASHRAE 90.1-2004Whole BuildingTransportation | ASHRAE 90.1-2004 | Whole Building | Transportation | 1 |  | 280
ASHRAE 90.1-2004Whole BuildingWarehouse | ASHRAE 90.1-2004 | Whole Building | Warehouse | 0.8 |  | 281
ASHRAE 90.1-2004Whole BuildingWorkshop | ASHRAE 90.1-2004 | Whole Building | Workshop | 1.4 |  | 282
ASHRAE 90.1-2004WorkshopWorkshop | ASHRAE 90.1-2004 | Workshop | Workshop | 1.9 |  | 359
ASHRAE 90.1-2007Whole BuildingAutomotive Facility | ASHRAE 90.1-2007 | Whole Building | Automotive Facility | 0.9 |  | 376
ASHRAE 90.1-2007Whole BuildingConvention Center | ASHRAE 90.1-2007 | Whole Building | Convention Center | 1.2 |  | 377
ASHRAE 90.1-2007Whole BuildingCourt House | ASHRAE 90.1-2007 | Whole Building | Court House | 1.2 |  | 378
ASHRAE 90.1-2007Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2007 | Whole Building | Dining: Bar Lounge/Leisure | 1.3 |  | 379
ASHRAE 90.1-2007Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2007 | Whole Building | Dining: Cafeteria/Fast Food | 1.4 |  | 380
ASHRAE 90.1-2007Whole BuildingDining: Family | ASHRAE 90.1-2007 | Whole Building | Dining: Family | 1.6 |  | 381
ASHRAE 90.1-2007Whole BuildingDormitory | ASHRAE 90.1-2007 | Whole Building | Dormitory | 1 |  | 382
ASHRAE 90.1-2007Whole BuildingExercise Center | ASHRAE 90.1-2007 | Whole Building | Exercise Center | 1 |  | 383
ASHRAE 90.1-2007Whole BuildingGymnasium | ASHRAE 90.1-2007 | Whole Building | Gymnasium | 1.1 |  | 384
ASHRAE 90.1-2007Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2007 | Whole Building | Health Care-Clinic | 1 |  | 385
ASHRAE 90.1-2007Whole BuildingHospital | ASHRAE 90.1-2007 | Whole Building | Hospital | 1.2 |  | 386
ASHRAE 90.1-2007Whole BuildingHotel | ASHRAE 90.1-2007 | Whole Building | Hotel | 1 |  | 387
ASHRAE 90.1-2007Whole BuildingLibrary | ASHRAE 90.1-2007 | Whole Building | Library | 1.3 |  | 388
ASHRAE 90.1-2007Whole BuildingManufacturing Facility | ASHRAE 90.1-2007 | Whole Building | Manufacturing Facility | 1.3 |  | 389
ASHRAE 90.1-2007Whole BuildingMotel | ASHRAE 90.1-2007 | Whole Building | Motel | 1 |  | 390
ASHRAE 90.1-2007Whole BuildingMotion Picture Theater | ASHRAE 90.1-2007 | Whole Building | Motion Picture Theater | 1.2 |  | 391
ASHRAE 90.1-2007Whole BuildingMulti-Family | ASHRAE 90.1-2007 | Whole Building | Multi-Family | 0.7 |  | 392
ASHRAE 90.1-2007Whole BuildingMuseum | ASHRAE 90.1-2007 | Whole Building | Museum | 1.1 |  | 393
ASHRAE 90.1-2007Whole BuildingOffice | ASHRAE 90.1-2007 | Whole Building | Office | 1 |  | 394
ASHRAE 90.1-2007Whole BuildingParking Garage | ASHRAE 90.1-2007 | Whole Building | Parking Garage | 0.3 |  | 395
ASHRAE 90.1-2007Whole BuildingPenitentiary | ASHRAE 90.1-2007 | Whole Building | Penitentiary | 1 |  | 396
ASHRAE 90.1-2007Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2007 | Whole Building | Performing Arts Theater | 1.6 |  | 397
ASHRAE 90.1-2007Whole BuildingPolice/Fire Station | ASHRAE 90.1-2007 | Whole Building | Police/Fire Station | 1 |  | 398
ASHRAE 90.1-2007Whole BuildingPost Office | ASHRAE 90.1-2007 | Whole Building | Post Office | 1.1 |  | 399
ASHRAE 90.1-2007Whole BuildingReligious Building | ASHRAE 90.1-2007 | Whole Building | Religious Building | 1.3 |  | 400
ASHRAE 90.1-2007Whole BuildingRetail | ASHRAE 90.1-2007 | Whole Building | Retail | 1.5 |  | 401
ASHRAE 90.1-2007Whole BuildingSchool/University | ASHRAE 90.1-2007 | Whole Building | School/University | 1.2 |  | 402
ASHRAE 90.1-2007Whole BuildingSports Arena | ASHRAE 90.1-2007 | Whole Building | Sports Arena | 1.1 |  | 403
ASHRAE 90.1-2007Whole BuildingTown Hall | ASHRAE 90.1-2007 | Whole Building | Town Hall | 1.1 |  | 404
ASHRAE 90.1-2007Whole BuildingTransportation | ASHRAE 90.1-2007 | Whole Building | Transportation | 1 |  | 405
ASHRAE 90.1-2007Whole BuildingWarehouse | ASHRAE 90.1-2007 | Whole Building | Warehouse | 0.8 |  | 406
ASHRAE 90.1-2007Whole BuildingWorkshop | ASHRAE 90.1-2007 | Whole Building | Workshop | 1.4 |  | 407
ASHRAE 90.1-2007Office-EnclosedGeneral | ASHRAE 90.1-2007 | Office-Enclosed | General | 1.1 |  | 408
ASHRAE 90.1-2007Office-Open PlanGeneral | ASHRAE 90.1-2007 | Office-Open Plan | General | 1.1 |  | 409
ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | 1.3 |  | 410
ASHRAE 90.1-2007Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2007 | Classroom/Lecture/Training | General | 1.4 |  | 411
ASHRAE 90.1-2007Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2007 | Classroom/Lecture/Training | For Penitentiary | 1.3 |  | 412
ASHRAE 90.1-2007LobbyGeneral | ASHRAE 90.1-2007 | Lobby | General | 1.3 |  | 413
ASHRAE 90.1-2007LobbyFor Hotel | ASHRAE 90.1-2007 | Lobby | For Hotel | 1.1 |  | 414
ASHRAE 90.1-2007LobbyFor Performing Arts Theater | ASHRAE 90.1-2007 | Lobby | For Performing Arts Theater | 3.3 |  | 415
ASHRAE 90.1-2007LobbyFor Motion Picture Theater | ASHRAE 90.1-2007 | Lobby | For Motion Picture Theater | 1.1 |  | 416
ASHRAE 90.1-2007Audience/Seating AreaGeneral | ASHRAE 90.1-2007 | Audience/Seating Area | General | 0.9 |  | 417
ASHRAE 90.1-2007Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2007 | Audience/Seating Area | For Gymnasium | 0.4 |  | 418
ASHRAE 90.1-2007Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-2007 | Audience/Seating Area | For Exercise Center | 0.3 |  | 419
ASHRAE 90.1-2007Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2007 | Audience/Seating Area | For Convention Center | 0.7 |  | 420
ASHRAE 90.1-2007Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2007 | Audience/Seating Area | For Penitentiary | 0.7 |  | 421
ASHRAE 90.1-2007Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2007 | Audience/Seating Area | For Religious Buildings | 1.7 |  | 422
ASHRAE 90.1-2007Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-2007 | Audience/Seating Area | For Sports Arena | 0.4 |  | 423
ASHRAE 90.1-2007Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-2007 | Audience/Seating Area | For Performing Arts Theater | 2.6 |  | 424
ASHRAE 90.1-2007Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2007 | Audience/Seating Area | For Motion Picture Theater | 1.2 |  | 425
ASHRAE 90.1-2007Audience/Seating AreaFor Transportation | ASHRAE 90.1-2007 | Audience/Seating Area | For Transportation | 0.5 |  | 426
ASHRAE 90.1-2007AtriumFirst Three Floors | ASHRAE 90.1-2007 | Atrium | First Three Floors | 0.6 |  | 427
ASHRAE 90.1-2007AtriumEach Floor over First Three Floors | ASHRAE 90.1-2007 | Atrium | Each Floor over First Three Floors | 0.2 |  | 428
ASHRAE 90.1-2007Lounge/RecreationGeneral | ASHRAE 90.1-2007 | Lounge/Recreation | General | 1.2 |  | 429
ASHRAE 90.1-2007Lounge/RecreationFor Hospital | ASHRAE 90.1-2007 | Lounge/Recreation | For Hospital | 0.8 |  | 430
ASHRAE 90.1-2007Dining AreaGeneral | ASHRAE 90.1-2007 | Dining Area | General | 0.9 |  | 431
ASHRAE 90.1-2007Dining AreaFor Penitentiary | ASHRAE 90.1-2007 | Dining Area | For Penitentiary | 1.3 |  | 432
ASHRAE 90.1-2007Dining AreaFor Hotel | ASHRAE 90.1-2007 | Dining Area | For Hotel | 1.3 |  | 433
ASHRAE 90.1-2007Dining AreaFor Motel | ASHRAE 90.1-2007 | Dining Area | For Motel | 1.2 |  | 434
ASHRAE 90.1-2007Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2007 | Dining Area | For Bar Lounge/Leisure Dining | 1.4 |  | 435
ASHRAE 90.1-2007Dining AreaFor Family Dining | ASHRAE 90.1-2007 | Dining Area | For Family Dining | 2.1 |  | 436
ASHRAE 90.1-2007Food PreparationGeneral | ASHRAE 90.1-2007 | Food Preparation | General | 1.2 |  | 437
ASHRAE 90.1-2007LaboratoryGeneral | ASHRAE 90.1-2007 | Laboratory | General | 1.4 |  | 438
ASHRAE 90.1-2007RestroomsGeneral | ASHRAE 90.1-2007 | Restrooms | General | 0.9 |  | 439
ASHRAE 90.1-2007Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-2007 | Dressing/Locker/Fitting Room | General | 0.6 |  | 440
ASHRAE 90.1-2007Corridor/TransitionGeneral | ASHRAE 90.1-2007 | Corridor/Transition | General | 0.5 |  | 441
ASHRAE 90.1-2007Corridor/TransitionFor Hospital | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | 1 |  | 442
ASHRAE 90.1-2007Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-2007 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 443
ASHRAE 90.1-2007Stairs-ActiveGeneral | ASHRAE 90.1-2007 | Stairs-Active | General | 0.6 |  | 444
ASHRAE 90.1-2007Active StorageGeneral | ASHRAE 90.1-2007 | Active Storage | General | 0.8 |  | 445
ASHRAE 90.1-2007Active StorageFor Hospital | ASHRAE 90.1-2007 | Active Storage | For Hospital | 0.9 |  | 446
ASHRAE 90.1-2007Inactive storageGeneral | ASHRAE 90.1-2007 | Inactive storage | General | 0.3 |  | 447
ASHRAE 90.1-2007Inactive storageFor Museum | ASHRAE 90.1-2007 | Inactive storage | For Museum | 0.8 |  | 448
ASHRAE 90.1-2007Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Playing Area | 1.4 |  | 449
ASHRAE 90.1-2007Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Exercise Area | 0.9 |  | 450
ASHRAE 90.1-2007Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-2007 | Courthouse/Police Station/Penitentiary | Courtroom | 1.9 |  | 451
ASHRAE 90.1-2007Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-2007 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.9 |  | 452
ASHRAE 90.1-2007Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-2007 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.3 |  | 453
ASHRAE 90.1-2007Fire StationsFire Station Engine Room | ASHRAE 90.1-2007 | Fire Stations | Fire Station Engine Room | 0.8 |  | 454
ASHRAE 90.1-2007Fire StationsSleeping Quarters | ASHRAE 90.1-2007 | Fire Stations | Sleeping Quarters | 0.3 |  | 455
ASHRAE 90.1-2007Post OfficeSorting Area | ASHRAE 90.1-2007 | Post Office | Sorting Area | 1.2 |  | 456
ASHRAE 90.1-2007Convention CenterExhibit Space | ASHRAE 90.1-2007 | Convention Center | Exhibit Space | 1.3 |  | 457
ASHRAE 90.1-2007LibraryCard File and Cataloging | ASHRAE 90.1-2007 | Library | Card File and Cataloging | 1.1 |  | 458
ASHRAE 90.1-2007LibraryStacks | ASHRAE 90.1-2007 | Library | Stacks | 1.7 |  | 459
ASHRAE 90.1-2007LibraryReading Area | ASHRAE 90.1-2007 | Library | Reading Area | 1.2 |  | 460
ASHRAE 90.1-2007HospitalEmergency | ASHRAE 90.1-2007 | Hospital | Emergency | 2.7 |  | 461
ASHRAE 90.1-2007HospitalRecovery | ASHRAE 90.1-2007 | Hospital | Recovery | 0.8 |  | 462
ASHRAE 90.1-2007HospitalNurse Station | ASHRAE 90.1-2007 | Hospital | Nurse Station | 1 |  | 463
ASHRAE 90.1-2007HospitalExam/Treatment | ASHRAE 90.1-2007 | Hospital | Exam/Treatment | 1.5 |  | 464
ASHRAE 90.1-2007HospitalPharmacy | ASHRAE 90.1-2007 | Hospital | Pharmacy | 1.2 |  | 465
ASHRAE 90.1-2007HospitalPatient Room | ASHRAE 90.1-2007 | Hospital | Patient Room | 0.7 |  | 466
ASHRAE 90.1-2007HospitalOperating Room | ASHRAE 90.1-2007 | Hospital | Operating Room | 2.2 |  | 467
ASHRAE 90.1-2007HospitalNursery | ASHRAE 90.1-2007 | Hospital | Nursery | 0.6 |  | 468
ASHRAE 90.1-2007HospitalMedical Supply | ASHRAE 90.1-2007 | Hospital | Medical Supply | 1.4 |  | 469
ASHRAE 90.1-2007HospitalPhysical Therapy | ASHRAE 90.1-2007 | Hospital | Physical Therapy | 0.9 |  | 470
ASHRAE 90.1-2007HospitalRadiology | ASHRAE 90.1-2007 | Hospital | Radiology | 0.4 |  | 471
ASHRAE 90.1-2007HospitalLaundry-Washing | ASHRAE 90.1-2007 | Hospital | Laundry-Washing | 0.6 |  | 472
ASHRAE 90.1-2007AutomotiveService/Repair | ASHRAE 90.1-2007 | Automotive | Service/Repair | 0.7 |  | 473
ASHRAE 90.1-2007ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2007 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.2 |  | 474
ASHRAE 90.1-2007ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-2007 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.7 |  | 475
ASHRAE 90.1-2007ManufacturingDetailed Manufacturing | ASHRAE 90.1-2007 | Manufacturing | Detailed Manufacturing | 2.1 |  | 476
ASHRAE 90.1-2007ManufacturingEquipment Room | ASHRAE 90.1-2007 | Manufacturing | Equipment Room | 1.2 |  | 477
ASHRAE 90.1-2007ManufacturingControl Room | ASHRAE 90.1-2007 | Manufacturing | Control Room | 0.5 |  | 478
ASHRAE 90.1-2007Hotel/MotelGuest Rooms | ASHRAE 90.1-2007 | Hotel/Motel | Guest Rooms | 1.1 |  | 479
ASHRAE 90.1-2007DormitoryLiving Quarters | ASHRAE 90.1-2007 | Dormitory | Living Quarters | 1.1 |  | 480
ASHRAE 90.1-2007MuseumGeneral Exhibition | ASHRAE 90.1-2007 | Museum | General Exhibition | 1 |  | 481
ASHRAE 90.1-2007MuseumRestoration | ASHRAE 90.1-2007 | Museum | Restoration | 1.7 |  | 482
ASHRAE 90.1-2007Electrical/MechanicalGeneral | ASHRAE 90.1-2007 | Electrical/Mechanical | General | 1.5 |  | 483
ASHRAE 90.1-2007WorkshopGeneral | ASHRAE 90.1-2007 | Workshop | General | 1.9 |  | 484
ASHRAE 90.1-2007Bank/OfficeBanking Activity Area | ASHRAE 90.1-2007 | Bank/Office | Banking Activity Area | 1.5 |  | 485
ASHRAE 90.1-2007Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2007 | Religious Buildings | Worship Pulpit, Choir | 2.4 |  | 486
ASHRAE 90.1-2007Religious BuildingsFellowship Hall | ASHRAE 90.1-2007 | Religious Buildings | Fellowship Hall | 0.9 |  | 487
ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | 1.7 |  | 488
ASHRAE 90.1-2007Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Mall Concourse | 1.7 |  | 489
ASHRAE 90.1-2007Sports ArenaRing Sports Area | ASHRAE 90.1-2007 | Sports Arena | Ring Sports Area | 2.7 |  | 490
ASHRAE 90.1-2007Sports ArenaCourt Sports Area | ASHRAE 90.1-2007 | Sports Arena | Court Sports Area | 2.3 |  | 491
ASHRAE 90.1-2007Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-2007 | Sports Arena | Indoor Playing Field Area | 1.4 |  | 492
ASHRAE 90.1-2007WarehouseFine Material Storage | ASHRAE 90.1-2007 | Warehouse | Fine Material Storage | 1.4 |  | 493
ASHRAE 90.1-2007WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2007 | Warehouse | Medium/Bulky Material Storage | 0.9 |  | 494
ASHRAE 90.1-2007Parking GarageGarage Area | ASHRAE 90.1-2007 | Parking Garage | Garage Area | 0.2 |  | 495
ASHRAE 90.1-2007TransportationAirport-Concourse | ASHRAE 90.1-2007 | Transportation | Airport-Concourse | 0.6 |  | 496
ASHRAE 90.1-2007TransportationAir/Train/Bus-Baggage Area | ASHRAE 90.1-2007 | Transportation | Air/Train/Bus-Baggage Area | 1 |  | 497
ASHRAE 90.1-2007TransportationTerminal-Ticket Counter | ASHRAE 90.1-2007 | Transportation | Terminal-Ticket Counter | 1.5 |  | 498
ASHRAE 90.1-2007Exterior SpacesGeneral | ASHRAE 90.1-2007 | Exterior Spaces | General | 0 |  | 499
ASHRAE 90.1-2007AtticsGeneral | ASHRAE 90.1-2007 | Attics | General | 0 |  | 500
GGHC v2.2Health CareAnesthesia Storage | GGHC v2.2 | Health Care | Anesthesia Storage | 3 |  | 501
GGHC v2.2Health CareAngiographic-All Other Types | GGHC v2.2 | Health Care | Angiographic-All Other Types | 3 |  | 502
GGHC v2.2Health CareAngiographic-Heart Only | GGHC v2.2 | Health Care | Angiographic-Heart Only | 3 |  | 503
GGHC v2.2Health CareAutopsy | GGHC v2.2 | Health Care | Autopsy | 1.2 |  | 504
GGHC v2.2Health CareBathroom/ Public | GGHC v2.2 | Health Care | Bathroom/ Public | 0.6 |  | 505
GGHC v2.2Health CareBedpan Room | GGHC v2.2 | Health Care | Bedpan Room | 0.5 |  | 506
GGHC v2.2Health CareCast Room | GGHC v2.2 | Health Care | Cast Room | 3 |  | 507
GGHC v2.2Health CareClean Linen Storage | GGHC v2.2 | Health Care | Clean Linen Storage | 0.5 |  | 508
GGHC v2.2Health CareClean Utility / Workroom | GGHC v2.2 | Health Care | Clean Utility / Workroom | 1.2 |  | 509
GGHC v2.2Health CareConference Rooms | GGHC v2.2 | Health Care | Conference Rooms | 1.2 |  | 510
GGHC v2.2Health CareCorridors | GGHC v2.2 | Health Care | Corridors | 0.6 |  | 511
GGHC v2.2Health CareCystoscopy | GGHC v2.2 | Health Care | Cystoscopy | 3 |  | 512
GGHC v2.2Health CareDarkroom | GGHC v2.2 | Health Care | Darkroom | 0.3 |  | 513
GGHC v2.2Health CareDecontamination | GGHC v2.2 | Health Care | Decontamination | 1.2 |  | 514
GGHC v2.2Health CareDelivery Room | GGHC v2.2 | Health Care | Delivery Room | 4.5 |  | 515
GGHC v2.2Health CareDietary Day Storage | GGHC v2.2 | Health Care | Dietary Day Storage | 0.5 |  | 516
GGHC v2.2Health CareDining Room | GGHC v2.2 | Health Care | Dining Room | 1.1 |  | 517
GGHC v2.2Health CareDishwashing | GGHC v2.2 | Health Care | Dishwashing | 1.7 |  | 518
GGHC v2.2Health CareEndoscopy | GGHC v2.2 | Health Care | Endoscopy | 3 |  | 519
GGHC v2.2Health CareHistology | GGHC v2.2 | Health Care | Histology | 4.5 |  | 520
GGHC v2.2Health CareIsolation | GGHC v2.2 | Health Care | Isolation | 0.5 |  | 521
GGHC v2.2Health CareJanitors Closet / Utility | GGHC v2.2 | Health Care | Janitors Closet / Utility | 0.5 |  | 522
GGHC v2.2Health CareKitchen, Food Preparation | GGHC v2.2 | Health Care | Kitchen, Food Preparation | 1.7 |  | 523
GGHC v2.2Health CareLabor/ Delivery/Recovery | GGHC v2.2 | Health Care | Labor/ Delivery/Recovery | 4.5 |  | 524
GGHC v2.2Health CareL / D / R / Post Partum | GGHC v2.2 | Health Care | L / D / R / Post Partum | 0.7 |  | 525
GGHC v2.2Health CareLaboratory | GGHC v2.2 | Health Care | Laboratory | 3 |  | 526
GGHC v2.2Health CareLinen Storage, Clean | GGHC v2.2 | Health Care | Linen Storage, Clean | 0.5 |  | 527
GGHC v2.2Health CareLobby | GGHC v2.2 | Health Care | Lobby | 1.1 |  | 528
GGHC v2.2Health CareLockers | GGHC v2.2 | Health Care | Lockers | 0.7 |  | 529
GGHC v2.2Health CareMammography | GGHC v2.2 | Health Care | Mammography | 3 |  | 530
GGHC v2.2Health CareMechanical Equipment Room | GGHC v2.2 | Health Care | Mechanical Equipment Room | 0.7 |  | 531
GGHC v2.2Health CareMedical Records | GGHC v2.2 | Health Care | Medical Records | 3 |  | 532
GGHC v2.2Health CareNuclear Medicine, Hot Lab | GGHC v2.2 | Health Care | Nuclear Medicine, Hot Lab | 1.2 |  | 533
GGHC v2.2Health CareNursery, General | GGHC v2.2 | Health Care | Nursery, General | 3 |  | 534
GGHC v2.2Health CareNursery, Exam | GGHC v2.2 | Health Care | Nursery, Exam | 0.7 |  | 535
GGHC v2.2Health CareNursing Stations- General | GGHC v2.2 | Health Care | Nursing Stations- General | 1.2 |  | 536
GGHC v2.2Health CareOperating Room | GGHC v2.2 | Health Care | Operating Room | 4.5 |  | 537
GGHC v2.2Health CarePathology | GGHC v2.2 | Health Care | Pathology | 3 |  | 538
GGHC v2.2Health CarePatient Room | GGHC v2.2 | Health Care | Patient Room | 0.5 |  | 539
GGHC v2.2Health CarePharmacy / Medicine Room | GGHC v2.2 | Health Care | Pharmacy / Medicine Room | 3 |  | 540
GGHC v2.2Health CarePhysical Therapy and Hydrotherapy | GGHC v2.2 | Health Care | Physical Therapy and Hydrotherapy | 1.2 |  | 541
GGHC v2.2Health CareRecovery | GGHC v2.2 | Health Care | Recovery | 3 |  | 542
GGHC v2.2Health CareScrub Up Area, Surgical Corridor | GGHC v2.2 | Health Care | Scrub Up Area, Surgical Corridor | 4.5 |  | 543
GGHC v2.2Health CareSoiled Linen, Sorting | GGHC v2.2 | Health Care | Soiled Linen, Sorting | 1.2 |  | 544
GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | 3 |  | 545
GGHC v2.2Health CareSpecial Procedure Room, Invasive | GGHC v2.2 | Health Care | Special Procedure Room, Invasive | 3 |  | 546
GGHC v2.2Health CareStairways | GGHC v2.2 | Health Care | Stairways | 0.6 |  | 547
GGHC v2.2Health CareSterilizer Room | GGHC v2.2 | Health Care | Sterilizer Room | 1.2 |  | 548
GGHC v2.2Health CareSub-Sterile | GGHC v2.2 | Health Care | Sub-Sterile | 0.7 |  | 549
GGHC v2.2Health CareSurgical Supply | GGHC v2.2 | Health Care | Surgical Supply | 1.2 |  | 550
GGHC v2.2Health CareTrash Chute Room | GGHC v2.2 | Health Care | Trash Chute Room | 0.5 |  | 551
GGHC v2.2Health CareTrauma | GGHC v2.2 | Health Care | Trauma | 3 |  | 552
GGHC v2.2Health CareTreatment / Examination | GGHC v2.2 | Health Care | Treatment / Examination | 1.2 |  | 553
GGHC v2.2Health CareUnsterile Supply | GGHC v2.2 | Health Care | Unsterile Supply | 0.5 |  | 554
GGHC v2.2Health CareWaiting Areas/Lounges | GGHC v2.2 | Health Care | Waiting Areas/Lounges | 1.1 |  | 555
GGHC v2.2Health CareX-ray, Diagnostic and Treatment | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | 3 |  | 556
ASHRAE 189.1-2009Whole BuildingAutomotive Facility | ASHRAE 189.1-2009 | Whole Building | Automotive Facility | 0.81
ASHRAE 189.1-2009Whole BuildingConvention Center | ASHRAE 189.1-2009 | Whole Building | Convention Center | 1.08
ASHRAE 189.1-2009Whole BuildingCourt House | ASHRAE 189.1-2009 | Whole Building | Court House | 1.08
ASHRAE 189.1-2009Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 189.1-2009 | Whole Building | Dining: Bar Lounge/Leisure | 1.17
ASHRAE 189.1-2009Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 189.1-2009 | Whole Building | Dining: Cafeteria/Fast Food | 1.26
ASHRAE 189.1-2009Whole BuildingDining: Family | ASHRAE 189.1-2009 | Whole Building | Dining: Family | 1.44
ASHRAE 189.1-2009Whole BuildingDormitory | ASHRAE 189.1-2009 | Whole Building | Dormitory | 0.9
ASHRAE 189.1-2009Whole BuildingExercise Center | ASHRAE 189.1-2009 | Whole Building | Exercise Center | 0.9
ASHRAE 189.1-2009Whole BuildingGymnasium | ASHRAE 189.1-2009 | Whole Building | Gymnasium | 0.99
ASHRAE 189.1-2009Whole BuildingHealth Care-Clinic | ASHRAE 189.1-2009 | Whole Building | Health Care-Clinic | 0.9
ASHRAE 189.1-2009Whole BuildingHospital | ASHRAE 189.1-2009 | Whole Building | Hospital | 1.08
ASHRAE 189.1-2009Whole BuildingHotel | ASHRAE 189.1-2009 | Whole Building | Hotel | 0.9
ASHRAE 189.1-2009Whole BuildingLibrary | ASHRAE 189.1-2009 | Whole Building | Library | 1.17
ASHRAE 189.1-2009Whole BuildingManufacturing Facility | ASHRAE 189.1-2009 | Whole Building | Manufacturing Facility | 1.17
ASHRAE 189.1-2009Whole BuildingMotel | ASHRAE 189.1-2009 | Whole Building | Motel | 0.9
ASHRAE 189.1-2009Whole BuildingMotion Picture Theater | ASHRAE 189.1-2009 | Whole Building | Motion Picture Theater | 1.08
ASHRAE 189.1-2009Whole BuildingMulti-Family | ASHRAE 189.1-2009 | Whole Building | Multi-Family | 0.63
ASHRAE 189.1-2009Whole BuildingMuseum | ASHRAE 189.1-2009 | Whole Building | Museum | 0.99
ASHRAE 189.1-2009Whole BuildingOffice | ASHRAE 189.1-2009 | Whole Building | Office | 0.9
ASHRAE 189.1-2009Whole BuildingParking Garage | ASHRAE 189.1-2009 | Whole Building | Parking Garage | 0.27
ASHRAE 189.1-2009Whole BuildingPenitentiary | ASHRAE 189.1-2009 | Whole Building | Penitentiary | 0.9
ASHRAE 189.1-2009Whole BuildingPerforming Arts Theater | ASHRAE 189.1-2009 | Whole Building | Performing Arts Theater | 1.44
ASHRAE 189.1-2009Whole BuildingPolice/Fire Station | ASHRAE 189.1-2009 | Whole Building | Police/Fire Station | 0.9
ASHRAE 189.1-2009Whole BuildingPost Office | ASHRAE 189.1-2009 | Whole Building | Post Office | 0.99
ASHRAE 189.1-2009Whole BuildingReligious Building | ASHRAE 189.1-2009 | Whole Building | Religious Building | 1.17
ASHRAE 189.1-2009Whole BuildingRetail | ASHRAE 189.1-2009 | Whole Building | Retail | 1.35
ASHRAE 189.1-2009Whole BuildingSchool/University | ASHRAE 189.1-2009 | Whole Building | School/University | 1.08
ASHRAE 189.1-2009Whole BuildingSports Arena | ASHRAE 189.1-2009 | Whole Building | Sports Arena | 0.99
ASHRAE 189.1-2009Whole BuildingTown Hall | ASHRAE 189.1-2009 | Whole Building | Town Hall | 0.99
ASHRAE 189.1-2009Whole BuildingTransportation | ASHRAE 189.1-2009 | Whole Building | Transportation | 0.9
ASHRAE 189.1-2009Whole BuildingWarehouse | ASHRAE 189.1-2009 | Whole Building | Warehouse | 0.72
ASHRAE 189.1-2009Whole BuildingWorkshop | ASHRAE 189.1-2009 | Whole Building | Workshop | 1.26
ASHRAE 189.1-2009Office-EnclosedGeneral | ASHRAE 189.1-2009 | Office-Enclosed | General | 0.99
ASHRAE 189.1-2009Office-Open PlanGeneral | ASHRAE 189.1-2009 | Office-Open Plan | General | 0.99
ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | 1.17
ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | 1.26
ASHRAE 189.1-2009Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 189.1-2009 | Classroom/Lecture/Training | For Penitentiary | 1.17
ASHRAE 189.1-2009LobbyGeneral | ASHRAE 189.1-2009 | Lobby | General | 1.17
ASHRAE 189.1-2009LobbyFor Hotel | ASHRAE 189.1-2009 | Lobby | For Hotel | 0.99
ASHRAE 189.1-2009LobbyFor Performing Arts Theater | ASHRAE 189.1-2009 | Lobby | For Performing Arts Theater | 2.97
ASHRAE 189.1-2009LobbyFor Motion Picture Theater | ASHRAE 189.1-2009 | Lobby | For Motion Picture Theater | 0.99
ASHRAE 189.1-2009Audience/Seating AreaGeneral | ASHRAE 189.1-2009 | Audience/Seating Area | General | 0.81
ASHRAE 189.1-2009Audience/Seating AreaFor Gymnasium | ASHRAE 189.1-2009 | Audience/Seating Area | For Gymnasium | 0.36
ASHRAE 189.1-2009Audience/Seating AreaFor Exercise Center | ASHRAE 189.1-2009 | Audience/Seating Area | For Exercise Center | 0.27
ASHRAE 189.1-2009Audience/Seating AreaFor Convention Center | ASHRAE 189.1-2009 | Audience/Seating Area | For Convention Center | 0.63
ASHRAE 189.1-2009Audience/Seating AreaFor Penitentiary | ASHRAE 189.1-2009 | Audience/Seating Area | For Penitentiary | 0.63
ASHRAE 189.1-2009Audience/Seating AreaFor Religious Buildings | ASHRAE 189.1-2009 | Audience/Seating Area | For Religious Buildings | 1.53
ASHRAE 189.1-2009Audience/Seating AreaFor Sports Arena | ASHRAE 189.1-2009 | Audience/Seating Area | For Sports Arena | 0.36
ASHRAE 189.1-2009Audience/Seating AreaFor Performing Arts Theater | ASHRAE 189.1-2009 | Audience/Seating Area | For Performing Arts Theater | 2.34
ASHRAE 189.1-2009Audience/Seating AreaFor Motion Picture Theater | ASHRAE 189.1-2009 | Audience/Seating Area | For Motion Picture Theater | 1.08
ASHRAE 189.1-2009Audience/Seating AreaFor Transportation | ASHRAE 189.1-2009 | Audience/Seating Area | For Transportation | 0.45
ASHRAE 189.1-2009AtriumFirst Three Floors | ASHRAE 189.1-2009 | Atrium | First Three Floors | 0.54
ASHRAE 189.1-2009AtriumEach Floor over First Three Floors | ASHRAE 189.1-2009 | Atrium | Each Floor over First Three Floors | 0.18
ASHRAE 189.1-2009Lounge/RecreationGeneral | ASHRAE 189.1-2009 | Lounge/Recreation | General | 1.08
ASHRAE 189.1-2009Lounge/RecreationFor Hospital | ASHRAE 189.1-2009 | Lounge/Recreation | For Hospital | 0.72
ASHRAE 189.1-2009Dining AreaGeneral | ASHRAE 189.1-2009 | Dining Area | General | 0.81
ASHRAE 189.1-2009Dining AreaFor Penitentiary | ASHRAE 189.1-2009 | Dining Area | For Penitentiary | 1.17
ASHRAE 189.1-2009Dining AreaFor Hotel | ASHRAE 189.1-2009 | Dining Area | For Hotel | 1.17
ASHRAE 189.1-2009Dining AreaFor Motel | ASHRAE 189.1-2009 | Dining Area | For Motel | 1.08
ASHRAE 189.1-2009Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 189.1-2009 | Dining Area | For Bar Lounge/Leisure Dining | 1.26
ASHRAE 189.1-2009Dining AreaFor Family Dining | ASHRAE 189.1-2009 | Dining Area | For Family Dining | 1.89
ASHRAE 189.1-2009Food PreparationGeneral | ASHRAE 189.1-2009 | Food Preparation | General | 1.08
ASHRAE 189.1-2009LaboratoryGeneral | ASHRAE 189.1-2009 | Laboratory | General | 1.26
ASHRAE 189.1-2009RestroomsGeneral | ASHRAE 189.1-2009 | Restrooms | General | 0.81
ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | 0.54
ASHRAE 189.1-2009Corridor/TransitionGeneral | ASHRAE 189.1-2009 | Corridor/Transition | General | 0.45
ASHRAE 189.1-2009Corridor/TransitionFor Hospital | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | 0.9
ASHRAE 189.1-2009Corridor/TransitionFor Manufacturing Facility | ASHRAE 189.1-2009 | Corridor/Transition | For Manufacturing Facility | 0.45
ASHRAE 189.1-2009Stairs-ActiveGeneral | ASHRAE 189.1-2009 | Stairs-Active | General | 0.54
ASHRAE 189.1-2009Active StorageGeneral | ASHRAE 189.1-2009 | Active Storage | General | 0.72
ASHRAE 189.1-2009Active StorageFor Hospital | ASHRAE 189.1-2009 | Active Storage | For Hospital | 0.81
ASHRAE 189.1-2009Inactive storageGeneral | ASHRAE 189.1-2009 | Inactive storage | General | 0.27
ASHRAE 189.1-2009Inactive storageFor Museum | ASHRAE 189.1-2009 | Inactive storage | For Museum | 0.72
ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | 1.26
ASHRAE 189.1-2009Gymnasium/Exercise CenterExercise Area | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Exercise Area | 0.81
ASHRAE 189.1-2009Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 189.1-2009 | Courthouse/Police Station/Penitentiary | Courtroom | 1.71
ASHRAE 189.1-2009Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 189.1-2009 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.81
ASHRAE 189.1-2009Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 189.1-2009 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.17
ASHRAE 189.1-2009Fire StationsFire Station Engine Room | ASHRAE 189.1-2009 | Fire Stations | Fire Station Engine Room | 0.72
ASHRAE 189.1-2009Fire StationsSleeping Quarters | ASHRAE 189.1-2009 | Fire Stations | Sleeping Quarters | 0.27
ASHRAE 189.1-2009Post OfficeSorting Area | ASHRAE 189.1-2009 | Post Office | Sorting Area | 1.08
ASHRAE 189.1-2009Convention CenterExhibit Space | ASHRAE 189.1-2009 | Convention Center | Exhibit Space | 1.17
ASHRAE 189.1-2009LibraryCard File and Cataloging | ASHRAE 189.1-2009 | Library | Card File and Cataloging | 0.99
ASHRAE 189.1-2009LibraryStacks | ASHRAE 189.1-2009 | Library | Stacks | 1.53
ASHRAE 189.1-2009LibraryReading Area | ASHRAE 189.1-2009 | Library | Reading Area | 1.08
ASHRAE 189.1-2009HospitalEmergency | ASHRAE 189.1-2009 | Hospital | Emergency | 2.43
ASHRAE 189.1-2009HospitalRecovery | ASHRAE 189.1-2009 | Hospital | Recovery | 0.72
ASHRAE 189.1-2009HospitalNurse Station | ASHRAE 189.1-2009 | Hospital | Nurse Station | 0.9
ASHRAE 189.1-2009HospitalExam/Treatment | ASHRAE 189.1-2009 | Hospital | Exam/Treatment | 1.35
ASHRAE 189.1-2009HospitalPharmacy | ASHRAE 189.1-2009 | Hospital | Pharmacy | 1.08
ASHRAE 189.1-2009HospitalPatient Room | ASHRAE 189.1-2009 | Hospital | Patient Room | 0.63
ASHRAE 189.1-2009HospitalOperating Room | ASHRAE 189.1-2009 | Hospital | Operating Room | 1.98
ASHRAE 189.1-2009HospitalNursery | ASHRAE 189.1-2009 | Hospital | Nursery | 0.54
ASHRAE 189.1-2009HospitalMedical Supply | ASHRAE 189.1-2009 | Hospital | Medical Supply | 1.26
ASHRAE 189.1-2009HospitalPhysical Therapy | ASHRAE 189.1-2009 | Hospital | Physical Therapy | 0.81
ASHRAE 189.1-2009HospitalRadiology | ASHRAE 189.1-2009 | Hospital | Radiology | 0.36
ASHRAE 189.1-2009HospitalLaundry-Washing | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | 0.54
ASHRAE 189.1-2009AutomotiveService/Repair | ASHRAE 189.1-2009 | Automotive | Service/Repair | 0.63
ASHRAE 189.1-2009ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 189.1-2009 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.08
ASHRAE 189.1-2009ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 189.1-2009 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.53
ASHRAE 189.1-2009ManufacturingDetailed Manufacturing | ASHRAE 189.1-2009 | Manufacturing | Detailed Manufacturing | 1.89
ASHRAE 189.1-2009ManufacturingEquipment Room | ASHRAE 189.1-2009 | Manufacturing | Equipment Room | 1.08
ASHRAE 189.1-2009ManufacturingControl Room | ASHRAE 189.1-2009 | Manufacturing | Control Room | 0.45
ASHRAE 189.1-2009Hotel/MotelGuest Rooms | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | 0.99
ASHRAE 189.1-2009DormitoryLiving Quarters | ASHRAE 189.1-2009 | Dormitory | Living Quarters | 0.99
ASHRAE 189.1-2009MuseumGeneral Exhibition | ASHRAE 189.1-2009 | Museum | General Exhibition | 0.9
ASHRAE 189.1-2009MuseumRestoration | ASHRAE 189.1-2009 | Museum | Restoration | 1.53
ASHRAE 189.1-2009Electrical/MechanicalGeneral | ASHRAE 189.1-2009 | Electrical/Mechanical | General | 1.35
ASHRAE 189.1-2009WorkshopGeneral | ASHRAE 189.1-2009 | Workshop | General | 1.71
ASHRAE 189.1-2009Bank/OfficeBanking Activity Area | ASHRAE 189.1-2009 | Bank/Office | Banking Activity Area | 1.35
ASHRAE 189.1-2009Religious BuildingsWorship Pulpit, Choir | ASHRAE 189.1-2009 | Religious Buildings | Worship Pulpit, Choir | 2.16
ASHRAE 189.1-2009Religious BuildingsFellowship Hall | ASHRAE 189.1-2009 | Religious Buildings | Fellowship Hall | 0.81
ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | 1.53
ASHRAE 189.1-2009Retail (not including accent lighting)Mall Concourse | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Mall Concourse | 1.53
ASHRAE 189.1-2009Sports ArenaRing Sports Area | ASHRAE 189.1-2009 | Sports Arena | Ring Sports Area | 2.43
ASHRAE 189.1-2009Sports ArenaCourt Sports Area | ASHRAE 189.1-2009 | Sports Arena | Court Sports Area | 2.07
ASHRAE 189.1-2009Sports ArenaIndoor Playing Field Area | ASHRAE 189.1-2009 | Sports Arena | Indoor Playing Field Area | 1.26
ASHRAE 189.1-2009WarehouseFine Material Storage | ASHRAE 189.1-2009 | Warehouse | Fine Material Storage | 1.26
ASHRAE 189.1-2009WarehouseMedium/Bulky Material Storage | ASHRAE 189.1-2009 | Warehouse | Medium/Bulky Material Storage | 0.81
ASHRAE 189.1-2009Parking GarageGarage Area | ASHRAE 189.1-2009 | Parking Garage | Garage Area | 0.18
ASHRAE 189.1-2009TransportationAirport-Concourse | ASHRAE 189.1-2009 | Transportation | Airport-Concourse | 0.54
ASHRAE 189.1-2009TransportationAir/Train/Bus-Baggage Area | ASHRAE 189.1-2009 | Transportation | Air/Train/Bus-Baggage Area | 0.9
ASHRAE 189.1-2009TransportationTerminal-Ticket Counter | ASHRAE 189.1-2009 | Transportation | Terminal-Ticket Counter | 1.35
ASHRAE 189.1-2009Exterior SpacesGeneral | ASHRAE 189.1-2009 | Exterior Spaces | General | 0
ASHRAE 189.1-2009AtticsGeneral | ASHRAE 189.1-2009 | Attics | General | 0
ASHRAE 90.1-2010Whole BuildingAutomotive Facility | ASHRAE 90.1-2010 | Whole Building | Automotive Facility | 0.82
ASHRAE 90.1-2010Whole BuildingConvention Center | ASHRAE 90.1-2010 | Whole Building | Convention Center | 1.08
ASHRAE 90.1-2010Whole BuildingCourt House | ASHRAE 90.1-2010 | Whole Building | Court House | 1.05
ASHRAE 90.1-2010Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2010 | Whole Building | Dining: Bar Lounge/Leisure | 0.99
ASHRAE 90.1-2010Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2010 | Whole Building | Dining: Cafeteria/Fast Food | 0.9
ASHRAE 90.1-2010Whole BuildingDining: Family | ASHRAE 90.1-2010 | Whole Building | Dining: Family | 0.89
ASHRAE 90.1-2010Whole BuildingDormitory | ASHRAE 90.1-2010 | Whole Building | Dormitory | 0.61
ASHRAE 90.1-2010Whole BuildingExercise Center | ASHRAE 90.1-2010 | Whole Building | Exercise Center | 0.88
ASHRAE 90.1-2010Whole BuildingFire Station | ASHRAE 90.1-2010 | Whole Building | Fire Station | 0.71
ASHRAE 90.1-2010Whole BuildingGymnasium | ASHRAE 90.1-2010 | Whole Building | Gymnasium | 1
ASHRAE 90.1-2010Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2010 | Whole Building | Health Care-Clinic | 0.87
ASHRAE 90.1-2010Whole BuildingHospital | ASHRAE 90.1-2010 | Whole Building | Hospital | 1.21
ASHRAE 90.1-2010Whole BuildingHotel | ASHRAE 90.1-2010 | Whole Building | Hotel | 1
ASHRAE 90.1-2010Whole BuildingLibrary | ASHRAE 90.1-2010 | Whole Building | Library | 1.18
ASHRAE 90.1-2010Whole BuildingManufacturing Facility | ASHRAE 90.1-2010 | Whole Building | Manufacturing Facility | 1.11
ASHRAE 90.1-2010Whole BuildingMotel | ASHRAE 90.1-2010 | Whole Building | Motel | 0.88
ASHRAE 90.1-2010Whole BuildingMotion Picture Theater | ASHRAE 90.1-2010 | Whole Building | Motion Picture Theater | 0.83
ASHRAE 90.1-2010Whole BuildingMulti-Family | ASHRAE 90.1-2010 | Whole Building | Multi-Family | 0.6
ASHRAE 90.1-2010Whole BuildingMuseum | ASHRAE 90.1-2010 | Whole Building | Museum | 1.06
ASHRAE 90.1-2010Whole BuildingOffice | ASHRAE 90.1-2010 | Whole Building | Office | 0.9
ASHRAE 90.1-2010Whole BuildingParking Garage | ASHRAE 90.1-2010 | Whole Building | Parking Garage | 0.25
ASHRAE 90.1-2010Whole BuildingPenitentiary | ASHRAE 90.1-2010 | Whole Building | Penitentiary | 0.97
ASHRAE 90.1-2010Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2010 | Whole Building | Performing Arts Theater | 1.39
ASHRAE 90.1-2010Whole BuildingPolice Station | ASHRAE 90.1-2010 | Whole Building | Police Station | 0.96
ASHRAE 90.1-2010Whole BuildingPost Office | ASHRAE 90.1-2010 | Whole Building | Post Office | 0.87
ASHRAE 90.1-2010Whole BuildingReligious Building | ASHRAE 90.1-2010 | Whole Building | Religious Building | 1.05
ASHRAE 90.1-2010Whole BuildingRetail | ASHRAE 90.1-2010 | Whole Building | Retail | 1.4
ASHRAE 90.1-2010Whole BuildingSchool/University | ASHRAE 90.1-2010 | Whole Building | School/University | 0.99
ASHRAE 90.1-2010Whole BuildingSports Arena | ASHRAE 90.1-2010 | Whole Building | Sports Arena | 0.78
ASHRAE 90.1-2010Whole BuildingTown Hall | ASHRAE 90.1-2010 | Whole Building | Town Hall | 0.92
ASHRAE 90.1-2010Whole BuildingTransportation | ASHRAE 90.1-2010 | Whole Building | Transportation | 0.77
ASHRAE 90.1-2010Whole BuildingWarehouse | ASHRAE 90.1-2010 | Whole Building | Warehouse | 0.66
ASHRAE 90.1-2010Whole BuildingWorkshop | ASHRAE 90.1-2010 | Whole Building | Workshop | 1.2
ASHRAE 90.1-2010Office-EnclosedGeneral | ASHRAE 90.1-2010 | Office-Enclosed | General | 1.11
ASHRAE 90.1-2010Office-Open PlanGeneral | ASHRAE 90.1-2010 | Office-Open Plan | General | 0.98
ASHRAE 90.1-2010Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2010 | Conference/Meeting/Multipurpose | General | 1.23
ASHRAE 90.1-2010Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2010 | Classroom/Lecture/Training | General | 1.24
ASHRAE 90.1-2010Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2010 | Classroom/Lecture/Training | For Penitentiary | 1.34
ASHRAE 90.1-2010LobbyGeneral | ASHRAE 90.1-2010 | Lobby | General | 0.9
ASHRAE 90.1-2010LobbyFor Elevator | ASHRAE 90.1-2010 | Lobby | For Elevator | 0.64
ASHRAE 90.1-2010LobbyFor Hotel | ASHRAE 90.1-2010 | Lobby | For Hotel | 1.06
ASHRAE 90.1-2010LobbyFor Performing Arts Theater | ASHRAE 90.1-2010 | Lobby | For Performing Arts Theater | 2
ASHRAE 90.1-2010LobbyFor Motion Picture Theater | ASHRAE 90.1-2010 | Lobby | For Motion Picture Theater | 0.52
ASHRAE 90.1-2010Audience/Seating AreaFor Auditorium | ASHRAE 90.1-2010 | Audience/Seating Area | For Auditorium | 0.79
ASHRAE 90.1-2010Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2010 | Audience/Seating Area | For Gymnasium | 0.43
ASHRAE 90.1-2010Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-2010 | Audience/Seating Area | For Exercise Center
ASHRAE 90.1-2010Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2010 | Audience/Seating Area | For Convention Center | 0.82
ASHRAE 90.1-2010Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2010 | Audience/Seating Area | For Penitentiary | 0.43
ASHRAE 90.1-2010Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2010 | Audience/Seating Area | For Religious Buildings | 1.53
ASHRAE 90.1-2010Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-2010 | Audience/Seating Area | For Sports Arena | 0.43
ASHRAE 90.1-2010Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-2010 | Audience/Seating Area | For Performing Arts Theater | 2.43
ASHRAE 90.1-2010Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2010 | Audience/Seating Area | For Motion Picture Theater | 1.14
ASHRAE 90.1-2010Audience/Seating AreaFor Transportation | ASHRAE 90.1-2010 | Audience/Seating Area | For Transportation | 0.54
ASHRAE 90.1-2010AtriumFirst Forty Feet in Height | ASHRAE 90.1-2010 | Atrium | First Forty Feet in Height | 0.03
ASHRAE 90.1-2010AtriumHeight Above Forty Feet | ASHRAE 90.1-2010 | Atrium | Height Above Forty Feet | 0.02
ASHRAE 90.1-2010Lounge/RecreationGeneral | ASHRAE 90.1-2010 | Lounge/Recreation | General | 0.73
ASHRAE 90.1-2010Lounge/RecreationFor Hospital | ASHRAE 90.1-2010 | Lounge/Recreation | For Hospital | 1.07
ASHRAE 90.1-2010Dining AreaGeneral | ASHRAE 90.1-2010 | Dining Area | General | 0.65
ASHRAE 90.1-2010Dining AreaFor Penitentiary | ASHRAE 90.1-2010 | Dining Area | For Penitentiary | 1.07
ASHRAE 90.1-2010Dining AreaFor Hotel | ASHRAE 90.1-2010 | Dining Area | For Hotel | 0.82
ASHRAE 90.1-2010Dining AreaFor Highway Lodging | ASHRAE 90.1-2010 | Dining Area | For Highway Lodging | 0.88
ASHRAE 90.1-2010Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2010 | Dining Area | For Bar Lounge/Leisure Dining | 1.31
ASHRAE 90.1-2010Dining AreaFor Family Dining | ASHRAE 90.1-2010 | Dining Area | For Family Dining | 0.89
ASHRAE 90.1-2010Food PreparationGeneral | ASHRAE 90.1-2010 | Food Preparation | General | 0.99
ASHRAE 90.1-2010LaboratoryFor Classrooms | ASHRAE 90.1-2010 | Laboratory | For Classrooms | 1.28
ASHRAE 90.1-2010LaboratoryFor Medical/Industrial/Research | ASHRAE 90.1-2010 | Laboratory | For Medical/Industrial/Research | 1.81
ASHRAE 90.1-2010RestroomsGeneral | ASHRAE 90.1-2010 | Restrooms | General | 0.98
ASHRAE 90.1-2010Dressing/Fitting RoomFor Performing Arts Theater | ASHRAE 90.1-2010 | Dressing/Fitting Room | For Performing Arts Theater | 0.4
ASHRAE 90.1-2010Dressing/Fitting RoomFor Retail | ASHRAE 90.1-2010 | Dressing/Fitting Room | For Retail | 0.87
ASHRAE 90.1-2010Locker RoomGeneral | ASHRAE 90.1-2010 | Locker Room | General | 0.75
ASHRAE 90.1-2010Corridor/TransitionGeneral | ASHRAE 90.1-2010 | Corridor/Transition | General | 0.66
ASHRAE 90.1-2010Corridor/TransitionFor Hospital | ASHRAE 90.1-2010 | Corridor/Transition | For Hospital | 0.89
ASHRAE 90.1-2010Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-2010 | Corridor/Transition | For Manufacturing Facility | 0.41
ASHRAE 90.1-2010StairwayGeneral | ASHRAE 90.1-2010 | Stairway | General | 0.69
ASHRAE 90.1-2010StorageGeneral | ASHRAE 90.1-2010 | Storage | General | 0.63
ASHRAE 90.1-2010Gymnasium/Fitness CenterPlaying Area | ASHRAE 90.1-2010 | Gymnasium/Fitness Center | Playing Area | 1.2
ASHRAE 90.1-2010Gymnasium/Fitness CenterFitness Area | ASHRAE 90.1-2010 | Gymnasium/Fitness Center | Fitness Area | 0.72
ASHRAE 90.1-2010Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-2010 | Courthouse/Police Station/Penitentiary | Courtroom | 1.72
ASHRAE 90.1-2010Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-2010 | Courthouse/Police Station/Penitentiary | Confinement Cells | 1.1
ASHRAE 90.1-2010Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-2010 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.17
ASHRAE 90.1-2010Fire StationEngine Room | ASHRAE 90.1-2010 | Fire Station | Engine Room | 0.56
ASHRAE 90.1-2010Fire StationSleeping Quarters | ASHRAE 90.1-2010 | Fire Station | Sleeping Quarters | 0.25
ASHRAE 90.1-2010Post OfficeSorting Area | ASHRAE 90.1-2010 | Post Office | Sorting Area | 0.94
ASHRAE 90.1-2010Convention CenterExhibit Space | ASHRAE 90.1-2010 | Convention Center | Exhibit Space | 1.45
ASHRAE 90.1-2010LibraryCard File and Cataloging | ASHRAE 90.1-2010 | Library | Card File and Cataloging | 0.72
ASHRAE 90.1-2010LibraryStacks | ASHRAE 90.1-2010 | Library | Stacks | 1.71
ASHRAE 90.1-2010LibraryReading Area | ASHRAE 90.1-2010 | Library | Reading Area | 0.93
ASHRAE 90.1-2010HospitalEmergency | ASHRAE 90.1-2010 | Hospital | Emergency | 2.26
ASHRAE 90.1-2010HospitalRecovery | ASHRAE 90.1-2010 | Hospital | Recovery | 1.15
ASHRAE 90.1-2010HospitalNurse Station | ASHRAE 90.1-2010 | Hospital | Nurse Station | 0.87
ASHRAE 90.1-2010HospitalExam/Treatment | ASHRAE 90.1-2010 | Hospital | Exam/Treatment | 1.66
ASHRAE 90.1-2010HospitalPharmacy | ASHRAE 90.1-2010 | Hospital | Pharmacy | 1.14
ASHRAE 90.1-2010HospitalPatient Room | ASHRAE 90.1-2010 | Hospital | Patient Room | 0.62
ASHRAE 90.1-2010HospitalOperating Room | ASHRAE 90.1-2010 | Hospital | Operating Room | 1.89
ASHRAE 90.1-2010HospitalNursery | ASHRAE 90.1-2010 | Hospital | Nursery | 0.88
ASHRAE 90.1-2010HospitalMedical Supply | ASHRAE 90.1-2010 | Hospital | Medical Supply | 1.27
ASHRAE 90.1-2010HospitalPhysical Therapy | ASHRAE 90.1-2010 | Hospital | Physical Therapy | 0.91
ASHRAE 90.1-2010HospitalRadiology/Imaging | ASHRAE 90.1-2010 | Hospital | Radiology/Imaging | 1.32
ASHRAE 90.1-2010HospitalLaundry-Washing | ASHRAE 90.1-2010 | Hospital | Laundry-Washing | 0.6
ASHRAE 90.1-2010AutomotiveService/Repair | ASHRAE 90.1-2010 | Automotive | Service/Repair | 0.67
ASHRAE 90.1-2010ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2010 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.19
ASHRAE 90.1-2010ManufacturingHigh Bay (25-50 ft Floor to Ceiling Height) | ASHRAE 90.1-2010 | Manufacturing | High Bay (25-50 ft Floor to Ceiling Height) | 1.23
ASHRAE 90.1-2010ManufacturingExtra High Bay (>50 ft Floor to Ceiling Height) | ASHRAE 90.1-2010 | Manufacturing | Extra High Bay (>50 ft Floor to Ceiling Height) | 1.05
ASHRAE 90.1-2010ManufacturingDetailed Manufacturing | ASHRAE 90.1-2010 | Manufacturing | Detailed Manufacturing | 1.29
ASHRAE 90.1-2010ManufacturingEquipment Room | ASHRAE 90.1-2010 | Manufacturing | Equipment Room | 0.95
ASHRAE 90.1-2010Guest RoomFor Highway Lodging | ASHRAE 90.1-2010 | Guest Room | For Highway Lodging | 0.75
ASHRAE 90.1-2010Guest RoomFor Hotel | ASHRAE 90.1-2010 | Guest Room | For Hotel | 1.11
ASHRAE 90.1-2010DormitoryLiving Quarters | ASHRAE 90.1-2010 | Dormitory | Living Quarters | 0.38
ASHRAE 90.1-2010MuseumGeneral Exhibition | ASHRAE 90.1-2010 | Museum | General Exhibition | 1.05
ASHRAE 90.1-2010MuseumRestoration | ASHRAE 90.1-2010 | Museum | Restoration | 1.02
ASHRAE 90.1-2010Electrical/MechanicalGeneral | ASHRAE 90.1-2010 | Electrical/Mechanical | General | 0.95
ASHRAE 90.1-2010WorkshopGeneral | ASHRAE 90.1-2010 | Workshop | General | 1.59
ASHRAE 90.1-2010Bank/OfficeBanking Activity Area | ASHRAE 90.1-2010 | Bank/Office | Banking Activity Area | 1.38
ASHRAE 90.1-2010Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2010 | Religious Buildings | Worship Pulpit, Choir | 1.53
ASHRAE 90.1-2010Religious BuildingsFellowship Hall | ASHRAE 90.1-2010 | Religious Buildings | Fellowship Hall | 0.64
ASHRAE 90.1-2010Sales AreaFor Retail | ASHRAE 90.1-2010 | Sales Area | For Retail | 1.68
ASHRAE 90.1-2010Sales AreaGeneral | ASHRAE 90.1-2010 | Sales Area | General | 1.68
ASHRAE 90.1-2010RetailMall Concourse | ASHRAE 90.1-2010 | Retail | Mall Concourse | 1.1
ASHRAE 90.1-2010Sports ArenaRing Sports Arena | ASHRAE 90.1-2010 | Sports Arena | Ring Sports Arena | 2.68
ASHRAE 90.1-2010Sports ArenaCourt Sports Arena - Class 4 | ASHRAE 90.1-2010 | Sports Arena | Court Sports Arena - Class 4 | 0.72
ASHRAE 90.1-2010Sports ArenaCourt Sports Arena - Class 3 | ASHRAE 90.1-2010 | Sports Arena | Court Sports Arena - Class 3 | 1.2
ASHRAE 90.1-2010Sports ArenaCourt Sports Arena - Class 2 | ASHRAE 90.1-2010 | Sports Arena | Court Sports Arena - Class 2 | 1.92
ASHRAE 90.1-2010Sports ArenaCourt Sports Arena - Class 1 | ASHRAE 90.1-2010 | Sports Arena | Court Sports Arena - Class 1 | 3.01
ASHRAE 90.1-2010WarehouseFine Material Storage | ASHRAE 90.1-2010 | Warehouse | Fine Material Storage | 0.95
ASHRAE 90.1-2010WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2010 | Warehouse | Medium/Bulky Material Storage | 0.58
ASHRAE 90.1-2010Parking GarageGarage Area | ASHRAE 90.1-2010 | Parking Garage | Garage Area | 0.19
ASHRAE 90.1-2010TransportationAirport-Concourse | ASHRAE 90.1-2010 | Transportation | Airport-Concourse | 0.36
ASHRAE 90.1-2010TransportationAir/Train/Bus-Baggage Area | ASHRAE 90.1-2010 | Transportation | Air/Train/Bus-Baggage Area | 0.76
ASHRAE 90.1-2010TransportationTerminal-Ticket Counter | ASHRAE 90.1-2010 | Transportation | Terminal-Ticket Counter | 1.08

## ConstructionSets
A Construction Set lists the typical constructions for each surface type in a building for a given building type and climate zone.
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27
|  |  |  | Exterior Surfaces |  |  | Interior Surfaces |  |  | Ground Contact Surfaces |  |  | Exterior Sub Surfaces | [7 empty] | Interior Sub Surfaces |  |  | Misc Surfaces
Template | Building Type | Space Type | Climate Zone Set | Exterior Walls | Exterior Floors | Exterior Roofs | Interior Walls | Interior Floors | Interior Ceilings | Ground Contact Walls | Ground Contact Floors | Ground Contact Ceilings | Exterior Fixed Windows | Exterior Operable Windows | Exterior Doors | Exterior Glass Doors | Exterior Overhead Doors | Exterior Skylights | Tubular Daylight Domes | Tubular Daylight Diffusers | Interior Fixed Windows | Interior Operable Windows | Interior Doors | Space Shading | Building Shading | Site Shading | Interior Partitions
189.1-2009 | FullServiceRestaurant |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | FullServiceRestaurant |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | FullServiceRestaurant |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | FullServiceRestaurant |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | FullServiceRestaurant |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | FullServiceRestaurant |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Hospital |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Hospital |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Hospital |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Hospital |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Hospital |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Hospital |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Hospital |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 7 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | MidriseApartment |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | MidriseApartment |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | MidriseApartment |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | MidriseApartment |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | MidriseApartment |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | MidriseApartment |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Office |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Office |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Office |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Office |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Office |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Office |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Office |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Outpatient |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Outpatient |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Outpatient |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Outpatient |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Outpatient |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Outpatient |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | PrimarySchool |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | PrimarySchool |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | PrimarySchool |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | PrimarySchool |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | PrimarySchool |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | PrimarySchool |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | QuickServiceRestaurant |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | QuickServiceRestaurant |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | QuickServiceRestaurant |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | QuickServiceRestaurant |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | QuickServiceRestaurant |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | QuickServiceRestaurant |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 6-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | QuickServiceRestaurant |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 6-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Retail |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Retail |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Retail |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Retail |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Retail |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Retail |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Retail |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SecondarySchool |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SecondarySchool |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SecondarySchool |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SecondarySchool |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SecondarySchool |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SecondarySchool |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SmallHotel |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SmallHotel |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SmallHotel |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SmallHotel |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SmallHotel |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SmallHotel |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | StripMall |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | StripMall |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | StripMall |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | StripMall |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | StripMall |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | StripMall |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SuperMarket |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SuperMarket |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SuperMarket |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SuperMarket |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SuperMarket |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SuperMarket |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SuperMarket |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Warehouse |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 1-3 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Warehouse |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 1-3 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Warehouse |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 1-3 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Warehouse |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 4-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Warehouse |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 4-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Warehouse |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 4-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 |  | Attic | ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | ASHRAE 189.1-2009 AtticFloor ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | ASHRAE 189.1-2009 AtticFloor ClimateZone 1-8 | ASHRAE 189.1-2009 AtticFloor ClimateZone 1-8 | ASHRAE 189.1-2009 AtticFloor ClimateZone 1-8
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 1 | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 2a | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 2b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 3a | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 3b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 3b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 3c | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 4a | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 4b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 4c | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 5a | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 5b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 6a | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 6b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 7 | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 8 | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Metal ClimateZone 1 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Metal ClimateZone 2a | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Metal ClimateZone 2b | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Metal ClimateZone 3a | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Metal ClimateZone 3b LAS | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Metal ClimateZone 3b LAX | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Metal ClimateZone 3c | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Metal ClimateZone 4a | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Metal ClimateZone 4b | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Metal ClimateZone 4c | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Metal ClimateZone 5 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Metal ClimateZone 6a | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Metal ClimateZone 6b | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Metal ClimateZone 7 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Metal ClimateZone 8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 |  | Attic | ClimateZone 1 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 1 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 1 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 1 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 1
DOE Ref 1980-2004 |  | Attic | ClimateZone 2a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2a
DOE Ref 1980-2004 |  | Attic | ClimateZone 2b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2b
DOE Ref 1980-2004 |  | Attic | ClimateZone 3a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3a
DOE Ref 1980-2004 |  | Attic | ClimateZone 3b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAS | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAS | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAS | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAS
DOE Ref 1980-2004 |  | Attic | ClimateZone 3b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAX | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAX | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAX | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAX
DOE Ref 1980-2004 |  | Attic | ClimateZone 4a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4a
DOE Ref 1980-2004 |  | Attic | ClimateZone 4b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4b
DOE Ref 1980-2004 |  | Attic | ClimateZone 4c | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4c | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4c | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4c | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4c
DOE Ref 1980-2004 |  | Attic | ClimateZone 5a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a
DOE Ref 1980-2004 |  | Attic | ClimateZone 5b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5b
DOE Ref 1980-2004 |  | Attic | ClimateZone 6a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6a
DOE Ref 1980-2004 |  | Attic | ClimateZone 6b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6b
DOE Ref 1980-2004 |  | Attic | ClimateZone 7 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 7 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 7 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 7 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 7
DOE Ref 1980-2004 |  | Attic | ClimateZone 8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 8
DOE Ref 2004 | FullServiceRestaurant |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | FullServiceRestaurant |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | FullServiceRestaurant |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | FullServiceRestaurant |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | FullServiceRestaurant |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | FullServiceRestaurant |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | FullServiceRestaurant |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Hospital |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Hospital |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Hospital |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Hospital |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Hospital |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Hospital |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Hospital |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Hospital |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resH 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resH 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 5-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 5-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | LargeHotel |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | MidriseApartment |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | MidriseApartment |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resA 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resA 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | MidriseApartment |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | MidriseApartment |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 4-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | MidriseApartment |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 4-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | MidriseApartment |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | MidriseApartment |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Office |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Office |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Office |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Office |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Office |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Office |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Office |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Office |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Outpatient |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Outpatient |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Outpatient |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Outpatient |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Outpatient |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Outpatient |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Outpatient |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | PrimarySchool |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | PrimarySchool |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | PrimarySchool |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | PrimarySchool |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | PrimarySchool |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | PrimarySchool |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | PrimarySchool |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | QuickServiceRestaurant |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | QuickServiceRestaurant |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | QuickServiceRestaurant |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | QuickServiceRestaurant |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | QuickServiceRestaurant |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | QuickServiceRestaurant |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | QuickServiceRestaurant |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Retail |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Retail |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Retail |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Retail |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Retail |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Retail |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Retail |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Retail |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SecondarySchool |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SecondarySchool |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SecondarySchool |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SecondarySchool |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SecondarySchool |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SecondarySchool |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SecondarySchool |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SmallHotel |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SmallHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SmallHotel |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SmallHotel |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 4-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SmallHotel |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 4-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SmallHotel |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SmallHotel |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | StripMall |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | StripMall |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | StripMall |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | StripMall |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | StripMall |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | StripMall |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | StripMall |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SuperMarket |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SuperMarket |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SuperMarket |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SuperMarket |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SuperMarket |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SuperMarket |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SuperMarket |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | SuperMarket |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Warehouse |  | ClimateZone 1 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 1 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Warehouse |  | ClimateZone 2 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 2-3 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 2 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Warehouse |  | ClimateZone 3 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 2-3 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 3-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Warehouse |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 4 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 3-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Warehouse |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 5 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Warehouse |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 6-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Warehouse |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 6-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 | Warehouse |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 6-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 2004 |  | Attic | ClimateZone 1-5 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 1-5 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 1-5 | ASHRAE 90.1-2004 AtticFloor ClimateZone 1-5 | ASHRAE 90.1-2004 AtticFloor ClimateZone 1-5
DOE Ref 2004 |  | Attic | ClimateZone 6-8 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 6-8 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 6-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 6-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 6-8
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Metal ClimateZone 1-2 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 3a | CBECS Before-1980 ExtWall Metal ClimateZone 3a | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 3b | CBECS Before-1980 ExtWall Metal ClimateZone 3b | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 3c | CBECS Before-1980 ExtWall Metal ClimateZone 3c | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 4a | CBECS Before-1980 ExtWall Metal ClimateZone 4a | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 4b | CBECS Before-1980 ExtWall Metal ClimateZone 4b | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 4c | CBECS Before-1980 ExtWall Metal ClimateZone 4c | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 5a | CBECS Before-1980 ExtWall Metal ClimateZone 5a | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 5b | CBECS Before-1980 ExtWall Metal ClimateZone 5b | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 6 | CBECS Before-1980 ExtWall Metal ClimateZone 6 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 7 | CBECS Before-1980 ExtWall Metal ClimateZone 7 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 8 | CBECS Before-1980 ExtWall Metal ClimateZone 8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 |  | Attic | ClimateZone 1-3 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 1-3 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 1-3 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 1-3 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 1-3
DOE Ref Pre-1980 |  | Attic | ClimateZone 4a | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4a | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4a | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4a | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4a
DOE Ref Pre-1980 |  | Attic | ClimateZone 4b | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4b | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4b | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4b | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4b
DOE Ref Pre-1980 |  | Attic | ClimateZone 4c | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4c | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4c | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4c | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4c
DOE Ref Pre-1980 |  | Attic | ClimateZone 5a | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a
DOE Ref Pre-1980 |  | Attic | ClimateZone 5b | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5b | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5b | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5b | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5b
DOE Ref Pre-1980 |  | Attic | ClimateZone 6 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 6 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 6 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 6 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 6
DOE Ref Pre-1980 |  | Attic | ClimateZone 7 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 7 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 7 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 7 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 7
DOE Ref Pre-1980 |  | Attic | ClimateZone 8 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 8 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 8
90.1-2007 | FullServiceRestaurant |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | FullServiceRestaurant |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | FullServiceRestaurant |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | FullServiceRestaurant |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | FullServiceRestaurant |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | FullServiceRestaurant |  | ClimateZone 5-6 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | FullServiceRestaurant |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | FullServiceRestaurant |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 6-7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 6-7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 5-6 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 5-6 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 5-6 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 6-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 6-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 5-6 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 5-6 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 5-6 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 1 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 1 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 2-3 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 2 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 3 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 2-3 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 3-7 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 4 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 3-7 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 5 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 3-7 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 6-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 3-7 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 6-8 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 6-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 3-7 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 6-8 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 6-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 8 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 6-8 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 |  | Attic | ClimateZone 1 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 1 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 1 | ASHRAE 90.1-2007 AtticFloor ClimateZone 1 | ASHRAE 90.1-2007 AtticFloor ClimateZone 1
90.1-2007 |  | Attic | ClimateZone 2-7 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 2-7 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 2-7 | ASHRAE 90.1-2007 AtticFloor ClimateZone 2-7 | ASHRAE 90.1-2007 AtticFloor ClimateZone 2-7
90.1-2007 |  | Attic | ClimateZone 8 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 8 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 8
90.1-2010 | FullServiceRestaurant |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | FullServiceRestaurant |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | FullServiceRestaurant |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | FullServiceRestaurant |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | FullServiceRestaurant |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | FullServiceRestaurant |  | ClimateZone 5-6 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | FullServiceRestaurant |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | FullServiceRestaurant |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 6-7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 6-7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 5-6 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 5-6 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 5-6 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 6-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 6-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 5-6 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 5-6 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 5-6 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 1 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 2-4 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 3 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 2-4 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 2-4 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 5 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 6-7 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 6-8 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 6-7 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 6-8 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 8 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 6-8 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 |  | Attic | ClimateZone 1 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 1 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 1 | ASHRAE 90.1-2010 AtticFloor ClimateZone 1 | ASHRAE 90.1-2010 AtticFloor ClimateZone 1
90.1-2010 |  | Attic | ClimateZone 2-7 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 2-7 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 2-7 | ASHRAE 90.1-2010 AtticFloor ClimateZone 2-7 | ASHRAE 90.1-2010 AtticFloor ClimateZone 2-7
90.1-2010 |  | Attic | ClimateZone 8 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 8 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 8
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 3a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 6-7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 6-7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition

## Constructions
A Construction is a particular combination of materials that represents a typical building envelope cross section. Constructions are referenced on the Construction Sets tab.
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
[5 empty] | Outside |  |  |  |  | Inside
Name | Construction Standard | Climate Zone Set | Intended Surface Type | Standards Construction Type | Material 1 | Material 2 | Material 3 | Material 4 | Material 5 | Material 6
ASHRAE 189.1-2009 AtticFloor ClimateZone 1-8 | ASHRAE 189.1-2009 | ClimateZone 1-8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | ASHRAE 189.1-2009 | ClimateZone 1 | ExteriorRoof | IEAD | Roof Membrane | Roof Insulation [18] | Metal Decking
ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | ASHRAE 189.1-2009 | ClimateZone 2-5 | ExteriorRoof | IEAD | Roof Membrane | Roof Insulation [21] | Metal Decking
ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | ASHRAE 189.1-2009 | ClimateZone 6 | ExteriorRoof | IEAD | Roof Membrane | Roof Insulation [24] | Metal Decking
ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | ASHRAE 189.1-2009 | ClimateZone 7-8 | ExteriorRoof | IEAD | Roof Membrane | Roof Insulation [26] | Metal Decking
ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 1 | ASHRAE 189.1-2009 | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing | Roof Insulation [19] | Metal Decking
ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 2-5 | ASHRAE 189.1-2009 | ClimateZone 2-5 | ExteriorRoof | Metal | Metal Roofing | Roof Insulation [22] | Metal Decking
ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | ASHRAE 189.1-2009 | ClimateZone 6 | ExteriorRoof | Metal | Metal Roofing | Roof Insulation [25] | Metal Decking
ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 7-8 | ASHRAE 189.1-2009 | ClimateZone 7-8 | ExteriorRoof | Metal | Metal Roofing | Roof Insulation [27] | Metal Decking
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ASHRAE 189.1-2009 | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [31] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ASHRAE 189.1-2009 | ClimateZone 2 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [35] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ASHRAE 189.1-2009 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [36] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ASHRAE 189.1-2009 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [37] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ASHRAE 189.1-2009 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [40] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ASHRAE 189.1-2009 | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [42] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ASHRAE 189.1-2009 | ClimateZone 7-8 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [44] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 1 | ASHRAE 189.1-2009 | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [35] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 2 | ASHRAE 189.1-2009 | ClimateZone 2 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [36] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 3 | ASHRAE 189.1-2009 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [37] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 4 | ASHRAE 189.1-2009 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [40] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 5 | ASHRAE 189.1-2009 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [42] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 6 | ASHRAE 189.1-2009 | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [44] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 7 | ASHRAE 189.1-2009 | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [44] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 8 | ASHRAE 189.1-2009 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [46] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Metal ClimateZone 1-3 | ASHRAE 189.1-2009 | ClimateZone 1-3 | ExteriorWall | Metal | Metal Siding | Wall Insulation [32] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Metal ClimateZone 4-8 | ASHRAE 189.1-2009 | ClimateZone 4-8 | ExteriorWall | Metal | Metal Siding | Wall Insulation [38] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ASHRAE 189.1-2009 | ClimateZone 1-3 | ExteriorWall | SteelFramed | MAT-SHEATH | Wall Insulation [33] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ASHRAE 189.1-2009 | ClimateZone 4-8 | ExteriorWall | SteelFramed | MAT-SHEATH | Wall Insulation [39] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 1-4 | ASHRAE 189.1-2009 | ClimateZone 1-4 | ExteriorWall | WoodFramed | Wood Siding | Wall Insulation [34] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 5 | ASHRAE 189.1-2009 | ClimateZone 5 | ExteriorWall | WoodFramed | Wood Siding | Wall Insulation [41] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 6-8 | ASHRAE 189.1-2009 | ClimateZone 6-8 | ExteriorWall | WoodFramed | Wood Siding | Wall Insulation [43] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 | ClimateZone 1 | ExteriorWindow |  | Theoretical Glass [167]
ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 | ClimateZone 2 | ExteriorWindow |  | Theoretical Glass [197]
ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 | ClimateZone 3 | ExteriorWindow |  | Theoretical Glass [202]
ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 | ClimateZone 4-5 | ExteriorWindow |  | Theoretical Glass [207]
ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 | ClimateZone 6 | ExteriorWindow |  | Theoretical Glass [216]
ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 | ClimateZone 7-8 | ExteriorWindow |  | Theoretical Glass [221]
ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | ASHRAE 189.1-2009 | ClimateZone 4-5 | ExteriorWindow |  | Theoretical Glass [216]
ASHRAE 90.1-2004 AtticFloor ClimateZone 1-5 | ASHRAE 90.1-2004 | ClimateZone 1-5 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-5.18 | 1/2IN Gypsum
ASHRAE 90.1-2004 AtticFloor ClimateZone 6-8 | ASHRAE 90.1-2004 | ClimateZone 6-8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-6.52 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | ASHRAE 90.1-2004 | ClimateZone 1-4 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.79 | Metal Decking
ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.85 | Metal Decking
ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 1 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.85 | Metal Decking
ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.79 | Metal Decking
ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.72 | Metal Decking
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 1 | ASHRAE 90.1-2004 | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 2 | ASHRAE 90.1-2004 | ClimateZone 2 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-1.05 | Metal Decking
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 3-4 | ASHRAE 90.1-2004 | ClimateZone 3-4 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-1.81 | Metal Decking
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 5-6 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-1.87 | Metal Decking
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-1.81 | Metal Decking
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.50 | Metal Decking
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ASHRAE 90.1-2004 | ClimateZone 1-2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ASHRAE 90.1-2004 | ClimateZone 3-4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.17 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ASHRAE 90.1-2004 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.43 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ASHRAE 90.1-2004 | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.69 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.96 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.20 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 1-2 | ASHRAE 90.1-2004 | ClimateZone 1-2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.17 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 3 | ASHRAE 90.1-2004 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.43 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 4 | ASHRAE 90.1-2004 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.69 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 5-6 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.96 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.20 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.48 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Metal ClimateZone 1 | ASHRAE 90.1-2004 | ClimateZone 1 | ExteriorWall | Metal | Metal Siding | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Metal ClimateZone 2-3 | ASHRAE 90.1-2004 | ClimateZone 2-3 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.77 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Metal ClimateZone 4 | ASHRAE 90.1-2004 | ClimateZone 4 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.12 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Metal ClimateZone 5 | ASHRAE 90.1-2004 | ClimateZone 5 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.24 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Metal ClimateZone 6-8 | ASHRAE 90.1-2004 | ClimateZone 6-8 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.37 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ASHRAE 90.1-2004 | ClimateZone 1-4 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.42 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.10 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ASHRAE 90.1-2004 | ClimateZone 7-8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.75 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 3 | ASHRAE 90.1-2004 | ClimateZone 3 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.10 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 4-6 | ASHRAE 90.1-2004 | ClimateZone 4-6 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.75 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-3.21 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ASHRAE 90.1-2004 | ClimateZone 1-7 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.98 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-3.45 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 | ClimateZone 1-2 | ExteriorWindow |  | Fixed Window 5.84/0.25/0.11
ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 | ClimateZone 3a-3b | ExteriorWindow |  | Fixed Window 3.24/0.25/0.16
ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 | ClimateZone 3c | ExteriorWindow |  | Fixed Window 5.84/0.39/0.22
ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 | ClimateZone 4-6 | ExteriorWindow |  | Fixed Window 3.24/0.39/0.31
ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorWindow |  | Fixed Window 3.24/0.49/0.41
ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWindow |  | Fixed Window 2.62/0.30/0.21
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 3c | ASHRAE 90.1-2004 | ClimateZone 3c | ExteriorWindow |  | Fixed Window 5.84/0.61/0.47
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 4-6 | ASHRAE 90.1-2004 | ClimateZone 4-6 | ExteriorWindow |  | Fixed Window 3.81/0.39/0.27
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorWindow |  | Fixed Window 3.81/0.49/0.38
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWindow |  | Fixed Window 2.67/0.30/0.21
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resA 3a-3b | ASHRAE 90.1-2004 | ClimateZone 3a-3b | ExteriorWindow |  | Fixed Window 3.81/0.39/0.27
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resH 3a-3b | ASHRAE 90.1-2004 | ClimateZone 3a-3b | ExteriorWindow |  | Fixed Window 3.24/0.39/0.31
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 | ClimateZone 1-8 | ExteriorWindow |  | Fixed Window 5.84/0.70/0.60
AtticRoof ClimateZone 1-8 |  | ClimateZone 1-8 | AtticRoof | WoodFramed | Roof Membrane | Metal Decking
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 1 |  | ClimateZone 1 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.38 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2a |  | ClimateZone 2a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.67 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2b |  | ClimateZone 2b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.83 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3a |  | ClimateZone 3a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.45 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAS |  | ClimateZone 3b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.67 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAX |  | ClimateZone 3b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-1.76 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4a |  | ClimateZone 4a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.04 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4b |  | ClimateZone 4b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.99 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4c |  | ClimateZone 4c | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.75 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a |  | ClimateZone 5a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.32 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5b |  | ClimateZone 5b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.45 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6a |  | ClimateZone 6a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.91 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6b |  | ClimateZone 6b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.59 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 7 |  | ClimateZone 7 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-4.40 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 8 |  | ClimateZone 8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-5.68 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 |  | ClimateZone 1 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.38 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a |  | ClimateZone 2a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.67 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b |  | ClimateZone 2b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.83 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a |  | ClimateZone 3a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.44 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.66 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-1.76 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c |  | ClimateZone 3c | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.00 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a |  | ClimateZone 4a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.03 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b |  | ClimateZone 4b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.99 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c |  | ClimateZone 4c | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.75 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a |  | ClimateZone 5a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.38 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b |  | ClimateZone 5b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.51 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b 1 |  | ClimateZone 5b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.51 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a |  | ClimateZone 6a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.97 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b |  | ClimateZone 6b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.65 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 |  | ClimateZone 7 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-4.41 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 |  | ClimateZone 8 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-5.75 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 1 |  | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.38 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 2a |  | ClimateZone 2a | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.67 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 2b |  | ClimateZone 2b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.83 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 3a |  | ClimateZone 3a | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.44 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.66 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-1.76 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 3c |  | ClimateZone 3c | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.00 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 4a |  | ClimateZone 4a | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.03 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 4b |  | ClimateZone 4b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.99 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 4c |  | ClimateZone 4c | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.75 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 5a |  | ClimateZone 5a | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.38 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 5b |  | ClimateZone 5b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.38 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 6a |  | ClimateZone 6a | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.97 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 6b |  | ClimateZone 6b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.65 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 7 |  | ClimateZone 7 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-4.41 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 8 |  | ClimateZone 8 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-5.75 | Metal Decking
CBECS 1980-2004 ExtWall Mass ClimateZone 1 |  | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 2a |  | ClimateZone 2a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.52 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 2b |  | ClimateZone 2b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.43 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.61 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.61 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.47 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.93 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a |  | ClimateZone 4c-5a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.76 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 5b |  | ClimateZone 5b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.26 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 6a |  | ClimateZone 6a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.48 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 6b |  | ClimateZone 6b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.23 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.89 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-3.75 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 1 |  | ClimateZone 1 | ExteriorWall | Metal | Metal Siding | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 2a |  | ClimateZone 2a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.98 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 2b |  | ClimateZone 2b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.54 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.16 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.91 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.61 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.16 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.79 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.57 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.72 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 5 |  | ClimateZone 5 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.96 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 6a |  | ClimateZone 6a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-2.52 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 6b |  | ClimateZone 6b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-2.25 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-2.85 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-3.72 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 |  | ClimateZone 1 | ExteriorWall | SteelFramed | Wood Siding | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a |  | ClimateZone 2a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.17 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b |  | ClimateZone 2b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.73 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b 1 |  | ClimateZone 2b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.73 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.36 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.10 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.80 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.36 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.98 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.76 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.92 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 |  | ClimateZone 5 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.15 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a |  | ClimateZone 6a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.71 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b |  | ClimateZone 6b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.44 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-3.04 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-3.91 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 1 |  | ClimateZone 1 | ExteriorWall | WoodFramed | Wood Siding | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 2a |  | ClimateZone 2a | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.17 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 2b |  | ClimateZone 2b | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-0.73 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.36 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.10 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-0.80 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.36 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.98 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.76 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.92 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 5 |  | ClimateZone 5 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-2.15 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 6a |  | ClimateZone 6a | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-2.71 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 6b |  | ClimateZone 6b | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-2.44 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-3.04 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-3.91 | 1/2IN Gypsum
CBECS 1980-2004 ExtWindow ClimateZone 1-2 |  | ClimateZone 1-2 | ExteriorWindow |  | Fixed Window 5.84/0.25/0.11
CBECS 1980-2004 ExtWindow ClimateZone 3a |  | ClimateZone 3a | ExteriorWindow |  | Fixed Window 4.09/0.26/0.13
CBECS 1980-2004 ExtWindow ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorWindow |  | Fixed Window 5.84/0.25/0.11
CBECS 1980-2004 ExtWindow ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorWindow |  | Fixed Window 5.84/0.44/0.27
CBECS 1980-2004 ExtWindow ClimateZone 3c |  | ClimateZone 3c | ExteriorWindow |  | Fixed Window 4.09/0.39/0.25
CBECS 1980-2004 ExtWindow ClimateZone 4a |  | ClimateZone 4a | ExteriorWindow |  | Fixed Window 3.35/0.36/0.27
CBECS 1980-2004 ExtWindow ClimateZone 4b |  | ClimateZone 4b | ExteriorWindow |  | Fixed Window 4.09/0.36/0.23
CBECS 1980-2004 ExtWindow ClimateZone 4c |  | ClimateZone 4c | ExteriorWindow |  | Fixed Window 4.09/0.39/0.25
CBECS 1980-2004 ExtWindow ClimateZone 5 |  | ClimateZone 5 | ExteriorWindow |  | Fixed Window 3.35/0.39/0.31
CBECS 1980-2004 ExtWindow ClimateZone 6 |  | ClimateZone 6 | ExteriorWindow |  | Fixed Window 2.96/0.39/0.31
CBECS 1980-2004 ExtWindow ClimateZone 7 |  | ClimateZone 7 | ExteriorWindow |  | Fixed Window 2.96/0.49/0.41
CBECS 1980-2004 ExtWindow ClimateZone 8 |  | ClimateZone 8 | ExteriorWindow |  | Fixed Window 2.96/0.62/0.54
CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 |  | ClimateZone 1-8 | ExteriorWindow |  | Fixed Window 5.84/0.25/0.11
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 1-3 |  | ClimateZone 1-3 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-1.76 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4a |  | ClimateZone 4a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Res Insulation-2.05 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4b |  | ClimateZone 4b | AtticFloor | WoodFramed | 1/2IN Gypsum | IEAD NonRes Roof Insulation-1.98 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4c |  | ClimateZone 4c | AtticFloor | WoodFramed | 1/2IN Gypsum | IEAD NonRes Roof Insulation-2.07 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a |  | ClimateZone 5a | AtticFloor | WoodFramed | 1/2IN Gypsum | IEAD NonRes Roof Insulation-2.50 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5b |  | ClimateZone 5b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Res Insulation-2.37 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 6 |  | ClimateZone 6 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.99 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 7 |  | ClimateZone 7 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Res Insulation-2.93 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 8 |  | ClimateZone 8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.99 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 |  | ClimateZone 1-3 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-1.76 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 4a |  | ClimateZone 4a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.04 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 4b |  | ClimateZone 4b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-1.98 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 4c |  | ClimateZone 4c | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.07 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 5a |  | ClimateZone 5a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.50 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 5b |  | ClimateZone 5b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.37 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 6 |  | ClimateZone 6 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.99 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 7 |  | ClimateZone 7 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.93 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 7 1 |  | ClimateZone 7 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.93 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 8 |  | ClimateZone 8 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.99 | Metal Decking
CBECS Before-1980 ExtWall Mass ClimateZone 1-2 |  | ClimateZone 1-2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.77 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.78 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 3b |  | ClimateZone 3b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.77 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.79 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.99 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.96 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.01 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 5a |  | ClimateZone 5a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.13 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 5b |  | ClimateZone 5b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.09 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 6 |  | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.22 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.30 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.41 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 1-2 |  | ClimateZone 1-2 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.57 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.59 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 3b |  | ClimateZone 3b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.57 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.59 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.80 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.77 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.81 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 5a |  | ClimateZone 5a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.94 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 5b |  | ClimateZone 5b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.90 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 6 |  | ClimateZone 6 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.02 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.10 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.22 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b |  | ClimateZone 1-3b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.77 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.79 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.99 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.96 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.01 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a |  | ClimateZone 5a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.13 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b |  | ClimateZone 5b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.09 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 |  | ClimateZone 6 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.22 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.30 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.41 | 1/2IN Gypsum
CBECS Before-1980 ExtWindow ClimateZone 1-4 |  | ClimateZone 1-4 | ExteriorWindow |  | Fixed Window 5.84/0.54/0.38
CBECS Before-1980 ExtWindow ClimateZone 5-8 |  | ClimateZone 5-8 | ExteriorWindow |  | Fixed Window 3.53/0.41/0.32
CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 |  | ClimateZone 1-8 | ExteriorWindow |  | Fixed Window 5.84/0.54/0.38
Exterior Door |  | ClimateZone 1-8 | ExteriorDoor |  | F08 Metal surface | I01 25mm insulation board
ExtSlab 4in ClimateZone 1-8 |  | ClimateZone 1-8 | ExteriorFloor |  | MAT-CC05 4 HW CONCRETE
ExtSlab 8in ClimateZone 1-8 |  | ClimateZone 1-8 | ExteriorFloor |  | MAT-CC05 8 HW CONCRETE
ExtSlabCarpet 4in ClimateZone 1-8 |  | ClimateZone 1-8 | ExteriorFloor |  | MAT-CC05 4 HW CONCRETE | CP02 CARPET PAD
ExtSlabCarpet 8in ClimateZone 1-8 |  | ClimateZone 1-8 | ExteriorFloor |  | MAT-CC05 8 HW CONCRETE | CP02 CARPET PAD
Interior Ceiling |  | ClimateZone 1-8 | InteriorCeiling |  | M11 100mm lightweight concrete | F05 Ceiling air space resistance | F16 Acoustic tile
Interior Door |  | ClimateZone 1-8 | InteriorDoor |  | G05 25mm wood
Interior Floor |  | ClimateZone 1-8 | InteriorFloor |  | F16 Acoustic tile | F05 Ceiling air space resistance | M11 100mm lightweight concrete
Interior Partition |  | ClimateZone 1-8 | InteriorPartition |  | G05 25mm wood
Interior Wall |  | ClimateZone 1-8 | InteriorWall |  | G01a 19mm gypsum board | F04 Wall air space resistance | G01a 19mm gypsum board
Interior Window |  | ClimateZone 1-8 | InteriorWindow |  | Clear 3mm
ASHRAE 90.1-2007 AtticFloor ClimateZone 1 | ASHRAE 90.1-2007 | ClimateZone 1 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-27.44 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 AtticFloor ClimateZone 2-7 | ASHRAE 90.1-2007 | ClimateZone 2-5 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-35.07 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 AtticFloor ClimateZone 8 | ASHRAE 90.1-2007 | ClimateZone 8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-45.65 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 AtticFloor ClimateZone 1-2 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1-2 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-10.37 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 AtticFloor ClimateZone 3-5 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1-5 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-16.90 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 AtticFloor ClimateZone 6-8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 6-8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-27.44 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-14.76 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | ASHRAE 90.1-2007 | ClimateZone 5-6 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-19.72 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1-2 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1-2 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-3.47 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 3-4 Semiheated | ASHRAE 90.1-2007 | ClimateZone 3-4 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-4.66 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 5 Semiheated | ASHRAE 90.1-2007 | ClimateZone 5 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-7.29 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 6-7 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-9.64 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-14.76 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 1-7 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-14.60 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 8 | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-19.63 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 1 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing
ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 2 Semiheated | ASHRAE 90.1-2007 | ClimateZone 2 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-5.21 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 3-7 Semiheated | ASHRAE 90.1-2007 | ClimateZone 3-4 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-9.53 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-13.11 IP | Metal Decking
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 2 | ASHRAE 90.1-2007 | ClimateZone 2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-4.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ASHRAE 90.1-2007 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-5.74 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 4 | ASHRAE 90.1-2007 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-7.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 5 | ASHRAE 90.1-2007 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-8.72 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 6 | ASHRAE 90.1-2007 | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-10.11 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ASHRAE 90.1-2007 | ClimateZone 7-8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-11.70 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-4.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 2 | ASHRAE 90.1-2007 | ClimateZone 2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-5.74 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 3 | ASHRAE 90.1-2007 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-7.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 4 | ASHRAE 90.1-2007 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-8.72 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 5 | ASHRAE 90.1-2007 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-10.11 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 6-7 | ASHRAE 90.1-2007 | ClimateZone 6-7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-11.70 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 8 | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-16.84 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 1-4 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1-4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 5-6 Semiheated | ASHRAE 90.1-2007 | ClimateZone 5-6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-4.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7 Semiheated | ASHRAE 90.1-2007 | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-5.74 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-7.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Metal ClimateZone 1-6 | ASHRAE 90.1-2007 | ClimateZone 1-6 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-7.55 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Metal ClimateZone 7-8 | ASHRAE 90.1-2007 | ClimateZone 7-8 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-16.24 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Metal ClimateZone 1 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWall | Metal | Metal Siding | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Metal ClimateZone 2-3 Semiheated | ASHRAE 90.1-2007 | ClimateZone 2-3 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-4.14 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Metal ClimateZone 4 Semiheated | ASHRAE 90.1-2007 | ClimateZone 4 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-6.16 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Metal ClimateZone 5 Semiheated | ASHRAE 90.1-2007 | ClimateZone 5 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-6.83 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 6-8 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-7.55 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ASHRAE 90.1-2007 | ClimateZone 1-2 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-6.25 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ASHRAE 90.1-2007 | ClimateZone 3 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-10.09 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ASHRAE 90.1-2007 | ClimateZone 4-8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-13.81 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-6.25 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ASHRAE 90.1-2007 | ClimateZone 2-6 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-13.81 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 7 | ASHRAE 90.1-2007 | ClimateZone 7 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-21.99 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 8 | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-25.21 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWall | SteelFramed | Wood Siding | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 2-7 Semiheated | ASHRAE 90.1-2007 | ClimateZone 2-7 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-6.25 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-10.09 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 1-4 | ASHRAE 90.1-2007 | ClimateZone 1-4 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-9.42 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 5 | ASHRAE 90.1-2007 | ClimateZone 5 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-13.81 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 6-7 | ASHRAE 90.1-2007 | ClimateZone 6-7 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-17.79 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 8 | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-25.96 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 1 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWall | WoodFramed | Wood Siding | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 2-8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 2-8 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-9.42 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Fixed Window 5.84/0.25/0.11
ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Fixed Window 4.26/0.25/0.16
ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | Fixed Window 3.69/0.25/0.16
ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 | ClimateZone 4-6 | ExteriorWindow | Metal framing (all other) | Fixed Window 3.12/0.40/0.31
ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 | ClimateZone 7-8 | ExteriorWindow | Metal framing (all other) | Fixed Window 2.56/0.45/0.35
ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1-5 | ExteriorWindow | Metal framing (all other) | Fixed Window 5.84/0.70/0.60
ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 6-8 | ExteriorWindow | Metal framing (all other) | Fixed Window 3.69/0.70/0.60
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 5.84/0.25/0.11
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 2 | ASHRAE 90.1-2007 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 4.26/0.25/0.16
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 3 | ASHRAE 90.1-2007 | ClimateZone 3 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 3.69/0.25/0.16
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 4 | ASHRAE 90.1-2007 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 2.30/0.40/0.31
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 5-6 | ASHRAE 90.1-2007 | ClimateZone 5-6 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 2.00/0.40/0.31
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 7-8 | ASHRAE 90.1-2007 | ClimateZone 7-8 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 2.00/0.45/0.35
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1-5 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 5.84/0.70/0.60
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 6-8 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 3.69/0.70/0.60
ASHRAE 90.1-2010 AtticFloor ClimateZone 1 | ASHRAE 90.1-2010 | ClimateZone 1 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-27.44 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 AtticFloor ClimateZone 2-7 | ASHRAE 90.1-2010 | ClimateZone 2-7 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-35.07 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 AtticFloor ClimateZone 8 | ASHRAE 90.1-2010 | ClimateZone 8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-45.65 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 AtticFloor ClimateZone 1-2 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1-2 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-10.37 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 AtticFloor ClimateZone 3-5 Semiheated | ASHRAE 90.1-2010 | ClimateZone 3-5 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-16.90 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 AtticFloor ClimateZone 6-8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 6-8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-27.44 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-14.76 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | ASHRAE 90.1-2010 | ClimateZone 2-8 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-19.72 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1-2 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1-2 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-3.47 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 3-4 Semiheated | ASHRAE 90.1-2010 | ClimateZone 3-4 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-4.66 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 5 Semiheated | ASHRAE 90.1-2010 | ClimateZone 5 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-7.29 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 6-7 Semiheated | ASHRAE 90.1-2010 | ClimateZone 6-7 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-9.64 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-14.76 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-14.60 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 2-5 | ASHRAE 90.1-2010 | ClimateZone 2-5 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-17.40 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 6-7 | ASHRAE 90.1-2010 | ClimateZone 6-7 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-19.63 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 8 | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-27.79 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 1 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-5.21 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 2-4 Semiheated | ASHRAE 90.1-2010 | ClimateZone 2-4 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-9.53 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 5 Semiheated | ASHRAE 90.1-2010 | ClimateZone 5 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-11.27 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 6-7 Semiheated | ASHRAE 90.1-2010 | ClimateZone 6-7 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-13.11 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-14.60 IP | Metal Decking
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 2 | ASHRAE 90.1-2010 | ClimateZone 2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-4.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ASHRAE 90.1-2010 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-5.74 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 4 | ASHRAE 90.1-2010 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-7.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 5 | ASHRAE 90.1-2010 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-8.72 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 6 | ASHRAE 90.1-2010 | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-10.11 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ASHRAE 90.1-2010 | ClimateZone 7-8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-16.84 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-4.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 2 | ASHRAE 90.1-2010 | ClimateZone 2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-5.74 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 3 | ASHRAE 90.1-2010 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-7.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 4 | ASHRAE 90.1-2010 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-8.72 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 5 | ASHRAE 90.1-2010 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-10.11 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 6-7 | ASHRAE 90.1-2010 | ClimateZone 6-7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-11.70 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 8 | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-16.84 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 1-4 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1-4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 5-6 Semiheated | ASHRAE 90.1-2010 | ClimateZone 5-6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-4.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7 Semiheated | ASHRAE 90.1-2010 | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-5.74 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-7.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-2 | ASHRAE 90.1-2010 | ClimateZone 1-2 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-9.45 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Metal ClimateZone 3-4 | ASHRAE 90.1-2010 | ClimateZone 3-4 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-10.60 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Metal ClimateZone 5-6 | ASHRAE 90.1-2010 | ClimateZone 5-6 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-13.19 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Metal ClimateZone 7-8 | ASHRAE 90.1-2010 | ClimateZone 7-8 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-16.24 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1-8 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-7.55 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ASHRAE 90.1-2010 | ClimateZone 1-2 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-6.25 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ASHRAE 90.1-2010 | ClimateZone 3 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-10.09 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ASHRAE 90.1-2010 | ClimateZone 4-8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-13.81 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-6.25 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ASHRAE 90.1-2010 | ClimateZone 2-6 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-13.81 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 7 | ASHRAE 90.1-2010 | ClimateZone 7 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-21.99 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 8 | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-25.21 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWall | SteelFramed | Wood Siding | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 2-7 Semiheated | ASHRAE 90.1-2010 | ClimateZone 2-7 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-6.25 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-10.09 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ASHRAE 90.1-2010 | ClimateZone 1-4 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-9.42 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 5 | ASHRAE 90.1-2010 | ClimateZone 5 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-13.81 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 6-7 | ASHRAE 90.1-2010 | ClimateZone 6-7 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-17.79 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 8 | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-25.96 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWall | WoodFramed | Wood Siding | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 2-8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 2-8 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-9.42 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Fixed Window 5.84/0.25/0.11
ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Fixed Window 4.26/0.25/0.16
ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | Fixed Window 3.69/0.25/0.16
ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 | ClimateZone 4-6 | ExteriorWindow | Metal framing (all other) | Fixed Window 3.12/0.40/0.31
ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 | ClimateZone 7-8 | ExteriorWindow | Metal framing (all other) | Fixed Window 2.56/0.45/0.35
ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1-5 | ExteriorWindow | Metal framing (all other) | Fixed Window 5.84/0.70/0.60
ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 6-8 | ExteriorWindow | Metal framing (all other) | Fixed Window 3.69/0.70/0.60
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 5.84/0.25/0.11
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 2 | ASHRAE 90.1-2010 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 4.26/0.25/0.16
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 3 | ASHRAE 90.1-2010 | ClimateZone 3 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 3.69/0.25/0.16
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 4 | ASHRAE 90.1-2010 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 2.30/0.40/0.31
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 5-6 | ASHRAE 90.1-2010 | ClimateZone 5-6 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 2.00/0.40/0.31
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 7-8 | ASHRAE 90.1-2010 | ClimateZone 7-8 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 2.00/0.45/0.35
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1-5 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 5.84/0.70/0.60
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 6-8 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 3.69/0.70/0.60

## Materials
Each Material represents a layer of typical building material. Materials are referenced on the Constructions tab.
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
|  | Opaque Material Properties | [9 empty] | Simple Glazing Material Properties |  |  | Detailed Glazing Material Properties
Name | Material Type | Roughness | Thickness (in) | Conductivity (Btu*in/hr*ft^2*F) | Resistance (hr*ft^2*F/Btu) | Density (lb/ft^3) | Specific Heat (Btu/lbm*F) | Thermal Absorptance | Solar Absorptance | Visible Absorptance | Gas Type | U-Factor (Btu/hr*ft^2*F) | Solar Heat Gain Coefficient | Visible Transmittance | Optical Data Type | Solar Transmittance At Normal Incidence | Front Side Solar Reflectance At Normal Incidence | Back Side Solar Relectance At Normal Incidence | Visible Transmittance At Normal Incidence | Front Side Visible Reflectance At Normal Incidence | Back Side Visible Relectance At Normal Incidence | Infrared Transmittance At Normal Incidence | Front Side Infrared Hemispherical Emissivity | Back Side Infrared Hemispherical Emissivity | Dirt Correction Factor For Solar And Visible Transmittance | Solar Diffusing
1/2IN Gypsum | StandardOpaqueMaterial | Smooth | 0.5 | 1.1094 | 0.45071 | 48.9997 | 0.19824 | 0.9 | 0.4 | 0.4
1IN Stucco | StandardOpaqueMaterial | Smooth | 0.99606 | 4.7966 | 0.20766 | 115.9912 | 0.19991 | 0.9 | 0.92 | 0.92
8IN Concrete HW | StandardOpaqueMaterial | MediumRough | 8.0039 | 11.9921 | 0.66743 | 140.0259 | 0.19991 | 0.9 | 0.65 | 0.65
8IN CONCRETE HW RefBldg | StandardOpaqueMaterial | Rough | 8 | 9.0898 | 0.88011 | 139.8386 | 0.19987 | 0.9 | 0.7 | 0.7
Air 13mm | Gas |  | 0.5 | [7 empty] | Air
AtticFloor Insulation | StandardOpaqueMaterial | MediumRough | 9.3661 | 0.33974 | 27.5685 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-1.76 | StandardOpaqueMaterial | MediumRough | 2.6224 | 0.33974 | 7.719 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-2.38 | StandardOpaqueMaterial | MediumRough | 3.8162 | 0.33974 | 11.2327 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-2.45 | StandardOpaqueMaterial | MediumRough | 3.9437 | 0.33974 | 11.608 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-2.67 | StandardOpaqueMaterial | MediumRough | 4.3727 | 0.33974 | 12.8707 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-2.75 | StandardOpaqueMaterial | MediumRough | 4.5336 | 0.33974 | 13.3442 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-2.99 | StandardOpaqueMaterial | MediumRough | 4.9835 | 0.33974 | 14.6685 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.04 | StandardOpaqueMaterial | MediumRough | 5.0827 | 0.33974 | 14.9607 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.32 | StandardOpaqueMaterial | MediumRough | 5.7407 | 0.33974 | 16.8973 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.45 | StandardOpaqueMaterial | MediumRough | 5.9921 | 0.33974 | 17.6373 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.59 | StandardOpaqueMaterial | MediumRough | 6.264 | 0.33974 | 18.4376 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.67 | StandardOpaqueMaterial | MediumRough | 6.3031 | 0.33974 | 18.5528 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.83 | StandardOpaqueMaterial | MediumRough | 6.6109 | 0.33974 | 19.4587 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.91 | StandardOpaqueMaterial | MediumRough | 6.8803 | 0.33974 | 20.2518 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-4.40 | StandardOpaqueMaterial | MediumRough | 7.7188 | 0.33974 | 22.7197 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-5.18 | StandardOpaqueMaterial | MediumRough | 11.9138 | 0.33974 | 35.0673 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-5.68 | StandardOpaqueMaterial | MediumRough | 10.2901 | 0.33974 | 30.2881 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-6.52 | StandardOpaqueMaterial | MediumRough | 11.9138 | 0.33974 | 35.0673 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Res Insulation-2.05 | StandardOpaqueMaterial | MediumRough | 3.1755 | 0.33974 | 9.347 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Res Insulation-2.37 | StandardOpaqueMaterial | MediumRough | 3.8007 | 0.33974 | 11.187 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Res Insulation-2.93 | StandardOpaqueMaterial | MediumRough | 4.8875 | 0.33974 | 14.386 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Insulation R-10.37 IP | StandardOpaqueMaterial | MediumRough | 3.5246 | 0.33974 | 10.3743 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Insulation R-16.90 IP | StandardOpaqueMaterial | MediumRough | 5.7404 | 0.33974 | 16.8965 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Insulation R-27.44 IP | StandardOpaqueMaterial | MediumRough | 9.3226 | 0.33974 | 27.4403 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Insulation R-35.07 IP | StandardOpaqueMaterial | MediumRough | 11.9132 | 0.33974 | 35.0656 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Insulation R-45.65 IP | StandardOpaqueMaterial | MediumRough | 15.5083 | 0.33974 | 45.6476 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Clear 3mm | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.837 | 0.075 | 0.075 | 0.898 | 0.081 | 0.081 | 0 | 0.84 | 0.84 | 1 | FALSE
CP02 CARPET PAD | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00019108 | 0.9 | 0.8 | 0.8
F04 Wall air space resistance | AirGap |  |  | 46.2231 | 0.021634
F05 Ceiling air space resistance | AirGap |  |  | 38.5193 | 0.025961
F08 Metal surface | StandardOpaqueMaterial | Smooth | 0.031496 | 313.9476 | 0.00010032 | 488.4364 | 0.11942 | 0.9 | 0.7 | 0.7
F16 Acoustic tile | StandardOpaqueMaterial | MediumSmooth | 0.75197 | 0.41601 | 1.8076 | 22.9735 | 0.14092 | 0.9 | 0.3 | 0.3
Fixed Window 2.00/0.40/0.31 | SimpleGlazing | [10 empty] | 0.35 | 0.4 | 0.31
Fixed Window 2.00/0.45/0.35 | SimpleGlazing | [10 empty] | 0.35 | 0.45 | 0.35
Fixed Window 2.30/0.40/0.31 | SimpleGlazing | [10 empty] | 0.4 | 0.4 | 0.31
Fixed Window 2.56/0.45/0.35 | SimpleGlazing | [10 empty] | 0.45 | 0.45 | 0.35
Fixed Window 2.62/0.30/0.21 | SimpleGlazing | [10 empty] | 0.45998 | 0.3 | 0.21
Fixed Window 2.67/0.30/0.21 | SimpleGlazing | [10 empty] | 0.46998 | 0.49 | 0.38
Fixed Window 2.96/0.39/0.31 | SimpleGlazing | [10 empty] | 0.51998 | 0.39 | 0.31
Fixed Window 2.96/0.49/0.41 | SimpleGlazing | [10 empty] | 0.51998 | 0.49 | 0.41
Fixed Window 2.96/0.62/0.54 | SimpleGlazing | [10 empty] | 0.51998 | 0.62 | 0.54
Fixed Window 3.12/0.40/0.31 | SimpleGlazing | [10 empty] | 0.55 | 0.4 | 0.31
Fixed Window 3.24/0.25/0.16 | SimpleGlazing | [10 empty] | 0.56997 | 0.25 | 0.16
Fixed Window 3.24/0.39/0.31 | SimpleGlazing | [10 empty] | 0.56997 | 0.39 | 0.31
Fixed Window 3.24/0.49/0.41 | SimpleGlazing | [10 empty] | 0.56997 | 0.49 | 0.41
Fixed Window 3.35/0.36/0.27 | SimpleGlazing | [10 empty] | 0.58997 | 0.36 | 0.27
Fixed Window 3.35/0.39/0.31 | SimpleGlazing | [10 empty] | 0.58997 | 0.39 | 0.31
Fixed Window 3.53/0.41/0.32 | SimpleGlazing | [10 empty] | 0.61997 | 0.41 | 0.32
Fixed Window 3.69/0.25/0.16 | SimpleGlazing | [10 empty] | 0.65 | 0.25 | 0.16
Fixed Window 3.69/0.70/0.60 | SimpleGlazing | [10 empty] | 0.65 | 0.7 | 0.6
Fixed Window 3.81/0.39/0.27 | SimpleGlazing | [10 empty] | 0.51998 | 0.39 | 0.27
Fixed Window 3.81/0.49/0.38 | SimpleGlazing | [10 empty] | 0.51998 | 0.49 | 0.38
Fixed Window 4.09/0.26/0.13 | SimpleGlazing | [10 empty] | 0.71997 | 0.25 | 0.13
Fixed Window 4.09/0.36/0.23 | SimpleGlazing | [10 empty] | 0.71997 | 0.36 | 0.23
Fixed Window 4.09/0.39/0.25 | SimpleGlazing | [10 empty] | 0.71997 | 0.39 | 0.25
Fixed Window 4.26/0.25/0.16 | SimpleGlazing | [10 empty] | 0.75 | 0.25 | 0.16
Fixed Window 5.84/0.25/0.11 | SimpleGlazing | [10 empty] | 1.0285 | 0.25 | 0.11
Fixed Window 5.84/0.39/0.22 | SimpleGlazing | [10 empty] | 1.0285 | 0.39 | 0.22
Fixed Window 5.84/0.44/0.27 | SimpleGlazing | [10 empty] | 1.0285 | 0.44 | 0.27
Fixed Window 5.84/0.54/0.38 | SimpleGlazing | [10 empty] | 1.0285 | 0.54 | 0.38
Fixed Window 5.84/0.61/0.47 | SimpleGlazing | [10 empty] | 1.0285 | 0.61 | 0.47
Fixed Window 5.84/0.70/0.60 | SimpleGlazing | [10 empty] | 1.0285 | 0.7 | 0.6
G01a 19mm gypsum board | StandardOpaqueMaterial | MediumSmooth | 0.74803 | 1.1094 | 0.67429 | 49.9424 | 0.26034 | 0.9 | 0.4 | 0.4
G05 25mm wood | StandardOpaqueMaterial | MediumSmooth | 1 | 1.04 | 0.96152 | 37.9562 | 0.38932 | 0.9 | 0.5 | 0.5
I01 25mm insulation board | StandardOpaqueMaterial | MediumRough | 1 | 0.208 | 4.8076 | 2.6844 | 0.289 | 0.9 | 0.6 | 0.6
I02 50mm insulation board | StandardOpaqueMaterial | MediumRough | 2 | 0.208 | 9.6152 | 2.6844 | 0.289 | 0.9 | 0.6 | 0.6
IEAD NonRes Roof Insulation-1.76 | StandardOpaqueMaterial | MediumRough | 2.9126 | 0.33974 | 8.5731 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-1.98 | StandardOpaqueMaterial | MediumRough | 3.3325 | 0.33974 | 9.8091 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.00 | StandardOpaqueMaterial | MediumRough | 3.3759 | 0.33974 | 9.9368 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.04 | StandardOpaqueMaterial | MediumRough | 3.4657 | 0.33974 | 10.2011 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.07 | StandardOpaqueMaterial | MediumRough | 3.5122 | 0.33974 | 10.3379 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.37 | StandardOpaqueMaterial | MediumRough | 4.0909 | 0.33974 | 12.0411 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.38 | StandardOpaqueMaterial | MediumRough | 4.1064 | 0.33974 | 12.0868 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.44 | StandardOpaqueMaterial | MediumRough | 4.2339 | 0.33974 | 12.4621 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.50 | StandardOpaqueMaterial | MediumRough | 4.3392 | 0.33974 | 12.7722 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.67 | StandardOpaqueMaterial | MediumRough | 4.6629 | 0.33974 | 13.7248 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.75 | StandardOpaqueMaterial | MediumRough | 4.8237 | 0.33974 | 14.1983 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.79 | StandardOpaqueMaterial | MediumRough | 4.908 | 0.33974 | 14.4464 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.85 | StandardOpaqueMaterial | MediumRough | 5.0133 | 0.33974 | 14.7564 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.93 | StandardOpaqueMaterial | MediumRough | 5.1777 | 0.33974 | 15.2401 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.99 | StandardOpaqueMaterial | MediumRough | 5.2736 | 0.33974 | 15.5226 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.03 | StandardOpaqueMaterial | MediumRough | 5.3729 | 0.33974 | 15.8148 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.38 | StandardOpaqueMaterial | MediumRough | 6.0309 | 0.33974 | 17.7514 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.51 | StandardOpaqueMaterial | MediumRough | 6.2823 | 0.33974 | 18.4914 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.65 | StandardOpaqueMaterial | MediumRough | 6.5542 | 0.33974 | 19.2917 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.66 | StandardOpaqueMaterial | MediumRough | 6.5933 | 0.33974 | 19.4069 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.72 | StandardOpaqueMaterial | MediumRough | 6.6986 | 0.33974 | 19.7169 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.83 | StandardOpaqueMaterial | MediumRough | 6.9011 | 0.33974 | 20.3128 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.97 | StandardOpaqueMaterial | MediumRough | 7.1705 | 0.33974 | 21.1059 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-4.41 | StandardOpaqueMaterial | MediumRough | 8.009 | 0.33974 | 23.5738 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-5.75 | StandardOpaqueMaterial | MediumRough | 10.5803 | 0.33974 | 31.1422 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD Roof Insulation R-3.47 IP | StandardOpaqueMaterial | MediumRough | 1.1788 | 0.33974 | 3.4698 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD Roof Insulation R-4.66 IP | StandardOpaqueMaterial | MediumRough | 1.5842 | 0.33974 | 4.663 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD Roof Insulation R-7.29 IP | StandardOpaqueMaterial | MediumRough | 2.4754 | 0.33974 | 7.286 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD Roof Insulation R-9.64 IP | StandardOpaqueMaterial | MediumRough | 3.2735 | 0.33974 | 9.6354 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD Roof Insulation R-14.76 IP | StandardOpaqueMaterial | MediumRough | 5.0131 | 0.33974 | 14.7557 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD Roof Insulation R-19.72 IP | StandardOpaqueMaterial | MediumRough | 6.6983 | 0.33974 | 19.716 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
M01 100mm brick | StandardOpaqueMaterial | MediumRough | 4 | 6.1708 | 0.64822 | 119.8617 | 0.18869 | 0.9 | 0.7 | 0.7
M11 100mm lightweight concrete | StandardOpaqueMaterial | MediumRough | 4 | 3.6747 | 1.0885 | 79.9078 | 0.20063 | 0.9 | 0.5 | 0.5
M15 200mm heavyweight concrete | StandardOpaqueMaterial | MediumRough | 8 | 13.5203 | 0.5917 | 139.8386 | 0.21496 | 0.9 | 0.5 | 0.5
Mass NonRes Wall Insulation-0.43 | StandardOpaqueMaterial | MediumRough | 0.017196 | 0.33974 | 0.050616 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.52 | StandardOpaqueMaterial | MediumRough | 0.18781 | 0.33974 | 0.55279 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.61 | StandardOpaqueMaterial | MediumRough | 0.3601 | 0.33974 | 1.0599 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.77 | StandardOpaqueMaterial | MediumRough | 0.66572 | 0.33974 | 1.9595 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.78 | StandardOpaqueMaterial | MediumRough | 0.69855 | 0.33974 | 2.0561 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.79 | StandardOpaqueMaterial | MediumRough | 0.70529 | 0.33974 | 2.076 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.93 | StandardOpaqueMaterial | MediumRough | 0.97671 | 0.33974 | 2.8749 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.96 | StandardOpaqueMaterial | MediumRough | 1.035 | 0.33974 | 3.0465 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.99 | StandardOpaqueMaterial | MediumRough | 1.0973 | 0.33974 | 3.2297 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.01 | StandardOpaqueMaterial | MediumRough | 1.13 | 0.33974 | 3.326 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.09 | StandardOpaqueMaterial | MediumRough | 1.2988 | 0.33974 | 3.8229 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.13 | StandardOpaqueMaterial | MediumRough | 1.3664 | 0.33974 | 4.022 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.17 | StandardOpaqueMaterial | MediumRough | 1.4386 | 0.33974 | 4.2343 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.22 | StandardOpaqueMaterial | MediumRough | 1.5317 | 0.33974 | 4.5083 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.26 | StandardOpaqueMaterial | MediumRough | 1.6154 | 0.33974 | 4.7547 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.30 | StandardOpaqueMaterial | MediumRough | 1.6867 | 0.33974 | 4.9648 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.41 | StandardOpaqueMaterial | MediumRough | 1.9066 | 0.33974 | 5.6118 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.43 | StandardOpaqueMaterial | MediumRough | 1.9508 | 0.33974 | 5.7419 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.47 | StandardOpaqueMaterial | MediumRough | 2.0198 | 0.33974 | 5.9452 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.69 | StandardOpaqueMaterial | MediumRough | 2.4554 | 0.33974 | 7.2273 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.76 | StandardOpaqueMaterial | MediumRough | 2.5861 | 0.33974 | 7.6119 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.96 | StandardOpaqueMaterial | MediumRough | 2.9636 | 0.33974 | 8.7231 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-2.20 | StandardOpaqueMaterial | MediumRough | 3.4355 | 0.33974 | 10.1121 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-2.23 | StandardOpaqueMaterial | MediumRough | 3.4892 | 0.33974 | 10.2703 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-2.48 | StandardOpaqueMaterial | MediumRough | 3.9738 | 0.33974 | 11.6966 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-2.89 | StandardOpaqueMaterial | MediumRough | 4.7583 | 0.33974 | 14.0057 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-3.75 | StandardOpaqueMaterial | MediumRough | 6.4174 | 0.33974 | 18.8891 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass Wall Insulation R-4.23 IP | StandardOpaqueMaterial | MediumRough | 1.4385 | 0.33974 | 4.234 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass Wall Insulation R-5.74 IP | StandardOpaqueMaterial | MediumRough | 1.9507 | 0.33974 | 5.7416 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass Wall Insulation R-7.23 IP | StandardOpaqueMaterial | MediumRough | 2.4553 | 0.33974 | 7.2269 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass Wall Insulation R-8.72 IP | StandardOpaqueMaterial | MediumRough | 2.9634 | 0.33974 | 8.7226 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass Wall Insulation R-10.11 IP | StandardOpaqueMaterial | MediumRough | 3.4353 | 0.33974 | 10.1115 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass Wall Insulation R-11.70 IP | StandardOpaqueMaterial | MediumRough | 3.9736 | 0.33974 | 11.696 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass Wall Insulation R-16.84 IP | StandardOpaqueMaterial | MediumRough | 5.722 | 0.33974 | 16.8423 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
MAT-CC05 4 HW CONCRETE | StandardOpaqueMaterial | Rough | 4 | 9.0898 | 0.44005 | 139.8386 | 0.19987 | 0.9 | 0.85 | 0.85
MAT-CC05 8 HW CONCRETE | StandardOpaqueMaterial | Rough | 8 | 9.0898 | 0.88011 | 139.8386 | 0.19987 | 0.9 | 0.85 | 0.85
MAT-SHEATH | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.54 | StandardOpaqueMaterial | MediumRough | 0.60417 | 0.33974 | 1.7783 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.57 | StandardOpaqueMaterial | MediumRough | 0.66572 | 0.33974 | 1.9595 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.59 | StandardOpaqueMaterial | MediumRough | 0.69855 | 0.33974 | 2.0561 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.61 | StandardOpaqueMaterial | MediumRough | 0.73287 | 0.33974 | 2.1571 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.77 | StandardOpaqueMaterial | MediumRough | 1.035 | 0.33974 | 3.0465 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.80 | StandardOpaqueMaterial | MediumRough | 1.0973 | 0.33974 | 3.2297 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.81 | StandardOpaqueMaterial | MediumRough | 1.13 | 0.33974 | 3.326 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.90 | StandardOpaqueMaterial | MediumRough | 1.2988 | 0.33974 | 3.8229 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.91 | StandardOpaqueMaterial | MediumRough | 1.312 | 0.33974 | 3.8618 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.94 | StandardOpaqueMaterial | MediumRough | 1.3664 | 0.33974 | 4.022 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.98 | StandardOpaqueMaterial | MediumRough | 1.4536 | 0.33974 | 4.2785 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.02 | StandardOpaqueMaterial | MediumRough | 1.5317 | 0.33974 | 4.5083 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.10 | StandardOpaqueMaterial | MediumRough | 1.6867 | 0.33974 | 4.9648 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.12 | StandardOpaqueMaterial | MediumRough | 1.724 | 0.33974 | 5.0745 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.16 | StandardOpaqueMaterial | MediumRough | 1.802 | 0.33974 | 5.3041 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.22 | StandardOpaqueMaterial | MediumRough | 1.9066 | 0.33974 | 5.6118 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.24 | StandardOpaqueMaterial | MediumRough | 1.9508 | 0.33974 | 5.7419 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.37 | StandardOpaqueMaterial | MediumRough | 2.1952 | 0.33974 | 6.4614 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.57 | StandardOpaqueMaterial | MediumRough | 2.5861 | 0.33974 | 7.6119 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.72 | StandardOpaqueMaterial | MediumRough | 2.8815 | 0.33974 | 8.4815 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.79 | StandardOpaqueMaterial | MediumRough | 3.006 | 0.33974 | 8.848 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.96 | StandardOpaqueMaterial | MediumRough | 3.3319 | 0.33974 | 9.8072 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-2.25 | StandardOpaqueMaterial | MediumRough | 3.9074 | 0.33974 | 11.501 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-2.52 | StandardOpaqueMaterial | MediumRough | 4.4155 | 0.33974 | 12.9968 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-2.85 | StandardOpaqueMaterial | MediumRough | 5.0464 | 0.33974 | 14.8537 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-3.72 | StandardOpaqueMaterial | MediumRough | 6.7387 | 0.33974 | 19.8347 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-4.14 IP | StandardOpaqueMaterial | MediumRough | 1.4044 | 0.33974 | 4.1339 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-6.16 IP | StandardOpaqueMaterial | MediumRough | 2.0934 | 0.33974 | 6.1618 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-6.83 IP | StandardOpaqueMaterial | MediumRough | 2.3201 | 0.33974 | 6.8292 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-7.55 IP | StandardOpaqueMaterial | MediumRough | 2.5646 | 0.33974 | 7.5487 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-9.45 IP | StandardOpaqueMaterial | MediumRough | 3.2112 | 0.33974 | 9.4518 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-10.60 IP | StandardOpaqueMaterial | MediumRough | 3.6026 | 0.33974 | 10.6039 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-13.19 IP | StandardOpaqueMaterial | MediumRough | 4.4818 | 0.33974 | 13.1919 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-16.24 IP | StandardOpaqueMaterial | MediumRough | 5.5184 | 0.33974 | 16.243 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Decking | StandardOpaqueMaterial | MediumSmooth | 0.059055 | 312.0478 | 0.00018925 | 479.4467 | 0.099933 | 0.9 | 0.6 | 0.6
Metal Roofing | StandardOpaqueMaterial | MediumSmooth | 0.059055 | 312.0478 | 0.00018925 | 479.4467 | 0.099933 | 0.9 | 0.6 | 0.6
Metal Semi-Cond Roof Insulation-1.05 | StandardOpaqueMaterial | MediumRough | 1.6641 | 0.33974 | 4.8981 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-1.76 | StandardOpaqueMaterial | MediumRough | 3.0272 | 0.33974 | 8.9102 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-1.81 | StandardOpaqueMaterial | MediumRough | 3.1322 | 0.33974 | 9.2195 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-1.87 | StandardOpaqueMaterial | MediumRough | 3.2376 | 0.33974 | 9.5295 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.00 | StandardOpaqueMaterial | MediumRough | 3.4905 | 0.33974 | 10.2739 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.38 | StandardOpaqueMaterial | MediumRough | 4.2209 | 0.33974 | 12.4239 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.44 | StandardOpaqueMaterial | MediumRough | 4.3484 | 0.33974 | 12.7993 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.50 | StandardOpaqueMaterial | MediumRough | 4.4538 | 0.33974 | 13.1093 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.67 | StandardOpaqueMaterial | MediumRough | 4.7774 | 0.33974 | 14.062 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.75 | StandardOpaqueMaterial | MediumRough | 4.9383 | 0.33974 | 14.5355 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.99 | StandardOpaqueMaterial | MediumRough | 5.3882 | 0.33974 | 15.8597 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.03 | StandardOpaqueMaterial | MediumRough | 5.4875 | 0.33974 | 16.1519 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.38 | StandardOpaqueMaterial | MediumRough | 6.1454 | 0.33974 | 18.0886 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.65 | StandardOpaqueMaterial | MediumRough | 6.6687 | 0.33974 | 19.6289 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.66 | StandardOpaqueMaterial | MediumRough | 6.7078 | 0.33974 | 19.7441 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.83 | StandardOpaqueMaterial | MediumRough | 7.0156 | 0.33974 | 20.6499 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.97 | StandardOpaqueMaterial | MediumRough | 7.2851 | 0.33974 | 21.443 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-4.41 | StandardOpaqueMaterial | MediumRough | 8.1235 | 0.33974 | 23.9109 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-5.75 | StandardOpaqueMaterial | MediumRough | 10.6948 | 0.33974 | 31.4793 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-5.21 IP | StandardOpaqueMaterial | MediumRough | 1.7692 | 0.33974 | 5.2076 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-9.53 IP | StandardOpaqueMaterial | MediumRough | 3.2373 | 0.33974 | 9.5289 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-11.27 IP | StandardOpaqueMaterial | MediumRough | 3.8281 | 0.33974 | 11.2678 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-13.11 IP | StandardOpaqueMaterial | MediumRough | 4.4535 | 0.33974 | 13.1085 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-14.60 IP | StandardOpaqueMaterial | MediumRough | 4.9616 | 0.33974 | 14.6042 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-17.40 IP | StandardOpaqueMaterial | MediumRough | 5.912 | 0.33974 | 17.4014 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-19.63 IP | StandardOpaqueMaterial | MediumRough | 6.6683 | 0.33974 | 19.6278 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-27.79 IP | StandardOpaqueMaterial | MediumRough | 9.4417 | 0.33974 | 27.7911 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Siding | StandardOpaqueMaterial | Smooth | 0.059055 | 311.7289 | 0.00018944 | 479.9998 | 0.097927 | 0.9 | 0.6 | 0.6
Roof Insulation [18] | StandardOpaqueMaterial | MediumRough | 6.6654 | 0.33974 | 19.619 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [19] | StandardOpaqueMaterial | MediumRough | 7.3543 | 0.33974 | 21.6469 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [21] | StandardOpaqueMaterial | MediumRough | 8.2874 | 0.33974 | 24.3934 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [22] | StandardOpaqueMaterial | MediumRough | 9.2835 | 0.33974 | 27.3252 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [24] | StandardOpaqueMaterial | MediumRough | 10.2402 | 0.33974 | 30.1411 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [25] | StandardOpaqueMaterial | MediumRough | 10.3543 | 0.33974 | 30.4772 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [26] | StandardOpaqueMaterial | MediumRough | 11.5787 | 0.33974 | 34.0812 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [27] | StandardOpaqueMaterial | MediumRough | 11.6929 | 0.33974 | 34.4172 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Membrane | StandardOpaqueMaterial | VeryRough | 0.37402 | 1.1094 | 0.33715 | 69.9998 | 0.34872 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.73 | StandardOpaqueMaterial | MediumRough | 0.79836 | 0.33974 | 2.3499 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.77 | StandardOpaqueMaterial | MediumRough | 0.85991 | 0.33974 | 2.5311 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.79 | StandardOpaqueMaterial | MediumRough | 0.89947 | 0.33974 | 2.6475 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.80 | StandardOpaqueMaterial | MediumRough | 0.92705 | 0.33974 | 2.7287 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.96 | StandardOpaqueMaterial | MediumRough | 1.2292 | 0.33974 | 3.6181 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.99 | StandardOpaqueMaterial | MediumRough | 1.2914 | 0.33974 | 3.8013 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.01 | StandardOpaqueMaterial | MediumRough | 1.3242 | 0.33974 | 3.8976 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.09 | StandardOpaqueMaterial | MediumRough | 1.493 | 0.33974 | 4.3945 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.10 | StandardOpaqueMaterial | MediumRough | 1.5062 | 0.33974 | 4.4333 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.13 | StandardOpaqueMaterial | MediumRough | 1.5606 | 0.33974 | 4.5936 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.17 | StandardOpaqueMaterial | MediumRough | 1.6477 | 0.33974 | 4.85 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.22 | StandardOpaqueMaterial | MediumRough | 1.7259 | 0.33974 | 5.0799 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.30 | StandardOpaqueMaterial | MediumRough | 1.8809 | 0.33974 | 5.5363 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.36 | StandardOpaqueMaterial | MediumRough | 1.9962 | 0.33974 | 5.8757 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.41 | StandardOpaqueMaterial | MediumRough | 2.1008 | 0.33974 | 6.1834 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.42 | StandardOpaqueMaterial | MediumRough | 2.1227 | 0.33974 | 6.2479 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.76 | StandardOpaqueMaterial | MediumRough | 2.7803 | 0.33974 | 8.1835 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.92 | StandardOpaqueMaterial | MediumRough | 3.0757 | 0.33974 | 9.0531 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.98 | StandardOpaqueMaterial | MediumRough | 3.2002 | 0.33974 | 9.4195 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-2.10 | StandardOpaqueMaterial | MediumRough | 3.4274 | 0.33974 | 10.0884 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-2.15 | StandardOpaqueMaterial | MediumRough | 3.5261 | 0.33974 | 10.3787 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-2.44 | StandardOpaqueMaterial | MediumRough | 4.1015 | 0.33974 | 12.0726 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-2.71 | StandardOpaqueMaterial | MediumRough | 4.6097 | 0.33974 | 13.5684 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-2.75 | StandardOpaqueMaterial | MediumRough | 4.6914 | 0.33974 | 13.8088 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-3.04 | StandardOpaqueMaterial | MediumRough | 5.2406 | 0.33974 | 15.4252 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-3.21 | StandardOpaqueMaterial | MediumRough | 5.5601 | 0.33974 | 16.3657 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-3.91 | StandardOpaqueMaterial | MediumRough | 6.9328 | 0.33974 | 20.4063 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame Wall Insulation R-1.02 IP | StandardOpaqueMaterial | MediumRough | 0.34789 | 0.33974 | 1.024 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame Wall Insulation R-6.25 IP | StandardOpaqueMaterial | MediumRough | 2.1226 | 0.33974 | 6.2476 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame Wall Insulation R-10.09 IP | StandardOpaqueMaterial | MediumRough | 3.4272 | 0.33974 | 10.0878 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame Wall Insulation R-13.81 IP | StandardOpaqueMaterial | MediumRough | 4.6912 | 0.33974 | 13.8081 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame Wall Insulation R-21.99 IP | StandardOpaqueMaterial | MediumRough | 7.4718 | 0.33974 | 21.9926 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame Wall Insulation R-25.21 IP | StandardOpaqueMaterial | MediumRough | 8.5649 | 0.33974 | 25.2101 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Theoretical Glass [167] | StandardGlazing |  | 0.11811 | 14.6109 | 0.068442 | [9 empty] | SpectralAverage | 0.2374 | 0.7126 | 0.7126 | 0.2512 | 0.6988 | 0.6988 | 0 | 0.985 | 0.985 | 1 | FALSE
Theoretical Glass [197] | StandardGlazing |  | 0.11811 | 0.28774 | 3.4754 | [9 empty] | SpectralAverage | 0.2349 | 0.7151 | 0.7151 | 0.2512 | 0.6988 | 0.6988 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [202] | StandardGlazing |  | 0.11811 | 0.13312 | 7.5119 | [9 empty] | SpectralAverage | 0.2325 | 0.7175 | 0.7175 | 0.3192 | 0.6308 | 0.6308 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [207] | StandardGlazing |  | 0.11811 | 0.092215 | 10.8442 | [9 empty] | SpectralAverage | 0.3311 | 0.6189 | 0.6189 | 0.44 | 0.51 | 0.51 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [216] | StandardGlazing |  | 0.11811 | 0.092215 | 10.8442 | [9 empty] | SpectralAverage | 0.3801 | 0.5699 | 0.5699 | 0.5079 | 0.4421 | 0.4421 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [221] | StandardGlazing |  | 0.11811 | 0.061708 | 16.2054 | [9 empty] | SpectralAverage | 0.4296 | 0.5204 | 0.5204 | 0.4503 | 0.4997 | 0.4997 | 0 | 0.9 | 0.9 | 1 | FALSE
Wall Insulation [31] | StandardOpaqueMaterial | MediumRough | 1.3268 | 0.29953 | 4.4296 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [32] | StandardOpaqueMaterial | MediumRough | 3.5315 | 0.31201 | 11.3187 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [33] | StandardOpaqueMaterial | MediumRough | 3.0748 | 0.31201 | 9.8549 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [34] | StandardOpaqueMaterial | MediumRough | 4.3465 | 0.31201 | 13.9307 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [35] | StandardOpaqueMaterial | MediumRough | 1.7795 | 0.29953 | 5.9411 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [36] | StandardOpaqueMaterial | MediumRough | 2.2283 | 0.29953 | 7.4396 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [37] | StandardOpaqueMaterial | MediumRough | 2.6811 | 0.29953 | 8.9512 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [38] | StandardOpaqueMaterial | MediumRough | 5.4961 | 0.31201 | 17.6152 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [39] | StandardOpaqueMaterial | MediumRough | 4.6614 | 0.31201 | 14.9401 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [40] | StandardOpaqueMaterial | MediumRough | 3.126 | 0.29953 | 10.4364 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [41] | StandardOpaqueMaterial | MediumRough | 5.5315 | 0.31201 | 17.7288 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [42] | StandardOpaqueMaterial | MediumRough | 3.5984 | 0.29953 | 12.0137 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [43] | StandardOpaqueMaterial | MediumRough | 6.2323 | 0.31201 | 19.9749 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [44] | StandardOpaqueMaterial | MediumRough | 4.3465 | 0.29953 | 14.5111 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [46] | StandardOpaqueMaterial | MediumRough | 6.4331 | 0.29953 | 21.4775 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wood Frame NonRes Wall Insulation-0.73 | StandardOpaqueMaterial | MediumRough | 0.79836 | 0.33974 | 2.3499 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-0.80 | StandardOpaqueMaterial | MediumRough | 0.92705 | 0.33974 | 2.7287 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.10 | StandardOpaqueMaterial | MediumRough | 1.5062 | 0.33974 | 4.4333 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.17 | StandardOpaqueMaterial | MediumRough | 1.6477 | 0.33974 | 4.85 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.36 | StandardOpaqueMaterial | MediumRough | 1.9962 | 0.33974 | 5.8757 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.76 | StandardOpaqueMaterial | MediumRough | 2.7803 | 0.33974 | 8.1835 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.92 | StandardOpaqueMaterial | MediumRough | 3.0757 | 0.33974 | 9.0531 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.98 | StandardOpaqueMaterial | MediumRough | 3.2002 | 0.33974 | 9.4195 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-2.15 | StandardOpaqueMaterial | MediumRough | 3.5261 | 0.33974 | 10.3787 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-2.44 | StandardOpaqueMaterial | MediumRough | 4.1015 | 0.33974 | 12.0726 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-2.71 | StandardOpaqueMaterial | MediumRough | 4.6097 | 0.33974 | 13.5684 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-3.04 | StandardOpaqueMaterial | MediumRough | 5.2406 | 0.33974 | 15.4252 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-3.45 | StandardOpaqueMaterial | MediumRough | 6.0446 | 0.33974 | 17.7918 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-3.91 | StandardOpaqueMaterial | MediumRough | 6.9328 | 0.33974 | 20.4063 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame Wall Insulation R-1.61 IP | StandardOpaqueMaterial | MediumRough | 0.54621 | 0.33974 | 1.6077 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame Wall Insulation R-9.42 IP | StandardOpaqueMaterial | MediumRough | 3.2 | 0.33974 | 9.419 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame Wall Insulation R-13.81 IP | StandardOpaqueMaterial | MediumRough | 4.6912 | 0.33974 | 13.8081 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame Wall Insulation R-17.79 IP | StandardOpaqueMaterial | MediumRough | 6.0443 | 0.33974 | 17.7909 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame Wall Insulation R-25.96 IP | StandardOpaqueMaterial | MediumRough | 8.8199 | 0.33974 | 25.9609 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Siding | StandardOpaqueMaterial | MediumSmooth | 0.3937 | 0.76268 | 0.51621 | 33.9995 | 0.289 | 0.9 | 0.78 | 0.78

## Lookups
These lookups are used to help users avoid input mistakes on other tabs. Please do not edit or delete existing entries or rename tables. You may add entries at the bottom of the list, but please avoid near-duplicates.
Intended Surface Type Lookup | Standards Construction Type Lookup | Building Type Lookup | Space Type Lookup | Lighting Standards Lookup | Ventilation Standards Lookup | Material Type Lookup
Name | Name | Name | Name | Name | Name | Name
AtticFloor | Mass | FullServiceRestaurant | Dining | ASHRAE 90.1-1999 | ASHRAE 62.1-1999 | StandardOpaqueMaterial
AtticWall | SteelFramed | Hospital | Kitchen | ASHRAE 90.1-2001 | ASHRAE 62.1-2004 | AirGap
AtticRoof | WoodFramed | LargeHotel | Corridor | ASHRAE 90.1-2004 | ASHRAE 62.1-2007 | StandardGlazing
DemisingFloor | IEAD | MidriseApartment | ER_Exam | ASHRAE 90.1-2007 | GGHC v2.2 | MasslessOpaqueMaterial
DemisingWall | View | Office | ER_NurseStn | ASHRAE 189.1-2009 | AIA 2001 | SimpleGlazing
DemisingRoof | Daylight | Outpatient | ER_Trauma | ASHRAE 90.1-2010 |  | Gas
ExteriorFloor | Swinging | PrimarySchool | ER_Triage
ExteriorWall | NonSwinging | QuickServiceRestaurant | ICU_NurseStn
ExteriorRoof | Heated | Retail | ICU_Open
ExteriorWindow | Unheated | SecondarySchool | ICU_PatRm
ExteriorDoor | RollUp | SmallHotel | Lab
GlassDoor | Sliding | StripMall | Lobby
GroundContactFloor | Metal | SuperMarket | NurseStn
GroundContactWall | Nonmetal framing (all) | Warehouse | Office
GroundContactRoof | Metal framing (curtainwall/storefront) | SmallOffice | OR
InteriorFloor | Metal framing (entrance door) |  | PatCorridor
InteriorWall | Metal framing (all other) |  | PatRoom
InteriorCeiling |  |  | PhysTherapy
InteriorPartition |  |  | Radiology
InteriorWindow |  |  | Banquet
InteriorDoor |  |  | Cafe
OverheadDoor |  |  | GuestRoom
Skylight |  |  | Laundry
TubularDaylightDome |  |  | Mechanical
TubularDaylightDiffuser |  |  | Retail
Storage
WholeBuilding
Apartment
BreakRoom
ClosedOffice
Conference
Elec/MechRoom
IT_Room
OpenOffice
PrintRoom
Restroom
Stair
Vending
WholeBuilding - Lg Office
WholeBuilding - Md Office
WholeBuilding - Sm Office
Anesthesia
BioHazard
CleanWork
DressingRoom
Exam
Hall
Janitor
LockerRoom
Lounge
MedGas
MRI
MRI_Control
NurseStation
PACU
PhysicalTherapy
PreOp
ProcedureRoom
Soil Work
Toilet
Xray
Cafeteria
Classroom
Gym
Library
Back_Space
Entry
Point_of_Sale
Auditorium
Exercise
GuestLounge
Meeting
PublicRestroom
StaffLounge
Deli/Bakery
DryStorage
Sales/Produce
Bulk
Fine
Attic
Plenum