## Notes
Heading | Note
General | All numbers were taken from DOE reference buildings; mapped back to original data source (standards, etc) where possible
Infiltration | Numbers from DOE reference buildings converted to cfm/ft^2 of exterior surface area
Colors | Color scheme based on redder for more public, bluer for more private; helps modelers be able to associate color with loads instead of random color assignment
Service Water Heating | Not currently put into space types; water-usage loads are not like equipment loads in E+
Thermostats | Not currently put into space types; limitation with OpenStudio (can only have 1 component in .osc)
Exhaust | Not currently put into space types; exhaust not like equipment/lighting loads in E+; HVAC needs setup on a per-zone basis
Occupancy | Occupancy from standards not used in space types b/c numbers were generally found to be unrealistically high by ref bldg creators; conservative for sizing OA but not for modeling realistic occupancy

## Templates
Templates combine standards and prototype data to create space types and construction sets, templates for each building type are exported to OSM format
Name
NREL_HighPerformance_2009
CBECS_1980-2004
CBECS_Before-1980
NREL_1980-2004
NREL_1999
NREL_2001
NREL_2004
NREL_2007
NREL_2009
NREL_Before-1980
Xcel EDA 2007

## Standards
Standards are actual standards documents issued by a standards organization
Name
AIA 2001
ASHRAE 169-2006
ASHRAE 189.1-2009
ASHRAE 62.1-1999
ASHRAE 62.1-2004
ASHRAE 62.1-2007
ASHRAE 90.1-1999
ASHRAE 90.1-2001
ASHRAE 90.1-2004
ASHRAE 90.1-2007
GGHC v2.2
CEC Title24-2005
CEC Title24-2008

## ClimateZones
A climate zone is a geographic area defined in a standards document
Name | Standard | Representative City | BCL Weather Component
ASHRAE 169-2006-1A | ASHRAE 169-2006
ASHRAE 169-2006-1B | ASHRAE 169-2006
ASHRAE 169-2006-2A | ASHRAE 169-2006
ASHRAE 169-2006-2B | ASHRAE 169-2006
ASHRAE 169-2006-3A | ASHRAE 169-2006
ASHRAE 169-2006-3B | ASHRAE 169-2006
ASHRAE 169-2006-3C | ASHRAE 169-2006
ASHRAE 169-2006-4A | ASHRAE 169-2006
ASHRAE 169-2006-4B | ASHRAE 169-2006
ASHRAE 169-2006-4C | ASHRAE 169-2006
ASHRAE 169-2006-5A | ASHRAE 169-2006
ASHRAE 169-2006-5B | ASHRAE 169-2006
ASHRAE 169-2006-5C | ASHRAE 169-2006
ASHRAE 169-2006-6A | ASHRAE 169-2006
ASHRAE 169-2006-6B | ASHRAE 169-2006
ASHRAE 169-2006-7A | ASHRAE 169-2006
ASHRAE 169-2006-7B | ASHRAE 169-2006
ASHRAE 169-2006-8A | ASHRAE 169-2006
ASHRAE 169-2006-8B | ASHRAE 169-2006
CEC 2005-1 | CEC Title24-2005
CEC 2005-2 | CEC Title24-2005
CEC 2005-3 | CEC Title24-2005
CEC 2005-4 | CEC Title24-2005
CEC 2005-5 | CEC Title24-2005
CEC 2005-6 | CEC Title24-2005
CEC 2005-7 | CEC Title24-2005
CEC 2005-8 | CEC Title24-2005
CEC 2005-9 | CEC Title24-2005
CEC 2005-10 | CEC Title24-2005
CEC 2008-1 | CEC Title24-2008
CEC 2008-2 | CEC Title24-2008
CEC 2008-3 | CEC Title24-2008
CEC 2008-4 | CEC Title24-2008
CEC 2008-5 | CEC Title24-2008
CEC 2008-6 | CEC Title24-2008
CEC 2008-7 | CEC Title24-2008
CEC 2008-8 | CEC Title24-2008
CEC 2008-9 | CEC Title24-2008
CEC 2008-10 | CEC Title24-2008

## ClimateZoneSets
A climate zone set is a group of climate zones
Name | Climate Zone | Climate Zone2 | Climate Zone3 | Climate Zone4 | Climate Zone5 | Climate Zone6 | Climate Zone7 | Climate Zone8 | Climate Zone9 | Climate Zone10 | Climate Zone11 | Climate Zone12 | Climate Zone13 | Climate Zone14 | Climate Zone15 | Climate Zone16 | Climate Zone17 | Climate Zone18 | Climate Zone19 | Climate Zone20 | Climate Zone21 | Climate Zone22 | Climate Zone23 | Climate Zone24 | Climate Zone25 | Climate Zone26 | Climate Zone27 | Climate Zone28 | Climate Zone29 | Climate Zone30 | Climate Zone31 | Climate Zone32 | Climate Zone33 | Climate Zone34 | Climate Zone35 | Climate Zone36 | Climate Zone37 | Climate Zone38 | Climate Zone39
All Climates | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B | CEC 2005-1 | CEC 2005-2 | CEC 2005-3 | CEC 2005-4 | CEC 2005-5 | CEC 2005-6 | CEC 2005-7 | CEC 2005-8 | CEC 2005-9 | CEC 2005-10 | CEC 2008-1 | CEC 2008-2 | CEC 2008-3 | CEC 2008-4 | CEC 2008-5 | CEC 2008-6 | CEC 2008-7 | CEC 2008-8 | CEC 2008-9 | CEC 2008-10
ClimateZone 1 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B
ClimateZone 1-2 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B
ClimateZone 1-3 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C
ClimateZone 1-3b | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B
ClimateZone 1-4 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C
ClimateZone 1-5 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C
ClimateZone 1-8 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B
ClimateZone 1-8 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 1a | ASHRAE 169-2006-1A
ClimateZone 1b | ASHRAE 169-2006-1B
ClimateZone 2 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B
ClimateZone 2-5 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C
ClimateZone 2-5 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C
ClimateZone 2a | ASHRAE 169-2006-2A
ClimateZone 2b | ASHRAE 169-2006-2B
ClimateZone 3 | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C
ClimateZone 3-4 | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C
ClimateZone 3a | ASHRAE 169-2006-3A
ClimateZone 3a-3b | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B
ClimateZone 3b | ASHRAE 169-2006-3B
ClimateZone 3c | ASHRAE 169-2006-3C
ClimateZone 4 | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C
ClimateZone 4-5 | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C
ClimateZone 4-6 | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B
ClimateZone 4-8 | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 4a | ASHRAE 169-2006-4A
ClimateZone 4b | ASHRAE 169-2006-4B
ClimateZone 4c | ASHRAE 169-2006-4C
ClimateZone 4c-5a | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A
ClimateZone 5 | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C
ClimateZone 5-6 | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B
ClimateZone 5-8 | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 5a | ASHRAE 169-2006-5A
ClimateZone 5b | ASHRAE 169-2006-5B
ClimateZone 5c | ASHRAE 169-2006-5C
ClimateZone 6 | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B
ClimateZone 6-8 | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 6a | ASHRAE 169-2006-6A
ClimateZone 6b | ASHRAE 169-2006-6B
ClimateZone 7 | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B
ClimateZone 7-8 | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 7a | ASHRAE 169-2006-7A
ClimateZone 7b | ASHRAE 169-2006-7B
ClimateZone 8 | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 8a | ASHRAE 169-2006-8A
ClimateZone 8b | ASHRAE 169-2006-8B

## SpaceTypes
|  | 0 | 1 | 2 | 3 | 4 | 11 | 12 | 13 | 14 | 17 | 18 | 19 | 20 | 21 |  |  |  | 25 | 26 | 27 | 28 | 29 | 34 | 35 | 36 | 41 | 43 | 44 | 46 | 47 | 48 |  |  |  | 50 | 51 |  |  |  | 53 | 54 | 55
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49
|  | COLUMN KEY |  |  |  | Color | Lighting | [12 empty] | Ventilation | [6 empty] | Occupancy |  |  | Infiltration |  | Gas Equipment |  |  |  |  | Electric Plug Loads |  |  |  |  | Thermostats - not currently part of a space type |  | Service Hot Water - not currently part of a space type | [6 empty] | Exhaust - Not currently part of a space type
Full Space Type Name | ImportOrder | Template | Climate Zone Set | BuildingType | SpaceType | R_G_B | Lighting Standard | Lighting Primary Space Type | Lighting Secondary Space Type | LookupColumn | Lighting (W/person) | OSM Lighting (W/ft) | STD Lighting (W/ft^2) | STD Lighting (W/person) | STD Lighting (W/ft) | Fraction to Return Air | Fraction Radiant | Fraction Visible | Lighting Sch | Ventilation Standard | Ventilation Primary Space Type | Ventilation Secondary Space Type | Lookup | STD Ventilation (ft^3/min*ft^2) | STD Ventilation (ft^3/min*person) | STD Ventilation (ach) | OSM Occupancy (people/1000 ft^2)2 | Occupancy Sch | Activity Sch | Infiltration (ft^3/min*ft^2 ext) | Infiltration Sch | OSM Gas Equipment (Btu/hr*ft^2) | Gas Equipment Fraction Latent | Gas Equipment Fraction Radiant | Gas Equipment Fraction Lost | Gas Equipment Sch | OSM Electric Equipment (W/ft^2) | Fraction Latent | Fraction Radiant2 | Fraction Lost | Electric Equipment Sch | Heating Setpoint Schedule | Cooling Setpoint Schedule | Peak Flow Rate (gal/h) | area (ft^2) | calculated (gal/h*ft^2) | Target Temperature Schedule (c) | Sensible Fraction Schedule (c) | Latent Fraction Schedule (c) | Flow Rate Fraction Schedule | 62.1-2004 Exhaust (cfm/ft2) | Total Exhaust (cfm) | Exhaust Fan total eff. | Exhaust Fan DP (in.w.g.) | Exhaust Fan Elec. Power (W) | Elec Power w/sf | Exhaust Sch
CBECS_1980-2004_FullServiceRestaurant_Dining | 20 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: FullServiceRestaurant; 3 3: Dining; 4 4: 31_169_34; 19 11: 2.54; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: FullServiceRestaurant_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Food and Beverage Service; 21 20: Dining Rooms; 21 21: ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 67; 21 26: FullServiceRestaurant_Bldg_Occ; 21 27: FullServiceRestaurant_Activity; 21 28: 0.2232; 21 29: FullServiceRestaurant_Infil_Half_On; 21 35: 5.6; 21 36: 0.25; 21 37: 0.3; 21 38: 0; 21 39: FullServiceRestaurant_Bldg_Equip; 21 40: FullServiceRestaurant_HtgSetp; 21 41: FullServiceRestaurant_ClgSetp
CBECS_1980-2004_FullServiceRestaurant_Kitchen | 242 | NREL_1980-2004 | ClimateZone 1-8 | FullServiceRestaurant | Kitchen | 78_222_133 | [6 empty] | 1.52 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | FullServiceRestaurant_Bldg_Occ | FullServiceRestaurant_Activity | 0.2232 | FullServiceRestaurant_Infil_Half_On | 378.75 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant_Gas_Equip | 35 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant_Bldg_Equip | FullServiceRestaurant_HtgSetp_Kitchen | FullServiceRestaurant_ClgSetp_Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant_SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant_Kitchen_Exhaust
ASHRAE_90.1-2004_FullServiceRestaurant_Dining | 418 | NREL_2004 | ClimateZone 1-8 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | For Family Dining | ASHRAE 90.1-2004Dining AreaFor Family Dining |  |  | 2.1 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 67 | FullServiceRestaurant_Bldg_Occ | FullServiceRestaurant_Activity | 0.0595 | FullServiceRestaurant_Infil_Half_On | [5 empty] | 5.6 | 0.25 | 0.3 | 0 | FullServiceRestaurant_Bldg_Equip | FullServiceRestaurant_HtgSetp | FullServiceRestaurant_ClgSetp
ASHRAE_90.1-2004_FullServiceRestaurant_Kitchen | 12 | NREL_2004 | ClimateZone 1-8 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | FullServiceRestaurant_Bldg_Occ | FullServiceRestaurant_Activity | 0.0595 | FullServiceRestaurant_Infil_Half_On | 378.75 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant_Gas_Equip | 35 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant_Bldg_Equip | FullServiceRestaurant_HtgSetp_Kitchen | FullServiceRestaurant_ClgSetp_Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant_SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant_Kitchen_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_FullServiceRestaurant_Dining | 122 | NREL_2009 | ClimateZone 1-3 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Family Dining | ASHRAE 189.1-2009Dining AreaFor Family Dining |  |  | 1.89 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 67 | FullServiceRestaurant_Bldg_Occ | FullServiceRestaurant_Activity | 0.0595 | FullServiceRestaurant_Infil_Half_On | [5 empty] | 4.08 | 0.25 | 0.3 | 0 | FullServiceRestaurant_Bldg_Equip | FullServiceRestaurant_HtgSetp | FullServiceRestaurant_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_FullServiceRestaurant_Dining | 554 | NREL_2009 | ClimateZone 4-8 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Family Dining | ASHRAE 189.1-2009Dining AreaFor Family Dining |  |  | 1.89 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 67 | FullServiceRestaurant_Bldg_Occ | FullServiceRestaurant_Activity | 0.0446 | FullServiceRestaurant_Infil_Half_On | [5 empty] | 4.08 | 0.25 | 0.3 | 0 | FullServiceRestaurant_Bldg_Equip | FullServiceRestaurant_HtgSetp | FullServiceRestaurant_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_FullServiceRestaurant_Kitchen | 44 | NREL_2009 | ClimateZone 1-3 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | FullServiceRestaurant_Bldg_Occ | FullServiceRestaurant_Activity | 0.0595 | FullServiceRestaurant_Infil_Half_On | 276.72 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant_Gas_Equip | 25.5 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant_Bldg_Equip | FullServiceRestaurant_HtgSetp_Kitchen | FullServiceRestaurant_ClgSetp_Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant_SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant_Kitchen_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_FullServiceRestaurant_Kitchen | 448 | NREL_2009 | ClimateZone 4-8 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | FullServiceRestaurant_Bldg_Occ | FullServiceRestaurant_Activity | 0.0446 | FullServiceRestaurant_Infil_Half_On | 276.72 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant_Gas_Equip | 25.5 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant_Bldg_Equip | FullServiceRestaurant_HtgSetp_Kitchen | FullServiceRestaurant_ClgSetp_Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant_SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant_Kitchen_Exhaust
CBECS_Before-1980_FullServiceRestaurant_Dining | 107 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: FullServiceRestaurant; 3 3: Dining; 4 4: 31_169_34; 19 11: 2.77; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: FullServiceRestaurant_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Food and Beverage Service; 21 20: Dining Rooms; 21 21: ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 67; 21 26: FullServiceRestaurant_Bldg_Occ; 21 27: FullServiceRestaurant_Activity; 21 28: 0.2232; 21 29: FullServiceRestaurant_Infil_Half_On; 21 35: 5.6; 21 36: 0.25; 21 37: 0.3; 21 38: 0; 21 39: FullServiceRestaurant_Bldg_Equip; 21 40: FullServiceRestaurant_HtgSetp; 21 41: FullServiceRestaurant_ClgSetp
CBECS_Before-1980_FullServiceRestaurant_Kitchen | 128 | NREL_Before-1980 | ClimateZone 1-8 | FullServiceRestaurant | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | FullServiceRestaurant_Bldg_Occ | FullServiceRestaurant_Activity | 0.2232 | FullServiceRestaurant_Infil_Half_On | 378.75 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant_Gas_Equip | 35 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant_Bldg_Equip | FullServiceRestaurant_HtgSetp_Kitchen | FullServiceRestaurant_ClgSetp_Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant_SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant_Kitchen_Exhaust
|  | Xcel EDA 2007 | ClimateZone 1-8 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | For Family Dining | ASHRAE 90.1-2007Dining AreaFor Family Dining |  |  | 2.1 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant_Bldg_Light | ASHRAE 62.1-2007 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-2007Food and Beverage ServiceDining Rooms | #N/A | #N/A | #N/A | 67 | FullServiceRestaurant_Bldg_Occ | FullServiceRestaurant_Activity | 0.0446 | FullServiceRestaurant_Infil_Half_On | [5 empty] | 4.08 | 0.25 | 0.3 | 0 | FullServiceRestaurant_Bldg_Equip | FullServiceRestaurant_HtgSetp | FullServiceRestaurant_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant_Bldg_Light | ASHRAE 62.1-2007 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-2007Food and Beverage ServiceKitchens (cooking) | #N/A | #N/A | #N/A | 5 | FullServiceRestaurant_Bldg_Occ | FullServiceRestaurant_Activity | 0.0446 | FullServiceRestaurant_Infil_Half_On | 276.72 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant_Gas_Equip | 25.5 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant_Bldg_Equip | FullServiceRestaurant_HtgSetp_Kitchen | FullServiceRestaurant_ClgSetp_Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant_SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant_Kitchen_Exhaust
CBECS_1980-2004_Hospital_Corridor | 49 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: Corridor; 4 4: 169_31_31; 19 11: 1.36; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 1; 21 26: Hospital_Critical_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Bldg_HtgSetp; 21 41: Hospital_Bldg_ClgSetp
CBECS_1980-2004_Hospital_Dining | 538 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: Dining; 4 4: 31_169_34; 19 11: 2.58; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Food and Beverage Service; 21 20: Dining Rooms; 21 21: ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 10; 21 26: Hospital_Critical_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Bldg_HtgSetp; 21 41: Hospital_Bldg_ClgSetp
CBECS_1980-2004_Hospital_ER_Exam | 50 | NREL_1980-2004 | ClimateZone 1-8 | Hospital | ER_Exam | 169_31_159 | [6 empty] | 3.84 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
CBECS_1980-2004_Hospital_ER_NurseStn | 450 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: ER_NurseStn; 4 4: 31_162_169; 19 11: 1.66; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: AIA 2001; 21 19: Surgery and Critical Care; 21 20: ER Waiting Room; 21 21: AIA 2001Surgery and Critical CareER Waiting Room; 21 22: 0; 21 23: 0; 21 24: 2; 21 25: 6.25; 21 26: Hospital_Critical_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 1.36; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Critical_HtgSetp; 21 41: Hospital_Critical_HtgSetp
CBECS_1980-2004_Hospital_ER_Trama | 34 | NREL_1980-2004 | ClimateZone 1-8 | Hospital | ER_Trama | 169_31_159 | [6 empty] | 3.84 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
CBECS_1980-2004_Hospital_ER_Triage | 293 | NREL_1980-2004 | ClimateZone 1-8 | Hospital | ER_Triage | 169_31_159 | [6 empty] | 3.84 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
CBECS_1980-2004_Hospital_ICU_NurseStn | 248 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: ICU_NurseStn; 4 4: 31_162_169; 19 11: 1.71; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: AIA 2001; 21 19: Surgery and Critical Care; 21 20: Critical and Intensive Care; 21 21: AIA 2001Surgery and Critical CareCritical and Intensive Care; 21 22: 0; 21 23: 0; 21 24: 2; 21 25: 5; 21 26: Hospital_Critical_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 2; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Critical_HtgSetp; 21 41: Hospital_Critical_HtgSetp
CBECS_1980-2004_Hospital_ICU_Open | 415 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: ICU_Open; 4 4: 78_167_222; 19 11: 3.84; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: AIA 2001; 21 19: Surgery and Critical Care; 21 20: Critical and Intensive Care; 21 21: AIA 2001Surgery and Critical CareCritical and Intensive Care; 21 22: 0; 21 23: 0; 21 24: 2; 21 25: 20; 21 26: Hospital_Critical_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 3; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Critical_HtgSetp; 21 41: Hospital_Critical_HtgSetp
CBECS_1980-2004_Hospital_ICU_PatRm | 52 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: ICU_PatRm; 4 4: 78_167_222; 19 11: 3.84; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: AIA 2001; 21 19: Surgery and Critical Care; 21 20: Critical and Intensive Care; 21 21: AIA 2001Surgery and Critical CareCritical and Intensive Care; 21 22: 0; 21 23: 0; 21 24: 2; 21 25: 5; 21 26: Hospital_Critical_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 3; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Critical_HtgSetp; 21 41: Hospital_Critical_HtgSetp
CBECS_1980-2004_Hospital_Kitchen | 373 | NREL_1980-2004 | ClimateZone 1-8 | Hospital | Kitchen | 78_222_133 | [6 empty] | 1.42 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | 96.7 | 0.1 | 0.2 | 0.7 | Hospital_Kitchen_Gas | 7.5 | 0.2 | 0.5 | 0.1 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital_Kitchen_Exhaust
CBECS_1980-2004_Hospital_Lab | 154 | NREL_1980-2004 | ClimateZone 1-8 | Hospital | Lab | 204_120_230 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital_SWH
CBECS_1980-2004_Hospital_Lobby/Records | 33 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: Lobby; 4 4: 31_162_169; 19 11: 1.46; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Lobbies; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 7.14; 21 26: Hospital_Bldg_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 0.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Bldg_HtgSetp; 21 41: Hospital_Bldg_ClgSetp
CBECS_1980-2004_Hospital_NurseStn | 258 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: NurseStn; 4 4: 31_162_169; 19 11: 1.46; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Reception Areas; 21 21: ASHRAE 62.1-1999OfficesReception Areas; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 7.14; 21 26: Hospital_Bldg_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 1.04; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Bldg_HtgSetp; 21 41: Hospital_Bldg_ClgSetp
CBECS_1980-2004_Hospital_Office | 108 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: Office; 4 4: 120_230_199; 19 11: 2.4; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 6.99; 21 26: Hospital_Bldg_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Bldg_HtgSetp; 21 41: Hospital_Bldg_ClgSetp
CBECS_1980-2004_Hospital_OR | 265 | NREL_1980-2004 | ClimateZone 1-8 | Hospital | OR | 169_31_159 | [6 empty] | 9.75 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 5 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH
CBECS_1980-2004_Hospital_PatCorridor | 324 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: PatCorridor; 4 4: 169_31_31; 19 11: 1.36; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 1; 21 26: Hospital_Critical_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Critical_HtgSetp; 21 41: Hospital_Critical_ClgSetp
CBECS_1980-2004_Hospital_PatRoom | 286 | NREL_1980-2004 | ClimateZone 1-8 | Hospital | PatRoom | 78_167_222 | [6 empty] | 2.19 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
CBECS_1980-2004_Hospital_PhysTherapy | 137 | NREL_1980-2004 | ClimateZone 1-8 | Hospital | PhysTherapy | 154_230_120 | [6 empty] | 2.5 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital_SWH
CBECS_1980-2004_Hospital_Radiology | 452 | NREL_1980-2004 | ClimateZone 1-8 | Hospital | Radiology | 136_78_222 | [6 empty] | 2.21 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 10 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
ASHRAE_90.1-2004_Hospital_Corridor | 470 | NREL_2004 | ClimateZone 1-8 | Hospital | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | ASHRAE 90.1-2004Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
ASHRAE_90.1-2004_Hospital_Dining | 51 | NREL_2004 | ClimateZone 1-8 | Hospital | Dining | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 10 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
ASHRAE_90.1-2004_Hospital_ER_Exam | 204 | NREL_2004 | ClimateZone 1-8 | Hospital | ER_Exam | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
ASHRAE_90.1-2004_Hospital_ER_NurseStn | 30 | NREL_2004 | ClimateZone 1-8 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 1.36 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
ASHRAE_90.1-2004_Hospital_ER_Trama | 177 | NREL_2004 | ClimateZone 1-8 | Hospital | ER_Trama | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
ASHRAE_90.1-2004_Hospital_ER_Triage | 90 | NREL_2004 | ClimateZone 1-8 | Hospital | ER_Triage | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
ASHRAE_90.1-2004_Hospital_ICU_NurseStn | 102 | NREL_2004 | ClimateZone 1-8 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
ASHRAE_90.1-2004_Hospital_ICU_Open | 409 | NREL_2004 | ClimateZone 1-8 | Hospital | ICU_Open | 78_167_222 | ASHRAE 90.1-2004 | Hospital | Recovery | ASHRAE 90.1-2004HospitalRecovery |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
ASHRAE_90.1-2004_Hospital_ICU_PatRm | 386 | NREL_2004 | ClimateZone 1-8 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 90.1-2004 | Hospital | Patient Room | ASHRAE 90.1-2004HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
ASHRAE_90.1-2004_Hospital_Kitchen | 423 | NREL_2004 | ClimateZone 1-8 | Hospital | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | 96.7 | 0.1 | 0.2 | 0.7 | Hospital_Kitchen_Gas | 7.5 | 0.2 | 0.5 | 0.1 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital_Kitchen_Exhaust
ASHRAE_90.1-2004_Hospital_Lab | 475 | NREL_2004 | ClimateZone 1-8 | Hospital | Lab | 204_120_230 | ASHRAE 90.1-2004 | Laboratory | General | ASHRAE 90.1-2004LaboratoryGeneral |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital_SWH
ASHRAE_90.1-2004_Hospital_Lobby/Records | 228 | NREL_2004 | ClimateZone 1-8 | Hospital | Lobby | 31_162_169 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 7.14 | Hospital_Bldg_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 0.1 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
ASHRAE_90.1-2004_Hospital_NurseStn | 367 | NREL_2004 | ClimateZone 1-8 | Hospital | NurseStn | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 7.14 | Hospital_Bldg_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 1.04 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
ASHRAE_90.1-2004_Hospital_Office | 239 | NREL_2004 | ClimateZone 1-8 | Hospital | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 6.99 | Hospital_Bldg_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
ASHRAE_90.1-2004_Hospital_OR | 97 | NREL_2004 | ClimateZone 1-8 | Hospital | OR | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Operating Room | ASHRAE 90.1-2004HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 5 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH
ASHRAE_90.1-2004_Hospital_PatCorridor | 512 | NREL_2004 | ClimateZone 1-8 | Hospital | PatCorridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | ASHRAE 90.1-2004Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp
ASHRAE_90.1-2004_Hospital_PatRoom | 134 | NREL_2004 | ClimateZone 1-8 | Hospital | PatRoom | 78_167_222 | ASHRAE 90.1-2004 | Hospital | Patient Room | ASHRAE 90.1-2004HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
ASHRAE_90.1-2004_Hospital_PhysTherapy | 306 | NREL_2004 | ClimateZone 1-8 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 90.1-2004 | Hospital | Physical Therapy | ASHRAE 90.1-2004HospitalPhysical Therapy |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital_SWH
ASHRAE_90.1-2004_Hospital_Radiology | 57 | NREL_2004 | ClimateZone 1-8 | Hospital | Radiology | 136_78_222 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 10 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_Corridor | 37 | NREL_2009 | ClimateZone 1-3 | Hospital | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_Corridor | 296 | NREL_2009 | ClimateZone 4-8 | Hospital | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_Dining | 376 | NREL_2009 | ClimateZone 1-3 | Hospital | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 10 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_Dining | 558 | NREL_2009 | ClimateZone 4-8 | Hospital | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 10 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_ER_Exam | 56 | NREL_2009 | ClimateZone 1-3 | Hospital | ER_Exam | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_ER_Exam | 121 | NREL_2009 | ClimateZone 4-8 | Hospital | ER_Exam | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_ER_NurseStn | 150 | NREL_2009 | ClimateZone 1-3 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 0.99 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_ER_NurseStn | 166 | NREL_2009 | ClimateZone 4-8 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 0.99 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_ER_Trama | 330 | NREL_2009 | ClimateZone 1-3 | Hospital | ER_Trama | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_ER_Trama | 213 | NREL_2009 | ClimateZone 4-8 | Hospital | ER_Trama | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_ER_Triage | 530 | NREL_2009 | ClimateZone 1-3 | Hospital | ER_Triage | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 1.97 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_ER_Triage | 74 | NREL_2009 | ClimateZone 4-8 | Hospital | ER_Triage | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 1.97 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_ICU_NurseStn | 560 | NREL_2009 | ClimateZone 1-3 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_ICU_NurseStn | 110 | NREL_2009 | ClimateZone 4-8 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_ICU_Open | 27 | NREL_2009 | ClimateZone 1-3 | Hospital | ICU_Open | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Recovery | ASHRAE 189.1-2009HospitalRecovery |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_ICU_Open | 210 | NREL_2009 | ClimateZone 4-8 | Hospital | ICU_Open | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Recovery | ASHRAE 189.1-2009HospitalRecovery |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_ICU_PatRm | 476 | NREL_2009 | ClimateZone 1-3 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_ICU_PatRm | 433 | NREL_2009 | ClimateZone 4-8 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_Kitchen | 162 | NREL_2009 | ClimateZone 1-3 | Hospital | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | 70.46 | 0.1 | 0.2 | 0.7 | Hospital_Kitchen_Gas | 5.47 | 0.2 | 0.5 | 0.1 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital_Kitchen_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_Kitchen | 451 | NREL_2009 | ClimateZone 4-8 | Hospital | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | 70.46 | 0.1 | 0.2 | 0.7 | Hospital_Kitchen_Gas | 5.47 | 0.2 | 0.5 | 0.1 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital_Kitchen_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_Lab | 85 | NREL_2009 | ClimateZone 1-3 | Hospital | Lab | 204_120_230 | ASHRAE 189.1-2009 | Laboratory | General | ASHRAE 189.1-2009LaboratoryGeneral |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 3.22 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital_SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_Lab | 22 | NREL_2009 | ClimateZone 4-8 | Hospital | Lab | 204_120_230 | ASHRAE 189.1-2009 | Laboratory | General | ASHRAE 189.1-2009LaboratoryGeneral |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 3.22 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital_SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_Lobby/Records | 365 | NREL_2009 | ClimateZone 1-3 | Hospital | Lobby | 31_162_169 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 7.14 | Hospital_Bldg_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_Lobby/Records | 486 | NREL_2009 | ClimateZone 4-8 | Hospital | Lobby | 31_162_169 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 7.14 | Hospital_Bldg_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_NurseStn | 244 | NREL_2009 | ClimateZone 1-3 | Hospital | NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 7.14 | Hospital_Bldg_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 0.76 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_NurseStn | 109 | NREL_2009 | ClimateZone 4-8 | Hospital | NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 7.14 | Hospital_Bldg_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 0.76 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_Office | 48 | NREL_2009 | ClimateZone 1-3 | Hospital | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 6.99 | Hospital_Bldg_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_Office | 318 | NREL_2009 | ClimateZone 4-8 | Hospital | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 6.99 | Hospital_Bldg_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_OR | 327 | NREL_2009 | ClimateZone 1-3 | Hospital | OR | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_OR | 26 | NREL_2009 | ClimateZone 4-8 | Hospital | OR | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_PatCorridor | 73 | NREL_2009 | ClimateZone 1-3 | Hospital | PatCorridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_PatCorridor | 397 | NREL_2009 | ClimateZone 4-8 | Hospital | PatCorridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_PatRoom | 246 | NREL_2009 | ClimateZone 1-3 | Hospital | PatRoom | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_PatRoom | 103 | NREL_2009 | ClimateZone 4-8 | Hospital | PatRoom | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_PhysTherapy | 66 | NREL_2009 | ClimateZone 1-3 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 189.1-2009 | Hospital | Physical Therapy | ASHRAE 189.1-2009HospitalPhysical Therapy |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital_SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_PhysTherapy | 38 | NREL_2009 | ClimateZone 4-8 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 189.1-2009 | Hospital | Physical Therapy | ASHRAE 189.1-2009HospitalPhysical Therapy |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital_SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Hospital_Radiology | 299 | NREL_2009 | ClimateZone 1-3 | Hospital | Radiology | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0595 | Hospital_Infil_Quarter_On | [5 empty] | 7.28 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
ASHRAE_189.1-2009_ClimateZone 4-8_Hospital_Radiology | 5 | NREL_2009 | ClimateZone 4-8 | Hospital | Radiology | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 7.28 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
CBECS_Before-1980_Hospital_Corridor | 96 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: Corridor; 4 4: 169_31_31; 19 11: 1.32; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 1; 21 26: Hospital_Critical_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Bldg_HtgSetp; 21 41: Hospital_Bldg_ClgSetp
CBECS_Before-1980_Hospital_Dining | 400 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: Dining; 4 4: 31_169_34; 19 11: 2.77; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Food and Beverage Service; 21 20: Dining Rooms; 21 21: ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 10; 21 26: Hospital_Critical_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Bldg_HtgSetp; 21 41: Hospital_Bldg_ClgSetp
CBECS_Before-1980_Hospital_ER_Exam | 508 | NREL_Before-1980 | ClimateZone 1-8 | Hospital | ER_Exam | 169_31_159 | [6 empty] | 5 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
CBECS_Before-1980_Hospital_ER_NurseStn | 527 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: ER_NurseStn; 4 4: 31_162_169; 19 11: 1.64; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: AIA 2001; 21 19: Surgery and Critical Care; 21 20: ER Waiting Room; 21 21: AIA 2001Surgery and Critical CareER Waiting Room; 21 22: 0; 21 23: 0; 21 24: 2; 21 25: 6.25; 21 26: Hospital_Critical_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 1.36; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Critical_HtgSetp; 21 41: Hospital_Critical_HtgSetp
CBECS_Before-1980_Hospital_ER_Trama | 243 | NREL_Before-1980 | ClimateZone 1-8 | Hospital | ER_Trama | 169_31_159 | [6 empty] | 5 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
CBECS_Before-1980_Hospital_ER_Triage | 237 | NREL_Before-1980 | ClimateZone 1-8 | Hospital | ER_Triage | 169_31_159 | [6 empty] | 5 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
CBECS_Before-1980_Hospital_ICU_NurseStn | 143 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: ICU_NurseStn; 4 4: 31_162_169; 19 11: 1.64; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: AIA 2001; 21 19: Surgery and Critical Care; 21 20: Critical and Intensive Care; 21 21: AIA 2001Surgery and Critical CareCritical and Intensive Care; 21 22: 0; 21 23: 0; 21 24: 2; 21 25: 5; 21 26: Hospital_Critical_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 2; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Critical_HtgSetp; 21 41: Hospital_Critical_HtgSetp
CBECS_Before-1980_Hospital_ICU_Open | 407 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: ICU_Open; 4 4: 78_167_222; 19 11: 4.22; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: AIA 2001; 21 19: Surgery and Critical Care; 21 20: Critical and Intensive Care; 21 21: AIA 2001Surgery and Critical CareCritical and Intensive Care; 21 22: 0; 21 23: 0; 21 24: 2; 21 25: 20; 21 26: Hospital_Critical_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 3; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Critical_HtgSetp; 21 41: Hospital_Critical_HtgSetp
CBECS_Before-1980_Hospital_ICU_PatRm | 76 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: ICU_PatRm; 4 4: 78_167_222; 19 11: 4.22; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: AIA 2001; 21 19: Surgery and Critical Care; 21 20: Critical and Intensive Care; 21 21: AIA 2001Surgery and Critical CareCritical and Intensive Care; 21 22: 0; 21 23: 0; 21 24: 2; 21 25: 5; 21 26: Hospital_Critical_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 3; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Critical_HtgSetp; 21 41: Hospital_Critical_HtgSetp
CBECS_Before-1980_Hospital_Kitchen | 126 | NREL_Before-1980 | ClimateZone 1-8 | Hospital | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | 96.7 | 0.1 | 0.2 | 0.7 | Hospital_Kitchen_Gas | 7.5 | 0.2 | 0.5 | 0.1 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital_Kitchen_Exhaust
CBECS_Before-1980_Hospital_Lab | 482 | NREL_Before-1980 | ClimateZone 1-8 | Hospital | Lab | 204_120_230 | [6 empty] | 1.9 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital_SWH
CBECS_Before-1980_Hospital_Lobby/Records | 323 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: Lobby; 4 4: 31_162_169; 19 11: 1.49; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Lobbies; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 7.14; 21 26: Hospital_Bldg_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 0.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Bldg_HtgSetp; 21 41: Hospital_Bldg_ClgSetp
CBECS_Before-1980_Hospital_NurseStn | 183 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: NurseStn; 4 4: 31_162_169; 19 11: 1.53; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Reception Areas; 21 21: ASHRAE 62.1-1999OfficesReception Areas; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 7.14; 21 26: Hospital_Bldg_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 1.04; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Bldg_HtgSetp; 21 41: Hospital_Bldg_ClgSetp
CBECS_Before-1980_Hospital_Office | 152 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: Office; 4 4: 120_230_199; 19 11: 1.9; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 6.99; 21 26: Hospital_Bldg_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Bldg_HtgSetp; 21 41: Hospital_Bldg_ClgSetp
CBECS_Before-1980_Hospital_OR | 493 | NREL_Before-1980 | ClimateZone 1-8 | Hospital | OR | 169_31_159 | [6 empty] | 10 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 5 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH
CBECS_Before-1980_Hospital_PatCorridor | 529 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Hospital; 3 3: PatCorridor; 4 4: 169_31_31; 19 11: 1.32; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Hospital_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 1; 21 26: Hospital_Critical_Occ; 21 27: Hospital_Activity; 21 28: 0.2232; 21 29: Hospital_Infil_Quarter_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Hospital_Bldg_Equip; 21 40: Hospital_Critical_HtgSetp; 21 41: Hospital_Critical_ClgSetp
CBECS_Before-1980_Hospital_PatRoom | 380 | NREL_Before-1980 | ClimateZone 1-8 | Hospital | PatRoom | 78_167_222 | [6 empty] | 1.85 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
CBECS_Before-1980_Hospital_PhysTherapy | 163 | NREL_Before-1980 | ClimateZone 1-8 | Hospital | PhysTherapy | 154_230_120 | [6 empty] | 2.51 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital_SWH
CBECS_Before-1980_Hospital_Radiology | 260 | NREL_Before-1980 | ClimateZone 1-8 | Hospital | Radiology | 136_78_222 | [6 empty] | 3.3 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.2232 | Hospital_Infil_Quarter_On | [5 empty] | 10 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | ASHRAE 90.1-2007Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 1 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | Dining | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-2007 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-2007Food and Beverage ServiceDining Rooms | #N/A | #N/A | #N/A | 10 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | ER_Exam | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 0.99 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | ER_Trama | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | ER_Triage | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 1.97 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | ICU_Open | 78_167_222 | ASHRAE 90.1-2007 | Hospital | Recovery | ASHRAE 90.1-2007HospitalRecovery |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 90.1-2007 | Hospital | Patient Room | ASHRAE 90.1-2007HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_HtgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-2007 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-2007Food and Beverage ServiceKitchens (cooking) | #N/A | #N/A | #N/A | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | 70.46 | 0.1 | 0.2 | 0.7 | Hospital_Kitchen_Gas | 5.47 | 0.2 | 0.5 | 0.1 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital_Kitchen_Exhaust
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | Lab | 204_120_230 | ASHRAE 90.1-2007 | Laboratory | General | ASHRAE 90.1-2007LaboratoryGeneral |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-2007 | Education | Laboratories | ASHRAE 62.1-2007EducationLaboratories | #N/A | #N/A | #N/A | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 3.22 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital_SWH
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | Lobby | 31_162_169 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies | #N/A | #N/A | #N/A | 7.14 | Hospital_Bldg_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | NurseStn | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-2007 | Offices | Reception Areas | ASHRAE 62.1-2007OfficesReception Areas | #N/A | #N/A | #N/A | 7.14 | Hospital_Bldg_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 0.76 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-2007 | Offices | Office Space | ASHRAE 62.1-2007OfficesOffice Space | #N/A | #N/A | #N/A | 6.99 | Hospital_Bldg_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | OR | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Operating Room | ASHRAE 90.1-2007HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital_SWH
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | PatCorridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | ASHRAE 90.1-2007Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 1 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | PatRoom | 78_167_222 | ASHRAE 90.1-2007 | Hospital | Patient Room | ASHRAE 90.1-2007HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital_Critical_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Critical_HtgSetp | Hospital_Critical_ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 90.1-2007 | Hospital | Physical Therapy | ASHRAE 90.1-2007HospitalPhysical Therapy |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital_SWH
|  | Xcel EDA 2007 | ClimateZone 1-8 | Hospital | Radiology | 136_78_222 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Hospital_Bldg_Light | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital_Bldg_Occ | Hospital_Activity | 0.0446 | Hospital_Infil_Quarter_On | [5 empty] | 7.28 | 0 | 0.5 | 0 | Hospital_Bldg_Equip | Hospital_Bldg_HtgSetp | Hospital_Bldg_ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital_SWH_Extd
CBECS_1980-2004_LargeHotel_Banquet | 501 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: LargeHotel; 3 3: Banquet; 4 4: 230_196_120; 19 11: 2.56; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: LargeHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Conference rooms; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 67; 21 26: LargeHotel_Bldg_Occ; 21 27: LargeHotel_Activity; 21 28: 0.2232; 21 29: LargeHotel_Infil_Quarter_On; 21 35: 6.3; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: LargeHotel_Bldg_Equip; 21 40: LargeHotel_HtgSetp; 21 41: LargeHotel_ClgSetp
CBECS_1980-2004_LargeHotel_Cafe | 389 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: LargeHotel; 3 3: Cafe; 4 4: 31_169_34; 19 11: 1.46; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: LargeHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Food and Beverage Service; 21 20: Cafeteria, fast food; 21 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 67; 21 26: LargeHotel_Bldg_Occ; 21 27: LargeHotel_Activity; 21 28: 0.2232; 21 29: LargeHotel_Infil_Quarter_On; 21 35: 0.5; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: LargeHotel_Bldg_Equip; 21 40: LargeHotel_HtgSetp; 21 41: LargeHotel_ClgSetp
CBECS_1980-2004_LargeHotel_Corridor | 222 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: LargeHotel; 3 3: Corridor; 4 4: 169_31_31; 19 11: 1.22; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: LargeHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 1; 21 26: LargeHotel_Bldg_Occ; 21 27: LargeHotel_Activity; 21 28: 0.2232; 21 29: LargeHotel_Infil_Quarter_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: LargeHotel_Bldg_Equip; 21 40: LargeHotel_HtgSetp_Corridor; 21 41: LargeHotel_ClgSetp_Corridor
CBECS_1980-2004_LargeHotel_GuestRoom | 417 | NREL_1980-2004 | ClimateZone 1-8 | LargeHotel | GuestRoom | 78_167_222 | [6 empty] | 1.77 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 3.57 | LargeHotel_GuestRoom_Occ | LargeHotel_Activity | 0.2232 | LargeHotel_Infil_Quarter_On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel_GuestRoom_Equip | LargeHotel_HtgSetp_GuestRoom | LargeHotel_ClgSetp_GuestRoom | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel_SWH_GuestRoom
CBECS_1980-2004_LargeHotel_Kitchen | 218 | NREL_1980-2004 | ClimateZone 1-8 | LargeHotel | Kitchen | 78_222_133 | [6 empty] | 1.56 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.2232 | LargeHotel_Infil_Quarter_On | 511 | 0.1 | 0.2 | 0.7 | LargeHotel_Kitchen_Gas | 47.22 | 0.2 | 0.5 | 0.1 | LargeHotel_Kitchen_Equip | LargeHotel_HtgSetp_Kitchen | LargeHotel_ClgSetp_Kitchen | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel_SWH_Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel_Kitchen_Exhaust
CBECS_1980-2004_LargeHotel_Laundry | 67 | NREL_1980-2004 | ClimateZone 1-8 | LargeHotel | Laundry | 120_149_230 | [6 empty] | 1.14 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 4 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.2232 | LargeHotel_Infil_Quarter_On | 170 | 0 | 0.5 | 0 | LargeHotel_LaundryRoom_Gas | 5.73 | 0 | 0.5 | 0 | LargeHotel_LaundryRoom_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel_SWH_Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel_Laundry_Exhaust_ALWAYS_ON
CBECS_1980-2004_LargeHotel_Lobby | 313 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: LargeHotel; 3 3: Lobby; 4 4: 230_157_120; 19 11: 1.88; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: LargeHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Lobbies; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 30; 21 26: LargeHotel_Bldg_Occ; 21 27: LargeHotel_Activity; 21 28: 0.2232; 21 29: LargeHotel_Infil_Quarter_On; 21 35: 0.75; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: LargeHotel_Bldg_Equip; 21 40: LargeHotel_HtgSetp; 21 41: LargeHotel_ClgSetp
CBECS_1980-2004_LargeHotel_Mechanical | 224 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: LargeHotel; 3 3: Mechanical; 4 4: 41_31_169; 19 11: 0.8; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: LargeHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: LargeHotel_Bldg_Occ; 21 27: LargeHotel_Activity; 21 28: 0.2232; 21 29: LargeHotel_Infil_Quarter_On; 21 35: 0.5; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: LargeHotel_Bldg_Equip; 21 40: LargeHotel_HtgSetp; 21 41: LargeHotel_ClgSetp
CBECS_1980-2004_LargeHotel_Retail | 219 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: LargeHotel; 3 3: Retail; 4 4: 171_222_78; 19 11: 3.54; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: LargeHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Basement and street; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; 21 22: 0.3; 21 23: 0; 21 24: 0; 21 25: 15; 21 26: LargeHotel_Bldg_Occ; 21 27: LargeHotel_Activity; 21 28: 0.2232; 21 29: LargeHotel_Infil_Quarter_On; 21 35: 1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: LargeHotel_Bldg_Equip; 21 40: LargeHotel_HtgSetp; 21 41: LargeHotel_ClgSetp
CBECS_1980-2004_LargeHotel_Storage | 83 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: LargeHotel; 3 3: Storage; 4 4: 120_149_230; 19 11: 0.37; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: LargeHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Shipping and receiving; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 2; 21 26: LargeHotel_Bldg_Occ; 21 27: LargeHotel_Activity; 21 28: 0.2232; 21 29: LargeHotel_Infil_Quarter_On; 21 35: 0.25; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: LargeHotel_Bldg_Equip; 21 40: LargeHotel_HtgSetp; 21 41: LargeHotel_ClgSetp
ASHRAE_90.1-2004_LargeHotel_Banquet | 369 | NREL_2004 | ClimateZone 1-8 | LargeHotel | Banquet | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 67 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 6.3 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_90.1-2004_LargeHotel_Cafe | 62 | NREL_2004 | ClimateZone 1-8 | LargeHotel | Cafe | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | For Hotel | ASHRAE 90.1-2004Dining AreaFor Hotel |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 67 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.5 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_90.1-2004_LargeHotel_Corridor | 440 | NREL_2004 | ClimateZone 1-8 | LargeHotel | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp_Corridor | LargeHotel_ClgSetp_Corridor
ASHRAE_90.1-2004_LargeHotel_GuestRoom | 101 | NREL_2004 | ClimateZone 1-8 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2004 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2004Hotel/MotelGuest Rooms |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 3.57 | LargeHotel_GuestRoom_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel_GuestRoom_Equip | LargeHotel_HtgSetp_GuestRoom | LargeHotel_ClgSetp_GuestRoom | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel_SWH_GuestRoom
ASHRAE_90.1-2004_LargeHotel_Kitchen | 398 | NREL_2004 | ClimateZone 1-8 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | 511 | 0.1 | 0.2 | 0.7 | LargeHotel_Kitchen_Gas | 47.22 | 0.2 | 0.5 | 0.1 | LargeHotel_Kitchen_Equip | LargeHotel_HtgSetp_Kitchen | LargeHotel_ClgSetp_Kitchen | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel_SWH_Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel_Kitchen_Exhaust
ASHRAE_90.1-2004_LargeHotel_Laundry | 288 | NREL_2004 | ClimateZone 1-8 | LargeHotel | Laundry | 120_149_230 | ASHRAE 90.1-2004 | Hospital | Laundry-Washing | ASHRAE 90.1-2004HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 4 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | 170 | 0 | 0.5 | 0 | LargeHotel_LaundryRoom_Gas | 5.73 | 0 | 0.5 | 0 | LargeHotel_LaundryRoom_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel_SWH_Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel_Laundry_Exhaust_ALWAYS_ON
ASHRAE_90.1-2004_LargeHotel_Lobby | 171 | NREL_2004 | ClimateZone 1-8 | LargeHotel | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | For Hotel | ASHRAE 90.1-2004LobbyFor Hotel |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.75 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_90.1-2004_LargeHotel_Mechanical | 14 | NREL_2004 | ClimateZone 1-8 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.5 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_90.1-2004_LargeHotel_Retail | 526 | NREL_2004 | ClimateZone 1-8 | LargeHotel | Retail | 171_222_78 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 1 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_90.1-2004_LargeHotel_Storage | 355 | NREL_2004 | ClimateZone 1-8 | LargeHotel | Storage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 2 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.25 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Banquet | 25 | NREL_2009 | ClimateZone 1-3 | LargeHotel | Banquet | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 67 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 3 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Banquet | 229 | NREL_2009 | ClimateZone 4-8 | LargeHotel | Banquet | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 67 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 3 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Cafe | 225 | NREL_2009 | ClimateZone 1-3 | LargeHotel | Cafe | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Hotel | ASHRAE 189.1-2009Dining AreaFor Hotel |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 67 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Cafe | 510 | NREL_2009 | ClimateZone 4-8 | LargeHotel | Cafe | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Hotel | ASHRAE 189.1-2009Dining AreaFor Hotel |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 67 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Corridor | 54 | NREL_2009 | ClimateZone 1-3 | LargeHotel | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp_Corridor | LargeHotel_ClgSetp_Corridor
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Corridor | 388 | NREL_2009 | ClimateZone 4-8 | LargeHotel | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp_Corridor | LargeHotel_ClgSetp_Corridor
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_GuestRoom | 396 | NREL_2009 | ClimateZone 1-3 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | ASHRAE 189.1-2009Hotel/MotelGuest Rooms |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 3.57 | LargeHotel_GuestRoom_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.68 | 0 | 0.5 | 0 | LargeHotel_GuestRoom_Equip | LargeHotel_HtgSetp_GuestRoom | LargeHotel_ClgSetp_GuestRoom | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel_SWH_GuestRoom
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_GuestRoom | 71 | NREL_2009 | ClimateZone 4-8 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | ASHRAE 189.1-2009Hotel/MotelGuest Rooms |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 3.57 | LargeHotel_GuestRoom_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.68 | 0 | 0.5 | 0 | LargeHotel_GuestRoom_Equip | LargeHotel_HtgSetp_GuestRoom | LargeHotel_ClgSetp_GuestRoom | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel_SWH_GuestRoom
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Kitchen | 173 | NREL_2009 | ClimateZone 1-3 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | 373.8 | 0.1 | 0.2 | 0.7 | LargeHotel_Kitchen_Gas | 24.16 | 0.2 | 0.5 | 0.1 | LargeHotel_Kitchen_Equip | LargeHotel_HtgSetp_Kitchen | LargeHotel_ClgSetp_Kitchen | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel_SWH_Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel_Kitchen_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Kitchen | 287 | NREL_2009 | ClimateZone 4-8 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | 373.8 | 0.1 | 0.2 | 0.7 | LargeHotel_Kitchen_Gas | 24.16 | 0.2 | 0.5 | 0.1 | LargeHotel_Kitchen_Equip | LargeHotel_HtgSetp_Kitchen | LargeHotel_ClgSetp_Kitchen | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel_SWH_Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel_Kitchen_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Laundry | 203 | NREL_2009 | ClimateZone 1-3 | LargeHotel | Laundry | 120_149_230 | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | ASHRAE 189.1-2009HospitalLaundry-Washing |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 4 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | 123.8 | 0 | 0.5 | 0 | LargeHotel_LaundryRoom_Gas | 2.93 | 0 | 0.5 | 0 | LargeHotel_LaundryRoom_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel_SWH_Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel_Laundry_Exhaust_ALWAYS_ON
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Laundry | 252 | NREL_2009 | ClimateZone 4-8 | LargeHotel | Laundry | 120_149_230 | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | ASHRAE 189.1-2009HospitalLaundry-Washing |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 4 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | 123.8 | 0 | 0.5 | 0 | LargeHotel_LaundryRoom_Gas | 2.93 | 0 | 0.5 | 0 | LargeHotel_LaundryRoom_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel_SWH_Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel_Laundry_Exhaust_ALWAYS_ON
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Lobby | 164 | NREL_2009 | ClimateZone 1-3 | LargeHotel | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | For Hotel | ASHRAE 189.1-2009LobbyFor Hotel |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.38 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Lobby | 39 | NREL_2009 | ClimateZone 4-8 | LargeHotel | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | For Hotel | ASHRAE 189.1-2009LobbyFor Hotel |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.38 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Mechanical | 412 | NREL_2009 | ClimateZone 1-3 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Mechanical | 551 | NREL_2009 | ClimateZone 4-8 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Retail | 272 | NREL_2009 | ClimateZone 1-3 | LargeHotel | Retail | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.51 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Retail | 437 | NREL_2009 | ClimateZone 4-8 | LargeHotel | Retail | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.51 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_LargeHotel_Storage | 471 | NREL_2009 | ClimateZone 1-3 | LargeHotel | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 2 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0595 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.13 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_LargeHotel_Storage | 478 | NREL_2009 | ClimateZone 4-8 | LargeHotel | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 2 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.13 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
CBECS_Before-1980_LargeHotel_Banquet | 142 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: LargeHotel; 3 3: Banquet; 4 4: 230_196_120; 19 11: 2.77; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: LargeHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Conference rooms; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 67; 21 26: LargeHotel_Bldg_Occ; 21 27: LargeHotel_Activity; 21 28: 0.2232; 21 29: LargeHotel_Infil_Quarter_On; 21 35: 6.3; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: LargeHotel_Bldg_Equip; 21 40: LargeHotel_HtgSetp; 21 41: LargeHotel_ClgSetp
CBECS_Before-1980_LargeHotel_Cafe | 291 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: LargeHotel; 3 3: Cafe; 4 4: 31_169_34; 19 11: 3.7; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: LargeHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Food and Beverage Service; 21 20: Cafeteria, fast food; 21 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 67; 21 26: LargeHotel_Bldg_Occ; 21 27: LargeHotel_Activity; 21 28: 0.2232; 21 29: LargeHotel_Infil_Quarter_On; 21 35: 0.5; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: LargeHotel_Bldg_Equip; 21 40: LargeHotel_HtgSetp; 21 41: LargeHotel_ClgSetp
CBECS_Before-1980_LargeHotel_Corridor | 212 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: LargeHotel; 3 3: Corridor; 4 4: 169_31_31; 19 11: 0.6; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: LargeHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 1; 21 26: LargeHotel_Bldg_Occ; 21 27: LargeHotel_Activity; 21 28: 0.2232; 21 29: LargeHotel_Infil_Quarter_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: LargeHotel_Bldg_Equip; 21 40: LargeHotel_HtgSetp_Corridor; 21 41: LargeHotel_ClgSetp_Corridor
CBECS_Before-1980_LargeHotel_GuestRoom | 464 | NREL_Before-1980 | ClimateZone 1-8 | LargeHotel | GuestRoom | 78_167_222 | [6 empty] | 1.4 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 3.57 | LargeHotel_GuestRoom_Occ | LargeHotel_Activity | 0.2232 | LargeHotel_Infil_Quarter_On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel_GuestRoom_Equip | LargeHotel_HtgSetp_GuestRoom | LargeHotel_ClgSetp_GuestRoom | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel_SWH_GuestRoom
CBECS_Before-1980_LargeHotel_Kitchen | 282 | NREL_Before-1980 | ClimateZone 1-8 | LargeHotel | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.2232 | LargeHotel_Infil_Quarter_On | 511 | 0.1 | 0.2 | 0.7 | LargeHotel_Kitchen_Gas | 47.22 | 0.2 | 0.5 | 0.1 | LargeHotel_Kitchen_Equip | LargeHotel_HtgSetp_Kitchen | LargeHotel_ClgSetp_Kitchen | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel_SWH_Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel_Kitchen_Exhaust
CBECS_Before-1980_LargeHotel_Laundry | 78 | NREL_Before-1980 | ClimateZone 1-8 | LargeHotel | Laundry | 120_149_230 | [6 empty] | 0.7 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 4 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.2232 | LargeHotel_Infil_Quarter_On | 170 | 0 | 0.5 | 0 | LargeHotel_LaundryRoom_Gas | 5.73 | 0 | 0.5 | 0 | LargeHotel_LaundryRoom_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel_SWH_Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel_Laundry_Exhaust_ALWAYS_ON
CBECS_Before-1980_LargeHotel_Lobby | 298 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: LargeHotel; 3 3: Lobby; 4 4: 230_157_120; 19 11: 1.45; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: LargeHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Lobbies; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 30; 21 26: LargeHotel_Bldg_Occ; 21 27: LargeHotel_Activity; 21 28: 0.2232; 21 29: LargeHotel_Infil_Quarter_On; 21 35: 0.75; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: LargeHotel_Bldg_Equip; 21 40: LargeHotel_HtgSetp; 21 41: LargeHotel_ClgSetp
CBECS_Before-1980_LargeHotel_Mechanical | 255 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: LargeHotel; 3 3: Mechanical; 4 4: 41_31_169; 19 11: 0.6; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: LargeHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: LargeHotel_Bldg_Occ; 21 27: LargeHotel_Activity; 21 28: 0.2232; 21 29: LargeHotel_Infil_Quarter_On; 21 35: 0.5; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: LargeHotel_Bldg_Equip; 21 40: LargeHotel_HtgSetp; 21 41: LargeHotel_ClgSetp
CBECS_Before-1980_LargeHotel_Retail | 339 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: LargeHotel; 3 3: Retail; 4 4: 171_222_78; 19 11: 5.04; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: LargeHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Basement and street; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; 21 22: 0.3; 21 23: 0; 21 24: 0; 21 25: 15; 21 26: LargeHotel_Bldg_Occ; 21 27: LargeHotel_Activity; 21 28: 0.2232; 21 29: LargeHotel_Infil_Quarter_On; 21 35: 1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: LargeHotel_Bldg_Equip; 21 40: LargeHotel_HtgSetp; 21 41: LargeHotel_ClgSetp
CBECS_Before-1980_LargeHotel_Storage | 149 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: LargeHotel; 3 3: Storage; 4 4: 120_149_230; 19 11: 0.62; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: LargeHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Shipping and receiving; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 2; 21 26: LargeHotel_Bldg_Occ; 21 27: LargeHotel_Activity; 21 28: 0.2232; 21 29: LargeHotel_Infil_Quarter_On; 21 35: 0.25; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: LargeHotel_Bldg_Equip; 21 40: LargeHotel_HtgSetp; 21 41: LargeHotel_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | LargeHotel | Banquet | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesConference rooms | #N/A | #N/A | #N/A | 67 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 3 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | LargeHotel | Cafe | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | For Hotel | ASHRAE 90.1-2007Dining AreaFor Hotel |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria, fast food | #N/A | #N/A | #N/A | 67 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | LargeHotel | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 1 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp_Corridor | LargeHotel_ClgSetp_Corridor
|  | Xcel EDA 2007 | ClimateZone 1-8 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2007 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2007Hotel/MotelGuest Rooms |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | #N/A | #N/A | #N/A | 3.57 | LargeHotel_GuestRoom_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.68 | 0 | 0.5 | 0 | LargeHotel_GuestRoom_Equip | LargeHotel_HtgSetp_GuestRoom | LargeHotel_ClgSetp_GuestRoom | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel_SWH_GuestRoom
|  | Xcel EDA 2007 | ClimateZone 1-8 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-2007 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-2007Food and Beverage ServiceKitchens (cooking) | #N/A | #N/A | #N/A | 5 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | 373.8 | 0.1 | 0.2 | 0.7 | LargeHotel_Kitchen_Gas | 24.16 | 0.2 | 0.5 | 0.1 | LargeHotel_Kitchen_Equip | LargeHotel_HtgSetp_Kitchen | LargeHotel_ClgSetp_Kitchen | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel_SWH_Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel_Kitchen_Exhaust
|  | Xcel EDA 2007 | ClimateZone 1-8 | LargeHotel | Laundry | 120_149_230 | ASHRAE 90.1-2007 | Hospital | Laundry-Washing | ASHRAE 90.1-2007HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-2007 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-2007Dry Cleaners, LaundriesCommercial Laundry | #N/A | #N/A | #N/A | 4 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | 123.8 | 0 | 0.5 | 0 | LargeHotel_LaundryRoom_Gas | 2.93 | 0 | 0.5 | 0 | LargeHotel_LaundryRoom_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel_SWH_Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel_Laundry_Exhaust_ALWAYS_ON
|  | Xcel EDA 2007 | ClimateZone 1-8 | LargeHotel | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | For Hotel | ASHRAE 90.1-2007LobbyFor Hotel |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies | #N/A | #N/A | #N/A | 30 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.38 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 0 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | LargeHotel | Retail | 171_222_78 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-2007 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-2007Retail Stores, Sales Floors, and Show Room FloorsBasement and street | #N/A | #N/A | #N/A | 15 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.51 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | LargeHotel | Storage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | LargeHotel_Bldg_Light | ASHRAE 62.1-2007 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-2007Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | #N/A | #N/A | #N/A | 2 | LargeHotel_Bldg_Occ | LargeHotel_Activity | 0.0446 | LargeHotel_Infil_Quarter_On | [5 empty] | 0.13 | 0 | 0.5 | 0 | LargeHotel_Bldg_Equip | LargeHotel_HtgSetp | LargeHotel_ClgSetp
CBECS_1980-2004_LargeOffice | 140 | NREL_1980-2004 | ClimateZone 1-8 | LargeOffice | WholeBuilding | 120_230_199 | [6 empty] | 1.5 |  |  | 0 | 0.7 | 0.2 | Large Office_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Large Office_Bldg_Occ | Large Office_Activity | 0.2232 | Large Office_Infil_Quarter_On | [5 empty] | 1 | 0 | 0.5 | 0 | Large Office_Bldg_Equip | Large Office_HtgSetp | Large Office_ClgSetp | 63.9 | 498588 | 0.00012816 | 43.3 | 0.2 | 0.05 | LargeOffice_SWH
ASHRAE_189.1-2009_ClimateZone 1-3_LargeOffice | 307 | NREL_2009 | ClimateZone 1-3 | LargeOffice | WholeBuilding | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Large Office_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Large Office_Bldg_Occ | Large Office_Activity | 0.0595 | Large Office_Infil_Quarter_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Large Office_Bldg_Equip | Large Office_HtgSetp | Large Office_ClgSetp | 63.9 | 498588 | 0.00012816 | 43.3 | 0.2 | 0.05 | LargeOffice_SWH
ASHRAE_189.1-2009_ClimateZone 4-8_LargeOffice | 410 | NREL_2009 | ClimateZone 4-8 | LargeOffice | WholeBuilding | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Large Office_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Large Office_Bldg_Occ | Large Office_Activity | 0.0446 | Large Office_Infil_Quarter_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Large Office_Bldg_Equip | Large Office_HtgSetp | Large Office_ClgSetp | 63.9 | 498588 | 0.00012816 | 43.3 | 0.2 | 0.05 | LargeOffice_SWH
CBECS_Before-1980_LargeOffice | 266 | NREL_Before-1980 | ClimateZone 1-8 | LargeOffice | WholeBuilding | 120_230_199 | [6 empty] | 1.9 |  |  | 0 | 0.7 | 0.2 | Large Office_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Large Office_Bldg_Occ | Large Office_Activity | 0.2232 | Large Office_Infil_Quarter_On | [5 empty] | 1 | 0 | 0.5 | 0 | Large Office_Bldg_Equip | Large Office_HtgSetp | Large Office_ClgSetp | 63.9 | 498588 | 0.00012816 | 43.3 | 0.2 | 0.05 | LargeOffice_SWH
CBECS_1980-2004_MediumOffice | 322 | NREL_1980-2004 | ClimateZone 1-8 | MediumOffice | WholeBuilding | 120_230_199 | [6 empty] | 1.57 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.2232 | Medium Office_Infil_Quarter_On | [5 empty] | 1 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | MediumOffice_SWH
ASHRAE_189.1-2009_ClimateZone 1-3_MediumOffice | 403 | NREL_2009 | ClimateZone 1-3 | MediumOffice | WholeBuilding | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0595 | Medium Office_Infil_Quarter_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | MediumOffice_SWH
ASHRAE_189.1-2009_ClimateZone 4-8_MediumOffice | 360 | NREL_2009 | ClimateZone 4-8 | MediumOffice | WholeBuilding | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0446 | Medium Office_Infil_Quarter_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | MediumOffice_SWH
CBECS_Before-1980_MediumOffice | 47 | NREL_Before-1980 | ClimateZone 1-8 | MediumOffice | WholeBuilding | 120_230_199 | [6 empty] | 1.9 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.2232 | Medium Office_Infil_Quarter_On | [5 empty] | 1 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | MediumOffice_SWH
CBECS_1980-2004_Mid-riseApartment_Apartment | 473 | NREL_1980-2004 | ClimateZone 1-8 | Mid-riseApartment | Apartment | 78_167_222 | [6 empty] | 0.36 |  |  | 0 | 0.7 | 0.2 | Mid-riseApartment_Apartment_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping area | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping area | 0 | 0 | 0 | 2.63 | Mid-riseApartment_Apartment_Occ | Mid-riseApartment_Activity | 0.2232 | Mid-riseApartment_Infil | [5 empty] | 0.5 | 0 | 0.5 | 0 | Mid-riseApartment_Apartment_Equip | Mid-riseApartment_Apartment_HtgSetp | Mid-riseApartment_Apartmentl_ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | Mid-riseApartment_DHW
CBECS_1980-2004_Mid-riseApartment_Corridor | 41 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Mid-riseApartment; 3 3: Corridor; 4 4: 169_31_31; 19 11: 0.92; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Mid-riseApartment_Corridor_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 28: 0.2232; 21 29: Mid-riseApartment_Infil; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 40: Mid-riseApartment_Apartment_HtgSetp; 21 41: Mid-riseApartment_Apartmentl_ClgSetp
CBECS_1980-2004_Mid-riseApartment_Office | 496 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Mid-riseApartment; 3 3: Office; 4 4: 120_230_199; 19 11: 2.04; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Mid-riseApartment_Office_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 2.11; 21 26: Mid-riseApartment_Office_Occ; 21 27: Mid-riseApartment_Activity; 21 28: 0.2232; 21 29: Mid-riseApartment_Infil; 21 35: 1.2; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Mid-riseApartment_Office_Equip; 21 40: Mid-riseApartment_HtgSetp_Office; 21 41: Mid-riseApartment_ClgSetp_Office
ASHRAE_90.1-2004_Mid-riseApartment_Apartment | 151 | NREL_2004 | ClimateZone 1-8 | Mid-riseApartment | Apartment | 78_167_222 | ASHRAE 90.1-2004 | Dormitory | Living Quarters | ASHRAE 90.1-2004DormitoryLiving Quarters |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Mid-riseApartment_Apartment_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping area | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping area | 0 | 0 | 0 | 2.63 | Mid-riseApartment_Apartment_Occ | Mid-riseApartment_Activity | 0.0595 | Mid-riseApartment_Infil | [5 empty] | 0.5 | 0 | 0.5 | 0 | Mid-riseApartment_Apartment_Equip | Mid-riseApartment_Apartment_HtgSetp | Mid-riseApartment_Apartmentl_ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | Mid-riseApartment_DHW
ASHRAE_90.1-2004_Mid-riseApartment_Corridor | 559 | NREL_2004 | ClimateZone 1-8 | Mid-riseApartment | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | Mid-riseApartment_Corridor_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  |  | 0.0595 | Mid-riseApartment_Infil | [5 empty] | 0 | 0 | 0.5 | 0 |  | Mid-riseApartment_Apartment_HtgSetp | Mid-riseApartment_Apartmentl_ClgSetp
ASHRAE_90.1-2004_Mid-riseApartment_Office | 345 | NREL_2004 | ClimateZone 1-8 | Mid-riseApartment | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Mid-riseApartment_Office_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 2.11 | Mid-riseApartment_Office_Occ | Mid-riseApartment_Activity | 0.0595 | Mid-riseApartment_Infil | [5 empty] | 1.2 | 0 | 0.5 | 0 | Mid-riseApartment_Office_Equip | Mid-riseApartment_HtgSetp_Office | Mid-riseApartment_ClgSetp_Office
ASHRAE_189.1-2009_ClimateZone 1-3_Mid-riseApartment_Apartment | 310 | NREL_2009 | ClimateZone 1-3 | Mid-riseApartment | Apartment | 78_167_222 | ASHRAE 189.1-2009 | Dormitory | Living Quarters | ASHRAE 189.1-2009DormitoryLiving Quarters |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Mid-riseApartment_Apartment_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping area | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping area | 0 | 0 | 0 | 2.63 | Mid-riseApartment_Apartment_Occ | Mid-riseApartment_Activity | 0.0595 | Mid-riseApartment_Infil | [5 empty] | 0.36 | 0 | 0.5 | 0 | Mid-riseApartment_Apartment_Equip | Mid-riseApartment_Apartment_HtgSetp | Mid-riseApartment_Apartmentl_ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | Mid-riseApartment_DHW
ASHRAE_189.1-2009_ClimateZone 4-8_Mid-riseApartment_Apartment | 466 | NREL_2009 | ClimateZone 4-8 | Mid-riseApartment | Apartment | 78_167_222 | ASHRAE 189.1-2009 | Dormitory | Living Quarters | ASHRAE 189.1-2009DormitoryLiving Quarters |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Mid-riseApartment_Apartment_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping area | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping area | 0 | 0 | 0 | 2.63 | Mid-riseApartment_Apartment_Occ | Mid-riseApartment_Activity | 0.0446 | Mid-riseApartment_Infil | [5 empty] | 0.36 | 0 | 0.5 | 0 | Mid-riseApartment_Apartment_Equip | Mid-riseApartment_Apartment_HtgSetp | Mid-riseApartment_Apartmentl_ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | Mid-riseApartment_DHW
ASHRAE_189.1-2009_ClimateZone 1-3_Mid-riseApartment_Corridor | 45 | NREL_2009 | ClimateZone 1-3 | Mid-riseApartment | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | Mid-riseApartment_Corridor_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  |  | 0.0595 | Mid-riseApartment_Infil | [5 empty] | 0 | 0 | 0.5 | 0 |  | Mid-riseApartment_Apartment_HtgSetp | Mid-riseApartment_Apartmentl_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Mid-riseApartment_Corridor | 363 | NREL_2009 | ClimateZone 4-8 | Mid-riseApartment | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | Mid-riseApartment_Corridor_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  |  | 0.0446 | Mid-riseApartment_Infil | [5 empty] | 0 | 0 | 0.5 | 0 |  | Mid-riseApartment_Apartment_HtgSetp | Mid-riseApartment_Apartmentl_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Mid-riseApartment_Office | 308 | NREL_2009 | ClimateZone 1-3 | Mid-riseApartment | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Mid-riseApartment_Office_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 2.11 | Mid-riseApartment_Office_Occ | Mid-riseApartment_Activity | 0.0595 | Mid-riseApartment_Infil | [5 empty] | 0.87 | 0 | 0.5 | 0 | Mid-riseApartment_Office_Equip | Mid-riseApartment_HtgSetp_Office | Mid-riseApartment_ClgSetp_Office
ASHRAE_189.1-2009_ClimateZone 4-8_Mid-riseApartment_Office | 270 | NREL_2009 | ClimateZone 4-8 | Mid-riseApartment | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Mid-riseApartment_Office_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 2.11 | Mid-riseApartment_Office_Occ | Mid-riseApartment_Activity | 0.0446 | Mid-riseApartment_Infil | [5 empty] | 0.87 | 0 | 0.5 | 0 | Mid-riseApartment_Office_Equip | Mid-riseApartment_HtgSetp_Office | Mid-riseApartment_ClgSetp_Office
CBECS_Before-1980_Mid-riseApartment_Apartment | 362 | NREL_Before-1980 | ClimateZone 1-8 | Mid-riseApartment | Apartment | 78_167_222 | [6 empty] | 0.36 |  |  | 0 | 0.7 | 0.2 | Mid-riseApartment_Apartment_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping area | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping area | 0 | 0 | 0 | 2.63 | Mid-riseApartment_Apartment_Occ | Mid-riseApartment_Activity | 0.2232 | Mid-riseApartment_Infil | [5 empty] | 0.5 | 0 | 0.5 | 0 | Mid-riseApartment_Apartment_Equip | Mid-riseApartment_Apartment_HtgSetp | Mid-riseApartment_Apartmentl_ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | Mid-riseApartment_DHW
CBECS_Before-1980_Mid-riseApartment_Corridor | 146 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Mid-riseApartment; 3 3: Corridor; 4 4: 169_31_31; 19 11: 0.92; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Mid-riseApartment_Corridor_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 28: 0.2232; 21 29: Mid-riseApartment_Infil; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 40: Mid-riseApartment_Apartment_HtgSetp; 21 41: Mid-riseApartment_Apartmentl_ClgSetp
CBECS_Before-1980_Mid-riseApartment_Office | 341 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Mid-riseApartment; 3 3: Office; 4 4: 120_230_199; 19 11: 2.04; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Mid-riseApartment_Office_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 2.11; 21 26: Mid-riseApartment_Office_Occ; 21 27: Mid-riseApartment_Activity; 21 28: 0.2232; 21 29: Mid-riseApartment_Infil; 21 35: 1.2; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Mid-riseApartment_Office_Equip; 21 40: Mid-riseApartment_HtgSetp_Office; 21 41: Mid-riseApartment_ClgSetp_Office
|  | Xcel EDA 2007 | ClimateZone 1-8 | Mid-riseApartment | Apartment | 78_167_222 | ASHRAE 90.1-2007 | Dormitory | Living Quarters | ASHRAE 90.1-2007DormitoryLiving Quarters |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Mid-riseApartment_Apartment_Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping area | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesDormitory sleeping area | 0 | 0 | 0 | 2.63 | Mid-riseApartment_Apartment_Occ | Mid-riseApartment_Activity | 0.0446 | Mid-riseApartment_Infil | [5 empty] | 0.36 | 0 | 0.5 | 0 | Mid-riseApartment_Apartment_Equip | Mid-riseApartment_Apartment_HtgSetp | Mid-riseApartment_Apartmentl_ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | Mid-riseApartment_DHW
|  | Xcel EDA 2007 | ClimateZone 1-8 | Mid-riseApartment | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | Mid-riseApartment_Corridor_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 0 |  |  | 0.0446 | Mid-riseApartment_Infil | [5 empty] | 0 | 0 | 0.5 | 0 |  | Mid-riseApartment_Apartment_HtgSetp | Mid-riseApartment_Apartmentl_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Mid-riseApartment | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Mid-riseApartment_Office_Light | ASHRAE 62.1-2007 | Offices | Office Space | ASHRAE 62.1-2007OfficesOffice Space | #N/A | #N/A | #N/A | 2.11 | Mid-riseApartment_Office_Occ | Mid-riseApartment_Activity | 0.0446 | Mid-riseApartment_Infil | [5 empty] | 0.87 | 0 | 0.5 | 0 | Mid-riseApartment_Office_Equip | Mid-riseApartment_HtgSetp_Office | Mid-riseApartment_ClgSetp_Office
|  | NREL_1980-2004 | ClimateZone 1-8 | Office | BreakRoom | 230_157_120 | [6 empty] | 3.1832 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 50 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 7.42 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_1980-2004 | ClimateZone 1-8 | Office | ClosedOffice | 120_230_199 | [6 empty] | 2.9179 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.75 | Office Work Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.83 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_1980-2004 | ClimateZone 1-8 | Office | Conference | 230_196_120 | [6 empty] | 3.4484 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 | 0 | 50 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_1980-2004 | ClimateZone 1-8 | Office | Corridor | 169_31_31 | [6 empty] | 1.3263 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Work Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_1980-2004 | ClimateZone 1-8 | Office | Elec/MechRoom | 41_31_169 | [6 empty] | 3.9789 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 0 |  | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_1980-2004 | ClimateZone 1-8 | Office | IT_Room | 41_31_169 | [6 empty] | 2.9179 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 5 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_1980-2004 | ClimateZone 1-8 | Office | Lobby | 230_157_120 | [6 empty] | 3.4484 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 10 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_1980-2004 | ClimateZone 1-8 | Office | OpenOffice | 120_230_199 | [6 empty] | 2.9179 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5.25 | Office Work Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.91 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_1980-2004 | ClimateZone 1-8 | Office | PrintRoom | 41_31_169 | [6 empty] | 2.9179 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_1980-2004 | ClimateZone 1-8 | Office | Restroom | 169_169_31 | [6 empty] | 2.3874 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office_Bldg_Occ
|  | NREL_1980-2004 | ClimateZone 1-8 | Office | Stair | 230_157_120 | [6 empty] | 1.5916 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_1980-2004 | ClimateZone 1-8 | Office | Storage | 120_149_230 | [6 empty] | 2.1221 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_1980-2004 | ClimateZone 1-8 | Office | Vending | 230_157_120 | [6 empty] | 1.3263 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 5.25 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_1980-2004 | ClimateZone 1-8 | Office | WholeBuilding - Md/Lg Office | 120_230_199 | [6 empty] | 1.57 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.2232 | Medium Office_Infil_Quarter_On | [5 empty] | 1 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | Office_SWH
|  | NREL_1980-2004 | ClimateZone 1-8 | Office | WholeBuilding - Sm Office | 120_230_199 | [6 empty] | 1.57 |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Small Office_Bldg_Occ | Small Office_Activity | 0.2232 | Small Office_Infil_Quarter_On | [5 empty] | 1 | 0 | 0.5 | 0 | Small Office_Bldg_Equip | Small Office_HtgSetp | Small Office_ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | Office_SWH
|  | NREL_2004 | ClimateZone 1-8 | Office | BreakRoom | 230_157_120 | ASHRAE 90.1-2004 | Lounge/Recreation | General | ASHRAE 90.1-2004Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 50 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 7.42 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2004 | ClimateZone 1-8 | Office | ClosedOffice | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.75 | Office Work Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.83 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2004 | ClimateZone 1-8 | Office | Conference | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 | 0 | 50 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2004 | ClimateZone 1-8 | Office | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Work Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2004 | ClimateZone 1-8 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 0 |  | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2004 | ClimateZone 1-8 | Office | IT_Room | 41_31_169 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 5 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2004 | ClimateZone 1-8 | Office | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral |  |  | 1.3 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 10 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2004 | ClimateZone 1-8 | Office | OpenOffice | 120_230_199 | ASHRAE 90.1-2004 | Office-Open Plan | General | ASHRAE 90.1-2004Office-Open PlanGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5.25 | Office Work Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.91 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2004 | ClimateZone 1-8 | Office | PrintRoom | 41_31_169 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2004 | ClimateZone 1-8 | Office | Restroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office_Bldg_Occ
|  | NREL_2004 | ClimateZone 1-8 | Office | Stair | 230_157_120 | ASHRAE 90.1-2004 | Stairs-Active | General | ASHRAE 90.1-2004Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2004 | ClimateZone 1-8 | Office | Storage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2004 | ClimateZone 1-8 | Office | Vending | 230_157_120 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 5.25 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2004 | ClimateZone 1-8 | Office | WholeBuilding - Md/Lg Office | 120_230_199 | ASHRAE 90.1-2004 | Whole Building | Office | ASHRAE 90.1-2004Whole BuildingOffice |  |  | 1 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0595 | Medium Office_Infil_Quarter_On | [5 empty] | 1 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | Office_SWH
|  | NREL_2004 | ClimateZone 1-8 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 90.1-2004 | Whole Building | Office | ASHRAE 90.1-2004Whole BuildingOffice |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Small Office_Bldg_Occ | Small Office_Activity | 0.0595 | Small Office_Infil_Quarter_On | [5 empty] | 1 | 0 | 0.5 | 0 | Small Office_Bldg_Equip | Small Office_HtgSetp | Small Office_ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | Office_SWH
|  | NREL_2009 | ClimateZone 1-3 | Office | BreakRoom | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 50 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 4.01 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 1-3 | Office | ClosedOffice | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.75 | Office Work Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.45 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 1-3 | Office | Conference | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 | 0 | 50 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 1-3 | Office | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Work Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 1-3 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 0 |  | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.15 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 1-3 | Office | IT_Room | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 5 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 1.08 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 1-3 | Office | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 10 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.04 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 1-3 | Office | OpenOffice | 120_230_199 | ASHRAE 189.1-2009 | Office-Open Plan | General | ASHRAE 189.1-2009Office-Open PlanGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5.25 | Office Work Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.49 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 1-3 | Office | PrintRoom | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.81 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 1-3 | Office | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0.15 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office_Bldg_Occ
|  | NREL_2009 | ClimateZone 1-3 | Office | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 1-3 | Office | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 1-3 | Office | Vending | 230_157_120 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Misc Occ | Office Activity | 0.0595 | Office Infil Quarter On | [5 empty] | 2.84 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 1-3 | Office | WholeBuilding - Md/Lg Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0595 | Medium Office_Infil_Quarter_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | Office_SWH
|  | NREL_2009 | ClimateZone 1-3 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Small Office_Bldg_Occ | Small Office_Activity | 0.0595 | Small Office_Infil_Quarter_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Small Office_Bldg_Equip | Small Office_HtgSetp | Small Office_ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | Office_SWH
|  | NREL_2009 | ClimateZone 4-8 | Office | BreakRoom | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 50 | Office Misc Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 4.01 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 4-8 | Office | ClosedOffice | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.75 | Office Work Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0.45 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 4-8 | Office | Conference | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 | 0 | 50 | Office Misc Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 4-8 | Office | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Work Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 4-8 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 0 |  | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0.15 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 4-8 | Office | IT_Room | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 5 | Office Misc Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 1.08 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 4-8 | Office | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 10 | Office Misc Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0.04 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 4-8 | Office | OpenOffice | 120_230_199 | ASHRAE 189.1-2009 | Office-Open Plan | General | ASHRAE 189.1-2009Office-Open PlanGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5.25 | Office Work Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0.49 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 4-8 | Office | PrintRoom | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0.81 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 4-8 | Office | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0.15 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office_Bldg_Occ
|  | NREL_2009 | ClimateZone 4-8 | Office | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 4-8 | Office | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 4-8 | Office | Vending | 230_157_120 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Misc Occ | Office Activity | 0.0446 | Office Infil Quarter On | [5 empty] | 2.84 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_2009 | ClimateZone 4-8 | Office | WholeBuilding - Md/Lg Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0446 | Medium Office_Infil_Quarter_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | Office_SWH
|  | NREL_2009 | ClimateZone 4-8 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Small Office_Bldg_Occ | Small Office_Activity | 0.0446 | Small Office_Infil_Quarter_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Small Office_Bldg_Equip | Small Office_HtgSetp | Small Office_ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | Office_SWH
|  | NREL_Before-1980 | ClimateZone 1-8 | Office | BreakRoom | 230_157_120 | [6 empty] | 0.67737 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 50 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 7.42 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_Before-1980 | ClimateZone 1-8 | Office | ClosedOffice | 120_230_199 | [6 empty] | 0.67737 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.75 | Office Work Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.83 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_Before-1980 | ClimateZone 1-8 | Office | Conference | 230_196_120 | [6 empty] | 0.93789 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 | 0 | 50 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_Before-1980 | ClimateZone 1-8 | Office | Corridor | 169_31_31 | [6 empty] | 0.93789 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Work Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_Before-1980 | ClimateZone 1-8 | Office | Elec/MechRoom | 41_31_169 | [6 empty] | 0.36474 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 0 |  | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_Before-1980 | ClimateZone 1-8 | Office | IT_Room | 41_31_169 | [6 empty] | 0.83368 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 5 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_Before-1980 | ClimateZone 1-8 | Office | Lobby | 230_157_120 | [6 empty] | 0.41684 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 10 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_Before-1980 | ClimateZone 1-8 | Office | OpenOffice | 120_230_199 | [6 empty] | 0.93789 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5.25 | Office Work Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.91 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_Before-1980 | ClimateZone 1-8 | Office | PrintRoom | 41_31_169 | [6 empty] | 0.52105 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_Before-1980 | ClimateZone 1-8 | Office | Restroom | 169_169_31 | [6 empty] | 0.52105 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office_Bldg_Occ
|  | NREL_Before-1980 | ClimateZone 1-8 | Office | Stair | 230_157_120 | [6 empty] | 0.46895 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_Before-1980 | ClimateZone 1-8 | Office | Storage | 120_149_230 | [6 empty] | 0.46895 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_Before-1980 | ClimateZone 1-8 | Office | Vending | 230_157_120 | [6 empty] | 0.52105 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Misc Occ | Office Activity | 0.2232 | Office Infil Quarter On | [5 empty] | 5.25 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | NREL_Before-1980 | ClimateZone 1-8 | Office | WholeBuilding - Md/Lg Office | 120_230_199 | [6 empty] | 1.9 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.2232 | Medium Office_Infil_Quarter_On | [5 empty] | 1 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | Office_SWH
|  | NREL_Before-1980 | ClimateZone 1-8 | Office | WholeBuilding - Sm Office | 120_230_199 | [6 empty] | 1.9 |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Small Office_Bldg_Occ | Small Office_Activity | 0.2232 | Small Office_Infil_Quarter_On | [5 empty] | 1 | 0 | 0.5 | 0 | Small Office_Bldg_Equip | Small Office_HtgSetp | Small Office_ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | Office_SWH
|  | Xcel EDA 2007 | ClimateZone 1-8 | Office | BreakRoom | 230_157_120 | ASHRAE 90.1-2007 | Lounge/Recreation | General | ASHRAE 90.1-2007Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-2007 | Offices | Reception Areas | ASHRAE 62.1-2007OfficesReception Areas | #N/A | #N/A | #N/A | 10 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0446 | Medium Office_Infil_Quarter_On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Office | ClosedOffice | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-2007 | Offices | Office Space | ASHRAE 62.1-2007OfficesOffice Space | #N/A | #N/A | #N/A | 5 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0446 | Medium Office_Infil_Quarter_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Office | Conference | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-2007 | Offices | Conference rooms | ASHRAE 62.1-2007OfficesConference rooms | #N/A | #N/A | #N/A | 46.45 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0446 | Medium Office_Infil_Quarter_On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Office | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 1 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0446 | Medium Office_Infil_Quarter_On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-2007 | Offices | Office Space | ASHRAE 62.1-2007OfficesOffice Space | #N/A | #N/A | #N/A | 0 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0446 | Medium Office_Infil_Quarter_On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Office | IT_Room | 41_31_169 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 4.65 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0446 | Medium Office_Infil_Quarter_On | [5 empty] | 0.8 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Office | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral |  |  | 1.3 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-2007 | Offices | Reception Areas | ASHRAE 62.1-2007OfficesReception Areas | #N/A | #N/A | #N/A | 10 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0446 | Medium Office_Infil_Quarter_On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
C |  | Xcel EDA 2007 | ClimateZone 1-8 | Office | OpenOffice | 120_230_199 | ASHRAE 90.1-2007 | Office-Open Plan | General | ASHRAE 90.1-2007Office-Open PlanGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-2007 | Offices | Office Space | ASHRAE 62.1-2007OfficesOffice Space | #N/A | #N/A | #N/A | 5 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0446 | Medium Office_Infil_Quarter_On | [5 empty] | 0.75 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Office | PrintRoom | 41_31_169 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 1 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0446 | Medium Office_Infil_Quarter_On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Office | Restroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-2007Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | #N/A | #N/A | #N/A | 9.29 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0446 | Medium Office_Infil_Quarter_On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office_Bldg_Occ
|  | Xcel EDA 2007 | ClimateZone 1-8 | Office | Stair | 230_157_120 | ASHRAE 90.1-2007 | Stairs-Active | General | ASHRAE 90.1-2007Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 0 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0446 | Medium Office_Infil_Quarter_On | [5 empty] | 0 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Office | Storage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 0 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0446 | Medium Office_Infil_Quarter_On | [5 empty] | 0 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Office | Vending | 230_157_120 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0.4 | 0.4 | 0.2 | Medium Office_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 1 | Medium Office_Bldg_Occ | Medium Office_Activity | 0.0446 | Medium Office_Infil_Quarter_On | [5 empty] | 2 | 0 | 0.5 | 0 | Medium Office_Bldg_Equip | Medium Office_HtgSetp | Medium Office_ClgSetp
CBECS_1980-2004_Outpatient_Anesthesia | 509 | NREL_1980-2004 | ClimateZone 1-8 | Outpatient | Anesthesia | 204_120_230 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
CBECS_1980-2004_Outpatient_BioHazard | 1 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: BioHazard; 4 4: 204_120_230; 19 11: 1; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: GGHC v2.2; 21 19: Health Care; 21 20: Bedpan Room; 21 21: GGHC v2.2Health CareBedpan Room; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 0.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_Cafe | 29 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Cafe; 4 4: 31_169_34; 19 11: 1.3; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Food and Beverage Service; 21 20: Cafeteria, fast food; 21 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 92.94; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_CleanWork | 352 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: CleanWork; 4 4: 204_120_230; 19 11: 1.3; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: GGHC v2.2; 21 19: Health Care; 21 20: Clean Utility / Workroom; 21 21: GGHC v2.2Health CareClean Utility / Workroom; 21 22: 0.3; 21 23: 0; 21 24: 0; 21 25: 18.58; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 2; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_Conference | 285 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Conference; 4 4: 230_196_120; 19 11: 1.8; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Conference rooms; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 46.45; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_DressingRoom | 325 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: DressingRoom; 4 4: 136_78_222; 19 11: 1.8; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Dormitory sleeping areas; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 4.65; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 1.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_Elec/MechRoom | 535 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Elec/MechRoom; 4 4: 41_31_169; 19 11: 0.7; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: GGHC v2.2; 21 19: Health Care; 21 20: Mechanical Equipment Room; 21 21: GGHC v2.2Health CareMechanical Equipment Room; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 5; 21 36: 0; 21 37: 0.3; 21 38: 0.7; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_Exam | 75 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Exam; 4 4: 136_78_222; 19 11: 1.6; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: GGHC v2.2; 21 19: Health Care; 21 20: Special Procedure Room, Diagnostic; 21 21: GGHC v2.2Health CareSpecial Procedure Room, Diagnostic; 21 22: 0.3; 21 23: 0; 21 24: 0; 21 25: 18.58; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 1.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_Hall | 82 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Hall; 4 4: 169_31_31; 19 11: 0.8; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 0.4; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_IT_Room | 59 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: IT_Room; 4 4: 41_31_169; 19 11: 1.8; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Telecommunication centers and data entry areas; 21 21: ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 4.65; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 1.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_Janitor | 338 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Janitor; 4 4: 120_149_230; 19 11: 1; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: GGHC v2.2; 21 19: Health Care; 21 20: Janitors Closet / Utility; 21 21: GGHC v2.2Health CareJanitors Closet / Utility; 21 22: 1.5; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 0; 21 36: 0; 21 37: 0.3; 21 38: 0.7; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_Lobby | 114 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Lobby; 4 4: 230_157_120; 19 11: 1; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Lobbies; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 27.87; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 1.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_LockerRoom | 487 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: LockerRoom; 4 4: 169_169_31; 19 11: 0.9; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: GGHC v2.2; 21 19: Health Care; 21 20: Lockers; 21 21: GGHC v2.2Health CareLockers; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 13.94; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 3; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_Lounge | 499 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Lounge; 4 4: 230_157_120; 19 11: 0.9; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Lobbies; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 13.94; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 3; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_MedGas | 249 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: MedGas; 4 4: 204_120_230; 19 11: 1; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Storage rooms; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 0.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_MRI | 518 | NREL_1980-2004 | ClimateZone 1-8 | Outpatient | MRI | 169_31_159 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 53.06 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
CBECS_1980-2004_Outpatient_MRI_Control | 481 | NREL_1980-2004 | ClimateZone 1-8 | Outpatient | MRI_Control | 136_78_222 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
CBECS_1980-2004_Outpatient_NurseStation | 515 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: NurseStation; 4 4: 31_162_169; 19 11: 2.1; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 18.58; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 2; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_Office | 139 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Office; 4 4: 120_230_199; 19 11: 1.8; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 4.65; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 1.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_OR | 458 | NREL_1980-2004 | ClimateZone 1-8 | Outpatient | OR | 169_31_159 | [6 empty] | 7 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | 23.9 | 0 | 0 | 0.5 | Outpatient_Bldg_Equip | 4 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp_OR | Outpatient_ClgSetp_OR | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
CBECS_1980-2004_Outpatient_PACU | 236 | NREL_1980-2004 | ClimateZone 1-8 | Outpatient | PACU | 169_31_159 | [6 empty] | 2.3 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
CBECS_1980-2004_Outpatient_PhysicalTherapy | 15 | NREL_1980-2004 | ClimateZone 1-8 | Outpatient | PhysicalTherapy | 154_230_120 | [6 empty] | 1.6 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 1.5 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
CBECS_1980-2004_Outpatient_PreOp | 420 | NREL_1980-2004 | ClimateZone 1-8 | Outpatient | PreOp | 169_31_159 | [6 empty] | 1.4 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
CBECS_1980-2004_Outpatient_ProcedureRoom | 215 | NREL_1980-2004 | ClimateZone 1-8 | Outpatient | ProcedureRoom | 169_31_159 | [6 empty] | 1.6 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
CBECS_1980-2004_Outpatient_Soil Work | 532 | NREL_1980-2004 | ClimateZone 1-8 | Outpatient | Soil Work | 204_120_230 | [6 empty] | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
CBECS_1980-2004_Outpatient_Stair | 19 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Stair; 4 4: 230_157_120; 19 11: 0.8; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_1980-2004_Outpatient_Toilet | 84 | NREL_1980-2004 | ClimateZone 1-8 | Outpatient | Toilet | 169_169_31 | [6 empty] | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 0.4 | 0 | 0.3 | 0.7 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
CBECS_1980-2004_Outpatient_Xray | 16 | NREL_1980-2004 | ClimateZone 1-8 | Outpatient | Xray | 169_31_159 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_90.1-2004_Outpatient_Anesthesia | 257 | NREL_2004 | ClimateZone 1-8 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 90.1-2004 | Hospital | Operating Room | ASHRAE 90.1-2004HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
ASHRAE_90.1-2004_Outpatient_BioHazard | 9 | NREL_2004 | ClimateZone 1-8 | Outpatient | BioHazard | 204_120_230 | ASHRAE 90.1-2004 | Active Storage | For Hospital | ASHRAE 90.1-2004Active StorageFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.1 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_Cafe | 333 | NREL_2004 | ClimateZone 1-8 | Outpatient | Cafe | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 92.94 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_CleanWork | 31 | NREL_2004 | ClimateZone 1-8 | Outpatient | CleanWork | 204_120_230 | ASHRAE 90.1-2004 | Hospital | Medical Supply | ASHRAE 90.1-2004HospitalMedical Supply |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_Conference | 507 | NREL_2004 | ClimateZone 1-8 | Outpatient | Conference | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 46.45 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_DressingRoom | 484 | NREL_2004 | ClimateZone 1-8 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 90.1-2004 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2004Dressing/Locker/Fitting RoomGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 4.65 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_Elec/MechRoom | 86 | NREL_2004 | ClimateZone 1-8 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 5 | 0 | 0.3 | 0.7 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_Exam | 517 | NREL_2004 | ClimateZone 1-8 | Outpatient | Exam | 136_78_222 | ASHRAE 90.1-2004 | Hospital | Exam/Treatment | ASHRAE 90.1-2004HospitalExam/Treatment |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_Hall | 490 | NREL_2004 | ClimateZone 1-8 | Outpatient | Hall | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | ASHRAE 90.1-2004Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.4 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_IT_Room | 479 | NREL_2004 | ClimateZone 1-8 | Outpatient | IT_Room | 41_31_169 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | 0 | 20 | 0 | 4.65 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_Janitor | 271 | NREL_2004 | ClimateZone 1-8 | Outpatient | Janitor | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_Lobby | 289 | NREL_2004 | ClimateZone 1-8 | Outpatient | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 27.87 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_LockerRoom | 304 | NREL_2004 | ClimateZone 1-8 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 90.1-2004 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2004Dressing/Locker/Fitting RoomGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_Lounge | 165 | NREL_2004 | ClimateZone 1-8 | Outpatient | Lounge | 230_157_120 | ASHRAE 90.1-2004 | Lounge/Recreation | For Hospital | ASHRAE 90.1-2004Lounge/RecreationFor Hospital |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 13.94 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_MedGas | 13 | NREL_2004 | ClimateZone 1-8 | Outpatient | MedGas | 204_120_230 | ASHRAE 90.1-2004 | Active Storage | For Hospital | ASHRAE 90.1-2004Active StorageFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.1 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_MRI | 168 | NREL_2004 | ClimateZone 1-8 | Outpatient | MRI | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 53.06 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
ASHRAE_90.1-2004_Outpatient_MRI_Control | 541 | NREL_2004 | ClimateZone 1-8 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
ASHRAE_90.1-2004_Outpatient_NurseStation | 127 | NREL_2004 | ClimateZone 1-8 | Outpatient | NurseStation | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_Office | 184 | NREL_2004 | ClimateZone 1-8 | Outpatient | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_OR | 147 | NREL_2004 | ClimateZone 1-8 | Outpatient | OR | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Operating Room | ASHRAE 90.1-2004HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | 23.9 | 0 | 0 | 0.5 | Outpatient_Bldg_Equip | 4 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp_OR | Outpatient_ClgSetp_OR | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_90.1-2004_Outpatient_PACU | 251 | NREL_2004 | ClimateZone 1-8 | Outpatient | PACU | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Recovery | ASHRAE 90.1-2004HospitalRecovery |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_90.1-2004_Outpatient_PhysicalTherapy | 80 | NREL_2004 | ClimateZone 1-8 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 90.1-2004 | Hospital | Physical Therapy | ASHRAE 90.1-2004HospitalPhysical Therapy |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1.5 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_90.1-2004_Outpatient_PreOp | 455 | NREL_2004 | ClimateZone 1-8 | Outpatient | PreOp | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Patient Room | ASHRAE 90.1-2004HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_90.1-2004_Outpatient_ProcedureRoom | 104 | NREL_2004 | ClimateZone 1-8 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_90.1-2004_Outpatient_Soil Work | 191 | NREL_2004 | ClimateZone 1-8 | Outpatient | Soil Work | 204_120_230 | ASHRAE 90.1-2004 | Hospital | Medical Supply | ASHRAE 90.1-2004HospitalMedical Supply |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
ASHRAE_90.1-2004_Outpatient_Stair | 537 | NREL_2004 | ClimateZone 1-8 | Outpatient | Stair | 230_157_120 | ASHRAE 90.1-2004 | Stairs-Active | General | ASHRAE 90.1-2004Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_90.1-2004_Outpatient_Toilet | 375 | NREL_2004 | ClimateZone 1-8 | Outpatient | Toilet | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.4 | 0 | 0.3 | 0.7 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
ASHRAE_90.1-2004_Outpatient_Xray | 216 | NREL_2004 | ClimateZone 1-8 | Outpatient | Xray | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Anesthesia | 300 | NREL_2009 | ClimateZone 1-3 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Anesthesia | 462 | NREL_2009 | ClimateZone 4-8 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_BioHazard | 542 | NREL_2009 | ClimateZone 1-3 | Outpatient | BioHazard | 204_120_230 | ASHRAE 189.1-2009 | Active Storage | For Hospital | ASHRAE 189.1-2009Active StorageFor Hospital |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_BioHazard | 337 | NREL_2009 | ClimateZone 4-8 | Outpatient | BioHazard | 204_120_230 | ASHRAE 189.1-2009 | Active Storage | For Hospital | ASHRAE 189.1-2009Active StorageFor Hospital |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Cafe | 201 | NREL_2009 | ClimateZone 1-3 | Outpatient | Cafe | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 92.94 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Cafe | 91 | NREL_2009 | ClimateZone 4-8 | Outpatient | Cafe | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 92.94 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_CleanWork | 393 | NREL_2009 | ClimateZone 1-3 | Outpatient | CleanWork | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Medical Supply | ASHRAE 189.1-2009HospitalMedical Supply |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_CleanWork | 178 | NREL_2009 | ClimateZone 4-8 | Outpatient | CleanWork | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Medical Supply | ASHRAE 189.1-2009HospitalMedical Supply |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Conference | 4 | NREL_2009 | ClimateZone 1-3 | Outpatient | Conference | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 46.45 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Conference | 111 | NREL_2009 | ClimateZone 4-8 | Outpatient | Conference | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 46.45 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_DressingRoom | 24 | NREL_2009 | ClimateZone 1-3 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 4.65 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_DressingRoom | 302 | NREL_2009 | ClimateZone 4-8 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 4.65 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Elec/MechRoom | 226 | NREL_2009 | ClimateZone 1-3 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 3.64 | 0 | 0.3 | 0.7 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Elec/MechRoom | 368 | NREL_2009 | ClimateZone 4-8 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 3.64 | 0 | 0.3 | 0.7 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Exam | 329 | NREL_2009 | ClimateZone 1-3 | Outpatient | Exam | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Exam/Treatment | ASHRAE 189.1-2009HospitalExam/Treatment |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Exam | 208 | NREL_2009 | ClimateZone 4-8 | Outpatient | Exam | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Exam/Treatment | ASHRAE 189.1-2009HospitalExam/Treatment |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Hall | 99 | NREL_2009 | ClimateZone 1-3 | Outpatient | Hall | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.29 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Hall | 453 | NREL_2009 | ClimateZone 4-8 | Outpatient | Hall | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.29 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_IT_Room | 274 | NREL_2009 | ClimateZone 1-3 | Outpatient | IT_Room | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | 0 | 20 | 0 | 4.65 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_IT_Room | 200 | NREL_2009 | ClimateZone 4-8 | Outpatient | IT_Room | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | 0 | 20 | 0 | 4.65 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Janitor | 220 | NREL_2009 | ClimateZone 1-3 | Outpatient | Janitor | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Janitor | 175 | NREL_2009 | ClimateZone 4-8 | Outpatient | Janitor | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Lobby | 446 | NREL_2009 | ClimateZone 1-3 | Outpatient | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 27.87 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Lobby | 194 | NREL_2009 | ClimateZone 4-8 | Outpatient | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 27.87 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_LockerRoom | 18 | NREL_2009 | ClimateZone 1-3 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_LockerRoom | 115 | NREL_2009 | ClimateZone 4-8 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Lounge | 468 | NREL_2009 | ClimateZone 1-3 | Outpatient | Lounge | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | For Hospital | ASHRAE 189.1-2009Lounge/RecreationFor Hospital |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 13.94 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Lounge | 441 | NREL_2009 | ClimateZone 4-8 | Outpatient | Lounge | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | For Hospital | ASHRAE 189.1-2009Lounge/RecreationFor Hospital |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 13.94 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_MedGas | 144 | NREL_2009 | ClimateZone 1-3 | Outpatient | MedGas | 204_120_230 | ASHRAE 189.1-2009 | Active Storage | For Hospital | ASHRAE 189.1-2009Active StorageFor Hospital |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_MedGas | 550 | NREL_2009 | ClimateZone 4-8 | Outpatient | MedGas | 204_120_230 | ASHRAE 189.1-2009 | Active Storage | For Hospital | ASHRAE 189.1-2009Active StorageFor Hospital |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_MRI | 354 | NREL_2009 | ClimateZone 1-3 | Outpatient | MRI | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 38.63 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_MRI | 138 | NREL_2009 | ClimateZone 4-8 | Outpatient | MRI | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 38.63 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_MRI_Control | 553 | NREL_2009 | ClimateZone 1-3 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_MRI_Control | 214 | NREL_2009 | ClimateZone 4-8 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_NurseStation | 77 | NREL_2009 | ClimateZone 1-3 | Outpatient | NurseStation | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_NurseStation | 161 | NREL_2009 | ClimateZone 4-8 | Outpatient | NurseStation | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Office | 43 | NREL_2009 | ClimateZone 1-3 | Outpatient | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Office | 320 | NREL_2009 | ClimateZone 4-8 | Outpatient | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_OR | 311 | NREL_2009 | ClimateZone 1-3 | Outpatient | OR | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | 17.4 | 0 | 0 | 0.5 | Outpatient_Bldg_Equip | 2.92 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp_OR | Outpatient_ClgSetp_OR | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_OR | 346 | NREL_2009 | ClimateZone 4-8 | Outpatient | OR | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | 17.4 | 0 | 0 | 0.5 | Outpatient_Bldg_Equip | 2.92 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp_OR | Outpatient_ClgSetp_OR | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_PACU | 247 | NREL_2009 | ClimateZone 1-3 | Outpatient | PACU | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Recovery | ASHRAE 189.1-2009HospitalRecovery |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_PACU | 546 | NREL_2009 | ClimateZone 4-8 | Outpatient | PACU | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Recovery | ASHRAE 189.1-2009HospitalRecovery |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_PhysicalTherapy | 281 | NREL_2009 | ClimateZone 1-3 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 189.1-2009 | Hospital | Physical Therapy | ASHRAE 189.1-2009HospitalPhysical Therapy |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1.09 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_PhysicalTherapy | 428 | NREL_2009 | ClimateZone 4-8 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 189.1-2009 | Hospital | Physical Therapy | ASHRAE 189.1-2009HospitalPhysical Therapy |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 1.09 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_PreOp | 133 | NREL_2009 | ClimateZone 1-3 | Outpatient | PreOp | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_PreOp | 92 | NREL_2009 | ClimateZone 4-8 | Outpatient | PreOp | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_ProcedureRoom | 46 | NREL_2009 | ClimateZone 1-3 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_ProcedureRoom | 544 | NREL_2009 | ClimateZone 4-8 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Soil Work | 182 | NREL_2009 | ClimateZone 1-3 | Outpatient | Soil Work | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Medical Supply | ASHRAE 189.1-2009HospitalMedical Supply |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Soil Work | 514 | NREL_2009 | ClimateZone 4-8 | Outpatient | Soil Work | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Medical Supply | ASHRAE 189.1-2009HospitalMedical Supply |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Stair | 467 | NREL_2009 | ClimateZone 1-3 | Outpatient | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Stair | 422 | NREL_2009 | ClimateZone 4-8 | Outpatient | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Toilet | 268 | NREL_2009 | ClimateZone 1-3 | Outpatient | Toilet | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.29 | 0 | 0.3 | 0.7 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Toilet | 279 | NREL_2009 | ClimateZone 4-8 | Outpatient | Toilet | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.29 | 0 | 0.3 | 0.7 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_Outpatient_Xray | 117 | NREL_2009 | ClimateZone 1-3 | Outpatient | Xray | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0595 | Outpatient_Infil | [5 empty] | 0.95 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
ASHRAE_189.1-2009_ClimateZone 4-8_Outpatient_Xray | 461 | NREL_2009 | ClimateZone 4-8 | Outpatient | Xray | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.95 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
CBECS_Before-1980_Outpatient_Anesthesia | 402 | NREL_Before-1980 | ClimateZone 1-8 | Outpatient | Anesthesia | 204_120_230 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
CBECS_Before-1980_Outpatient_BioHazard | 36 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: BioHazard; 4 4: 204_120_230; 19 11: 1; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: GGHC v2.2; 21 19: Health Care; 21 20: Bedpan Room; 21 21: GGHC v2.2Health CareBedpan Room; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 0.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_Cafe | 378 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Cafe; 4 4: 31_169_34; 19 11: 1.3; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Food and Beverage Service; 21 20: Cafeteria, fast food; 21 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 92.94; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_CleanWork | 314 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: CleanWork; 4 4: 204_120_230; 19 11: 1.3; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: GGHC v2.2; 21 19: Health Care; 21 20: Clean Utility / Workroom; 21 21: GGHC v2.2Health CareClean Utility / Workroom; 21 22: 0.3; 21 23: 0; 21 24: 0; 21 25: 18.58; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 2; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_Conference | 371 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Conference; 4 4: 230_196_120; 19 11: 1.8; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Conference rooms; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 46.45; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_DressingRoom | 547 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: DressingRoom; 4 4: 136_78_222; 19 11: 1.8; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Dormitory sleeping areas; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 4.65; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 1.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_Elec/MechRoom | 193 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Elec/MechRoom; 4 4: 41_31_169; 19 11: 0.7; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: GGHC v2.2; 21 19: Health Care; 21 20: Mechanical Equipment Room; 21 21: GGHC v2.2Health CareMechanical Equipment Room; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 5; 21 36: 0; 21 37: 0.3; 21 38: 0.7; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_Exam | 516 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Exam; 4 4: 136_78_222; 19 11: 1.6; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: GGHC v2.2; 21 19: Health Care; 21 20: Special Procedure Room, Diagnostic; 21 21: GGHC v2.2Health CareSpecial Procedure Room, Diagnostic; 21 22: 0.3; 21 23: 0; 21 24: 0; 21 25: 18.58; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 1.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_Hall | 88 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Hall; 4 4: 169_31_31; 19 11: 0.8; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 0.4; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_IT_Room | 519 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: IT_Room; 4 4: 41_31_169; 19 11: 1.8; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Telecommunication centers and data entry areas; 21 21: ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 4.65; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 1.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_Janitor | 264 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Janitor; 4 4: 120_149_230; 19 11: 1; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: GGHC v2.2; 21 19: Health Care; 21 20: Janitors Closet / Utility; 21 21: GGHC v2.2Health CareJanitors Closet / Utility; 21 22: 1.5; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 0; 21 36: 0; 21 37: 0.3; 21 38: 0.7; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_Lobby | 277 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Lobby; 4 4: 230_157_120; 19 11: 1; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Lobbies; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 27.87; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 1.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_LockerRoom | 235 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: LockerRoom; 4 4: 169_169_31; 19 11: 0.9; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: GGHC v2.2; 21 19: Health Care; 21 20: Lockers; 21 21: GGHC v2.2Health CareLockers; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 13.94; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 3; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_Lounge | 319 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Lounge; 4 4: 230_157_120; 19 11: 0.9; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Lobbies; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 13.94; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 3; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_MedGas | 157 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: MedGas; 4 4: 204_120_230; 19 11: 1; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Storage rooms; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 0.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_MRI | 207 | NREL_Before-1980 | ClimateZone 1-8 | Outpatient | MRI | 169_31_159 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 53.06 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
CBECS_Before-1980_Outpatient_MRI_Control | 189 | NREL_Before-1980 | ClimateZone 1-8 | Outpatient | MRI_Control | 136_78_222 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
CBECS_Before-1980_Outpatient_NurseStation | 125 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: NurseStation; 4 4: 31_162_169; 19 11: 2.1; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 18.58; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 2; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_Office | 221 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Office; 4 4: 120_230_199; 19 11: 1.8; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 4.65; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 1.1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_OR | 435 | NREL_Before-1980 | ClimateZone 1-8 | Outpatient | OR | 169_31_159 | [6 empty] | 7 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | 23.9 | 0 | 0 | 0.5 | Outpatient_Bldg_Equip | 4 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp_OR | Outpatient_ClgSetp_OR | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
CBECS_Before-1980_Outpatient_PACU | 42 | NREL_Before-1980 | ClimateZone 1-8 | Outpatient | PACU | 169_31_159 | [6 empty] | 2.3 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
CBECS_Before-1980_Outpatient_PhysicalTherapy | 351 | NREL_Before-1980 | ClimateZone 1-8 | Outpatient | PhysicalTherapy | 154_230_120 | [6 empty] | 1.6 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 1.5 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
CBECS_Before-1980_Outpatient_PreOp | 32 | NREL_Before-1980 | ClimateZone 1-8 | Outpatient | PreOp | 169_31_159 | [6 empty] | 1.4 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
CBECS_Before-1980_Outpatient_ProcedureRoom | 205 | NREL_Before-1980 | ClimateZone 1-8 | Outpatient | ProcedureRoom | 169_31_159 | [6 empty] | 1.6 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
CBECS_Before-1980_Outpatient_Soil Work | 238 | NREL_Before-1980 | ClimateZone 1-8 | Outpatient | Soil Work | 204_120_230 | [6 empty] | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
CBECS_Before-1980_Outpatient_Stair | 131 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Outpatient; 3 3: Stair; 4 4: 230_157_120; 19 11: 0.8; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Outpatient_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Outpatient_Bldg_Occ; 21 27: Outpatient_Activity; 21 28: 0.2232; 21 29: Outpatient_Infil; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Outpatient_Bldg_Equip; 21 40: Outpatient_HtgSetp; 21 41: Outpatient_ClgSetp
CBECS_Before-1980_Outpatient_Toilet | 425 | NREL_Before-1980 | ClimateZone 1-8 | Outpatient | Toilet | 169_169_31 | [6 empty] | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 0.4 | 0 | 0.3 | 0.7 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
CBECS_Before-1980_Outpatient_Xray | 392 | NREL_Before-1980 | ClimateZone 1-8 | Outpatient | Xray | 169_31_159 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.2232 | Outpatient_Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 90.1-2007 | Hospital | Operating Room | ASHRAE 90.1-2007HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | BioHazard | 204_120_230 | ASHRAE 90.1-2007 | Active Storage | For Hospital | ASHRAE 90.1-2007Active StorageFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | Cafe | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria, fast food | #N/A | #N/A | #N/A | 92.94 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | CleanWork | 204_120_230 | ASHRAE 90.1-2007 | Hospital | Medical Supply | ASHRAE 90.1-2007HospitalMedical Supply |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | Conference | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesConference rooms | #N/A | #N/A | #N/A | 46.45 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 90.1-2007 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2007Dressing/Locker/Fitting RoomGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | #N/A | #N/A | #N/A | 4.65 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 3.64 | 0 | 0.3 | 0.7 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | Exam | 136_78_222 | ASHRAE 90.1-2007 | Hospital | Exam/Treatment | ASHRAE 90.1-2007HospitalExam/Treatment |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | Hall | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | ASHRAE 90.1-2007Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.29 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | IT_Room | 41_31_169 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-2007 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-2007OfficesTelecommunication centers and data entry areas | #N/A | #N/A | #N/A | 4.65 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | Janitor | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies | #N/A | #N/A | #N/A | 27.87 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 90.1-2007 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2007Dressing/Locker/Fitting RoomGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | Lounge | 230_157_120 | ASHRAE 90.1-2007 | Lounge/Recreation | For Hospital | ASHRAE 90.1-2007Lounge/RecreationFor Hospital |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies | #N/A | #N/A | #N/A | 13.94 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | MedGas | 204_120_230 | ASHRAE 90.1-2007 | Active Storage | For Hospital | ASHRAE 90.1-2007Active StorageFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-2007 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-2007Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | #N/A | #N/A | #N/A | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | MRI | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 38.63 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient_SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | NurseStation | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-2007 | Offices | Office Space | ASHRAE 62.1-2007OfficesOffice Space | #N/A | #N/A | #N/A | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-2007 | Offices | Office Space | ASHRAE 62.1-2007OfficesOffice Space | #N/A | #N/A | #N/A | 4.65 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | OR | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Operating Room | ASHRAE 90.1-2007HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | 17.4 | 0 | 0 | 0.5 | Outpatient_Bldg_Equip | 2.92 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp_OR | Outpatient_ClgSetp_OR | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | PACU | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Recovery | ASHRAE 90.1-2007HospitalRecovery |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 90.1-2007 | Hospital | Physical Therapy | ASHRAE 90.1-2007HospitalPhysical Therapy |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 1.09 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | PreOp | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Patient Room | ASHRAE 90.1-2007HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | Soil Work | 204_120_230 | ASHRAE 90.1-2007 | Hospital | Medical Supply | ASHRAE 90.1-2007HospitalMedical Supply |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | Stair | 230_157_120 | ASHRAE 90.1-2007 | Stairs-Active | General | ASHRAE 90.1-2007Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | Toilet | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-2007Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | #N/A | #N/A | #N/A | 0 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.29 | 0 | 0.3 | 0.7 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
|  | Xcel EDA 2007 | ClimateZone 1-8 | Outpatient | Xray | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Outpatient_Bldg_Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient_Bldg_Occ | Outpatient_Activity | 0.0446 | Outpatient_Infil | [5 empty] | 0.95 | 0 | 0.5 | 0 | Outpatient_Bldg_Equip | Outpatient_HtgSetp | Outpatient_ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient_SWH
CBECS_1980-2004_PrimarySchool_Cafeteria | 192 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Cafeteria; 4 4: 31_169_34; 19 11: 1.4; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Food and Beverage Service; 21 20: Cafeteria, fast food; 21 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 66.67; 21 26: PrimarySchool_Cafeteria_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 2.36; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_HtgSetp; 21 41: PrimarySchool_ClgSetp
CBECS_1980-2004_PrimarySchool_Classroom | 444 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Classroom; 4 4: 120_230_199; 19 11: 2; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Classroom; 21 21: ASHRAE 62.1-1999EducationClassroom; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 23.22; 21 26: PrimarySchool_Bldg_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 1.39; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_HtgSetp; 21 41: PrimarySchool_ClgSetp
CBECS_1980-2004_PrimarySchool_Corridor | 438 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Corridor; 4 4: 169_31_31; 19 11: 0.9; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Corridors; 21 21: ASHRAE 62.1-1999EducationCorridors; 21 22: 0.1; 21 23: 0; 21 24: 0; 21 25: 9.29; 21 26: PrimarySchool_Bldg_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 0.37; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_BathCorrMechKitchen_HtgSetp; 21 41: PrimarySchool_BathCorrMechKitchenl_ClgSetp
CBECS_1980-2004_PrimarySchool_Gym | 347 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Gym; 4 4: 154_230_120; 19 11: 1.07; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Sports and Amusement; 21 20: Playing floors (gymnasium); 21 21: ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium); 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 27.9; 21 26: PrimarySchool_Gym_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 0.46; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_HtgSetp; 21 41: PrimarySchool_ClgSetp
CBECS_1980-2004_PrimarySchool_Kitchen | 106 | NREL_1980-2004 | ClimateZone 1-8 | PrimarySchool | Kitchen | 78_222_133 | [6 empty] | 1.6 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 13.93 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.2232 | PrimarySchool_Infil | 302.6 | 0.1 | 0.2 | 0.7 | PrimarySchool_Kitchen_Gas | 17.7 | 0.25 | 0.3 | 0.2 | PrimarySchool_Kitchen_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool_SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool_Kitchen_Exhaust
CBECS_1980-2004_PrimarySchool_Library | 348 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Library; 4 4: 230_196_120; 19 11: 2.11; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Libraries; 21 21: ASHRAE 62.1-1999EducationLibraries; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 21.36; 21 26: PrimarySchool_Bldg_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 1.39; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_HtgSetp; 21 41: PrimarySchool_ClgSetp
CBECS_1980-2004_PrimarySchool_Lobby | 391 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Lobby; 4 4: 230_157_120; 19 11: 1.14; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Corridors; 21 21: ASHRAE 62.1-1999EducationCorridors; 21 22: 0.1; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: PrimarySchool_Bldg_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 0.37; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_HtgSetp; 21 41: PrimarySchool_ClgSetp
CBECS_1980-2004_PrimarySchool_Mechanical | 395 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Mechanical; 4 4: 41_31_169; 19 11: 0.77; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0.93; 21 26: PrimarySchool_Bldg_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 0.37; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_BathCorrMechKitchen_HtgSetp; 21 41: PrimarySchool_BathCorrMechKitchenl_ClgSetp
CBECS_1980-2004_PrimarySchool_Office | 474 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Office; 4 4: 120_230_199; 19 11: 1.89; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 4.65; 21 26: PrimarySchool_Bldg_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_HtgSetp; 21 41: PrimarySchool_ClgSetp
CBECS_1980-2004_PrimarySchool_Restroom | 129 | NREL_1980-2004 | ClimateZone 1-8 | PrimarySchool | Restroom | 169_169_31 | [6 empty] | 0.9 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.2232 | PrimarySchool_Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool_SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
ASHRAE_90.1-2004_PrimarySchool_Cafeteria | 87 | NREL_2004 | ClimateZone 1-8 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 66.67 | PrimarySchool_Cafeteria_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 2.36 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Classroom | 411 | NREL_2004 | ClimateZone 1-8 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2004 | Classroom/Lecture/Training | General | ASHRAE 90.1-2004Classroom/Lecture/TrainingGeneral |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 15 | 0 | 23.22 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 1.39 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Corridor | 280 | NREL_2004 | ClimateZone 1-8 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.29 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Gym | 60 | NREL_2004 | ClimateZone 1-8 | PrimarySchool | Gym | 154_230_120 | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Playing Area | ASHRAE 90.1-2004Gymnasium/Exercise CenterPlaying Area |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 27.9 | PrimarySchool_Gym_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Kitchen | 231 | NREL_2004 | ClimateZone 1-8 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 13.93 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | 302.6 | 0.1 | 0.2 | 0.7 | PrimarySchool_Kitchen_Gas | 17.7 | 0.25 | 0.3 | 0.2 | PrimarySchool_Kitchen_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool_SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool_Kitchen_Exhaust
ASHRAE_90.1-2004_PrimarySchool_Library | 28 | NREL_2004 | ClimateZone 1-8 | PrimarySchool | Library | 230_196_120 | ASHRAE 90.1-2004 | Library | Reading Area | ASHRAE 90.1-2004LibraryReading Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 15 | 0 | 21.36 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | 0 |  |  |  |  | 1.39 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Lobby | 72 | NREL_2004 | ClimateZone 1-8 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Mechanical | 357 | NREL_2004 | ClimateZone 1-8 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Office | 342 | NREL_2004 | ClimateZone 1-8 | PrimarySchool | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 1 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_90.1-2004_PrimarySchool_Restroom | 10 | NREL_2004 | ClimateZone 1-8 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool_SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Cafeteria | 321 | NREL_2009 | ClimateZone 1-3 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 66.67 | PrimarySchool_Cafeteria_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 1.72 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Cafeteria | 457 | NREL_2009 | ClimateZone 4-8 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 66.67 | PrimarySchool_Cafeteria_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 1.72 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Classroom | 135 | NREL_2009 | ClimateZone 1-3 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 15 | 0 | 23.22 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Classroom | 344 | NREL_2009 | ClimateZone 4-8 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 15 | 0 | 23.22 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Corridor | 223 | NREL_2009 | ClimateZone 1-3 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.29 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Corridor | 11 | NREL_2009 | ClimateZone 4-8 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.29 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Gym | 523 | NREL_2009 | ClimateZone 1-3 | PrimarySchool | Gym | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 27.9 | PrimarySchool_Gym_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Gym | 480 | NREL_2009 | ClimateZone 4-8 | PrimarySchool | Gym | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 27.9 | PrimarySchool_Gym_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Kitchen | 463 | NREL_2009 | ClimateZone 1-3 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 13.93 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | 220.5 | 0.1 | 0.2 | 0.7 | PrimarySchool_Kitchen_Gas | 13.13 | 0.25 | 0.3 | 0.2 | PrimarySchool_Kitchen_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool_SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool_Kitchen_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Kitchen | 456 | NREL_2009 | ClimateZone 4-8 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 13.93 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | 220.5 | 0.1 | 0.2 | 0.7 | PrimarySchool_Kitchen_Gas | 13.13 | 0.25 | 0.3 | 0.2 | PrimarySchool_Kitchen_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool_SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool_Kitchen_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Library | 552 | NREL_2009 | ClimateZone 1-3 | PrimarySchool | Library | 230_196_120 | ASHRAE 189.1-2009 | Library | Reading Area | ASHRAE 189.1-2009LibraryReading Area |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 15 | 0 | 21.36 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Library | 361 | NREL_2009 | ClimateZone 4-8 | PrimarySchool | Library | 230_196_120 | ASHRAE 189.1-2009 | Library | Reading Area | ASHRAE 189.1-2009LibraryReading Area |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 15 | 0 | 21.36 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Lobby | 416 | NREL_2009 | ClimateZone 1-3 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Lobby | 364 | NREL_2009 | ClimateZone 4-8 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Mechanical | 525 | NREL_2009 | ClimateZone 1-3 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Mechanical | 294 | NREL_2009 | ClimateZone 4-8 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Office | 524 | NREL_2009 | ClimateZone 1-3 | PrimarySchool | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Office | 408 | NREL_2009 | ClimateZone 4-8 | PrimarySchool | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_PrimarySchool_Restroom | 170 | NREL_2009 | ClimateZone 1-3 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0595 | PrimarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool_SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
ASHRAE_189.1-2009_ClimateZone 4-8_PrimarySchool_Restroom | 390 | NREL_2009 | ClimateZone 4-8 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool_SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
CBECS_Before-1980_PrimarySchool_Cafeteria | 136 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Cafeteria; 4 4: 31_169_34; 19 11: 3.7; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Food and Beverage Service; 21 20: Cafeteria, fast food; 21 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 66.67; 21 26: PrimarySchool_Cafeteria_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 2.36; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_HtgSetp; 21 41: PrimarySchool_ClgSetp
CBECS_Before-1980_PrimarySchool_Classroom | 68 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Classroom; 4 4: 120_230_199; 19 11: 2.9; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Classroom; 21 21: ASHRAE 62.1-1999EducationClassroom; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 23.22; 21 26: PrimarySchool_Bldg_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 1.39; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_HtgSetp; 21 41: PrimarySchool_ClgSetp
CBECS_Before-1980_PrimarySchool_Corridor | 155 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Corridor; 4 4: 169_31_31; 19 11: 0.7; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Corridors; 21 21: ASHRAE 62.1-1999EducationCorridors; 21 22: 0.1; 21 23: 0; 21 24: 0; 21 25: 9.29; 21 26: PrimarySchool_Bldg_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 0.37; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_BathCorrMechKitchen_HtgSetp; 21 41: PrimarySchool_BathCorrMechKitchenl_ClgSetp
CBECS_Before-1980_PrimarySchool_Gym | 169 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Gym; 4 4: 154_230_120; 19 11: 0.8; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Sports and Amusement; 21 20: Playing floors (gymnasium); 21 21: ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium); 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 27.9; 21 26: PrimarySchool_Gym_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 0.46; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_HtgSetp; 21 41: PrimarySchool_ClgSetp
CBECS_Before-1980_PrimarySchool_Kitchen | 305 | NREL_Before-1980 | ClimateZone 1-8 | PrimarySchool | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 13.93 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.2232 | PrimarySchool_Infil | 302.6 | 0.1 | 0.2 | 0.7 | PrimarySchool_Kitchen_Gas | 17.7 | 0.25 | 0.3 | 0.2 | PrimarySchool_Kitchen_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool_SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool_Kitchen_Exhaust
CBECS_Before-1980_PrimarySchool_Library | 190 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Library; 4 4: 230_196_120; 19 11: 2.9; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Libraries; 21 21: ASHRAE 62.1-1999EducationLibraries; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 21.36; 21 26: PrimarySchool_Bldg_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 1.39; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_HtgSetp; 21 41: PrimarySchool_ClgSetp
CBECS_Before-1980_PrimarySchool_Lobby | 295 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Lobby; 4 4: 230_157_120; 19 11: 1.32; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Corridors; 21 21: ASHRAE 62.1-1999EducationCorridors; 21 22: 0.1; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: PrimarySchool_Bldg_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 0.37; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_HtgSetp; 21 41: PrimarySchool_ClgSetp
CBECS_Before-1980_PrimarySchool_Mechanical | 379 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Mechanical; 4 4: 41_31_169; 19 11: 0.6; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0.93; 21 26: PrimarySchool_Bldg_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 0.37; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_BathCorrMechKitchen_HtgSetp; 21 41: PrimarySchool_BathCorrMechKitchenl_ClgSetp
CBECS_Before-1980_PrimarySchool_Office | 8 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: PrimarySchool; 3 3: Office; 4 4: 120_230_199; 19 11: 2.9; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: PrimarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 4.65; 21 26: PrimarySchool_Bldg_Occ; 21 27: PrimarySchool_Activity; 21 28: 0.2232; 21 29: PrimarySchool_Infil; 21 35: 1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: PrimarySchool_Bldg_Equip; 21 40: PrimarySchool_HtgSetp; 21 41: PrimarySchool_ClgSetp
CBECS_Before-1980_PrimarySchool_Restroom | 148 | NREL_Before-1980 | ClimateZone 1-8 | PrimarySchool | Restroom | 169_169_31 | [6 empty] | 1.08 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.2232 | PrimarySchool_Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool_SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
|  | Xcel EDA 2007 | ClimateZone 1-8 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria, fast food | #N/A | #N/A | #N/A | 66.67 | PrimarySchool_Cafeteria_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 1.72 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2007 | Classroom/Lecture/Training | General | ASHRAE 90.1-2007Classroom/Lecture/TrainingGeneral |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-2007 | Education | Classroom | ASHRAE 62.1-2007EducationClassroom | #N/A | #N/A | #N/A | 23.22 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-2007 | Education | Corridors | ASHRAE 62.1-2007EducationCorridors | #N/A | #N/A | #N/A | 9.29 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | PrimarySchool | Gym | 154_230_120 | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Playing Area | ASHRAE 90.1-2007Gymnasium/Exercise CenterPlaying Area |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-2007 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-2007Sports and AmusementPlaying floors (gymnasium) | #N/A | #N/A | #N/A | 27.9 | PrimarySchool_Gym_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-2007 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-2007Food and Beverage ServiceKitchens (cooking) | #N/A | #N/A | #N/A | 13.93 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | 220.5 | 0.1 | 0.2 | 0.7 | PrimarySchool_Kitchen_Gas | 13.13 | 0.25 | 0.3 | 0.2 | PrimarySchool_Kitchen_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool_SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool_Kitchen_Exhaust
|  | Xcel EDA 2007 | ClimateZone 1-8 | PrimarySchool | Library | 230_196_120 | ASHRAE 90.1-2007 | Library | Reading Area | ASHRAE 90.1-2007LibraryReading Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-2007 | Education | Libraries | ASHRAE 62.1-2007EducationLibraries | #N/A | #N/A | #N/A | 21.36 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-2007 | Education | Corridors | ASHRAE 62.1-2007EducationCorridors | #N/A | #N/A | #N/A | 0 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 0.93 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | PrimarySchool | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-2007 | Offices | Office Space | ASHRAE 62.1-2007OfficesOffice Space | #N/A | #N/A | #N/A | 4.65 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_HtgSetp | PrimarySchool_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | PrimarySchool_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-2007Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | #N/A | #N/A | #N/A | 9.29 | PrimarySchool_Bldg_Occ | PrimarySchool_Activity | 0.0446 | PrimarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool_Bldg_Equip | PrimarySchool_BathCorrMechKitchen_HtgSetp | PrimarySchool_BathCorrMechKitchenl_ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool_SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
CBECS_1980-2004_QuickServiceRestaurant_Dining | 100 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: QuickServiceRestaurant; 3 3: Dining; 4 4: 31_169_34; 19 11: 1.44; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: QuickServiceRestaurant_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Food and Beverage Service; 21 20: Cafeteria, fast food; 21 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 67; 21 26: QuickServiceRestaurant_Bldg_Occ; 21 27: QuickServiceRestaurant_Activity; 21 28: 0.2232; 21 29: QuickServiceRestaurant_Infil_Half_On; 21 35: 12; 21 36: 0.25; 21 37: 0.3; 21 38: 0; 21 39: QuickServiceRestaurant_Bldg_Equip; 21 40: QuickServiceRestaurant_HtgSetp; 21 41: QuickServiceRestaurant_ClgSetp
CBECS_1980-2004_QuickServiceRestaurant_Kitchen | 303 | NREL_1980-2004 | ClimateZone 1-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | [6 empty] | 1.55 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | QuickServiceRestaurant_Bldg_Occ | QuickServiceRestaurant_Activity | 0.2232 | QuickServiceRestaurant_Infil_Half_On | 409.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant_Gas_Equip | 28 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant_Bldg_Equip | QuickServiceRestaurant_HtgSetp_Kitchen | QuickServiceRestaurant_ClgSetp_Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant_SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant_Kitchen_Exhaust
ASHRAE_90.1-2004_QuickServiceRestaurant_Dining | 370 | NREL_2004 | ClimateZone 1-8 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | For Family Dining | ASHRAE 90.1-2004Dining AreaFor Family Dining |  |  | 2.1 |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 67 | QuickServiceRestaurant_Bldg_Occ | QuickServiceRestaurant_Activity | 0.0595 | QuickServiceRestaurant_Infil_Half_On | [5 empty] | 12 | 0.25 | 0.3 | 0 | QuickServiceRestaurant_Bldg_Equip | QuickServiceRestaurant_HtgSetp | QuickServiceRestaurant_ClgSetp
ASHRAE_90.1-2004_QuickServiceRestaurant_Kitchen | 141 | NREL_2004 | ClimateZone 1-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | QuickServiceRestaurant_Bldg_Occ | QuickServiceRestaurant_Activity | 0.0595 | QuickServiceRestaurant_Infil_Half_On | 409.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant_Gas_Equip | 28 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant_Bldg_Equip | QuickServiceRestaurant_HtgSetp_Kitchen | QuickServiceRestaurant_ClgSetp_Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant_SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant_Kitchen_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_QuickServiceRestaurant_Dining | 502 | NREL_2009 | ClimateZone 1-3 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Family Dining | ASHRAE 189.1-2009Dining AreaFor Family Dining |  |  | 1.89 |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 67 | QuickServiceRestaurant_Bldg_Occ | QuickServiceRestaurant_Activity | 0.0595 | QuickServiceRestaurant_Infil_Half_On | [5 empty] | 8.74 | 0.25 | 0.3 | 0 | QuickServiceRestaurant_Bldg_Equip | QuickServiceRestaurant_HtgSetp | QuickServiceRestaurant_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_QuickServiceRestaurant_Dining | 359 | NREL_2009 | ClimateZone 4-8 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Family Dining | ASHRAE 189.1-2009Dining AreaFor Family Dining |  |  | 1.89 |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 67 | QuickServiceRestaurant_Bldg_Occ | QuickServiceRestaurant_Activity | 0.0446 | QuickServiceRestaurant_Infil_Half_On | [5 empty] | 8.74 | 0.25 | 0.3 | 0 | QuickServiceRestaurant_Bldg_Equip | QuickServiceRestaurant_HtgSetp | QuickServiceRestaurant_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_QuickServiceRestaurant_Kitchen | 64 | NREL_2009 | ClimateZone 1-3 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | QuickServiceRestaurant_Bldg_Occ | QuickServiceRestaurant_Activity | 0.0595 | QuickServiceRestaurant_Infil_Half_On | 298.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant_Gas_Equip | 20.4 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant_Bldg_Equip | QuickServiceRestaurant_HtgSetp_Kitchen | QuickServiceRestaurant_ClgSetp_Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant_SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant_Kitchen_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_QuickServiceRestaurant_Kitchen | 187 | NREL_2009 | ClimateZone 4-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | QuickServiceRestaurant_Bldg_Occ | QuickServiceRestaurant_Activity | 0.0446 | QuickServiceRestaurant_Infil_Half_On | 298.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant_Gas_Equip | 20.4 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant_Bldg_Equip | QuickServiceRestaurant_HtgSetp_Kitchen | QuickServiceRestaurant_ClgSetp_Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant_SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant_Kitchen_Exhaust
CBECS_Before-1980_QuickServiceRestaurant_Dining | 290 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: QuickServiceRestaurant; 3 3: Dining; 4 4: 31_169_34; 19 11: 3.7; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: QuickServiceRestaurant_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Food and Beverage Service; 21 20: Cafeteria, fast food; 21 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 67; 21 26: QuickServiceRestaurant_Bldg_Occ; 21 27: QuickServiceRestaurant_Activity; 21 28: 0.2232; 21 29: QuickServiceRestaurant_Infil_Half_On; 21 35: 12; 21 36: 0.25; 21 37: 0.3; 21 38: 0; 21 39: QuickServiceRestaurant_Bldg_Equip; 21 40: QuickServiceRestaurant_HtgSetp; 21 41: QuickServiceRestaurant_ClgSetp
CBECS_Before-1980_QuickServiceRestaurant_Kitchen | 153 | NREL_Before-1980 | ClimateZone 1-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 5 | QuickServiceRestaurant_Bldg_Occ | QuickServiceRestaurant_Activity | 0.2232 | QuickServiceRestaurant_Infil_Half_On | 409.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant_Gas_Equip | 28 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant_Bldg_Equip | QuickServiceRestaurant_HtgSetp_Kitchen | QuickServiceRestaurant_ClgSetp_Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant_SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant_Kitchen_Exhaust
|  | Xcel EDA 2007 | ClimateZone 1-8 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | For Family Dining | ASHRAE 90.1-2007Dining AreaFor Family Dining |  |  | 2.1 |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant_Bldg_Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria, fast food | #N/A | #N/A | #N/A | 67 | QuickServiceRestaurant_Bldg_Occ | QuickServiceRestaurant_Activity | 0.0446 | QuickServiceRestaurant_Infil_Half_On | [5 empty] | 8.74 | 0.25 | 0.3 | 0 | QuickServiceRestaurant_Bldg_Equip | QuickServiceRestaurant_HtgSetp | QuickServiceRestaurant_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant_Bldg_Light | ASHRAE 62.1-2007 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-2007Food and Beverage ServiceKitchens (cooking) | #N/A | #N/A | #N/A | 5 | QuickServiceRestaurant_Bldg_Occ | QuickServiceRestaurant_Activity | 0.0446 | QuickServiceRestaurant_Infil_Half_On | 298.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant_Gas_Equip | 20.4 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant_Bldg_Equip | QuickServiceRestaurant_HtgSetp_Kitchen | QuickServiceRestaurant_ClgSetp_Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant_SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant_Kitchen_Exhaust
CBECS_1980-2004_Retail_Back_Space | 384 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Retail; 3 3: Back_Space; 4 4: 120_149_230; 19 11: 1.17; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Retail_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Storage rooms; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 3.33; 21 26: Retail_Bldg_Occ; 21 27: Retail_Activity; 21 28: 0.2232; 21 29: Retail_Infil_Half_On; 21 35: 0.75; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Retail_Bldg_Equip; 21 40: Retail_HtgSetp; 21 41: Retail_ClgSetp
CBECS_1980-2004_Retail_Entry | 335 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Retail; 3 3: Entry; 4 4: 169_31_31; 19 11: 3.37; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Retail_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Basement and street; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; 21 22: 0.3; 21 23: 0; 21 24: 0; 21 25: 15; 21 26: Retail_Bldg_Occ; 21 27: Retail_Activity; 21 28: 0.2232; 21 29: Retail_Infil_Half_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Retail_Bldg_Equip; 21 40: Retail_HtgSetp; 21 41: Retail_ClgSetp
CBECS_1980-2004_Retail_Point_of_Sale | 81 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Retail; 3 3: Point_of_Sale; 4 4: 171_222_78; 19 11: 3.37; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Retail_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Basement and street; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; 21 22: 0.3; 21 23: 0; 21 24: 0; 21 25: 15; 21 26: Retail_Bldg_Occ; 21 27: Retail_Activity; 21 28: 0.2232; 21 29: Retail_Infil_Half_On; 21 35: 2; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Retail_Bldg_Equip; 21 40: Retail_HtgSetp; 21 41: Retail_ClgSetp
CBECS_1980-2004_Retail_Core | 495 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Retail; 3 3: Retail; 4 4: 171_222_78; 19 11: 3.37; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Retail_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Specialty Shops; 21 20: Clothiers, furniture; 21 21: ASHRAE 62.1-1999Specialty ShopsClothiers, furniture; 21 22: 0.3; 21 23: 0; 21 24: 0; 21 25: 15; 21 26: Retail_Bldg_Occ; 21 27: Retail_Activity; 21 28: 0.2232; 21 29: Retail_Infil_Half_On; 21 35: 0.3; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Retail_Bldg_Equip; 21 40: Retail_HtgSetp; 21 41: Retail_ClgSetp
ASHRAE_90.1-2004_Retail_Back_Space | 488 | NREL_2004 | ClimateZone 1-8 | Retail | Back_Space | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 3.33 | Retail_Bldg_Occ | Retail_Activity | 0.0595 | Retail_Infil_Half_On | [5 empty] | 0.75 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
ASHRAE_90.1-2004_Retail_Entry | 105 | NREL_2004 | ClimateZone 1-8 | Retail | Entry | 169_31_31 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Mall Concourse | ASHRAE 90.1-2004Retail (not including accent lighting)Mall Concourse |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail_Bldg_Occ | Retail_Activity | 0.0595 | Retail_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
ASHRAE_90.1-2004_Retail_Point_of_Sale | 63 | NREL_2004 | ClimateZone 1-8 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail_Bldg_Occ | Retail_Activity | 0.0595 | Retail_Infil_Half_On | [5 empty] | 2 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
ASHRAE_90.1-2004_Retail_Core | 556 | NREL_2004 | ClimateZone 1-8 | Retail | Retail | 171_222_78 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | 0.3 | 0 | 0 | 15 | Retail_Bldg_Occ | Retail_Activity | 0.0595 | Retail_Infil_Half_On | [5 empty] | 0.3 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Retail_Back_Space | 145 | NREL_2009 | ClimateZone 1-3 | Retail | Back_Space | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 3.33 | Retail_Bldg_Occ | Retail_Activity | 0.0595 | Retail_Infil_Half_On | [5 empty] | 0.546 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Retail_Back_Space | 328 | NREL_2009 | ClimateZone 4-8 | Retail | Back_Space | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 3.33 | Retail_Bldg_Occ | Retail_Activity | 0.0446 | Retail_Infil_Half_On | [5 empty] | 0.546 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Retail_Entry | 160 | NREL_2009 | ClimateZone 1-3 | Retail | Entry | 169_31_31 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Mall Concourse | ASHRAE 189.1-2009Retail (not including accent lighting)Mall Concourse |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail_Bldg_Occ | Retail_Activity | 0.0595 | Retail_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
|  | NREL_2009 | ClimateZone 4-8 | Retail | Entry | 169_31_31 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Mall Concourse | ASHRAE 189.1-2009Retail (not including accent lighting)Mall Concourse |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail_Bldg_Occ | Retail_Activity | 0.0446 | Retail_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Retail_Point_of_Sale | 350 | NREL_2009 | ClimateZone 1-3 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail_Bldg_Occ | Retail_Activity | 0.0595 | Retail_Infil_Half_On | [5 empty] | 1.45 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Retail_Point_of_Sale | 353 | NREL_2009 | ClimateZone 4-8 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail_Bldg_Occ | Retail_Activity | 0.0446 | Retail_Infil_Half_On | [5 empty] | 1.45 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Retail_Core | 413 | NREL_2009 | ClimateZone 1-3 | Retail | Retail | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | 0.3 | 0 | 0 | 15 | Retail_Bldg_Occ | Retail_Activity | 0.0595 | Retail_Infil_Half_On | [5 empty] | 0.22 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Retail_Core | 506 | NREL_2009 | ClimateZone 4-8 | Retail | Retail | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | 0.3 | 0 | 0 | 15 | Retail_Bldg_Occ | Retail_Activity | 0.0446 | Retail_Infil_Half_On | [5 empty] | 0.22 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
CBECS_Before-1980_Retail_Back_Space | 434 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Retail; 3 3: Back_Space; 4 4: 120_149_230; 19 11: 0.77; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Retail_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Storage rooms; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 3.33; 21 26: Retail_Bldg_Occ; 21 27: Retail_Activity; 21 28: 0.2232; 21 29: Retail_Infil_Half_On; 21 35: 0.75; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Retail_Bldg_Equip; 21 40: Retail_HtgSetp; 21 41: Retail_ClgSetp
CBECS_Before-1980_Retail_Entry | 156 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Retail; 3 3: Entry; 4 4: 169_31_31; 19 11: 5.04; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Retail_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Basement and street; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; 21 22: 0.3; 21 23: 0; 21 24: 0; 21 25: 15; 21 26: Retail_Bldg_Occ; 21 27: Retail_Activity; 21 28: 0.2232; 21 29: Retail_Infil_Half_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Retail_Bldg_Equip; 21 40: Retail_HtgSetp; 21 41: Retail_ClgSetp
CBECS_Before-1980_Retail_Point_of_Sale | 317 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Retail; 3 3: Point_of_Sale; 4 4: 171_222_78; 19 11: 5.04; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Retail_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Basement and street; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; 21 22: 0.3; 21 23: 0; 21 24: 0; 21 25: 15; 21 26: Retail_Bldg_Occ; 21 27: Retail_Activity; 21 28: 0.2232; 21 29: Retail_Infil_Half_On; 21 35: 2; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Retail_Bldg_Equip; 21 40: Retail_HtgSetp; 21 41: Retail_ClgSetp
CBECS_Before-1980_Retail_Core | 445 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Retail; 3 3: Retail; 4 4: 171_222_78; 19 11: 5.04; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: Retail_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Specialty Shops; 21 20: Clothiers, furniture; 21 21: ASHRAE 62.1-1999Specialty ShopsClothiers, furniture; 21 22: 0.3; 21 23: 0; 21 24: 0; 21 25: 15; 21 26: Retail_Bldg_Occ; 21 27: Retail_Activity; 21 28: 0.2232; 21 29: Retail_Infil_Half_On; 21 35: 0.3; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Retail_Bldg_Equip; 21 40: Retail_HtgSetp; 21 41: Retail_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Retail | Back_Space | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-2007 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-2007Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | #N/A | #N/A | #N/A | 3.33 | Retail_Bldg_Occ | Retail_Activity | 0.0446 | Retail_Infil_Half_On | [5 empty] | 0.546 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Retail | Entry | 169_31_31 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Mall Concourse | ASHRAE 90.1-2007Retail (not including accent lighting)Mall Concourse |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-2007 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-2007Retail Stores, Sales Floors, and Show Room FloorsBasement and street | #N/A | #N/A | #N/A | 15 | Retail_Bldg_Occ | Retail_Activity | 0.0446 | Retail_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-2007 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-2007Retail Stores, Sales Floors, and Show Room FloorsBasement and street | #N/A | #N/A | #N/A | 15 | Retail_Bldg_Occ | Retail_Activity | 0.0446 | Retail_Infil_Half_On | [5 empty] | 1.45 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Retail | Retail | 171_222_78 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | Retail_Bldg_Light | ASHRAE 62.1-2007 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-2007Specialty ShopsClothiers, furniture | #N/A | #N/A | #N/A | 15 | Retail_Bldg_Occ | Retail_Activity | 0.0446 | Retail_Infil_Half_On | [5 empty] | 0.22 | 0 | 0.5 | 0 | Retail_Bldg_Equip | Retail_HtgSetp | Retail_ClgSetp
CBECS_1980-2004_SecondarySchool_Auditorium | 534 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Auditorium; 4 4: 230_196_120; 19 11: 1.12; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Auditorium; 21 21: ASHRAE 62.1-1999EducationAuditorium; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 92.94; 21 26: SecondarySchool_Auditorium_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 0.46; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp; 21 41: SecondarySchool_ClgSetp
CBECS_1980-2004_SecondarySchool_Cafeteria | 79 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Cafeteria; 4 4: 31_169_34; 19 11: 1.34; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Food and Beverage Service; 21 20: Cafeteria, fast food; 21 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 66.84; 21 26: SecondarySchool_Bldg_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 1.79; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp; 21 41: SecondarySchool_ClgSetp
CBECS_1980-2004_SecondarySchool_Classroom | 197 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Classroom; 4 4: 120_230_199; 19 11: 2; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Classroom; 21 21: ASHRAE 62.1-1999EducationClassroom; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 23.22; 21 26: SecondarySchool_Bldg_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 0.93; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp; 21 41: SecondarySchool_ClgSetp
CBECS_1980-2004_SecondarySchool_Corridor | 555 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Corridor; 4 4: 169_31_31; 19 11: 0.86; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Corridors; 21 21: ASHRAE 62.1-1999EducationCorridors; 21 22: 0.1; 21 23: 0; 21 24: 0; 21 25: 9.31; 21 26: SecondarySchool_Bldg_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 0.37; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp_BathCorrMechKitchen; 21 41: SecondarySchool_ClgSetp_BathCorrMechKitchen
CBECS_1980-2004_SecondarySchool_Gym | 522 | NREL_1980-2004 | ClimateZone 1-8 | SecondarySchool | Gym | 154_230_120 | [6 empty] | 1.06 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 92.94 | SecondarySchool_Gym_Occ | SecondarySchool_Activity | 0.2232 | SecondarySchool_Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool_SWH_Showers
CBECS_1980-2004_SecondarySchool_Kitchen | 439 | NREL_1980-2004 | ClimateZone 1-8 | SecondarySchool | Kitchen | 78_222_133 | [6 empty] | 1.56 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 15.48 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.2232 | SecondarySchool_Infil | 354.9 | 0.1 | 0.2 | 0.7 | SecondarySchool_Kitchen_Gas | 20.65 | 0.25 | 0.3 | 0.2 | SecondarySchool_Kitchen_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool_SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool_Kitchen_Exhaust
CBECS_1980-2004_SecondarySchool_Library | 549 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Library; 4 4: 230_196_120; 19 11: 1.52; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Libraries; 21 21: ASHRAE 62.1-1999EducationLibraries; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 21.34; 21 26: SecondarySchool_Bldg_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 0.93; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp; 21 41: SecondarySchool_ClgSetp
CBECS_1980-2004_SecondarySchool_Lobby | 497 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Lobby; 4 4: 230_157_120; 19 11: 1.12; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Corridors; 21 21: ASHRAE 62.1-1999EducationCorridors; 21 22: 0.1; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: SecondarySchool_Bldg_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 0.37; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp; 21 41: SecondarySchool_ClgSetp
CBECS_1980-2004_SecondarySchool_Mechanical | 326 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Mechanical; 4 4: 41_31_169; 19 11: 0.75; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0.93; 21 26: SecondarySchool_Bldg_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 0.37; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp_BathCorrMechKitchen; 21 41: SecondarySchool_ClgSetp_BathCorrMechKitchen
CBECS_1980-2004_SecondarySchool_Office | 443 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Office; 4 4: 120_230_199; 19 11: 1.87; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 4.65; 21 26: SecondarySchool_Office_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp; 21 41: SecondarySchool_ClgSetp
CBECS_1980-2004_SecondarySchool_Restroom | 436 | NREL_1980-2004 | ClimateZone 1-8 | SecondarySchool | Restroom | 169_169_31 | [6 empty] | 0.89 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.2232 | SecondarySchool_Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool_SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
ASHRAE_90.1-2004_SecondarySchool_Auditorium | 454 | NREL_2004 | ClimateZone 1-8 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 90.1-2004 | Audience/Seating Area | General | ASHRAE 90.1-2004Audience/Seating AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Auditorium | ASHRAE 62.1-1999EducationAuditorium | 0 | 15 | 0 | 92.94 | SecondarySchool_Auditorium_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_90.1-2004_SecondarySchool_Cafeteria | 459 | NREL_2004 | ClimateZone 1-8 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 66.84 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 1.79 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_90.1-2004_SecondarySchool_Classroom | 419 | NREL_2004 | ClimateZone 1-8 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2004 | Classroom/Lecture/Training | General | ASHRAE 90.1-2004Classroom/Lecture/TrainingGeneral |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 15 | 0 | 23.22 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.93 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_90.1-2004_SecondarySchool_Corridor | 284 | NREL_2004 | ClimateZone 1-8 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.31 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen
ASHRAE_90.1-2004_SecondarySchool_Gym | 283 | NREL_2004 | ClimateZone 1-8 | SecondarySchool | Gym | 154_230_120 | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Playing Area | ASHRAE 90.1-2004Gymnasium/Exercise CenterPlaying Area |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 92.94 | SecondarySchool_Gym_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool_SWH_Showers
ASHRAE_90.1-2004_SecondarySchool_Kitchen | 385 | NREL_2004 | ClimateZone 1-8 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 15.48 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | 354.9 | 0.1 | 0.2 | 0.7 | SecondarySchool_Kitchen_Gas | 20.65 | 0.25 | 0.3 | 0.2 | SecondarySchool_Kitchen_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool_SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool_Kitchen_Exhaust
ASHRAE_90.1-2004_SecondarySchool_Library | 159 | NREL_2004 | ClimateZone 1-8 | SecondarySchool | Library | 230_196_120 | ASHRAE 90.1-2004 | Library | Reading Area | ASHRAE 90.1-2004LibraryReading Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 15 | 0 | 21.34 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.93 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_90.1-2004_SecondarySchool_Lobby | 58 | NREL_2004 | ClimateZone 1-8 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_90.1-2004_SecondarySchool_Mechanical | 494 | NREL_2004 | ClimateZone 1-8 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen
ASHRAE_90.1-2004_SecondarySchool_Office | 521 | NREL_2004 | ClimateZone 1-8 | SecondarySchool | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | SecondarySchool_Office_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 1 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_90.1-2004_SecondarySchool_Restroom | 275 | NREL_2004 | ClimateZone 1-8 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool_SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Auditorium | 273 | NREL_2009 | ClimateZone 1-3 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 189.1-2009 | Audience/Seating Area | General | ASHRAE 189.1-2009Audience/Seating AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Auditorium | ASHRAE 62.1-1999EducationAuditorium | 0 | 15 | 0 | 92.94 | SecondarySchool_Auditorium_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Auditorium | 253 | NREL_2009 | ClimateZone 4-8 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 189.1-2009 | Audience/Seating Area | General | ASHRAE 189.1-2009Audience/Seating AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Auditorium | ASHRAE 62.1-1999EducationAuditorium | 0 | 15 | 0 | 92.94 | SecondarySchool_Auditorium_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Cafeteria | 69 | NREL_2009 | ClimateZone 1-3 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 66.84 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Cafeteria | 424 | NREL_2009 | ClimateZone 4-8 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 | 0 | 66.84 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Classroom | 120 | NREL_2009 | ClimateZone 1-3 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 15 | 0 | 23.22 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Classroom | 382 | NREL_2009 | ClimateZone 4-8 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 15 | 0 | 23.22 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Corridor | 211 | NREL_2009 | ClimateZone 1-3 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.31 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Corridor | 112 | NREL_2009 | ClimateZone 4-8 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.31 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Gym | 174 | NREL_2009 | ClimateZone 1-3 | SecondarySchool | Gym | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 92.94 | SecondarySchool_Gym_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool_SWH_Showers
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Gym | 233 | NREL_2009 | ClimateZone 4-8 | SecondarySchool | Gym | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 92.94 | SecondarySchool_Gym_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool_SWH_Showers
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Kitchen | 349 | NREL_2009 | ClimateZone 1-3 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 15.48 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | 258.6 | 0.1 | 0.2 | 0.7 | SecondarySchool_Kitchen_Gas | 15.05 | 0.25 | 0.3 | 0.2 | SecondarySchool_Kitchen_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool_SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool_Kitchen_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Kitchen | 531 | NREL_2009 | ClimateZone 4-8 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 15.48 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | 258.6 | 0.1 | 0.2 | 0.7 | SecondarySchool_Kitchen_Gas | 15.05 | 0.25 | 0.3 | 0.2 | SecondarySchool_Kitchen_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool_SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool_Kitchen_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Library | 513 | NREL_2009 | ClimateZone 1-3 | SecondarySchool | Library | 230_196_120 | ASHRAE 189.1-2009 | Library | Reading Area | ASHRAE 189.1-2009LibraryReading Area |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 15 | 0 | 21.34 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Library | 256 | NREL_2009 | ClimateZone 4-8 | SecondarySchool | Library | 230_196_120 | ASHRAE 189.1-2009 | Library | Reading Area | ASHRAE 189.1-2009LibraryReading Area |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 15 | 0 | 21.34 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Lobby | 505 | NREL_2009 | ClimateZone 1-3 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Lobby | 332 | NREL_2009 | ClimateZone 4-8 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Mechanical | 98 | NREL_2009 | ClimateZone 1-3 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen | SecondarySchool_BathCorrMechKitchen_HtgSetp |  | #VALUE!
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Mechanical | 263 | NREL_2009 | ClimateZone 4-8 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Office | 334 | NREL_2009 | ClimateZone 1-3 | SecondarySchool | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | SecondarySchool_Office_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Office | 469 | NREL_2009 | ClimateZone 4-8 | SecondarySchool | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 4.65 | SecondarySchool_Office_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SecondarySchool_Restroom | 504 | NREL_2009 | ClimateZone 1-3 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0595 | SecondarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool_SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
ASHRAE_189.1-2009_ClimateZone 4-8_SecondarySchool_Restroom | 94 | NREL_2009 | ClimateZone 4-8 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool_SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
CBECS_Before-1980_SecondarySchool_Auditorium | 511 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Auditorium; 4 4: 230_196_120; 19 11: 1.45; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Auditorium; 21 21: ASHRAE 62.1-1999EducationAuditorium; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 92.94; 21 26: SecondarySchool_Auditorium_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 0.46; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp; 21 41: SecondarySchool_ClgSetp
CBECS_Before-1980_SecondarySchool_Cafeteria | 426 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Cafeteria; 4 4: 31_169_34; 19 11: 3.7; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Food and Beverage Service; 21 20: Cafeteria, fast food; 21 21: ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 66.84; 21 26: SecondarySchool_Bldg_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 1.79; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp; 21 41: SecondarySchool_ClgSetp
CBECS_Before-1980_SecondarySchool_Classroom | 358 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Classroom; 4 4: 120_230_199; 19 11: 2.9; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Classroom; 21 21: ASHRAE 62.1-1999EducationClassroom; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 23.22; 21 26: SecondarySchool_Bldg_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 0.93; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp; 21 41: SecondarySchool_ClgSetp
CBECS_Before-1980_SecondarySchool_Corridor | 124 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Corridor; 4 4: 169_31_31; 19 11: 0.7; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Corridors; 21 21: ASHRAE 62.1-1999EducationCorridors; 21 22: 0.1; 21 23: 0; 21 24: 0; 21 25: 9.31; 21 26: SecondarySchool_Bldg_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 0.37; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp_BathCorrMechKitchen; 21 41: SecondarySchool_ClgSetp_BathCorrMechKitchen
CBECS_Before-1980_SecondarySchool_Gym | 343 | NREL_Before-1980 | ClimateZone 1-8 | SecondarySchool | Gym | 154_230_120 | [6 empty] | 0.8 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 92.94 | SecondarySchool_Gym_Occ | SecondarySchool_Activity | 0.2232 | SecondarySchool_Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool_SWH_Showers
CBECS_Before-1980_SecondarySchool_Kitchen | 278 | NREL_Before-1980 | ClimateZone 1-8 | SecondarySchool | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 | 0 | 15.48 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.2232 | SecondarySchool_Infil | 354.9 | 0.1 | 0.2 | 0.7 | SecondarySchool_Kitchen_Gas | 20.65 | 0.25 | 0.3 | 0.2 | SecondarySchool_Kitchen_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool_SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool_Kitchen_Exhaust
CBECS_Before-1980_SecondarySchool_Library | 414 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Library; 4 4: 230_196_120; 19 11: 2.9; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Libraries; 21 21: ASHRAE 62.1-1999EducationLibraries; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 21.34; 21 26: SecondarySchool_Bldg_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 0.93; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp; 21 41: SecondarySchool_ClgSetp
CBECS_Before-1980_SecondarySchool_Lobby | 241 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Lobby; 4 4: 230_157_120; 19 11: 1.32; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Education; 21 20: Corridors; 21 21: ASHRAE 62.1-1999EducationCorridors; 21 22: 0.1; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: SecondarySchool_Bldg_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 0.37; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp; 21 41: SecondarySchool_ClgSetp
CBECS_Before-1980_SecondarySchool_Mechanical | 232 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Mechanical; 4 4: 41_31_169; 19 11: 0.6; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0.93; 21 26: SecondarySchool_Bldg_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 0.37; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp_BathCorrMechKitchen; 21 41: SecondarySchool_ClgSetp_BathCorrMechKitchen
CBECS_Before-1980_SecondarySchool_Office | 336 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SecondarySchool; 3 3: Office; 4 4: 120_230_199; 19 11: 2.9; 21 14: 0; 21 15: 0.37; 21 16: 0.2; 21 17: SecondarySchool_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 4.65; 21 26: SecondarySchool_Office_Occ; 21 27: SecondarySchool_Activity; 21 28: 0.2232; 21 29: SecondarySchool_Infil; 21 35: 1; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SecondarySchool_Bldg_Equip; 21 40: SecondarySchool_HtgSetp; 21 41: SecondarySchool_ClgSetp
CBECS_Before-1980_SecondarySchool_Restroom | 181 | NREL_Before-1980 | ClimateZone 1-8 | SecondarySchool | Restroom | 169_169_31 | [6 empty] | 1.08 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.2232 | SecondarySchool_Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool_SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
|  | Xcel EDA 2007 | ClimateZone 1-8 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 90.1-2007 | Audience/Seating Area | General | ASHRAE 90.1-2007Audience/Seating AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-2007 | Education | Auditorium | ASHRAE 62.1-2007EducationAuditorium | #N/A | #N/A | #N/A | 92.94 | SecondarySchool_Auditorium_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria, fast food | #N/A | #N/A | #N/A | 66.84 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2007 | Classroom/Lecture/Training | General | ASHRAE 90.1-2007Classroom/Lecture/TrainingGeneral |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-2007 | Education | Classroom | ASHRAE 62.1-2007EducationClassroom | #N/A | #N/A | #N/A | 23.22 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-2007 | Education | Corridors | ASHRAE 62.1-2007EducationCorridors | #N/A | #N/A | #N/A | 9.31 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen
|  | Xcel EDA 2007 | ClimateZone 1-8 | SecondarySchool | Gym | 154_230_120 | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Playing Area | ASHRAE 90.1-2007Gymnasium/Exercise CenterPlaying Area |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-2007 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-2007Sports and AmusementPlaying floors (gymnasium) | #N/A | #N/A | #N/A | 92.94 | SecondarySchool_Gym_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool_SWH_Showers
|  | Xcel EDA 2007 | ClimateZone 1-8 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-2007 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-2007Food and Beverage ServiceKitchens (cooking) | #N/A | #N/A | #N/A | 15.48 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | 258.6 | 0.1 | 0.2 | 0.7 | SecondarySchool_Kitchen_Gas | 15.05 | 0.25 | 0.3 | 0.2 | SecondarySchool_Kitchen_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool_SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool_Kitchen_Exhaust
|  | Xcel EDA 2007 | ClimateZone 1-8 | SecondarySchool | Library | 230_196_120 | ASHRAE 90.1-2007 | Library | Reading Area | ASHRAE 90.1-2007LibraryReading Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-2007 | Education | Libraries | ASHRAE 62.1-2007EducationLibraries | #N/A | #N/A | #N/A | 21.34 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-2007 | Education | Corridors | ASHRAE 62.1-2007EducationCorridors | #N/A | #N/A | #N/A | 0 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 0.93 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen
|  | Xcel EDA 2007 | ClimateZone 1-8 | SecondarySchool | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-2007 | Offices | Office Space | ASHRAE 62.1-2007OfficesOffice Space | #N/A | #N/A | #N/A | 4.65 | SecondarySchool_Office_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp | SecondarySchool_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-2007Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | #N/A | #N/A | #N/A | 9.29 | SecondarySchool_Bldg_Occ | SecondarySchool_Activity | 0.0446 | SecondarySchool_Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool_Bldg_Equip | SecondarySchool_HtgSetp_BathCorrMechKitchen | SecondarySchool_ClgSetp_BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool_SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
CBECS_1980-2004_SmallHotel_Corridor | 234 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: Corridor; 4 4: 169_31_31; 19 11: 0.88; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: SmallHotel_Bldg_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_Bldg_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
CBECS_1980-2004_SmallHotel_Exercise | 269 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: Exercise; 4 4: 154_230_120; 19 11: 1.37; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_Exercise_Light; 21 18: ASHRAE 62.1-1999; 21 19: Sports and Amusement; 21 20: Playing floors (gymnasium); 21 21: ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium); 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 30; 21 26: SmallHotel_Exercise_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 1.07; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_Exercise_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
CBECS_1980-2004_SmallHotel_GuestLounge | 262 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: GuestLounge; 4 4: 230_157_120; 19 11: 1.31; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Lobbies; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 30; 21 26: SmallHotel_Bldg_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 1.43; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_Bldg_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
CBECS_1980-2004_SmallHotel_GuestRoom | 250 | NREL_1980-2004 | ClimateZone 1-8 | SmallHotel | GuestRoom | 78_167_222 | [6 empty] | 1.92 |  |  | 0 | 0.7 | 0.2 | SmallHotel_GuestRoom_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 4.27 | SmallHotel_GuestRoom_Occ | SmallHotel_Activity | 0.2232 | SmallHotel_Infil_Half_On | [5 empty] | 1.33 | 0 | 0.5 | 0 | SmallHotel_GuestRoom_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel_SWH_GuestRoom
CBECS_1980-2004_SmallHotel_Laundry | 132 | NREL_1980-2004 | ClimateZone 1-8 | SmallHotel | Laundry | 120_149_230 | [6 empty] | 1.04 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Laundry_Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 10 | SmallHotel_Laundry_Occ | SmallHotel_Activity | 0.2232 | SmallHotel_Infil_Half_On | 58.4 |  |  |  | SmallHotel_Laundry_Gas | 2.03 | 0 | 0.5 | 0 | SmallHotel_Laundry_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel_SWH_Laundry
CBECS_1980-2004_SmallHotel_Mechanical | 309 | NREL_1980-2004 | ClimateZone 1-8 | SmallHotel | Mechanical | 41_31_169 | [6 empty] | 0.96 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.2232 | SmallHotel_Infil_Half_On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
CBECS_1980-2004_SmallHotel_Meeting | 40 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: Meeting; 4 4: 230_196_120; 19 11: 2.13; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_Meeting_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Conference rooms; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 50; 21 26: SmallHotel_Meeting_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 1.2; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_Meeting_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
CBECS_1980-2004_SmallHotel_Office | 21 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: Office; 4 4: 120_230_199; 19 11: 2.01; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_Office_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 7.14; 21 26: SmallHotel_Office_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 1.2; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_Office_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
CBECS_1980-2004_SmallHotel_PublicRestroom | 377 | NREL_1980-2004 | ClimateZone 1-8 | SmallHotel | PublicRestroom | 169_169_31 | [6 empty] | 1.1 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 2.85 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.2232 | SmallHotel_Infil_Half_On | [5 empty] | 1 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
CBECS_1980-2004_SmallHotel_StaffLounge | 498 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: StaffLounge; 4 4: 31_169_34; 19 11: 1.65; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_StaffLounge_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Lobbies; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 30; 21 26: SmallHotel_StaffLounge_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 7.17; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_StaffLounge_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
CBECS_1980-2004_SmallHotel_Stair | 61 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: Stair; 4 4: 230_157_120; 19 11: 0.82; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: SmallHotel_Bldg_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_Bldg_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
CBECS_1980-2004_SmallHotel_Storage | 383 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: Storage; 4 4: 120_149_230; 19 11: 0.45; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_Storage_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Shipping and receiving; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: SmallHotel_Bldg_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_Bldg_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
ASHRAE_90.1-2004_SmallHotel_Corridor | 259 | NREL_2004 | ClimateZone 1-8 | SmallHotel | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_90.1-2004_SmallHotel_Exercise | 399 | NREL_2004 | ClimateZone 1-8 | SmallHotel | Exercise | 154_230_120 | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 90.1-2004Gymnasium/Exercise CenterExercise Area |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Exercise_Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 30 | SmallHotel_Exercise_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 1.07 | 0 | 0.5 | 0 | SmallHotel_Exercise_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_90.1-2004_SmallHotel_GuestLounge | 180 | NREL_2004 | ClimateZone 1-8 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 90.1-2004 | Lounge/Recreation | General | ASHRAE 90.1-2004Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 1.43 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_90.1-2004_SmallHotel_GuestRoom | 528 | NREL_2004 | ClimateZone 1-8 | SmallHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2004 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2004Hotel/MotelGuest Rooms |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | SmallHotel_GuestRoom_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 4.27 | SmallHotel_GuestRoom_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 1.33 | 0 | 0.5 | 0 | SmallHotel_GuestRoom_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel_SWH_GuestRoom
ASHRAE_90.1-2004_SmallHotel_Laundry | 489 | NREL_2004 | ClimateZone 1-8 | SmallHotel | Laundry | 120_149_230 | ASHRAE 90.1-2004 | Hospital | Laundry-Washing | ASHRAE 90.1-2004HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Laundry_Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 10 | SmallHotel_Laundry_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | 58.4 |  |  |  | SmallHotel_Laundry_Gas | 2.03 | 0 | 0.5 | 0 | SmallHotel_Laundry_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel_SWH_Laundry
ASHRAE_90.1-2004_SmallHotel_Mechanical | 432 | NREL_2004 | ClimateZone 1-8 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_90.1-2004_SmallHotel_Meeting | 198 | NREL_2004 | ClimateZone 1-8 | SmallHotel | Meeting | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Meeting_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 50 | SmallHotel_Meeting_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 1.2 | 0 | 0.5 | 0 | SmallHotel_Meeting_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_90.1-2004_SmallHotel_Office | 93 | NREL_2004 | ClimateZone 1-8 | SmallHotel | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Office_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 7.14 | SmallHotel_Office_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 1.2 | 0 | 0.5 | 0 | SmallHotel_Office_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_90.1-2004_SmallHotel_PublicRestroom | 366 | NREL_2004 | ClimateZone 1-8 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 2.85 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 1 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
ASHRAE_90.1-2004_SmallHotel_StaffLounge | 442 | NREL_2004 | ClimateZone 1-8 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 90.1-2004 | Lounge/Recreation | General | ASHRAE 90.1-2004Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | SmallHotel_StaffLounge_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel_StaffLounge_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 7.17 | 0 | 0.5 | 0 | SmallHotel_StaffLounge_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_90.1-2004_SmallHotel_Stair | 533 | NREL_2004 | ClimateZone 1-8 | SmallHotel | Stair | 230_157_120 | ASHRAE 90.1-2004 | Stairs-Active | General | ASHRAE 90.1-2004Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_90.1-2004_SmallHotel_Storage | 374 | NREL_2004 | ClimateZone 1-8 | SmallHotel | Storage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Storage_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Corridor | 3 | NREL_2009 | ClimateZone 1-3 | SmallHotel | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Corridor | 261 | NREL_2009 | ClimateZone 4-8 | SmallHotel | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Exercise | 89 | NREL_2009 | ClimateZone 1-3 | SmallHotel | Exercise | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterExercise Area |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Exercise_Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 30 | SmallHotel_Exercise_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 0.55 | 0 | 0.5 | 0 | SmallHotel_Exercise_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Exercise | 167 | NREL_2009 | ClimateZone 4-8 | SmallHotel | Exercise | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterExercise Area |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Exercise_Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 | 0 | 30 | SmallHotel_Exercise_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0.55 | 0 | 0.5 | 0 | SmallHotel_Exercise_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_GuestLounge | 557 | NREL_2009 | ClimateZone 1-3 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 0.73 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_GuestLounge | 540 | NREL_2009 | ClimateZone 4-8 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0.73 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_GuestRoom | 254 | NREL_2009 | ClimateZone 1-3 | SmallHotel | GuestRoom | 78_167_222 | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | ASHRAE 189.1-2009Hotel/MotelGuest Rooms |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SmallHotel_GuestRoom_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 4.27 | SmallHotel_GuestRoom_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 0.68 | 0 | 0.5 | 0 | SmallHotel_GuestRoom_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel_SWH_GuestRoom
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_GuestRoom | 372 | NREL_2009 | ClimateZone 4-8 | SmallHotel | GuestRoom | 78_167_222 | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | ASHRAE 189.1-2009Hotel/MotelGuest Rooms |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SmallHotel_GuestRoom_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 4.27 | SmallHotel_GuestRoom_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0.68 | 0 | 0.5 | 0 | SmallHotel_GuestRoom_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel_SWH_GuestRoom
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Laundry | 340 | NREL_2009 | ClimateZone 1-3 | SmallHotel | Laundry | 120_149_230 | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | ASHRAE 189.1-2009HospitalLaundry-Washing |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Laundry_Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 10 | SmallHotel_Laundry_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | 42.6 |  |  |  | SmallHotel_Laundry_Gas | 1.04 | 0 | 0.5 | 0 | SmallHotel_Laundry_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel_SWH_Laundry
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Laundry | 312 | NREL_2009 | ClimateZone 4-8 | SmallHotel | Laundry | 120_149_230 | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | ASHRAE 189.1-2009HospitalLaundry-Washing |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Laundry_Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 10 | SmallHotel_Laundry_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | 42.6 |  |  |  | SmallHotel_Laundry_Gas | 1.04 | 0 | 0.5 | 0 | SmallHotel_Laundry_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel_SWH_Laundry
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Mechanical | 394 | NREL_2009 | ClimateZone 1-3 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Mechanical | 404 | NREL_2009 | ClimateZone 4-8 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Meeting | 356 | NREL_2009 | ClimateZone 1-3 | SmallHotel | Meeting | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Meeting_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 50 | SmallHotel_Meeting_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel_Meeting_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Meeting | 406 | NREL_2009 | ClimateZone 4-8 | SmallHotel | Meeting | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Meeting_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 50 | SmallHotel_Meeting_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel_Meeting_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Office | 381 | NREL_2009 | ClimateZone 1-3 | SmallHotel | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Office_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 7.14 | SmallHotel_Office_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel_Office_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Office | 491 | NREL_2009 | ClimateZone 4-8 | SmallHotel | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Office_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 7.14 | SmallHotel_Office_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel_Office_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_PublicRestroom | 2 | NREL_2009 | ClimateZone 1-3 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 2.85 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 0.51 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_PublicRestroom | 430 | NREL_2009 | ClimateZone 4-8 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 2.85 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0.51 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_StaffLounge | 176 | NREL_2009 | ClimateZone 1-3 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | SmallHotel_StaffLounge_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel_StaffLounge_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 3.67 | 0 | 0.5 | 0 | SmallHotel_StaffLounge_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_StaffLounge | 199 | NREL_2009 | ClimateZone 4-8 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | SmallHotel_StaffLounge_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel_StaffLounge_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 3.67 | 0 | 0.5 | 0 | SmallHotel_StaffLounge_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Stair | 227 | NREL_2009 | ClimateZone 1-3 | SmallHotel | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Stair | 485 | NREL_2009 | ClimateZone 4-8 | SmallHotel | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SmallHotel_Storage | 483 | NREL_2009 | ClimateZone 1-3 | SmallHotel | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Storage_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0595 | SmallHotel_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SmallHotel_Storage | 477 | NREL_2009 | ClimateZone 4-8 | SmallHotel | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Storage_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
CBECS_Before-1980_SmallHotel_Corridor | 35 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: Corridor; 4 4: 169_31_31; 19 11: 0.88; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: SmallHotel_Bldg_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_Bldg_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
CBECS_Before-1980_SmallHotel_Exercise | 500 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: Exercise; 4 4: 154_230_120; 19 11: 1.37; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_Exercise_Light; 21 18: ASHRAE 62.1-1999; 21 19: Sports and Amusement; 21 20: Playing floors (gymnasium); 21 21: ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium); 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 30; 21 26: SmallHotel_Exercise_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 1.07; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_Exercise_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
CBECS_Before-1980_SmallHotel_GuestLounge | 387 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: GuestLounge; 4 4: 230_157_120; 19 11: 1.31; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Lobbies; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 30; 21 26: SmallHotel_Bldg_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 1.43; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_Bldg_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
CBECS_Before-1980_SmallHotel_GuestRoom | 520 | NREL_Before-1980 | ClimateZone 1-8 | SmallHotel | GuestRoom | 78_167_222 | [6 empty] | 1.92 |  |  | 0 | 0.7 | 0.2 | SmallHotel_GuestRoom_Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 4.27 | SmallHotel_GuestRoom_Occ | SmallHotel_Activity | 0.2232 | SmallHotel_Infil_Half_On | [5 empty] | 1.33 | 0 | 0.5 | 0 | SmallHotel_GuestRoom_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel_SWH_GuestRoom
CBECS_Before-1980_SmallHotel_Laundry | 427 | NREL_Before-1980 | ClimateZone 1-8 | SmallHotel | Laundry | 120_149_230 | [6 empty] | 1.04 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Laundry_Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 10 | SmallHotel_Laundry_Occ | SmallHotel_Activity | 0.2232 | SmallHotel_Infil_Half_On | 58.4 |  |  |  | SmallHotel_Laundry_Gas | 2.03 | 0 | 0.5 | 0 | SmallHotel_Laundry_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel_SWH_Laundry
CBECS_Before-1980_SmallHotel_Mechanical | 316 | NREL_Before-1980 | ClimateZone 1-8 | SmallHotel | Mechanical | 41_31_169 | [6 empty] | 0.96 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.2232 | SmallHotel_Infil_Half_On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
CBECS_Before-1980_SmallHotel_Meeting | 267 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: Meeting; 4 4: 230_196_120; 19 11: 2.13; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_Meeting_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Conference rooms; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 50; 21 26: SmallHotel_Meeting_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 1.2; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_Meeting_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
CBECS_Before-1980_SmallHotel_Office | 186 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: Office; 4 4: 120_230_199; 19 11: 2.01; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_Office_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 7.14; 21 26: SmallHotel_Office_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 1.2; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_Office_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
CBECS_Before-1980_SmallHotel_PublicRestroom | 202 | NREL_Before-1980 | ClimateZone 1-8 | SmallHotel | PublicRestroom | 169_169_31 | [6 empty] | 1.1 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 2.85 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.2232 | SmallHotel_Infil_Half_On | [5 empty] | 1 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
CBECS_Before-1980_SmallHotel_StaffLounge | 130 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: StaffLounge; 4 4: 31_169_34; 19 11: 1.65; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_StaffLounge_Light; 21 18: ASHRAE 62.1-1999; 21 19: Hotels, Motels, Resorts, Dormitories; 21 20: Lobbies; 21 21: ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 30; 21 26: SmallHotel_StaffLounge_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 7.17; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_StaffLounge_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
CBECS_Before-1980_SmallHotel_Stair | 119 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: Stair; 4 4: 230_157_120; 19 11: 0.82; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Public Spaces; 21 20: Corridors and utilities; 21 21: ASHRAE 62.1-1999Public SpacesCorridors and utilities; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: SmallHotel_Bldg_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_Bldg_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
CBECS_Before-1980_SmallHotel_Storage | 447 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SmallHotel; 3 3: Storage; 4 4: 120_149_230; 19 11: 0.45; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SmallHotel_Storage_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Shipping and receiving; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: SmallHotel_Bldg_Occ; 21 27: SmallHotel_Activity; 21 28: 0.2232; 21 29: SmallHotel_Infil_Half_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SmallHotel_Bldg_Equip; 21 40: SmallHotel_HtgSetp; 21 41: SmallHotel_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SmallHotel | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SmallHotel | Exercise | 154_230_120 | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 90.1-2007Gymnasium/Exercise CenterExercise Area |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Exercise_Light | ASHRAE 62.1-2007 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-2007Sports and AmusementPlaying floors (gymnasium) | #N/A | #N/A | #N/A | 30 | SmallHotel_Exercise_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0.55 | 0 | 0.5 | 0 | SmallHotel_Exercise_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 90.1-2007 | Lounge/Recreation | General | ASHRAE 90.1-2007Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies | #N/A | #N/A | #N/A | 30 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0.73 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SmallHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2007 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2007Hotel/MotelGuest Rooms |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | SmallHotel_GuestRoom_Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies | #N/A | #N/A | #N/A | 4.27 | SmallHotel_GuestRoom_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0.68 | 0 | 0.5 | 0 | SmallHotel_GuestRoom_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel_SWH_GuestRoom
|  | Xcel EDA 2007 | ClimateZone 1-8 | SmallHotel | Laundry | 120_149_230 | ASHRAE 90.1-2007 | Hospital | Laundry-Washing | ASHRAE 90.1-2007HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Laundry_Light | ASHRAE 62.1-2007 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-2007Dry Cleaners, LaundriesCommercial Laundry | #N/A | #N/A | #N/A | 10 | SmallHotel_Laundry_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | 42.6 |  |  |  | SmallHotel_Laundry_Gas | 1.04 | 0 | 0.5 | 0 | SmallHotel_Laundry_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel_SWH_Laundry
|  | Xcel EDA 2007 | ClimateZone 1-8 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SmallHotel | Meeting | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Meeting_Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesConference rooms | #N/A | #N/A | #N/A | 50 | SmallHotel_Meeting_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel_Meeting_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SmallHotel | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Office_Light | ASHRAE 62.1-2007 | Offices | Office Space | ASHRAE 62.1-2007OfficesOffice Space | #N/A | #N/A | #N/A | 7.14 | SmallHotel_Office_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel_Office_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-2007Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | #N/A | #N/A | #N/A | 2.85 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0.51 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
|  | Xcel EDA 2007 | ClimateZone 1-8 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 90.1-2007 | Lounge/Recreation | General | ASHRAE 90.1-2007Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | SmallHotel_StaffLounge_Light | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies | #N/A | #N/A | #N/A | 30 | SmallHotel_StaffLounge_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 3.67 | 0 | 0.5 | 0 | SmallHotel_StaffLounge_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SmallHotel | Stair | 230_157_120 | ASHRAE 90.1-2007 | Stairs-Active | General | ASHRAE 90.1-2007Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Bldg_Light | ASHRAE 62.1-2007 | Public Spaces | Corridors and utilities | ASHRAE 62.1-2007Public SpacesCorridors and utilities | #N/A | #N/A | #N/A | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SmallHotel | Storage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | SmallHotel_Storage_Light | ASHRAE 62.1-2007 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-2007Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | #N/A | #N/A | #N/A | 0 | SmallHotel_Bldg_Occ | SmallHotel_Activity | 0.0446 | SmallHotel_Infil_Half_On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel_Bldg_Equip | SmallHotel_HtgSetp | SmallHotel_ClgSetp
CBECS_1980-2004_SmallOffice | 429 | NREL_1980-2004 | ClimateZone 1-8 | SmallOffice | WholeBuilding | 120_230_199 | [6 empty] | 1.81 |  |  | 0 | 0.7 | 0.2 | Small Office_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Small Office_Bldg_Occ | Small Office_Activity | 0.2232 | Small Office_Infil_Quarter_On | [5 empty] | 1 | 0 | 0.5 | 0 | Small Office_Bldg_Equip | Small Office_HtgSetp | Small Office_ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | SmallOffice_SWH
ASHRAE_189.1-2009_ClimateZone 1-3_SmallOffice | 118 | NREL_2009 | ClimateZone 1-3 | SmallOffice | WholeBuilding | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Small Office_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Small Office_Bldg_Occ | Small Office_Activity | 0.0595 | Small Office_Infil_Quarter_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Small Office_Bldg_Equip | Small Office_HtgSetp | Small Office_ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | SmallOffice_SWH
ASHRAE_189.1-2009_ClimateZone 4-8_SmallOffice | 53 | NREL_2009 | ClimateZone 4-8 | SmallOffice | WholeBuilding | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Small Office_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Small Office_Bldg_Occ | Small Office_Activity | 0.0446 | Small Office_Infil_Quarter_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Small Office_Bldg_Equip | Small Office_HtgSetp | Small Office_ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | SmallOffice_SWH
CBECS_Before-1980_SmallOffice | 276 | NREL_Before-1980 | ClimateZone 1-8 | SmallOffice | WholeBuilding | 120_230_199 | [6 empty] | 1.9 |  |  | 0 | 0.7 | 0.2 | Small Office_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | Small Office_Bldg_Occ | Small Office_Activity | 0.2232 | Small Office_Infil_Quarter_On | [5 empty] | 1 | 0 | 0.5 | 0 | Small Office_Bldg_Equip | Small Office_HtgSetp | Small Office_ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | SmallOffice_SWH
CBECS_1980-2004_StripMall | 230 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: StripMall; 3 3: WholeBuilding; 4 4: 171_222_78; 19 11: 3.58; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: StripMall_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Basement and street; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; 21 22: 0.3; 21 23: 0; 21 24: 0; 21 25: 15; 21 26: StripMall_Bldg_Occ; 21 27: StripMall_Activity; 21 28: 0.2232; 21 29: StripMall_Infil_Half_On; 21 35: 0.4; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: StripMall_Bldg_Equip; 21 40: StripMall_HtgSetp; 21 41: StripMall_ClgSetp
ASHRAE_90.1-2004_StripMall | 297 | NREL_2004 | ClimateZone 1-8 | StripMall | WholeBuilding | 171_222_78 | ASHRAE 90.1-2004 | Whole Building | Retail | ASHRAE 90.1-2004Whole BuildingRetail |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | StripMall_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | StripMall_Bldg_Occ | StripMall_Activity | 0.0595 | StripMall_Infil_Half_On | [5 empty] | 0.4 | 0 | 0.5 | 0 | StripMall_Bldg_Equip | StripMall_HtgSetp | StripMall_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_StripMall | 543 | NREL_2009 | ClimateZone 1-3 | StripMall | WholeBuilding | 171_222_78 | ASHRAE 189.1-2009 | Whole Building | Retail | ASHRAE 189.1-2009Whole BuildingRetail |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | StripMall_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | StripMall_Bldg_Occ | StripMall_Activity | 0.0595 | StripMall_Infil_Half_On | [5 empty] | 0.29 | 0 | 0.5 | 0 | StripMall_Bldg_Equip | StripMall_HtgSetp | StripMall_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_StripMall | 188 | NREL_2009 | ClimateZone 4-8 | StripMall | WholeBuilding | 171_222_78 | ASHRAE 189.1-2009 | Whole Building | Retail | ASHRAE 189.1-2009Whole BuildingRetail |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | StripMall_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | StripMall_Bldg_Occ | StripMall_Activity | 0.0446 | StripMall_Infil_Half_On | [5 empty] | 0.29 | 0 | 0.5 | 0 | StripMall_Bldg_Equip | StripMall_HtgSetp | StripMall_ClgSetp
CBECS_Before-1980_StripMall | 240 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: StripMall; 3 3: WholeBuilding; 4 4: 171_222_78; 19 11: 4.81; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: StripMall_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Basement and street; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street; 21 22: 0.3; 21 23: 0; 21 24: 0; 21 25: 15; 21 26: StripMall_Bldg_Occ; 21 27: StripMall_Activity; 21 28: 0.2232; 21 29: StripMall_Infil_Half_On; 21 35: 0.4; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: StripMall_Bldg_Equip; 21 40: StripMall_HtgSetp; 21 41: StripMall_ClgSetp
CBECS_1980-2004_SuperMarket_Deli/Bakery | 536 | NREL_1980-2004 | ClimateZone 1-8 | SuperMarket | Deli/Bakery | 31_169_34 | [6 empty] | 2.78 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.2232 | SuperMarket_Infil_Half_On | 8.53 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | 5 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket_SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
CBECS_1980-2004_SuperMarket_DryStorage | 245 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SuperMarket; 3 3: DryStorage; 4 4: 120_149_230; 19 11: 1.1; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SuperMarket_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Shipping and receiving; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 3.33; 21 26: SuperMarket_Bldg_Occ; 21 27: SuperMarket_Activity; 21 28: 0.2232; 21 29: SuperMarket_Infil_Half_On; 21 35: 0.75; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SuperMarket_Bldg_Equip; 21 40: SuperMarket_HtgSetp; 21 41: SuperMarket_ClgSetp
CBECS_1980-2004_SuperMarket_Office | 23 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SuperMarket; 3 3: Office; 4 4: 120_230_199; 19 11: 1.98; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SuperMarket_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 5; 21 26: SuperMarket_Bldg_Occ; 21 27: SuperMarket_Activity; 21 28: 0.2232; 21 29: SuperMarket_Infil_Half_On; 21 35: 0.75; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SuperMarket_Bldg_Equip; 21 40: SuperMarket_HtgSetp; 21 41: SuperMarket_ClgSetp
CBECS_1980-2004_SuperMarket_Sales/Produce | 472 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: SuperMarket; 3 3: Sales/Produce; 4 4: 230_196_120; 19 11: 2.78; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SuperMarket_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Specialty Shops; 21 20: Supermarket; 21 21: ASHRAE 62.1-1999Specialty ShopsSupermarket; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 8; 21 26: SuperMarket_Bldg_Occ; 21 27: SuperMarket_Activity; 21 28: 0.2232; 21 29: SuperMarket_Infil_Half_On; 21 35: 0.5; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SuperMarket_Bldg_Equip; 21 40: SuperMarket_HtgSetp; 21 41: SuperMarket_ClgSetp
ASHRAE_90.1-2004_SuperMarket_Deli/Bakery | 545 | NREL_2004 | ClimateZone 1-8 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0595 | SuperMarket_Infil_Half_On | 8.53 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | 5 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket_SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
ASHRAE_90.1-2004_SuperMarket_DryStorage | 465 | NREL_2004 | ClimateZone 1-8 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 3.33 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0595 | SuperMarket_Infil_Half_On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp
ASHRAE_90.1-2004_SuperMarket_Office | 421 | NREL_2004 | ClimateZone 1-8 | SuperMarket | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0595 | SuperMarket_Infil_Half_On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp
ASHRAE_90.1-2004_SuperMarket_Sales/Produce | 401 | NREL_2004 | ClimateZone 1-8 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0595 | SuperMarket_Infil_Half_On | [5 empty] | 0.5 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SuperMarket_Deli/Bakery | 172 | NREL_2009 | ClimateZone 1-3 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0595 | SuperMarket_Infil_Half_On | 6.25 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | 3.64 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket_SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
ASHRAE_189.1-2009_ClimateZone 4-8_SuperMarket_Deli/Bakery | 561 | NREL_2009 | ClimateZone 4-8 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0446 | SuperMarket_Infil_Half_On | 6.25 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | 3.64 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket_SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
ASHRAE_189.1-2009_ClimateZone 1-3_SuperMarket_DryStorage | 217 | NREL_2009 | ClimateZone 1-3 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 3.33 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0595 | SuperMarket_Infil_Half_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SuperMarket_DryStorage | 492 | NREL_2009 | ClimateZone 4-8 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 3.33 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0446 | SuperMarket_Infil_Half_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SuperMarket_Office | 179 | NREL_2009 | ClimateZone 1-3 | SuperMarket | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0595 | SuperMarket_Infil_Half_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SuperMarket_Office | 539 | NREL_2009 | ClimateZone 4-8 | SuperMarket | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 5 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0446 | SuperMarket_Infil_Half_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_SuperMarket_Sales/Produce | 116 | NREL_2009 | ClimateZone 1-3 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0595 | SuperMarket_Infil_Half_On | [5 empty] | 0.36 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_SuperMarket_Sales/Produce | 7 | NREL_2009 | ClimateZone 4-8 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0446 | SuperMarket_Infil_Half_On | [5 empty] | 0.36 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp
CBECS_Before-1980_SuperMarket_Deli/Bakery | 301 | NREL_Before-1980 | ClimateZone 1-8 | SuperMarket | Deli/Bakery | 31_169_34 | [6 empty] | 5.04 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.2232 | SuperMarket_Infil_Half_On | 8.53 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | 5 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket_SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
CBECS_Before-1980_SuperMarket_DryStorage | 195 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SuperMarket; 3 3: DryStorage; 4 4: 120_149_230; 19 11: 0.77; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SuperMarket_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Shipping and receiving; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving; 21 22: 0.15; 21 23: 0; 21 24: 0; 21 25: 3.33; 21 26: SuperMarket_Bldg_Occ; 21 27: SuperMarket_Activity; 21 28: 0.2232; 21 29: SuperMarket_Infil_Half_On; 21 35: 0.75; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SuperMarket_Bldg_Equip; 21 40: SuperMarket_HtgSetp; 21 41: SuperMarket_ClgSetp
CBECS_Before-1980_SuperMarket_Office | 292 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SuperMarket; 3 3: Office; 4 4: 120_230_199; 19 11: 2.9; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SuperMarket_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 5; 21 26: SuperMarket_Bldg_Occ; 21 27: SuperMarket_Activity; 21 28: 0.2232; 21 29: SuperMarket_Infil_Half_On; 21 35: 0.75; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SuperMarket_Bldg_Equip; 21 40: SuperMarket_HtgSetp; 21 41: SuperMarket_ClgSetp
CBECS_Before-1980_SuperMarket_Sales/Produce | 17 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: SuperMarket; 3 3: Sales/Produce; 4 4: 230_196_120; 19 11: 5.04; 21 14: 0; 21 15: 0.7; 21 16: 0.2; 21 17: SuperMarket_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Specialty Shops; 21 20: Supermarket; 21 21: ASHRAE 62.1-1999Specialty ShopsSupermarket; 21 22: 0; 21 23: 15; 21 24: 0; 21 25: 8; 21 26: SuperMarket_Bldg_Occ; 21 27: SuperMarket_Activity; 21 28: 0.2232; 21 29: SuperMarket_Infil_Half_On; 21 35: 0.5; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: SuperMarket_Bldg_Equip; 21 40: SuperMarket_HtgSetp; 21 41: SuperMarket_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-2007 | Specialty Shops | Supermarket | ASHRAE 62.1-2007Specialty ShopsSupermarket | #N/A | #N/A | #N/A | 8 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0446 | SuperMarket_Infil_Half_On | 6.25 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | 3.64 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket_SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
|  | Xcel EDA 2007 | ClimateZone 1-8 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-2007 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-2007Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | #N/A | #N/A | #N/A | 3.33 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0446 | SuperMarket_Infil_Half_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SuperMarket | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-2007 | Offices | Office Space | ASHRAE 62.1-2007OfficesOffice Space | #N/A | #N/A | #N/A | 5 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0446 | SuperMarket_Infil_Half_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | SuperMarket_Bldg_Light | ASHRAE 62.1-2007 | Specialty Shops | Supermarket | ASHRAE 62.1-2007Specialty ShopsSupermarket | #N/A | #N/A | #N/A | 8 | SuperMarket_Bldg_Occ | SuperMarket_Activity | 0.0446 | SuperMarket_Infil_Half_On | [5 empty] | 0.36 | 0 | 0.5 | 0 | SuperMarket_Bldg_Equip | SuperMarket_HtgSetp | SuperMarket_ClgSetp
CBECS_1980-2004_Warehouse_Bulk | 185 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Warehouse; 3 3: Bulk; 4 4: 41_31_169; 19 11: 0.31; 21 14: 0; 21 15: 0.5; 21 16: 0.2; 21 17: Warehouse_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Warehouses; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Warehouse_Bldg_Occ; 21 27: Warehouse_Activity; 21 28: 0.2232; 21 29: Always_On; 21 35: 0.25; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Warehouse_Bldg_Equip; 21 40: Warehouse_HtgSetp_BulkStorage; 21 41: Warehouse_ClgSetp
CBECS_1980-2004_Warehouse_Fine | 405 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Warehouse; 3 3: Fine; 4 4: 120_149_230; 19 11: 1.08; 21 14: 0; 21 15: 0.5; 21 16: 0.2; 21 17: Warehouse_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Warehouses; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Warehouse_Bldg_Occ; 21 27: Warehouse_Activity; 21 28: 0.2232; 21 29: Always_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Warehouse_Bldg_Equip; 21 40: Warehouse_HtgSetp_FineStorage; 21 41: Warehouse_ClgSetp_FineStorage
CBECS_1980-2004_Warehouse_Office | 460 | 0 0: NREL_1980-2004; 1 1: ClimateZone 1-8; 2 2: Warehouse; 3 3: Office; 4 4: 120_230_199; 19 11: 2.02; 21 14: 0; 21 15: 0.5; 21 16: 0.2; 21 17: Warehouse_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 1.96; 21 26: Warehouse_Bldg_Occ; 21 27: Warehouse_Activity; 21 28: 0.2232; 21 29: Always_On; 21 35: 0.75; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Warehouse_Bldg_Equip; 21 40: Warehouse_HtgSetp; 21 41: Warehouse_ClgSetp
ASHRAE_90.1-2004_Warehouse_Bulk | 449 | NREL_2004 | ClimateZone 1-8 | Warehouse | Bulk | 41_31_169 | ASHRAE 90.1-2004 | Warehouse | Medium/Bulky Material Storage | ASHRAE 90.1-2004WarehouseMedium/Bulky Material Storage |  |  | 0.9 |  |  | 0 | 0.5 | 0.2 | Warehouse_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse_Bldg_Occ | Warehouse_Activity | 0.0595 | Always_On | [5 empty] | 0.25 | 0 | 0.5 | 0 | Warehouse_Bldg_Equip | Warehouse_HtgSetp_BulkStorage | Warehouse_ClgSetp
ASHRAE_90.1-2004_Warehouse_Fine | 55 | NREL_2004 | ClimateZone 1-8 | Warehouse | Fine | 120_149_230 | ASHRAE 90.1-2004 | Warehouse | Fine Material Storage | ASHRAE 90.1-2004WarehouseFine Material Storage |  |  | 1.4 |  |  | 0 | 0.5 | 0.2 | Warehouse_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse_Bldg_Occ | Warehouse_Activity | 0.0595 | Always_On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse_Bldg_Equip | Warehouse_HtgSetp_FineStorage | Warehouse_ClgSetp_FineStorage
ASHRAE_90.1-2004_Warehouse_Office | 113 | NREL_2004 | ClimateZone 1-8 | Warehouse | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.5 | 0.2 | Warehouse_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 1.96 | Warehouse_Bldg_Occ | Warehouse_Activity | 0.0595 | Always_On | [5 empty] | 0.75 | 0 | 0.5 | 0 | Warehouse_Bldg_Equip | Warehouse_HtgSetp | Warehouse_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Warehouse_Bulk | 158 | NREL_2009 | ClimateZone 1-3 | Warehouse | Bulk | 41_31_169 | ASHRAE 189.1-2009 | Warehouse | Medium/Bulky Material Storage | ASHRAE 189.1-2009WarehouseMedium/Bulky Material Storage |  |  | 0.81 |  |  | 0 | 0.5 | 0.2 | Warehouse_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse_Bldg_Occ | Warehouse_Activity | 0.0595 | Always_On | [5 empty] | 0.17 | 0 | 0.5 | 0 | Warehouse_Bldg_Equip | Warehouse_HtgSetp_BulkStorage | Warehouse_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Warehouse_Bulk | 123 | NREL_2009 | ClimateZone 4-8 | Warehouse | Bulk | 41_31_169 | ASHRAE 189.1-2009 | Warehouse | Medium/Bulky Material Storage | ASHRAE 189.1-2009WarehouseMedium/Bulky Material Storage |  |  | 0.81 |  |  | 0 | 0.5 | 0.2 | Warehouse_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse_Bldg_Occ | Warehouse_Activity | 0.0446 | Always_On | [5 empty] | 0.17 | 0 | 0.5 | 0 | Warehouse_Bldg_Equip | Warehouse_HtgSetp_BulkStorage | Warehouse_ClgSetp
ASHRAE_189.1-2009_ClimateZone 1-3_Warehouse_Fine | 65 | NREL_2009 | ClimateZone 1-3 | Warehouse | Fine | 120_149_230 | ASHRAE 189.1-2009 | Warehouse | Fine Material Storage | ASHRAE 189.1-2009WarehouseFine Material Storage |  |  | 1.26 |  |  | 0 | 0.5 | 0.2 | Warehouse_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse_Bldg_Occ | Warehouse_Activity | 0.0595 | Always_On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse_Bldg_Equip | Warehouse_HtgSetp_FineStorage | Warehouse_ClgSetp_FineStorage
ASHRAE_189.1-2009_ClimateZone 4-8_Warehouse_Fine | 206 | NREL_2009 | ClimateZone 4-8 | Warehouse | Fine | 120_149_230 | ASHRAE 189.1-2009 | Warehouse | Fine Material Storage | ASHRAE 189.1-2009WarehouseFine Material Storage |  |  | 1.26 |  |  | 0 | 0.5 | 0.2 | Warehouse_Bldg_Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse_Bldg_Occ | Warehouse_Activity | 0.0446 | Always_On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse_Bldg_Equip | Warehouse_HtgSetp_FineStorage | Warehouse_ClgSetp_FineStorage
ASHRAE_189.1-2009_ClimateZone 1-3_Warehouse_Office | 315 | NREL_2009 | ClimateZone 1-3 | Warehouse | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.5 | 0.2 | Warehouse_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 1.96 | Warehouse_Bldg_Occ | Warehouse_Activity | 0.0595 | Always_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Warehouse_Bldg_Equip | Warehouse_HtgSetp | Warehouse_ClgSetp
ASHRAE_189.1-2009_ClimateZone 4-8_Warehouse_Office | 196 | NREL_2009 | ClimateZone 4-8 | Warehouse | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.5 | 0.2 | Warehouse_Bldg_Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 | 0 | 1.96 | Warehouse_Bldg_Occ | Warehouse_Activity | 0.0446 | Always_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Warehouse_Bldg_Equip | Warehouse_HtgSetp | Warehouse_ClgSetp
CBECS_Before-1980_Warehouse_Bulk | 331 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Warehouse; 3 3: Bulk; 4 4: 41_31_169; 19 11: 0.62; 21 14: 0; 21 15: 0.5; 21 16: 0.2; 21 17: Warehouse_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Warehouses; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Warehouse_Bldg_Occ; 21 27: Warehouse_Activity; 21 28: 0.2232; 21 29: Always_On; 21 35: 0.25; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Warehouse_Bldg_Equip; 21 40: Warehouse_HtgSetp_BulkStorage; 21 41: Warehouse_ClgSetp
CBECS_Before-1980_Warehouse_Fine | 209 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Warehouse; 3 3: Fine; 4 4: 120_149_230; 19 11: 1.08; 21 14: 0; 21 15: 0.5; 21 16: 0.2; 21 17: Warehouse_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Retail Stores, Sales Floors, and Show Room Floors; 21 20: Warehouses; 21 21: ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses; 21 22: 0.05; 21 23: 0; 21 24: 0; 21 25: 0; 21 26: Warehouse_Bldg_Occ; 21 27: Warehouse_Activity; 21 28: 0.2232; 21 29: Always_On; 21 35: 0; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Warehouse_Bldg_Equip; 21 40: Warehouse_HtgSetp_FineStorage; 21 41: Warehouse_ClgSetp_FineStorage
CBECS_Before-1980_Warehouse_Office | 95 | 0 0: NREL_Before-1980; 1 1: ClimateZone 1-8; 2 2: Warehouse; 3 3: Office; 4 4: 120_230_199; 19 11: 2.9; 21 14: 0; 21 15: 0.5; 21 16: 0.2; 21 17: Warehouse_Bldg_Light; 21 18: ASHRAE 62.1-1999; 21 19: Offices; 21 20: Office Space; 21 21: ASHRAE 62.1-1999OfficesOffice Space; 21 22: 0; 21 23: 20; 21 24: 0; 21 25: 1.96; 21 26: Warehouse_Bldg_Occ; 21 27: Warehouse_Activity; 21 28: 0.2232; 21 29: Always_On; 21 35: 0.75; 21 36: 0; 21 37: 0.5; 21 38: 0; 21 39: Warehouse_Bldg_Equip; 21 40: Warehouse_HtgSetp; 21 41: Warehouse_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Warehouse | Bulk | 41_31_169 | ASHRAE 90.1-2007 | Warehouse | Medium/Bulky Material Storage | ASHRAE 90.1-2007WarehouseMedium/Bulky Material Storage |  |  | 0.9 |  |  | 0 | 0.5 | 0.2 | Warehouse_Bldg_Light | ASHRAE 62.1-2007 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-2007Retail Stores, Sales Floors, and Show Room FloorsWarehouses | #N/A | #N/A | #N/A | 0 | Warehouse_Bldg_Occ | Warehouse_Activity | 0.0446 | Always_On | [5 empty] | 0.17 | 0 | 0.5 | 0 | Warehouse_Bldg_Equip | Warehouse_HtgSetp_BulkStorage | Warehouse_ClgSetp
|  | Xcel EDA 2007 | ClimateZone 1-8 | Warehouse | Fine | 120_149_230 | ASHRAE 90.1-2007 | Warehouse | Fine Material Storage | ASHRAE 90.1-2007WarehouseFine Material Storage |  |  | 1.4 |  |  | 0 | 0.5 | 0.2 | Warehouse_Bldg_Light | ASHRAE 62.1-2007 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-2007Retail Stores, Sales Floors, and Show Room FloorsWarehouses | #N/A | #N/A | #N/A | 0 | Warehouse_Bldg_Occ | Warehouse_Activity | 0.0446 | Always_On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse_Bldg_Equip | Warehouse_HtgSetp_FineStorage | Warehouse_ClgSetp_FineStorage
|  | Xcel EDA 2007 | ClimateZone 1-8 | Warehouse | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.5 | 0.2 | Warehouse_Bldg_Light | ASHRAE 62.1-2007 | Offices | Office Space | ASHRAE 62.1-2007OfficesOffice Space | #N/A | #N/A | #N/A | 1.96 | Warehouse_Bldg_Occ | Warehouse_Activity | 0.0446 | Always_On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Warehouse_Bldg_Equip | Warehouse_HtgSetp | Warehouse_ClgSetp
Note on AT26: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AT31: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AT33: NREL: average size across 8 rooms
Note on AT45: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AT50: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AT52: NREL: average size across 8 rooms
Note on AT73: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AT74: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AT83: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AT84: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AT87: NREL: average size across 8 rooms
Note on AT88: NREL: average size across 8 rooms
Note on AT102: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AT107: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AT109: NREL: average size across 8 rooms
Note on AT121: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AT126: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AT128: NREL: average size across 8 rooms
Note on F353: NREL: Step down and Recovery same as this
Note on BF361: NREL: Typical - ref has different schedule for 2nd and 3rd floor than first
Note on F484: NREL: Not adjusted for special computer classrroom with slightly higher plug loads
Note on BF511: NREL: Don’t see an elec object for this in ref building model like I do for other exhaust fans
Note on BF611: NREL: Don’t see an elec object for this in ref building model like I do for other exhaust fans
Note on BF675: NREL: Don’t see an elec object for this in ref building model like I do for other exhaust fans
Note on AZ716: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AZ720: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AZ724: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AZ725: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AZ732: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AZ736: NREL: This is for Deli. Bakery only has 0.33 cfm/sf

## Ventilation
|  |  |  | ventilation | ventilation | ventilation
VlookupColumn | Ventilation Standard | Primary Space Type | Secondary Space Type | ft^3/min*person | ft^3/min*ft^2 | ach | Notes
ASHRAE 62.1-1999Correctional FacilitiesCell | ASHRAE 62.1-1999 | Correctional Facilities | Cell | 20 | 0
ASHRAE 62.1-1999Correctional FacilitiesDining halls | ASHRAE 62.1-1999 | Correctional Facilities | Dining halls | 15 | 0
ASHRAE 62.1-1999Correctional FacilitiesGuard stations | ASHRAE 62.1-1999 | Correctional Facilities | Guard stations | 15 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial laundry | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial laundry | 25 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial dry cleaner | 30 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesStorage, pick up | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Storage, pick up | 35 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated laundries | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated laundries | 15 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated dry cleaner | 15 | 0
ASHRAE 62.1-1999EducationClassroom | ASHRAE 62.1-1999 | Education | Classroom | 15 | 0
ASHRAE 62.1-1999EducationLaboratories | ASHRAE 62.1-1999 | Education | Laboratories | 20 | 0
ASHRAE 62.1-1999EducationTraining shop | ASHRAE 62.1-1999 | Education | Training shop | 20 | 0
ASHRAE 62.1-1999EducationMusic rooms | ASHRAE 62.1-1999 | Education | Music rooms | 15 | 0
ASHRAE 62.1-1999EducationLibraries | ASHRAE 62.1-1999 | Education | Libraries | 15 | 0
ASHRAE 62.1-1999EducationAuditorium | ASHRAE 62.1-1999 | Education | Auditorium | 15 | 0
ASHRAE 62.1-1999EducationSmoking lounges | ASHRAE 62.1-1999 | Education | Smoking lounges | 60 | 0
ASHRAE 62.1-1999EducationCorridors | ASHRAE 62.1-1999 | Education | Corridors | 0 | 0.1
ASHRAE 62.1-1999EducationLocker rooms | ASHRAE 62.1-1999 | Education | Locker rooms | 0 | 0.5
ASHRAE 62.1-1999Food and Beverage ServiceDining rooms | ASHRAE 62.1-1999 | Food and Beverage Service | Dining rooms | 20 | 0
ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | 20 | 0
ASHRAE 62.1-1999Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-1999 | Food and Beverage Service | Bars, cocktail lounges | 30 | 0
ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | 15 | 0 |  | Exhaust >= 1.5 cfm/ft2, 7.5 L/s m2
ASHRAE 62.1-1999Garages, Repair, Service StationsEnclosed parking garage | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Enclosed parking garage | 0 | 1.5
ASHRAE 62.1-1999Garages, Repair, Service StationsAuto repair rooms | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Auto repair rooms | 0 | 1.5
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 25 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 15 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 30 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 15 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 15 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 0 | 0.5
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBedrooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Bedrooms | 0 | -9999 |  | 30 cfm/room, 15 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLiving rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Living rooms | 0 | -9999 |  | 30 cfm/room, 15 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBaths | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Baths | 0 | -9999 |  | 35 cfm/room, 18 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | 15 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | 20 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesAssembly rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Assembly rooms | 15 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | 15 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesGambling casinos | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Gambling casinos | 30 | 0
ASHRAE 62.1-1999OfficesOffice space | ASHRAE 62.1-1999 | Offices | Office space | 20 | 0
ASHRAE 62.1-1999OfficesReception areas | ASHRAE 62.1-1999 | Offices | Reception areas | 15 | 0
ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | 20 | 0
ASHRAE 62.1-1999OfficesConference rooms | ASHRAE 62.1-1999 | Offices | Conference rooms | 20 | 0
ASHRAE 62.1-1999Public SpacesSmoking lounge | ASHRAE 62.1-1999 | Public Spaces | Smoking lounge | 60 | 0
ASHRAE 62.1-1999Public SpacesCorridors and utilities | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | 0 | 0.05
ASHRAE 62.1-1999Public SpacesLocker and dressing rooms | ASHRAE 62.1-1999 | Public Spaces | Locker and dressing rooms | 0 | 0.5
ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | 0 | 0.96 |  | 50 cfm/wc or urinal, 25 L/s wc or urinal
ASHRAE 62.1-1999Public SpacesElevators | ASHRAE 62.1-1999 | Public Spaces | Elevators | 0 | 1
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsSmoking lounge | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Smoking lounge | 60 | 0
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | 0 | 0.05
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | 0 | 0.15
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | 0 | 0.15
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsUpper floors | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Upper floors | 0 | 0.2
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsDressing rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Dressing rooms | 0 | 0.2
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsMalls and arcades | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Malls and arcades | 0 | 0.2
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | 0 | 0.3
ASHRAE 62.1-1999Specialty ShopsBarber | ASHRAE 62.1-1999 | Specialty Shops | Barber | 15 | 0
ASHRAE 62.1-1999Specialty ShopsBeauty | ASHRAE 62.1-1999 | Specialty Shops | Beauty | 25 | 0
ASHRAE 62.1-1999Specialty ShopsReducing salons | ASHRAE 62.1-1999 | Specialty Shops | Reducing salons | 15 | 0
ASHRAE 62.1-1999Specialty ShopsFlorists | ASHRAE 62.1-1999 | Specialty Shops | Florists | 15 | 0
ASHRAE 62.1-1999Specialty ShopsHardware, drugs, fabric | ASHRAE 62.1-1999 | Specialty Shops | Hardware, drugs, fabric | 15 | 0
ASHRAE 62.1-1999Specialty ShopsSupermarket | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | 15 | 0
ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | 0 | 0.3
ASHRAE 62.1-1999Specialty ShopsPet shops | ASHRAE 62.1-1999 | Specialty Shops | Pet shops | 0 | 1
ASHRAE 62.1-2004Correctional FacilitiesDay room | ASHRAE 62.1-2004 | Correctional Facilities | Day room | 5 | 0.06
ASHRAE 62.1-2004Correctional FacilitiesGuard stations | ASHRAE 62.1-2004 | Correctional Facilities | Guard stations | 5 | 0.06
ASHRAE 62.1-2004Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2004 | Correctional Facilities | Booking/waiting | 7.5 | 0.06
ASHRAE 62.1-2004Educational FacilitiesLecture classroom | ASHRAE 62.1-2004 | Educational Facilities | Lecture classroom | 7.5 | 0.06
ASHRAE 62.1-2004Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2004 | Educational Facilities | Lecture hall (fixed seats) | 7.5 | 0.06
ASHRAE 62.1-2004Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2004 | Educational Facilities | Music/theater/dance | 10 | 0.06
ASHRAE 62.1-2004Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2004 | Educational Facilities | Multiuse assembly | 7.5 | 0.06
ASHRAE 62.1-2004GeneralConference/meeting | ASHRAE 62.1-2004 | General | Conference/meeting | 5 | 0.06
ASHRAE 62.1-2004GeneralCorridors | ASHRAE 62.1-2004 | General | Corridors |  | 0.06
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 5 | 0.06
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 5 | 0.06
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 7.5 | 0.06
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 5 | 0.06
ASHRAE 62.1-2004Office BuildingsOffice space | ASHRAE 62.1-2004 | Office Buildings | Office space | 5 | 0.06
ASHRAE 62.1-2004Office BuildingsReception areas | ASHRAE 62.1-2004 | Office Buildings | Reception areas | 5 | 0.06
ASHRAE 62.1-2004Office BuildingsTelephone/data entry | ASHRAE 62.1-2004 | Office Buildings | Telephone/data entry | 5 | 0.06
ASHRAE 62.1-2004Office BuildingsMain entry lobbies | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | 5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2004 | Miscellaneous Spaces | Bank vaults/safe deposit | 5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Computer (not printing) | 5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2004 | Miscellaneous Spaces | Transportation waiting | 7.5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesWarehouses | ASHRAE 62.1-2004 | Miscellaneous Spaces | Warehouses |  | 0.06 |  | B
ASHRAE 62.1-2004Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2004 | Public Assembly Spaces | Auditorium seating area | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2004 | Public Assembly Spaces | Places of religious worship | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesCourtrooms | ASHRAE 62.1-2004 | Public Assembly Spaces | Courtrooms | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2004 | Public Assembly Spaces | Legislative chambers | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesLobbies | ASHRAE 62.1-2004 | Public Assembly Spaces | Lobbies | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums/galleries | 7.5 | 0.06
ASHRAE 62.1-2004RetailMall common areas | ASHRAE 62.1-2004 | Retail | Mall common areas | 7.5 | 0.06
ASHRAE 62.1-2004RetailBarber shop | ASHRAE 62.1-2004 | Retail | Barber shop | 7.5 | 0.06
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 7.5 | 0.06
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 7.5 | 0.06
ASHRAE 62.1-2004RetailCoinoperated laundries | ASHRAE 62.1-2004 | Retail | Coinoperated laundries | 7.5 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentSpectator areas | ASHRAE 62.1-2004 | Sports and Entertainment | Spectator areas | 7.5 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2004 | Sports and Entertainment | Disco/dance floors | 20 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/aerobics room | 20 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/weight rooms | 20 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentStages, studios | ASHRAE 62.1-2004 | Sports and Entertainment | Stages, studios | 10 | 0.06 |  | D
ASHRAE 62.1-2007Correctional FacilitiesDay room | ASHRAE 62.1-2007 | Correctional Facilities | Day room | 5 | 0.06
ASHRAE 62.1-2007Correctional FacilitiesGuard stations | ASHRAE 62.1-2007 | Correctional Facilities | Guard stations | 5 | 0.06
ASHRAE 62.1-2007Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2007 | Correctional Facilities | Booking/waiting | 7.5 | 0.06
ASHRAE 62.1-2007Educational FacilitiesLecture classroom | ASHRAE 62.1-2007 | Educational Facilities | Lecture classroom | 7.5 | 0.06
ASHRAE 62.1-2007Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2007 | Educational Facilities | Lecture hall (fixed seats) | 7.5 | 0.06
ASHRAE 62.1-2007Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2007 | Educational Facilities | Music/theater/dance | 10 | 0.06
ASHRAE 62.1-2007Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2007 | Educational Facilities | Multiuse assembly | 7.5 | 0.06
ASHRAE 62.1-2007GeneralConference/meeting | ASHRAE 62.1-2007 | General | Conference/meeting | 5 | 0.06
ASHRAE 62.1-2007GeneralCorridors | ASHRAE 62.1-2007 | General | Corridors |  | 0.06
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 5 | 0.06
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 5 | 0.06
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 7.5 | 0.06
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsOffice space | ASHRAE 62.1-2007 | Office Buildings | Office space | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsReception areas | ASHRAE 62.1-2007 | Office Buildings | Reception areas | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsTelephone/data entry | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsMain entry lobbies | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | 5 | 0.06
ASHRAE 62.1-2007Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2007 | Miscellaneous Spaces | Bank vaults/safe deposit | 5 | 0.06
ASHRAE 62.1-2007Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Computer (not printing) | 5 | 0.06
ASHRAE 62.1-2007Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2007 | Miscellaneous Spaces | Transportation waiting | 7.5 | 0.06
ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses |  | 0.06 |  | B
ASHRAE 62.1-2007Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2007 | Public Assembly Spaces | Auditorium seating area | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2007 | Public Assembly Spaces | Places of religious worship | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesCourtrooms | ASHRAE 62.1-2007 | Public Assembly Spaces | Courtrooms | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2007 | Public Assembly Spaces | Legislative chambers | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesLobbies | ASHRAE 62.1-2007 | Public Assembly Spaces | Lobbies | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums/galleries | 7.5 | 0.06
ASHRAE 62.1-2007RetailMall common areas | ASHRAE 62.1-2007 | Retail | Mall common areas | 7.5 | 0.06
ASHRAE 62.1-2007RetailBarber shop | ASHRAE 62.1-2007 | Retail | Barber shop | 7.5 | 0.06
ASHRAE 62.1-2007RetailSupermarket | ASHRAE 62.1-2007 | Retail | Supermarket | 7.5 | 0.06
ASHRAE 62.1-2007RetailCoinoperated laundries | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | 7.5 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentSpectator areas | ASHRAE 62.1-2007 | Sports and Entertainment | Spectator areas | 7.5 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2007 | Sports and Entertainment | Disco/dance floors | 20 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/aerobics room | 20 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/weight rooms | 20 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentStages, studios | ASHRAE 62.1-2007 | Sports and Entertainment | Stages, studios | 10 | 0.06 |  | D
ASHRAE 62.1-1999Sports and AmusementSpectator areas | ASHRAE 62.1-1999 | Sports and Amusement | Spectator areas | 15 | 0
ASHRAE 62.1-2004Correctional FacilitiesCell | ASHRAE 62.1-2004 | Correctional Facilities | Cell | 5 | 0.12
ASHRAE 62.1-2004Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (ages 5-8) | 10 | 0.12
ASHRAE 62.1-2004Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (age 9 plus) | 10 | 0.12
ASHRAE 62.1-2004Educational FacilitiesComputer lab | ASHRAE 62.1-2004 | Educational Facilities | Computer lab | 10 | 0.12
ASHRAE 62.1-2004Educational FacilitiesMedia center | ASHRAE 62.1-2004 | Educational Facilities | Media center | 10 | 0.12 |  | A
ASHRAE 62.1-2004GeneralStorage rooms | ASHRAE 62.1-2004 | General | Storage rooms |  | 0.12 |  | B
ASHRAE 62.1-2004Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2004 | Miscellaneous Spaces | Photo studios | 5 | 0.12
ASHRAE 62.1-2004Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2004 | Miscellaneous Spaces | Shipping/receiving |  | 0.12 |  | B
ASHRAE 62.1-2004Public Assembly SpacesLibraries | ASHRAE 62.1-2004 | Public Assembly Spaces | Libraries | 5 | 0.12
ASHRAE 62.1-2004Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums (children’s) | 7.5 | 0.12
ASHRAE 62.1-2004RetailGeneral Sales | ASHRAE 62.1-2004 | Retail | General Sales | 7.5 | 0.12
ASHRAE 62.1-2004RetailBeauty and nail salons | ASHRAE 62.1-2004 | Retail | Beauty and nail salons | 20 | 0.12
ASHRAE 62.1-2004Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2004 | Sports and Entertainment | Bowling alley (seating) | 10 | 0.12
ASHRAE 62.1-2007Correctional FacilitiesCell | ASHRAE 62.1-2007 | Correctional Facilities | Cell | 5 | 0.12
ASHRAE 62.1-2007Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (ages 5-8) | 10 | 0.12
ASHRAE 62.1-2007Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (age 9 plus) | 10 | 0.12
ASHRAE 62.1-2007Educational FacilitiesComputer lab | ASHRAE 62.1-2007 | Educational Facilities | Computer lab | 10 | 0.12
ASHRAE 62.1-2007Educational FacilitiesMedia center | ASHRAE 62.1-2007 | Educational Facilities | Media center | 10 | 0.12 |  | A
ASHRAE 62.1-2007GeneralStorage rooms | ASHRAE 62.1-2007 | General | Storage rooms |  | 0.12 |  | B
ASHRAE 62.1-2007Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2007 | Miscellaneous Spaces | Photo studios | 5 | 0.12
ASHRAE 62.1-2007Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2007 | Miscellaneous Spaces | Shipping/receiving |  | 0.12 |  | B
ASHRAE 62.1-2007Public Assembly SpacesLibraries | ASHRAE 62.1-2007 | Public Assembly Spaces | Libraries | 5 | 0.12
ASHRAE 62.1-2007Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums (children’s) | 7.5 | 0.12
ASHRAE 62.1-2007RetailGeneral Sales | ASHRAE 62.1-2007 | Retail | General Sales | 7.5 | 0.12
ASHRAE 62.1-2007RetailBeauty and nail salons | ASHRAE 62.1-2007 | Retail | Beauty and nail salons | 20 | 0.12
ASHRAE 62.1-2007Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2007 | Sports and Entertainment | Bowling alley (seating) | 10 | 0.12
ASHRAE 62.1-1999Sports and AmusementGame rooms | ASHRAE 62.1-1999 | Sports and Amusement | Game rooms | 25 | 0
ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | 20 | 0
GGHC v2.2Health CareBathroom/ Public | GGHC v2.2 | Health Care | Bathroom/ Public |  | 0.15
GGHC v2.2Health CareBedpan Room | GGHC v2.2 | Health Care | Bedpan Room |  | 0.15
GGHC v2.2Health CareLobby | GGHC v2.2 | Health Care | Lobby |  | 0.15
GGHC v2.2Health CareLockers | GGHC v2.2 | Health Care | Lockers |  | 0.15
GGHC v2.2Health CareMechanical Equipment Room | GGHC v2.2 | Health Care | Mechanical Equipment Room |  | 0.15
GGHC v2.2Health CareMedical Records | GGHC v2.2 | Health Care | Medical Records |  | 0.15
GGHC v2.2Health CareNursing Stations- General | GGHC v2.2 | Health Care | Nursing Stations- General |  | 0.15
GGHC v2.2Health CareStairways | GGHC v2.2 | Health Care | Stairways |  | 0.15
GGHC v2.2Health CareWaiting Areas/Lounges | GGHC v2.2 | Health Care | Waiting Areas/Lounges |  | 0.15
ASHRAE 62.1-2004Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2004 | Educational Facilities | Daycare (through age 4) | 10 | 0.18
ASHRAE 62.1-2004Educational FacilitiesArt classroom | ASHRAE 62.1-2004 | Educational Facilities | Art classroom | 10 | 0.18
ASHRAE 62.1-2004Educational FacilitiesScience laboratories | ASHRAE 62.1-2004 | Educational Facilities | Science laboratories | 10 | 0.18 |  | E
ASHRAE 62.1-2004Educational FacilitiesWood/metal shop | ASHRAE 62.1-2004 | Educational Facilities | Wood/metal shop | 10 | 0.18
ASHRAE 62.1-2004Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2004 | Food and Beverage Service | Restaurant dining rooms | 7.5 | 0.18
ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | 7.5 | 0.18
ASHRAE 62.1-2004Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2004 | Food and Beverage Service | Bars, cocktail lounges | 7.5 | 0.18
ASHRAE 62.1-2004Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Pharmacy (prep. area) | 5 | 0.18
ASHRAE 62.1-2004RetailPet shops (animal areas) | ASHRAE 62.1-2004 | Retail | Pet shops (animal areas) | 7.5 | 0.18
ASHRAE 62.1-2004Sports and EntertainmentGambling casinos | ASHRAE 62.1-2004 | Sports and Entertainment | Gambling casinos | 7.5 | 0.18
ASHRAE 62.1-2004Sports and EntertainmentGame arcades | ASHRAE 62.1-2004 | Sports and Entertainment | Game arcades | 7.5 | 0.18
ASHRAE 62.1-2007Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2007 | Educational Facilities | Daycare (through age 4) | 10 | 0.18
ASHRAE 62.1-2007Educational FacilitiesArt classroom | ASHRAE 62.1-2007 | Educational Facilities | Art classroom | 10 | 0.18
ASHRAE 62.1-2007Educational FacilitiesScience laboratories | ASHRAE 62.1-2007 | Educational Facilities | Science laboratories | 10 | 0.18 |  | E
ASHRAE 62.1-2007Educational FacilitiesWood/metal shop | ASHRAE 62.1-2007 | Educational Facilities | Wood/metal shop | 10 | 0.18
ASHRAE 62.1-2007Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2007 | Food and Beverage Service | Restaurant dining rooms | 7.5 | 0.18
ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | 7.5 | 0.18
ASHRAE 62.1-2007Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2007 | Food and Beverage Service | Bars, cocktail lounges | 7.5 | 0.18
ASHRAE 62.1-2007Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Pharmacy (prep. area) | 5 | 0.18
ASHRAE 62.1-2007RetailPet shops (animal areas) | ASHRAE 62.1-2007 | Retail | Pet shops (animal areas) | 7.5 | 0.18
ASHRAE 62.1-2007Sports and EntertainmentGambling casinos | ASHRAE 62.1-2007 | Sports and Entertainment | Gambling casinos | 7.5 | 0.18
ASHRAE 62.1-2007Sports and EntertainmentGame arcades | ASHRAE 62.1-2007 | Sports and Entertainment | Game arcades | 7.5 | 0.18
ASHRAE 62.1-1999Sports and AmusementBallrooms and discos | ASHRAE 62.1-1999 | Sports and Amusement | Ballrooms and discos | 25 | 0
ASHRAE 62.1-1999Sports and AmusementBowling alleys (seating areas) | ASHRAE 62.1-1999 | Sports and Amusement | Bowling alleys (seating areas) | 25 | 0
ASHRAE 62.1-1999Sports and AmusementIce arenas (playing areas) | ASHRAE 62.1-1999 | Sports and Amusement | Ice arenas (playing areas) | 0 | 0.5 |  | Higher may be needed if internal combustion engines are operated for maintenance
ASHRAE 62.1-1999Sports and AmusementSwimming pools (pool and deck areas) | ASHRAE 62.1-1999 | Sports and Amusement | Swimming pools (pool and deck areas) | 0 | 0.5 |  | Higher may be needed for humidity control
ASHRAE 62.1-1999TheatersTicket booths | ASHRAE 62.1-1999 | Theaters | Ticket booths | 20 | 0
ASHRAE 62.1-2004Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Sports arena (play area) |  | 0.3
ASHRAE 62.1-2004Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Gym, stadium (play area) |  | 0.3
ASHRAE 62.1-2007Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Sports arena (play area) |  | 0.3
ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) |  | 0.3
GGHC v2.2Health CareAngiographic-All Other Types | GGHC v2.2 | Health Care | Angiographic-All Other Types |  | 0.3
GGHC v2.2Health CareAutopsy | GGHC v2.2 | Health Care | Autopsy |  | 0.3
GGHC v2.2Health CareCast Room | GGHC v2.2 | Health Care | Cast Room |  | 0.3
GGHC v2.2Health CareClean Linen Storage | GGHC v2.2 | Health Care | Clean Linen Storage |  | 0.3
GGHC v2.2Health CareClean Utility / Workroom | GGHC v2.2 | Health Care | Clean Utility / Workroom |  | 0.3
GGHC v2.2Health CareCorridors | GGHC v2.2 | Health Care | Corridors |  | 0.3
GGHC v2.2Health CareDarkroom | GGHC v2.2 | Health Care | Darkroom |  | 0.3
GGHC v2.2Health CareDecontamination | GGHC v2.2 | Health Care | Decontamination |  | 0.3
GGHC v2.2Health CareDietary Day Storage | GGHC v2.2 | Health Care | Dietary Day Storage |  | 0.3
GGHC v2.2Health CareDishwashing | GGHC v2.2 | Health Care | Dishwashing |  | 0.3
GGHC v2.2Health CareEndoscopy | GGHC v2.2 | Health Care | Endoscopy |  | 0.3
GGHC v2.2Health CareHistology | GGHC v2.2 | Health Care | Histology |  | 0.3
GGHC v2.2Health CareIsolation | GGHC v2.2 | Health Care | Isolation |  | 0.3
GGHC v2.2Health CareKitchen, Food Preparation | GGHC v2.2 | Health Care | Kitchen, Food Preparation |  | 0.3
GGHC v2.2Health CareLabor/ Delivery/Recovery | GGHC v2.2 | Health Care | Labor/ Delivery/Recovery |  | 0.3
GGHC v2.2Health CareL / D / R / Post Partum | GGHC v2.2 | Health Care | L / D / R / Post Partum |  | 0.3
GGHC v2.2Health CareLaboratory | GGHC v2.2 | Health Care | Laboratory |  | 0.3
GGHC v2.2Health CareLinen Storage, Clean | GGHC v2.2 | Health Care | Linen Storage, Clean |  | 0.3
GGHC v2.2Health CareMammography | GGHC v2.2 | Health Care | Mammography |  | 0.3
GGHC v2.2Health CareNuclear Medicine, Hot Lab | GGHC v2.2 | Health Care | Nuclear Medicine, Hot Lab |  | 0.3
GGHC v2.2Health CarePathology | GGHC v2.2 | Health Care | Pathology |  | 0.3
GGHC v2.2Health CarePatient Room | GGHC v2.2 | Health Care | Patient Room |  | 0.3
GGHC v2.2Health CarePharmacy / Medicine Room | GGHC v2.2 | Health Care | Pharmacy / Medicine Room |  | 0.3
GGHC v2.2Health CarePhysical Therapy and Hydrotherapy | GGHC v2.2 | Health Care | Physical Therapy and Hydrotherapy |  | 0.3
GGHC v2.2Health CareRecovery | GGHC v2.2 | Health Care | Recovery |  | 0.3
GGHC v2.2Health CareScrub Up Area, Surgical Corridor | GGHC v2.2 | Health Care | Scrub Up Area, Surgical Corridor |  | 0.3
GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic |  | 0.3
GGHC v2.2Health CareSub-Sterile | GGHC v2.2 | Health Care | Sub-Sterile |  | 0.3
GGHC v2.2Health CareSurgical Supply | GGHC v2.2 | Health Care | Surgical Supply |  | 0.3
GGHC v2.2Health CareTreatment / Examination | GGHC v2.2 | Health Care | Treatment / Examination |  | 0.3
GGHC v2.2Health CareUnsterile Supply | GGHC v2.2 | Health Care | Unsterile Supply |  | 0.3
GGHC v2.2Health CareX-ray, Diagnostic and Treatment | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment |  | 0.3
GGHC v2.2Health CareNursery, General | GGHC v2.2 | Health Care | Nursery, General |  | 0.45
GGHC v2.2Health CareNursery, Exam | GGHC v2.2 | Health Care | Nursery, Exam |  | 0.45
ASHRAE 62.1-2004Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2004 | Sports and Entertainment | Swimming (pool & deck) |  | 0.48 |  | C
ASHRAE 62.1-2007Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2007 | Sports and Entertainment | Swimming (pool & deck) |  | 0.48 |  | C
ASHRAE 62.1-1999TheatersLobbies | ASHRAE 62.1-1999 | Theaters | Lobbies | 20 | 0
ASHRAE 62.1-1999TheatersAuditorium | ASHRAE 62.1-1999 | Theaters | Auditorium | 15 | 0
ASHRAE 62.1-1999TheatersStages, studios | ASHRAE 62.1-1999 | Theaters | Stages, studios | 15 | 0
ASHRAE 62.1-1999TransportationWaiting rooms | ASHRAE 62.1-1999 | Transportation | Waiting rooms | 15 | 0
ASHRAE 62.1-1999TransportationPlatforms | ASHRAE 62.1-1999 | Transportation | Platforms | 15 | 0
ASHRAE 62.1-1999TransportationVehicles | ASHRAE 62.1-1999 | Transportation | Vehicles | 15 | 0
ASHRAE 62.1-1999WorkroomsMeat processing | ASHRAE 62.1-1999 | Workrooms | Meat processing | 15 | 0
GGHC v2.2Health CareConference Rooms | GGHC v2.2 | Health Care | Conference Rooms |  | 0.5
GGHC v2.2Health CareAngiographic-Heart Only | GGHC v2.2 | Health Care | Angiographic-Heart Only |  | 0.75
GGHC v2.2Health CareCystoscopy | GGHC v2.2 | Health Care | Cystoscopy |  | 0.75
GGHC v2.2Health CareDelivery Room | GGHC v2.2 | Health Care | Delivery Room |  | 0.75
GGHC v2.2Health CareOperating Room | GGHC v2.2 | Health Care | Operating Room |  | 0.75
GGHC v2.2Health CareSpecial Procedure Room, Invasive | GGHC v2.2 | Health Care | Special Procedure Room, Invasive |  | 0.75
GGHC v2.2Health CareTrauma | GGHC v2.2 | Health Care | Trauma |  | 0.75
ASHRAE 62.1-1999WorkroomsPhoto studios | ASHRAE 62.1-1999 | Workrooms | Photo studios | 15 | 0
ASHRAE 62.1-1999WorkroomsPharmacy | ASHRAE 62.1-1999 | Workrooms | Pharmacy | 15 | 0
ASHRAE 62.1-1999WorkroomsBank vaults | ASHRAE 62.1-1999 | Workrooms | Bank vaults | 15 | 0
GGHC v2.2Health CareAnesthesia Storage | GGHC v2.2 | Health Care | Anesthesia Storage |  | 1.2
ASHRAE 62.1-1999WorkroomsDarkrooms | ASHRAE 62.1-1999 | Workrooms | Darkrooms | 0 | 0.5
ASHRAE 62.1-1999WorkroomsDuplicating, printing | ASHRAE 62.1-1999 | Workrooms | Duplicating, printing | 0 | 0.5
GGHC v2.2Health CareDining Room | GGHC v2.2 | Health Care | Dining Room |  | 1.5
GGHC v2.2Health CareJanitors Closet / Utility | GGHC v2.2 | Health Care | Janitors Closet / Utility |  | 1.5
GGHC v2.2Health CareSoiled Linen, Sorting | GGHC v2.2 | Health Care | Soiled Linen, Sorting |  | 1.5
GGHC v2.2Health CareSterilizer Room | GGHC v2.2 | Health Care | Sterilizer Room |  | 1.5
GGHC v2.2Health CareTrash Chute Room | GGHC v2.2 | Health Care | Trash Chute Room |  | 1.5
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 25 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 30 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms |  | 0.5 |  | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 15
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 25 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 30 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms |  | 0.5 |  | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 15
AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms |  |  | 3
AIA 2001Surgery and Critical CareDelivery Room | AIA 2001 | Surgery and Critical Care | Delivery Room |  |  | 3
AIA 2001Surgery and Critical CareRecovery Room | AIA 2001 | Surgery and Critical Care | Recovery Room |  |  | 2
AIA 2001Surgery and Critical CareCritical and Intensive Care | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care |  |  | 2
AIA 2001Surgery and Critical CareNewborn Intensive Care | AIA 2001 | Surgery and Critical Care | Newborn Intensive Care |  |  | 2
AIA 2001Surgery and Critical CareTrauma Room | AIA 2001 | Surgery and Critical Care | Trauma Room |  |  | 3
AIA 2001Surgery and Critical CareEndoscopy | AIA 2001 | Surgery and Critical Care | Endoscopy |  |  | 2
AIA 2001Surgery and Critical CareBronchoscopy | AIA 2001 | Surgery and Critical Care | Bronchoscopy |  |  | 2
AIA 2001Surgery and Critical CareER Waiting Room | AIA 2001 | Surgery and Critical Care | ER Waiting Room |  |  | 2
AIA 2001Surgery and Critical CareTriage | AIA 2001 | Surgery and Critical Care | Triage |  |  | 2
AIA 2001Surgery and Critical CareRadiology Waiting Rooms | AIA 2001 | Surgery and Critical Care | Radiology Waiting Rooms |  |  | 2
AIA 2001Surgery and Critical CareProcedure Room | AIA 2001 | Surgery and Critical Care | Procedure Room |  |  | 3
AIA 2001NursingPatient Room | AIA 2001 | Nursing | Patient Room |  |  | 2
AIA 2001NursingNewborn Nursery Suite | AIA 2001 | Nursing | Newborn Nursery Suite |  |  | 2
AIA 2001NursingProtective Environment Room | AIA 2001 | Nursing | Protective Environment Room |  |  | 2
AIA 2001NursingAirborne Infection Isolation Room | AIA 2001 | Nursing | Airborne Infection Isolation Room |  |  | 2
AIA 2001NursingLabor/Delivery/Recovery | AIA 2001 | Nursing | Labor/Delivery/Recovery |  |  | 2
AIA 2001NursingLabor/Delivery/Recovery/Postpartum | AIA 2001 | Nursing | Labor/Delivery/Recovery/Postpartum |  |  | 2
AIA 2001AncillaryX-Ray (Surgical/Critical Care and Catheterization) | AIA 2001 | Ancillary | X-Ray (Surgical/Critical Care and Catheterization) |  |  | 3

## Occupancy
occupancy
VlookupColumn | Ventilation Standard | Primary Space Type | Secondary Space Type | people/1000 ft^2 | Notes
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial laundry | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial laundry | 10
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial dry cleaner | 30
ASHRAE 62.1-1999Dry Cleaners, LaundriesStorage, pick up | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Storage, pick up | 30
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated laundries | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated laundries | 20
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated dry cleaner | 20
ASHRAE 62.1-1999Food and Beverage ServiceDining rooms | ASHRAE 62.1-1999 | Food and Beverage Service | Dining rooms | 70
ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | 100
ASHRAE 62.1-1999Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-1999 | Food and Beverage Service | Bars, cocktail lounges | 100
ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | 20 | Exhaust >= 1.5 cfm/ft2, 7.5 L/s m2
ASHRAE 62.1-1999Garages, Repair, Service StationsEnclosed parking garage | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Enclosed parking garage | 0
ASHRAE 62.1-1999Garages, Repair, Service StationsAuto repair rooms | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Auto repair rooms | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBedrooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Bedrooms | 0 | 30 cfm/room, 15 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLiving rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Living rooms | 0 | 30 cfm/room, 15 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBaths | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Baths | 0 | 35 cfm/room, 18 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | 30
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | 50
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesAssembly rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Assembly rooms | 120
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | 20
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesGambling casinos | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Gambling casinos | 120
ASHRAE 62.1-1999OfficesOffice space | ASHRAE 62.1-1999 | Offices | Office space | 7
ASHRAE 62.1-1999OfficesReception areas | ASHRAE 62.1-1999 | Offices | Reception areas | 60
ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | 60
ASHRAE 62.1-1999OfficesConference rooms | ASHRAE 62.1-1999 | Offices | Conference rooms | 50
ASHRAE 62.1-1999Public SpacesCorridors and utilities | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | 0
ASHRAE 62.1-1999Public SpacesPublic restrooms | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | 0 | (Assume 12 toilet/625 ft^2) 50 cfm/wc or urinal, 25 L/s wc or urinal
ASHRAE 62.1-1999Public SpacesLocker and dressing rooms | ASHRAE 62.1-1999 | Public Spaces | Locker and dressing rooms | 0
ASHRAE 62.1-1999Public SpacesSmoking lounge | ASHRAE 62.1-1999 | Public Spaces | Smoking lounge | 70
ASHRAE 62.1-1999Public SpacesElevators | ASHRAE 62.1-1999 | Public Spaces | Elevators | 0
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | 30
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsUpper floors | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Upper floors | 20
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | 15
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsDressing rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Dressing rooms | 0
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsMalls and arcades | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Malls and arcades | 20
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | 10
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | 5
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsSmoking lounge | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Smoking lounge | 70
ASHRAE 62.1-1999Specialty ShopsBarber | ASHRAE 62.1-1999 | Specialty Shops | Barber | 25
ASHRAE 62.1-1999Specialty ShopsBeauty | ASHRAE 62.1-1999 | Specialty Shops | Beauty | 25
ASHRAE 62.1-1999Specialty ShopsReducing salons | ASHRAE 62.1-1999 | Specialty Shops | Reducing salons | 20
ASHRAE 62.1-1999Specialty ShopsFlorists | ASHRAE 62.1-1999 | Specialty Shops | Florists | 8
ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | 0
ASHRAE 62.1-1999Specialty ShopsHardware, drugs, fabric | ASHRAE 62.1-1999 | Specialty Shops | Hardware, drugs, fabric | 8
ASHRAE 62.1-1999Specialty ShopsSupermarket | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | 8
ASHRAE 62.1-1999Specialty ShopsPet shops | ASHRAE 62.1-1999 | Specialty Shops | Pet shops | 0
ASHRAE 62.1-1999Sports and AmusementSpectator areas | ASHRAE 62.1-1999 | Sports and Amusement | Spectator areas | 150
ASHRAE 62.1-1999Sports and AmusementGame rooms | ASHRAE 62.1-1999 | Sports and Amusement | Game rooms | 70
ASHRAE 62.1-1999Sports and AmusementIce arenas (playing areas) | ASHRAE 62.1-1999 | Sports and Amusement | Ice arenas (playing areas) | 0 | Higher may be needed if internal combustion engines are operated for maintenance
ASHRAE 62.1-1999Sports and AmusementSwimming pools (pool and deck areas) | ASHRAE 62.1-1999 | Sports and Amusement | Swimming pools (pool and deck areas) | 0 | Higher may be needed for humidity control
ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | 30
ASHRAE 62.1-1999Sports and AmusementBallrooms and discos | ASHRAE 62.1-1999 | Sports and Amusement | Ballrooms and discos | 100
ASHRAE 62.1-1999Sports and AmusementBowling alleys (seating areas) | ASHRAE 62.1-1999 | Sports and Amusement | Bowling alleys (seating areas) | 70
ASHRAE 62.1-1999TheatersTicket booths | ASHRAE 62.1-1999 | Theaters | Ticket booths | 60
ASHRAE 62.1-1999TheatersLobbies | ASHRAE 62.1-1999 | Theaters | Lobbies | 150
ASHRAE 62.1-1999TheatersAuditorium | ASHRAE 62.1-1999 | Theaters | Auditorium | 150
ASHRAE 62.1-1999TheatersStages, studios | ASHRAE 62.1-1999 | Theaters | Stages, studios | 70
ASHRAE 62.1-1999TransportationWaiting rooms | ASHRAE 62.1-1999 | Transportation | Waiting rooms | 100
ASHRAE 62.1-1999TransportationPlatforms | ASHRAE 62.1-1999 | Transportation | Platforms | 100
ASHRAE 62.1-1999TransportationVehicles | ASHRAE 62.1-1999 | Transportation | Vehicles | 150
ASHRAE 62.1-1999WorkroomsMeat processing | ASHRAE 62.1-1999 | Workrooms | Meat processing | 10
ASHRAE 62.1-1999WorkroomsPhoto studios | ASHRAE 62.1-1999 | Workrooms | Photo studios | 10
ASHRAE 62.1-1999WorkroomsDarkrooms | ASHRAE 62.1-1999 | Workrooms | Darkrooms | 10
ASHRAE 62.1-1999WorkroomsPharmacy | ASHRAE 62.1-1999 | Workrooms | Pharmacy | 20
ASHRAE 62.1-1999WorkroomsBank vaults | ASHRAE 62.1-1999 | Workrooms | Bank vaults | 5
ASHRAE 62.1-1999WorkroomsDuplicating, printing | ASHRAE 62.1-1999 | Workrooms | Duplicating, printing | 0
ASHRAE 62.1-1999EducationClassroom | ASHRAE 62.1-1999 | Education | Classroom | 50
ASHRAE 62.1-1999EducationLaboratories | ASHRAE 62.1-1999 | Education | Laboratories | 30
ASHRAE 62.1-1999EducationTraining shop | ASHRAE 62.1-1999 | Education | Training shop | 30
ASHRAE 62.1-1999EducationMusic rooms | ASHRAE 62.1-1999 | Education | Music rooms | 50
ASHRAE 62.1-1999EducationLibraries | ASHRAE 62.1-1999 | Education | Libraries | 20
ASHRAE 62.1-1999EducationLocker rooms | ASHRAE 62.1-1999 | Education | Locker rooms | 0
ASHRAE 62.1-1999EducationCorridors | ASHRAE 62.1-1999 | Education | Corridors | 0
ASHRAE 62.1-1999EducationAuditorium | ASHRAE 62.1-1999 | Education | Auditorium | 150
ASHRAE 62.1-1999EducationSmoking lounges | ASHRAE 62.1-1999 | Education | Smoking lounges | 70
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 10
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 20
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 20
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 20
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 20
ASHRAE 62.1-1999Correctional FacilitiesCell | ASHRAE 62.1-1999 | Correctional Facilities | Cell | 20
ASHRAE 62.1-1999Correctional FacilitiesDining halls | ASHRAE 62.1-1999 | Correctional Facilities | Dining halls | 100
ASHRAE 62.1-1999Correctional FacilitiesGuard stations | ASHRAE 62.1-1999 | Correctional Facilities | Guard stations | 40
ASHRAE 62.1-2004Correctional FacilitiesCell | ASHRAE 62.1-2004 | Correctional Facilities | Cell | 25
ASHRAE 62.1-2004Correctional FacilitiesDay room | ASHRAE 62.1-2004 | Correctional Facilities | Day room | 30
ASHRAE 62.1-2004Correctional FacilitiesGuard stations | ASHRAE 62.1-2004 | Correctional Facilities | Guard stations | 15
ASHRAE 62.1-2004Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2004 | Correctional Facilities | Booking/waiting | 50
ASHRAE 62.1-2004Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2004 | Educational Facilities | Daycare (through age 4) | 25
ASHRAE 62.1-2004Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (ages 5-8) | 25
ASHRAE 62.1-2004Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (age 9 plus) | 35
ASHRAE 62.1-2004Educational FacilitiesLecture classroom | ASHRAE 62.1-2004 | Educational Facilities | Lecture classroom | 65
ASHRAE 62.1-2004Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2004 | Educational Facilities | Lecture hall (fixed seats) | 150
ASHRAE 62.1-2004Educational FacilitiesArt classroom | ASHRAE 62.1-2004 | Educational Facilities | Art classroom | 20
ASHRAE 62.1-2004Educational FacilitiesScience laboratories | ASHRAE 62.1-2004 | Educational Facilities | Science laboratories | 25 | E
ASHRAE 62.1-2004Educational FacilitiesWood/metal shop | ASHRAE 62.1-2004 | Educational Facilities | Wood/metal shop | 20
ASHRAE 62.1-2004Educational FacilitiesComputer lab | ASHRAE 62.1-2004 | Educational Facilities | Computer lab | 25
ASHRAE 62.1-2004Educational FacilitiesMedia center | ASHRAE 62.1-2004 | Educational Facilities | Media center | 25 | A
ASHRAE 62.1-2004Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2004 | Educational Facilities | Music/theater/dance | 35
ASHRAE 62.1-2004Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2004 | Educational Facilities | Multiuse assembly | 100
ASHRAE 62.1-2004Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2004 | Food and Beverage Service | Restaurant dining rooms | 70
ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | 100
ASHRAE 62.1-2004Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2004 | Food and Beverage Service | Bars, cocktail lounges | 100
ASHRAE 62.1-2004GeneralConference/meeting | ASHRAE 62.1-2004 | General | Conference/meeting | 50
ASHRAE 62.1-2004GeneralCorridors | ASHRAE 62.1-2004 | General | Corridors | 0
ASHRAE 62.1-2004GeneralStorage rooms | ASHRAE 62.1-2004 | General | Storage rooms | 0 | B
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 10
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 20
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 30
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 120
ASHRAE 62.1-2004Office BuildingsOffice space | ASHRAE 62.1-2004 | Office Buildings | Office space | 5
ASHRAE 62.1-2004Office BuildingsReception areas | ASHRAE 62.1-2004 | Office Buildings | Reception areas | 30
ASHRAE 62.1-2004Office BuildingsTelephone/data entry | ASHRAE 62.1-2004 | Office Buildings | Telephone/data entry | 60
ASHRAE 62.1-2004Office BuildingsMain entry lobbies | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | 10
ASHRAE 62.1-2004Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2004 | Miscellaneous Spaces | Bank vaults/safe deposit | 5
ASHRAE 62.1-2004Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Computer (not printing) | 4
ASHRAE 62.1-2004Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Pharmacy (prep. area) | 10
ASHRAE 62.1-2004Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2004 | Miscellaneous Spaces | Photo studios | 10
ASHRAE 62.1-2004Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2004 | Miscellaneous Spaces | Shipping/receiving | 0 | B
ASHRAE 62.1-2004Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2004 | Miscellaneous Spaces | Transportation waiting | 100
ASHRAE 62.1-2004Miscellaneous SpacesWarehouses | ASHRAE 62.1-2004 | Miscellaneous Spaces | Warehouses | 0 | B
ASHRAE 62.1-2004Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2004 | Public Assembly Spaces | Auditorium seating area | 150
ASHRAE 62.1-2004Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2004 | Public Assembly Spaces | Places of religious worship | 120
ASHRAE 62.1-2004Public Assembly SpacesCourtrooms | ASHRAE 62.1-2004 | Public Assembly Spaces | Courtrooms | 70
ASHRAE 62.1-2004Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2004 | Public Assembly Spaces | Legislative chambers | 50
ASHRAE 62.1-2004Public Assembly SpacesLibraries | ASHRAE 62.1-2004 | Public Assembly Spaces | Libraries | 10
ASHRAE 62.1-2004Public Assembly SpacesLobbies | ASHRAE 62.1-2004 | Public Assembly Spaces | Lobbies | 150
ASHRAE 62.1-2004Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums (children’s) | 40
ASHRAE 62.1-2004Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums/galleries | 40
ASHRAE 62.1-2004RetailGeneral Sales | ASHRAE 62.1-2004 | Retail | General Sales | 15
ASHRAE 62.1-2004RetailMall common areas | ASHRAE 62.1-2004 | Retail | Mall common areas | 40
ASHRAE 62.1-2004RetailBarber shop | ASHRAE 62.1-2004 | Retail | Barber shop | 25
ASHRAE 62.1-2004RetailBeauty and nail salons | ASHRAE 62.1-2004 | Retail | Beauty and nail salons | 25
ASHRAE 62.1-2004RetailPet shops (animal areas) | ASHRAE 62.1-2004 | Retail | Pet shops (animal areas) | 10
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 8
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 8
ASHRAE 62.1-2004RetailCoinoperated laundries | ASHRAE 62.1-2004 | Retail | Coinoperated laundries | 20
ASHRAE 62.1-2004Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Sports arena (play area) | 0
ASHRAE 62.1-2004Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Gym, stadium (play area) | 30
ASHRAE 62.1-2004Sports and EntertainmentSpectator areas | ASHRAE 62.1-2004 | Sports and Entertainment | Spectator areas | 150
ASHRAE 62.1-2004Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2004 | Sports and Entertainment | Swimming (pool & deck) | 0 | C
ASHRAE 62.1-2004Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2004 | Sports and Entertainment | Disco/dance floors | 100
ASHRAE 62.1-2004Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/aerobics room | 40
ASHRAE 62.1-2004Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/weight rooms | 10
ASHRAE 62.1-2004Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2004 | Sports and Entertainment | Bowling alley (seating) | 40
ASHRAE 62.1-2004Sports and EntertainmentGambling casinos | ASHRAE 62.1-2004 | Sports and Entertainment | Gambling casinos | 120
ASHRAE 62.1-2004Sports and EntertainmentGame arcades | ASHRAE 62.1-2004 | Sports and Entertainment | Game arcades | 20
ASHRAE 62.1-2004Sports and EntertainmentStages, studios | ASHRAE 62.1-2004 | Sports and Entertainment | Stages, studios | 70 | D
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 10 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 20 | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 20
ASHRAE 62.1-2007Correctional FacilitiesCell | ASHRAE 62.1-2007 | Correctional Facilities | Cell | 25
ASHRAE 62.1-2007Correctional FacilitiesDay room | ASHRAE 62.1-2007 | Correctional Facilities | Day room | 30
ASHRAE 62.1-2007Correctional FacilitiesGuard stations | ASHRAE 62.1-2007 | Correctional Facilities | Guard stations | 15
ASHRAE 62.1-2007Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2007 | Correctional Facilities | Booking/waiting | 50
ASHRAE 62.1-2007Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2007 | Educational Facilities | Daycare (through age 4) | 25
ASHRAE 62.1-2007Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (ages 5-8) | 25
ASHRAE 62.1-2007Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (age 9 plus) | 35
ASHRAE 62.1-2007Educational FacilitiesLecture classroom | ASHRAE 62.1-2007 | Educational Facilities | Lecture classroom | 65
ASHRAE 62.1-2007Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2007 | Educational Facilities | Lecture hall (fixed seats) | 150
ASHRAE 62.1-2007Educational FacilitiesArt classroom | ASHRAE 62.1-2007 | Educational Facilities | Art classroom | 20
ASHRAE 62.1-2007Educational FacilitiesScience laboratories | ASHRAE 62.1-2007 | Educational Facilities | Science laboratories | 25 | E
ASHRAE 62.1-2007Educational FacilitiesWood/metal shop | ASHRAE 62.1-2007 | Educational Facilities | Wood/metal shop | 20
ASHRAE 62.1-2007Educational FacilitiesComputer lab | ASHRAE 62.1-2007 | Educational Facilities | Computer lab | 25
ASHRAE 62.1-2007Educational FacilitiesMedia center | ASHRAE 62.1-2007 | Educational Facilities | Media center | 25 | A
ASHRAE 62.1-2007Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2007 | Educational Facilities | Music/theater/dance | 35
ASHRAE 62.1-2007Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2007 | Educational Facilities | Multiuse assembly | 100
ASHRAE 62.1-2007Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2007 | Food and Beverage Service | Restaurant dining rooms | 70
ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | 100
ASHRAE 62.1-2007Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2007 | Food and Beverage Service | Bars, cocktail lounges | 100
ASHRAE 62.1-2007GeneralConference/meeting | ASHRAE 62.1-2007 | General | Conference/meeting | 50
ASHRAE 62.1-2007GeneralCorridors | ASHRAE 62.1-2007 | General | Corridors | 0
ASHRAE 62.1-2007GeneralStorage rooms | ASHRAE 62.1-2007 | General | Storage rooms | 0 | B
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 10
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 20
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 30
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 120
ASHRAE 62.1-2007Office BuildingsOffice space | ASHRAE 62.1-2007 | Office Buildings | Office space | 5
ASHRAE 62.1-2007Office BuildingsReception areas | ASHRAE 62.1-2007 | Office Buildings | Reception areas | 30
ASHRAE 62.1-2007Office BuildingsTelephone/data entry | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | 60
ASHRAE 62.1-2007Office BuildingsMain entry lobbies | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | 10
ASHRAE 62.1-2007Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2007 | Miscellaneous Spaces | Bank vaults/safe deposit | 5
ASHRAE 62.1-2007Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Computer (not printing) | 4
ASHRAE 62.1-2007Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Pharmacy (prep. area) | 10
ASHRAE 62.1-2007Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2007 | Miscellaneous Spaces | Photo studios | 10
ASHRAE 62.1-2007Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2007 | Miscellaneous Spaces | Shipping/receiving | 0 | B
ASHRAE 62.1-2007Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2007 | Miscellaneous Spaces | Transportation waiting | 100
ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses | 0 | B
ASHRAE 62.1-2007Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2007 | Public Assembly Spaces | Auditorium seating area | 150
ASHRAE 62.1-2007Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2007 | Public Assembly Spaces | Places of religious worship | 120
ASHRAE 62.1-2007Public Assembly SpacesCourtrooms | ASHRAE 62.1-2007 | Public Assembly Spaces | Courtrooms | 70
ASHRAE 62.1-2007Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2007 | Public Assembly Spaces | Legislative chambers | 50
ASHRAE 62.1-2007Public Assembly SpacesLibraries | ASHRAE 62.1-2007 | Public Assembly Spaces | Libraries | 10
ASHRAE 62.1-2007Public Assembly SpacesLobbies | ASHRAE 62.1-2007 | Public Assembly Spaces | Lobbies | 150
ASHRAE 62.1-2007Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums (children’s) | 40
ASHRAE 62.1-2007Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums/galleries | 40
ASHRAE 62.1-2007RetailGeneral Sales | ASHRAE 62.1-2007 | Retail | General Sales | 15
ASHRAE 62.1-2007RetailMall common areas | ASHRAE 62.1-2007 | Retail | Mall common areas | 40
ASHRAE 62.1-2007RetailBarber shop | ASHRAE 62.1-2007 | Retail | Barber shop | 25
ASHRAE 62.1-2007RetailBeauty and nail salons | ASHRAE 62.1-2007 | Retail | Beauty and nail salons | 25
ASHRAE 62.1-2007RetailPet shops (animal areas) | ASHRAE 62.1-2007 | Retail | Pet shops (animal areas) | 10
ASHRAE 62.1-2007RetailSupermarket | ASHRAE 62.1-2007 | Retail | Supermarket | 8
ASHRAE 62.1-2007RetailCoinoperated laundries | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | 20
ASHRAE 62.1-2007Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Sports arena (play area) | 0
ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) | 30
ASHRAE 62.1-2007Sports and EntertainmentSpectator areas | ASHRAE 62.1-2007 | Sports and Entertainment | Spectator areas | 150
ASHRAE 62.1-2007Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2007 | Sports and Entertainment | Swimming (pool & deck) | 0 | C
ASHRAE 62.1-2007Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2007 | Sports and Entertainment | Disco/dance floors | 100
ASHRAE 62.1-2007Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/aerobics room | 40
ASHRAE 62.1-2007Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/weight rooms | 10
ASHRAE 62.1-2007Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2007 | Sports and Entertainment | Bowling alley (seating) | 40
ASHRAE 62.1-2007Sports and EntertainmentGambling casinos | ASHRAE 62.1-2007 | Sports and Entertainment | Gambling casinos | 120
ASHRAE 62.1-2007Sports and EntertainmentGame arcades | ASHRAE 62.1-2007 | Sports and Entertainment | Game arcades | 20
ASHRAE 62.1-2007Sports and EntertainmentStages, studios | ASHRAE 62.1-2007 | Sports and Entertainment | Stages, studios | 70 | D
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 10 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 20 | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 20
GGHC v2.2Health CareAnesthesia Storage | GGHC v2.2 | Health Care | Anesthesia Storage | 5
GGHC v2.2Health CareAngiographic-All Other Types | GGHC v2.2 | Health Care | Angiographic-All Other Types | 5
GGHC v2.2Health CareAngiographic-Heart Only | GGHC v2.2 | Health Care | Angiographic-Heart Only | 5
GGHC v2.2Health CareAutopsy | GGHC v2.2 | Health Care | Autopsy | 5
GGHC v2.2Health CareBathroom/ Public | GGHC v2.2 | Health Care | Bathroom/ Public | 3.3
GGHC v2.2Health CareBedpan Room | GGHC v2.2 | Health Care | Bedpan Room | 5
GGHC v2.2Health CareCast Room | GGHC v2.2 | Health Care | Cast Room | 5
GGHC v2.2Health CareClean Linen Storage | GGHC v2.2 | Health Care | Clean Linen Storage | 1
GGHC v2.2Health CareClean Utility / Workroom | GGHC v2.2 | Health Care | Clean Utility / Workroom | 5
GGHC v2.2Health CareConference Rooms | GGHC v2.2 | Health Care | Conference Rooms | 20
GGHC v2.2Health CareCorridors | GGHC v2.2 | Health Care | Corridors | 10
GGHC v2.2Health CareCystoscopy | GGHC v2.2 | Health Care | Cystoscopy | 5
GGHC v2.2Health CareDarkroom | GGHC v2.2 | Health Care | Darkroom | 5
GGHC v2.2Health CareDecontamination | GGHC v2.2 | Health Care | Decontamination | 5
GGHC v2.2Health CareDelivery Room | GGHC v2.2 | Health Care | Delivery Room | 5
GGHC v2.2Health CareDietary Day Storage | GGHC v2.2 | Health Care | Dietary Day Storage | 2
GGHC v2.2Health CareDining Room | GGHC v2.2 | Health Care | Dining Room | 10
GGHC v2.2Health CareDishwashing | GGHC v2.2 | Health Care | Dishwashing | 5
GGHC v2.2Health CareEndoscopy | GGHC v2.2 | Health Care | Endoscopy | 5
GGHC v2.2Health CareHistology | GGHC v2.2 | Health Care | Histology | 5
GGHC v2.2Health CareIsolation | GGHC v2.2 | Health Care | Isolation | 5
GGHC v2.2Health CareJanitors Closet / Utility | GGHC v2.2 | Health Care | Janitors Closet / Utility | 1
GGHC v2.2Health CareKitchen, Food Preparation | GGHC v2.2 | Health Care | Kitchen, Food Preparation | 5
GGHC v2.2Health CareLabor/ Delivery/Recovery | GGHC v2.2 | Health Care | Labor/ Delivery/Recovery | 5
GGHC v2.2Health CareL / D / R / Post Partum | GGHC v2.2 | Health Care | L / D / R / Post Partum | 5
GGHC v2.2Health CareLaboratory | GGHC v2.2 | Health Care | Laboratory | 5
GGHC v2.2Health CareLinen Storage, Clean | GGHC v2.2 | Health Care | Linen Storage, Clean | 2
GGHC v2.2Health CareLobby | GGHC v2.2 | Health Care | Lobby | 10
GGHC v2.2Health CareLockers | GGHC v2.2 | Health Care | Lockers | 10
GGHC v2.2Health CareMammography | GGHC v2.2 | Health Care | Mammography | 5
GGHC v2.2Health CareMechanical Equipment Room | GGHC v2.2 | Health Care | Mechanical Equipment Room | 0.5
GGHC v2.2Health CareMedical Records | GGHC v2.2 | Health Care | Medical Records | 2
GGHC v2.2Health CareNuclear Medicine, Hot Lab | GGHC v2.2 | Health Care | Nuclear Medicine, Hot Lab | 5
GGHC v2.2Health CareNursery, General | GGHC v2.2 | Health Care | Nursery, General | 5
GGHC v2.2Health CareNursery, Exam | GGHC v2.2 | Health Care | Nursery, Exam | 5
GGHC v2.2Health CareNursing Stations- General | GGHC v2.2 | Health Care | Nursing Stations- General | 5
GGHC v2.2Health CareOperating Room | GGHC v2.2 | Health Care | Operating Room | 5
GGHC v2.2Health CarePathology | GGHC v2.2 | Health Care | Pathology | 5
GGHC v2.2Health CarePatient Room | GGHC v2.2 | Health Care | Patient Room | 5
GGHC v2.2Health CarePharmacy / Medicine Room | GGHC v2.2 | Health Care | Pharmacy / Medicine Room | 5
GGHC v2.2Health CarePhysical Therapy and Hydrotherapy | GGHC v2.2 | Health Care | Physical Therapy and Hydrotherapy | 5
GGHC v2.2Health CareRecovery | GGHC v2.2 | Health Care | Recovery | 5
GGHC v2.2Health CareScrub Up Area, Surgical Corridor | GGHC v2.2 | Health Care | Scrub Up Area, Surgical Corridor | 5
GGHC v2.2Health CareSoiled Linen, Sorting | GGHC v2.2 | Health Care | Soiled Linen, Sorting | 5
GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | 5
GGHC v2.2Health CareSpecial Procedure Room, Invasive | GGHC v2.2 | Health Care | Special Procedure Room, Invasive | 5
GGHC v2.2Health CareStairways | GGHC v2.2 | Health Care | Stairways | 1
GGHC v2.2Health CareSterilizer Room | GGHC v2.2 | Health Care | Sterilizer Room | 5
GGHC v2.2Health CareSub-Sterile | GGHC v2.2 | Health Care | Sub-Sterile | 5
GGHC v2.2Health CareSurgical Supply | GGHC v2.2 | Health Care | Surgical Supply | 5
GGHC v2.2Health CareTrash Chute Room | GGHC v2.2 | Health Care | Trash Chute Room | 0.5
GGHC v2.2Health CareTrauma | GGHC v2.2 | Health Care | Trauma | 5
GGHC v2.2Health CareTreatment / Examination | GGHC v2.2 | Health Care | Treatment / Examination | 5
GGHC v2.2Health CareUnsterile Supply | GGHC v2.2 | Health Care | Unsterile Supply | 2
GGHC v2.2Health CareWaiting Areas/Lounges | GGHC v2.2 | Health Care | Waiting Areas/Lounges | 10
GGHC v2.2Health CareX-ray, Diagnostic and Treatment | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | 5

## InteriorLighting
VLookupColumn | Lighting Standard | Primary Space Type | Secondary Space Type | W/ft^2 | W/ft | Import Order
ASHRAE 90.1-1999Whole BuildingAutomotive Facility | ASHRAE 90.1-1999 | Whole Building | Automotive Facility | 1.5 |  | 1
ASHRAE 90.1-1999Whole BuildingConvention Center | ASHRAE 90.1-1999 | Whole Building | Convention Center | 1.4 |  | 2
ASHRAE 90.1-1999Whole BuildingCourt House | ASHRAE 90.1-1999 | Whole Building | Court House | 1.4 |  | 3
ASHRAE 90.1-1999Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-1999 | Whole Building | Dining: Bar Lounge/Leisure | 1.5 |  | 4
ASHRAE 90.1-1999Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-1999 | Whole Building | Dining: Cafeteria/Fast Food | 1.8 |  | 5
ASHRAE 90.1-1999Whole BuildingDining: Family | ASHRAE 90.1-1999 | Whole Building | Dining: Family | 1.9 |  | 6
ASHRAE 90.1-1999Whole BuildingDormitory | ASHRAE 90.1-1999 | Whole Building | Dormitory | 1.5 |  | 7
ASHRAE 90.1-1999Whole BuildingExercise Center | ASHRAE 90.1-1999 | Whole Building | Exercise Center | 1.4 |  | 8
ASHRAE 90.1-1999Whole BuildingGymnasium | ASHRAE 90.1-1999 | Whole Building | Gymnasium | 1.7 |  | 9
ASHRAE 90.1-1999Whole BuildingHealth Care-Clinic | ASHRAE 90.1-1999 | Whole Building | Health Care-Clinic | 1.6 |  | 10
ASHRAE 90.1-1999Whole BuildingHospital | ASHRAE 90.1-1999 | Whole Building | Hospital | 1.6 |  | 11
ASHRAE 90.1-1999Whole BuildingHotel | ASHRAE 90.1-1999 | Whole Building | Hotel | 1.7 |  | 12
ASHRAE 90.1-1999Whole BuildingLibrary | ASHRAE 90.1-1999 | Whole Building | Library | 1.5 |  | 13
ASHRAE 90.1-1999Whole BuildingManufacturing Facility | ASHRAE 90.1-1999 | Whole Building | Manufacturing Facility | 2.2 |  | 14
ASHRAE 90.1-1999Whole BuildingMotel | ASHRAE 90.1-1999 | Whole Building | Motel | 2 |  | 15
ASHRAE 90.1-1999Whole BuildingMotion Picture Theater | ASHRAE 90.1-1999 | Whole Building | Motion Picture Theater | 1.6 |  | 16
ASHRAE 90.1-1999Whole BuildingMulti-Family | ASHRAE 90.1-1999 | Whole Building | Multi-Family | 1 |  | 17
ASHRAE 90.1-1999Whole BuildingMuseum | ASHRAE 90.1-1999 | Whole Building | Museum | 1.6 |  | 18
ASHRAE 90.1-1999Whole BuildingOffice | ASHRAE 90.1-1999 | Whole Building | Office | 1.3 |  | 19
ASHRAE 90.1-1999Whole BuildingParking Garage | ASHRAE 90.1-1999 | Whole Building | Parking Garage | 0.3 |  | 20
ASHRAE 90.1-1999Whole BuildingPenitentiary | ASHRAE 90.1-1999 | Whole Building | Penitentiary | 1.2 |  | 21
ASHRAE 90.1-1999Whole BuildingPerforming Arts Theater | ASHRAE 90.1-1999 | Whole Building | Performing Arts Theater | 1.5 |  | 22
ASHRAE 90.1-1999Whole BuildingPolice/Fire Station | ASHRAE 90.1-1999 | Whole Building | Police/Fire Station | 1.3 |  | 23
ASHRAE 90.1-1999Whole BuildingPost Office | ASHRAE 90.1-1999 | Whole Building | Post Office | 1.6 |  | 24
ASHRAE 90.1-1999Whole BuildingReligious Building | ASHRAE 90.1-1999 | Whole Building | Religious Building | 2.2 |  | 25
ASHRAE 90.1-1999Whole BuildingRetail | ASHRAE 90.1-1999 | Whole Building | Retail | 1.9 |  | 26
ASHRAE 90.1-1999Whole BuildingSchool/University | ASHRAE 90.1-1999 | Whole Building | School/University | 1.5 |  | 27
ASHRAE 90.1-1999Whole BuildingSports Arena | ASHRAE 90.1-1999 | Whole Building | Sports Arena | 1.5 |  | 28
ASHRAE 90.1-1999Whole BuildingTown Hall | ASHRAE 90.1-1999 | Whole Building | Town Hall | 1.4 |  | 29
ASHRAE 90.1-1999Whole BuildingTransportation | ASHRAE 90.1-1999 | Whole Building | Transportation | 1.2 |  | 30
ASHRAE 90.1-1999Whole BuildingWarehouse | ASHRAE 90.1-1999 | Whole Building | Warehouse | 1.2 |  | 31
ASHRAE 90.1-1999Whole BuildingWorkshop | ASHRAE 90.1-1999 | Whole Building | Workshop | 1.7 |  | 32
ASHRAE 90.1-1999Office-EnclosedGeneral | ASHRAE 90.1-1999 | Office-Enclosed | General | 1.5 |  | 33
ASHRAE 90.1-1999Office-Open PlanGeneral | ASHRAE 90.1-1999 | Office-Open Plan | General | 1.3 |  | 34
ASHRAE 90.1-1999Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-1999 | Conference/Meeting/Multipurpose | General | 1.5 |  | 35
ASHRAE 90.1-1999Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-1999 | Classroom/Lecture/Training | General | 1.6 |  | 36
ASHRAE 90.1-1999Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-1999 | Classroom/Lecture/Training | For Penitentiary | 1.4 |  | 37
ASHRAE 90.1-1999LobbyGeneral | ASHRAE 90.1-1999 | Lobby | General | 1.8 |  | 38
ASHRAE 90.1-1999LobbyFor Hotel | ASHRAE 90.1-1999 | Lobby | For Hotel | 1.8 |  | 39
ASHRAE 90.1-1999LobbyFor Performing Arts Theater | ASHRAE 90.1-1999 | Lobby | For Performing Arts Theater | 1.2 |  | 40
ASHRAE 90.1-1999LobbyFor Motion Picture Theater | ASHRAE 90.1-1999 | Lobby | For Motion Picture Theater | 0.8 |  | 41
ASHRAE 90.1-1999Audience/Seating AreaGeneral | ASHRAE 90.1-1999 | Audience/Seating Area | General | 0.5 |  | 42
ASHRAE 90.1-1999Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-1999 | Audience/Seating Area | For Gymnasium | 0.5 |  | 43
ASHRAE 90.1-1999Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-1999 | Audience/Seating Area | For Exercise Center | 0.5 |  | 44
ASHRAE 90.1-1999Audience/Seating AreaFor Convention Center | ASHRAE 90.1-1999 | Audience/Seating Area | For Convention Center | 0.5 |  | 45
ASHRAE 90.1-1999Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-1999 | Audience/Seating Area | For Penitentiary | 1.9 |  | 46
ASHRAE 90.1-1999Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-1999 | Audience/Seating Area | For Religious Buildings | 3.2 |  | 47
ASHRAE 90.1-1999Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-1999 | Audience/Seating Area | For Sports Arena | 0.5 |  | 48
ASHRAE 90.1-1999Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-1999 | Audience/Seating Area | For Performing Arts Theater | 1.8 |  | 49
ASHRAE 90.1-1999Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-1999 | Audience/Seating Area | For Motion Picture Theater | 1.3 |  | 50
ASHRAE 90.1-1999Audience/Seating AreaFor Transportation | ASHRAE 90.1-1999 | Audience/Seating Area | For Transportation | 1 |  | 51
ASHRAE 90.1-1999AtriumFirst Three Floors | ASHRAE 90.1-1999 | Atrium | First Three Floors | 1.3 |  | 52
ASHRAE 90.1-1999AtriumEach Floor over First Three Floors | ASHRAE 90.1-1999 | Atrium | Each Floor over First Three Floors | 0.2 |  | 53
ASHRAE 90.1-1999Lounge/RecreationGeneral | ASHRAE 90.1-1999 | Lounge/Recreation | General | 1.4 |  | 54
ASHRAE 90.1-1999Lounge/RecreationFor Hospital | ASHRAE 90.1-1999 | Lounge/Recreation | For Hospital | 1.4 |  | 55
ASHRAE 90.1-1999Dining AreaGeneral | ASHRAE 90.1-1999 | Dining Area | General | 1.4 |  | 56
ASHRAE 90.1-1999Dining AreaFor Penitentiary | ASHRAE 90.1-1999 | Dining Area | For Penitentiary | 1.4 |  | 57
ASHRAE 90.1-1999Dining AreaFor Hotel | ASHRAE 90.1-1999 | Dining Area | For Hotel | 1 |  | 58
ASHRAE 90.1-1999Dining AreaFor Motel | ASHRAE 90.1-1999 | Dining Area | For Motel | 1.2 |  | 59
ASHRAE 90.1-1999Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-1999 | Dining Area | For Bar Lounge/Leisure Dining | 1.2 |  | 60
ASHRAE 90.1-1999Dining AreaFor Family Dining | ASHRAE 90.1-1999 | Dining Area | For Family Dining | 2.2 |  | 61
ASHRAE 90.1-1999Food PreparationGeneral | ASHRAE 90.1-1999 | Food Preparation | General | 2.2 |  | 62
ASHRAE 90.1-1999LaboratoryGeneral | ASHRAE 90.1-1999 | Laboratory | General | 1.8 |  | 63
ASHRAE 90.1-1999RestroomsGeneral | ASHRAE 90.1-1999 | Restrooms | General | 1 |  | 64
ASHRAE 90.1-1999Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-1999 | Dressing/Locker/Fitting Room | General | 0.8 |  | 65
ASHRAE 90.1-1999Corridor/TransitionGeneral | ASHRAE 90.1-1999 | Corridor/Transition | General | 0.7 |  | 66
ASHRAE 90.1-1999Corridor/TransitionFor Hospital | ASHRAE 90.1-1999 | Corridor/Transition | For Hospital | 1.6 |  | 67
ASHRAE 90.1-1999Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-1999 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 68
ASHRAE 90.1-1999Stairs—ActiveGeneral | ASHRAE 90.1-1999 | Stairs—Active | General | 0.9 |  | 69
ASHRAE 90.1-1999Active StorageGeneral | ASHRAE 90.1-1999 | Active Storage | General | 1.1 |  | 70
ASHRAE 90.1-1999Active StorageFor Hospital | ASHRAE 90.1-1999 | Active Storage | For Hospital | 2.9 |  | 71
ASHRAE 90.1-1999Inactive storageGeneral | ASHRAE 90.1-1999 | Inactive storage | General | 0.3 |  | 72
ASHRAE 90.1-1999Inactive storageFor Museum | ASHRAE 90.1-1999 | Inactive storage | For Museum | 1.4 |  | 73
ASHRAE 90.1-1999Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-1999 | Gymnasium/Exercise Center | Playing Area | 1.9 |  | 74
ASHRAE 90.1-1999Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-1999 | Gymnasium/Exercise Center | Exercise Area | 1.1 |  | 75
ASHRAE 90.1-1999Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-1999 | Courthouse/Police Station/Penitentiary | Courtroom | 2.1 |  | 76
ASHRAE 90.1-1999Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-1999 | Courthouse/Police Station/Penitentiary | Confinement Cells | 1.1 |  | 77
ASHRAE 90.1-1999Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-1999 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.1 |  | 78
ASHRAE 90.1-1999Fire StationsFire Station Engine Room | ASHRAE 90.1-1999 | Fire Stations | Fire Station Engine Room | 0.9 |  | 79
ASHRAE 90.1-1999Fire StationsSleeping Quarters | ASHRAE 90.1-1999 | Fire Stations | Sleeping Quarters | 1.1 |  | 80
ASHRAE 90.1-1999Post OfficeSorting Area | ASHRAE 90.1-1999 | Post Office | Sorting Area | 1.7 |  | 81
ASHRAE 90.1-1999Convention CenterExhibit Space | ASHRAE 90.1-1999 | Convention Center | Exhibit Space | 3.3 |  | 82
ASHRAE 90.1-1999LibraryCard File and Cataloging | ASHRAE 90.1-1999 | Library | Card File and Cataloging | 1.4 |  | 83
ASHRAE 90.1-1999LibraryStacks | ASHRAE 90.1-1999 | Library | Stacks | 1.9 |  | 84
ASHRAE 90.1-1999LibraryReading Area | ASHRAE 90.1-1999 | Library | Reading Area | 1.8 |  | 85
ASHRAE 90.1-1999HospitalEmergency | ASHRAE 90.1-1999 | Hospital | Emergency | 2.8 |  | 86
ASHRAE 90.1-1999HospitalRecovery | ASHRAE 90.1-1999 | Hospital | Recovery | 2.6 |  | 87
ASHRAE 90.1-1999HospitalNurse Station | ASHRAE 90.1-1999 | Hospital | Nurse Station | 1.8 |  | 88
ASHRAE 90.1-1999HospitalExam/Treatment | ASHRAE 90.1-1999 | Hospital | Exam/Treatment | 1.6 |  | 89
ASHRAE 90.1-1999HospitalPharmacy | ASHRAE 90.1-1999 | Hospital | Pharmacy | 2.3 |  | 90
ASHRAE 90.1-1999HospitalPatient Room | ASHRAE 90.1-1999 | Hospital | Patient Room | 1.2 |  | 91
ASHRAE 90.1-1999HospitalOperating Room | ASHRAE 90.1-1999 | Hospital | Operating Room | 7.6 |  | 92
ASHRAE 90.1-1999HospitalNursery | ASHRAE 90.1-1999 | Hospital | Nursery | 1 |  | 93
ASHRAE 90.1-1999HospitalMedical Supply | ASHRAE 90.1-1999 | Hospital | Medical Supply | 3 |  | 94
ASHRAE 90.1-1999HospitalPhysical Therapy | ASHRAE 90.1-1999 | Hospital | Physical Therapy | 1.9 |  | 95
ASHRAE 90.1-1999HospitalRadiology | ASHRAE 90.1-1999 | Hospital | Radiology | 0.4 |  | 96
ASHRAE 90.1-1999HospitalLaundry—Washing | ASHRAE 90.1-1999 | Hospital | Laundry—Washing | 0.7 |  | 97
ASHRAE 90.1-1999AutomotiveService/Repair | ASHRAE 90.1-1999 | Automotive | Service/Repair | 1.4 |  | 98
ASHRAE 90.1-1999ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-1999 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 2.1 |  | 99
ASHRAE 90.1-1999ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-1999 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 3 |  | 100
ASHRAE 90.1-1999ManufacturingDetailed Manufacturing | ASHRAE 90.1-1999 | Manufacturing | Detailed Manufacturing | 6.2 |  | 101
ASHRAE 90.1-1999ManufacturingEquipment Room | ASHRAE 90.1-1999 | Manufacturing | Equipment Room | 0.8 |  | 102
ASHRAE 90.1-1999ManufacturingControl Room | ASHRAE 90.1-1999 | Manufacturing | Control Room | 0.5 |  | 103
ASHRAE 90.1-1999Hotel/MotelGuest Rooms | ASHRAE 90.1-1999 | Hotel/Motel | Guest Rooms | 2.5 |  | 104
ASHRAE 90.1-1999DormitoryLiving Quarters | ASHRAE 90.1-1999 | Dormitory | Living Quarters | 1.9 |  | 105
ASHRAE 90.1-1999MuseumGeneral Exhibition | ASHRAE 90.1-1999 | Museum | General Exhibition | 1.6 |  | 106
ASHRAE 90.1-1999MuseumRestoration | ASHRAE 90.1-1999 | Museum | Restoration | 2.5 |  | 107
ASHRAE 90.1-1999Electrical/MechanicalGeneral | ASHRAE 90.1-1999 | Electrical/Mechanical | General | 1.3 |  | 108
ASHRAE 90.1-1999WorkshopGeneral | ASHRAE 90.1-1999 | Workshop | General | 2.5 |  | 109
ASHRAE 90.1-1999Bank/OfficeBanking Activity Area | ASHRAE 90.1-1999 | Bank/Office | Banking Activity Area | 2.4 |  | 110
ASHRAE 90.1-1999Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-1999 | Religious Buildings | Worship Pulpit, Choir | 5.2 |  | 111
ASHRAE 90.1-1999Religious BuildingsFellowship Hall | ASHRAE 90.1-1999 | Religious Buildings | Fellowship Hall | 2.3 |  | 112
ASHRAE 90.1-1999Retail (not including accent lighting)Sales Area | ASHRAE 90.1-1999 | Retail (not including accent lighting) | Sales Area | 2.1 |  | 113
ASHRAE 90.1-1999Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-1999 | Retail (not including accent lighting) | Mall Concourse | 1.8 |  | 114
ASHRAE 90.1-1999Sports ArenaRing Sports Area | ASHRAE 90.1-1999 | Sports Arena | Ring Sports Area | 3.8 |  | 115
ASHRAE 90.1-1999Sports ArenaCourt Sports Area | ASHRAE 90.1-1999 | Sports Arena | Court Sports Area | 4.3 |  | 116
ASHRAE 90.1-1999Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-1999 | Sports Arena | Indoor Playing Field Area | 1.9 |  | 117
ASHRAE 90.1-1999WarehouseFine Material Storage | ASHRAE 90.1-1999 | Warehouse | Fine Material Storage | 1.6 |  | 118
ASHRAE 90.1-1999WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-1999 | Warehouse | Medium/Bulky Material Storage | 1.1 |  | 119
ASHRAE 90.1-1999Parking GarageGarage Area | ASHRAE 90.1-1999 | Parking Garage | Garage Area | 0.2 |  | 120
ASHRAE 90.1-1999TransportationAirport—Concourse | ASHRAE 90.1-1999 | Transportation | Airport—Concourse | 0.7 |  | 121
ASHRAE 90.1-1999TransportationAir/Train/Bus—Baggage Area | ASHRAE 90.1-1999 | Transportation | Air/Train/Bus—Baggage Area | 1.3 |  | 122
ASHRAE 90.1-1999TransportationTerminal—Ticket Counter | ASHRAE 90.1-1999 | Transportation | Terminal—Ticket Counter | 1.8 |  | 123
ASHRAE 90.1-1999Exterior SpacesGeneral | ASHRAE 90.1-1999 | Exterior Spaces | General | 0 |  | 124
ASHRAE 90.1-1999AtticsGeneral | ASHRAE 90.1-1999 | Attics | General | 0 |  | 125
ASHRAE 90.1-2001Whole BuildingAutomotive Facility | ASHRAE 90.1-2001 | Whole Building | Automotive Facility | 0.9 |  | 126
ASHRAE 90.1-2001Whole BuildingConvention Center | ASHRAE 90.1-2001 | Whole Building | Convention Center | 1.2 |  | 127
ASHRAE 90.1-2001Whole BuildingCourt House | ASHRAE 90.1-2001 | Whole Building | Court House | 1.2 |  | 128
ASHRAE 90.1-2001Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2001 | Whole Building | Dining: Bar Lounge/Leisure | 1.3 |  | 129
ASHRAE 90.1-2001Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2001 | Whole Building | Dining: Cafeteria/Fast Food | 1.4 |  | 130
ASHRAE 90.1-2001Whole BuildingDining: Family | ASHRAE 90.1-2001 | Whole Building | Dining: Family | 1.6 |  | 131
ASHRAE 90.1-2001Whole BuildingDormitory | ASHRAE 90.1-2001 | Whole Building | Dormitory | 1 |  | 132
ASHRAE 90.1-2001Whole BuildingExercise Center | ASHRAE 90.1-2001 | Whole Building | Exercise Center | 1 |  | 133
ASHRAE 90.1-2001Whole BuildingGymnasium | ASHRAE 90.1-2001 | Whole Building | Gymnasium | 1.1 |  | 134
ASHRAE 90.1-2001Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2001 | Whole Building | Health Care-Clinic | 1 |  | 135
ASHRAE 90.1-2001Whole BuildingHospital | ASHRAE 90.1-2001 | Whole Building | Hospital | 1.2 |  | 136
ASHRAE 90.1-2001Whole BuildingHotel | ASHRAE 90.1-2001 | Whole Building | Hotel | 1 |  | 137
ASHRAE 90.1-2001Whole BuildingLibrary | ASHRAE 90.1-2001 | Whole Building | Library | 1.3 |  | 138
ASHRAE 90.1-2001Whole BuildingManufacturing Facility | ASHRAE 90.1-2001 | Whole Building | Manufacturing Facility | 1.3 |  | 139
ASHRAE 90.1-2001Whole BuildingMotel | ASHRAE 90.1-2001 | Whole Building | Motel | 1 |  | 140
ASHRAE 90.1-2001Whole BuildingMotion Picture Theater | ASHRAE 90.1-2001 | Whole Building | Motion Picture Theater | 1.2 |  | 141
ASHRAE 90.1-2001Whole BuildingMulti-Family | ASHRAE 90.1-2001 | Whole Building | Multi-Family | 0.7 |  | 142
ASHRAE 90.1-2001Whole BuildingMuseum | ASHRAE 90.1-2001 | Whole Building | Museum | 1.1 |  | 143
ASHRAE 90.1-2001Whole BuildingOffice | ASHRAE 90.1-2001 | Whole Building | Office | 1 |  | 144
ASHRAE 90.1-2001Whole BuildingParking Garage | ASHRAE 90.1-2001 | Whole Building | Parking Garage | 0.3 |  | 145
ASHRAE 90.1-2001Whole BuildingPenitentiary | ASHRAE 90.1-2001 | Whole Building | Penitentiary | 1 |  | 146
ASHRAE 90.1-2001Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2001 | Whole Building | Performing Arts Theater | 1.6 |  | 147
ASHRAE 90.1-2001Whole BuildingPolice/Fire Station | ASHRAE 90.1-2001 | Whole Building | Police/Fire Station | 1 |  | 148
ASHRAE 90.1-2001Whole BuildingPost Office | ASHRAE 90.1-2001 | Whole Building | Post Office | 1.1 |  | 149
ASHRAE 90.1-2001Whole BuildingReligious Building | ASHRAE 90.1-2001 | Whole Building | Religious Building | 1.3 |  | 150
ASHRAE 90.1-2001Whole BuildingRetail | ASHRAE 90.1-2001 | Whole Building | Retail | 1.5 |  | 151
ASHRAE 90.1-2001Whole BuildingSchool/University | ASHRAE 90.1-2001 | Whole Building | School/University | 1.2 |  | 152
ASHRAE 90.1-2001Whole BuildingSports Arena | ASHRAE 90.1-2001 | Whole Building | Sports Arena | 1.1 |  | 153
ASHRAE 90.1-2001Whole BuildingTown Hall | ASHRAE 90.1-2001 | Whole Building | Town Hall | 1.1 |  | 154
ASHRAE 90.1-2001Whole BuildingTransportation | ASHRAE 90.1-2001 | Whole Building | Transportation | 1 |  | 155
ASHRAE 90.1-2001Whole BuildingWarehouse | ASHRAE 90.1-2001 | Whole Building | Warehouse | 0.8 |  | 156
ASHRAE 90.1-2001Whole BuildingWorkshop | ASHRAE 90.1-2001 | Whole Building | Workshop | 1.4 |  | 157
ASHRAE 90.1-2001Office-EnclosedGeneral | ASHRAE 90.1-2001 | Office-Enclosed | General | 1.1 |  | 158
ASHRAE 90.1-2001Office-Open PlanGeneral | ASHRAE 90.1-2001 | Office-Open Plan | General | 1.1 |  | 159
ASHRAE 90.1-2001Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2001 | Conference/Meeting/Multipurpose | General | 1.3 |  | 160
ASHRAE 90.1-2001Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2001 | Classroom/Lecture/Training | General | 1.4 |  | 161
ASHRAE 90.1-2001Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2001 | Classroom/Lecture/Training | For Penitentiary | 1.3 |  | 162
ASHRAE 90.1-2001LobbyGeneral | ASHRAE 90.1-2001 | Lobby | General | 1.3 |  | 163
ASHRAE 90.1-2001LobbyFor Hotel | ASHRAE 90.1-2001 | Lobby | For Hotel | 1.1 |  | 164
ASHRAE 90.1-2001LobbyFor Performing Arts Theater | ASHRAE 90.1-2001 | Lobby | For Performing Arts Theater | 3.3 |  | 165
ASHRAE 90.1-2001LobbyFor Motion Picture Theater | ASHRAE 90.1-2001 | Lobby | For Motion Picture Theater | 1.1 |  | 166
ASHRAE 90.1-2001Audience/Seating AreaGeneral | ASHRAE 90.1-2001 | Audience/Seating Area | General | 0.9 |  | 167
ASHRAE 90.1-2001Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2001 | Audience/Seating Area | For Gymnasium | 0.4 |  | 168
ASHRAE 90.1-2001Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-2001 | Audience/Seating Area | For Exercise Center | 0.3 |  | 169
ASHRAE 90.1-2001Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2001 | Audience/Seating Area | For Convention Center | 0.7 |  | 170
ASHRAE 90.1-2001Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2001 | Audience/Seating Area | For Penitentiary | 0.7 |  | 171
ASHRAE 90.1-2001Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2001 | Audience/Seating Area | For Religious Buildings | 1.7 |  | 172
ASHRAE 90.1-2001Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-2001 | Audience/Seating Area | For Sports Arena | 0.4 |  | 173
ASHRAE 90.1-2001Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-2001 | Audience/Seating Area | For Performing Arts Theater | 2.6 |  | 174
ASHRAE 90.1-2001Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2001 | Audience/Seating Area | For Motion Picture Theater | 1.2 |  | 175
ASHRAE 90.1-2001Audience/Seating AreaFor Transportation | ASHRAE 90.1-2001 | Audience/Seating Area | For Transportation | 0.5 |  | 176
ASHRAE 90.1-2001AtriumFirst Three Floors | ASHRAE 90.1-2001 | Atrium | First Three Floors | 0.6 |  | 177
ASHRAE 90.1-2001AtriumEach Floor over First Three Floors | ASHRAE 90.1-2001 | Atrium | Each Floor over First Three Floors | 0.2 |  | 178
ASHRAE 90.1-2001Lounge/RecreationGeneral | ASHRAE 90.1-2001 | Lounge/Recreation | General | 1.2 |  | 179
ASHRAE 90.1-2001Lounge/RecreationFor Hospital | ASHRAE 90.1-2001 | Lounge/Recreation | For Hospital | 0.8 |  | 180
ASHRAE 90.1-2001Dining AreaGeneral | ASHRAE 90.1-2001 | Dining Area | General | 0.9 |  | 181
ASHRAE 90.1-2001Dining AreaFor Penitentiary | ASHRAE 90.1-2001 | Dining Area | For Penitentiary | 1.3 |  | 182
ASHRAE 90.1-2001Dining AreaFor Hotel | ASHRAE 90.1-2001 | Dining Area | For Hotel | 1.3 |  | 183
ASHRAE 90.1-2001Dining AreaFor Motel | ASHRAE 90.1-2001 | Dining Area | For Motel | 1.2 |  | 184
ASHRAE 90.1-2001Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2001 | Dining Area | For Bar Lounge/Leisure Dining | 1.4 |  | 185
ASHRAE 90.1-2001Dining AreaFor Family Dining | ASHRAE 90.1-2001 | Dining Area | For Family Dining | 2.1 |  | 186
ASHRAE 90.1-2001Food PreparationGeneral | ASHRAE 90.1-2001 | Food Preparation | General | 1.2 |  | 187
ASHRAE 90.1-2001LaboratoryGeneral | ASHRAE 90.1-2001 | Laboratory | General | 1.4 |  | 188
ASHRAE 90.1-2001RestroomsGeneral | ASHRAE 90.1-2001 | Restrooms | General | 0.9 |  | 189
ASHRAE 90.1-2001Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-2001 | Dressing/Locker/Fitting Room | General | 0.6 |  | 190
ASHRAE 90.1-2001Corridor/TransitionGeneral | ASHRAE 90.1-2001 | Corridor/Transition | General | 0.5 |  | 191
ASHRAE 90.1-2001Corridor/TransitionFor Hospital | ASHRAE 90.1-2001 | Corridor/Transition | For Hospital | 1 |  | 192
ASHRAE 90.1-2001Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-2001 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 193
ASHRAE 90.1-2001Stairs—ActiveGeneral | ASHRAE 90.1-2001 | Stairs—Active | General | 0.6 |  | 194
ASHRAE 90.1-2001Active StorageGeneral | ASHRAE 90.1-2001 | Active Storage | General | 0.8 |  | 195
ASHRAE 90.1-2001Active StorageFor Hospital | ASHRAE 90.1-2001 | Active Storage | For Hospital | 0.9 |  | 196
ASHRAE 90.1-2001Inactive storageGeneral | ASHRAE 90.1-2001 | Inactive storage | General | 0.3 |  | 197
ASHRAE 90.1-2001Inactive storageFor Museum | ASHRAE 90.1-2001 | Inactive storage | For Museum | 0.8 |  | 198
ASHRAE 90.1-2001Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-2001 | Gymnasium/Exercise Center | Playing Area | 1.4 |  | 199
ASHRAE 90.1-2001Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-2001 | Gymnasium/Exercise Center | Exercise Area | 0.9 |  | 200
ASHRAE 90.1-2001Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-2001 | Courthouse/Police Station/Penitentiary | Courtroom | 1.9 |  | 201
ASHRAE 90.1-2001Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-2001 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.9 |  | 202
ASHRAE 90.1-2001Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-2001 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.3 |  | 203
ASHRAE 90.1-2001Fire StationsFire Station Engine Room | ASHRAE 90.1-2001 | Fire Stations | Fire Station Engine Room | 0.8 |  | 204
ASHRAE 90.1-2001Fire StationsSleeping Quarters | ASHRAE 90.1-2001 | Fire Stations | Sleeping Quarters | 0.3 |  | 205
ASHRAE 90.1-2001Post OfficeSorting Area | ASHRAE 90.1-2001 | Post Office | Sorting Area | 1.2 |  | 206
ASHRAE 90.1-2001Convention CenterExhibit Space | ASHRAE 90.1-2001 | Convention Center | Exhibit Space | 1.3 |  | 207
ASHRAE 90.1-2001LibraryCard File and Cataloging | ASHRAE 90.1-2001 | Library | Card File and Cataloging | 1.1 |  | 208
ASHRAE 90.1-2001LibraryStacks | ASHRAE 90.1-2001 | Library | Stacks | 1.7 |  | 209
ASHRAE 90.1-2001LibraryReading Area | ASHRAE 90.1-2001 | Library | Reading Area | 1.2 |  | 210
ASHRAE 90.1-2001HospitalEmergency | ASHRAE 90.1-2001 | Hospital | Emergency | 2.7 |  | 211
ASHRAE 90.1-2001HospitalRecovery | ASHRAE 90.1-2001 | Hospital | Recovery | 0.8 |  | 212
ASHRAE 90.1-2001HospitalNurse Station | ASHRAE 90.1-2001 | Hospital | Nurse Station | 1 |  | 213
ASHRAE 90.1-2001HospitalExam/Treatment | ASHRAE 90.1-2001 | Hospital | Exam/Treatment | 1.5 |  | 214
ASHRAE 90.1-2001HospitalPharmacy | ASHRAE 90.1-2001 | Hospital | Pharmacy | 1.2 |  | 215
ASHRAE 90.1-2001HospitalPatient Room | ASHRAE 90.1-2001 | Hospital | Patient Room | 0.7 |  | 216
ASHRAE 90.1-2001HospitalOperating Room | ASHRAE 90.1-2001 | Hospital | Operating Room | 2.2 |  | 217
ASHRAE 90.1-2001HospitalNursery | ASHRAE 90.1-2001 | Hospital | Nursery | 0.6 |  | 218
ASHRAE 90.1-2001HospitalMedical Supply | ASHRAE 90.1-2001 | Hospital | Medical Supply | 1.4 |  | 219
ASHRAE 90.1-2001HospitalPhysical Therapy | ASHRAE 90.1-2001 | Hospital | Physical Therapy | 0.9 |  | 220
ASHRAE 90.1-2001HospitalRadiology | ASHRAE 90.1-2001 | Hospital | Radiology | 0.4 |  | 221
ASHRAE 90.1-2001HospitalLaundry—Washing | ASHRAE 90.1-2001 | Hospital | Laundry—Washing | 0.6 |  | 222
ASHRAE 90.1-2001AutomotiveService/Repair | ASHRAE 90.1-2001 | Automotive | Service/Repair | 0.7 |  | 223
ASHRAE 90.1-2001ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2001 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.2 |  | 224
ASHRAE 90.1-2001ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-2001 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.7 |  | 225
ASHRAE 90.1-2001ManufacturingDetailed Manufacturing | ASHRAE 90.1-2001 | Manufacturing | Detailed Manufacturing | 2.1 |  | 226
ASHRAE 90.1-2001ManufacturingEquipment Room | ASHRAE 90.1-2001 | Manufacturing | Equipment Room | 1.2 |  | 227
ASHRAE 90.1-2001ManufacturingControl Room | ASHRAE 90.1-2001 | Manufacturing | Control Room | 0.5 |  | 228
ASHRAE 90.1-2001Hotel/MotelGuest Rooms | ASHRAE 90.1-2001 | Hotel/Motel | Guest Rooms | 1.1 |  | 229
ASHRAE 90.1-2001DormitoryLiving Quarters | ASHRAE 90.1-2001 | Dormitory | Living Quarters | 1.1 |  | 230
ASHRAE 90.1-2001MuseumGeneral Exhibition | ASHRAE 90.1-2001 | Museum | General Exhibition | 1 |  | 231
ASHRAE 90.1-2001MuseumRestoration | ASHRAE 90.1-2001 | Museum | Restoration | 1.7 |  | 232
ASHRAE 90.1-2001Electrical/MechanicalGeneral | ASHRAE 90.1-2001 | Electrical/Mechanical | General | 1.5 |  | 233
ASHRAE 90.1-2001WorkshopGeneral | ASHRAE 90.1-2001 | Workshop | General | 1.9 |  | 234
ASHRAE 90.1-2001Bank/OfficeBanking Activity Area | ASHRAE 90.1-2001 | Bank/Office | Banking Activity Area | 1.5 |  | 235
ASHRAE 90.1-2001Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2001 | Religious Buildings | Worship Pulpit, Choir | 2.4 |  | 236
ASHRAE 90.1-2001Religious BuildingsFellowship Hall | ASHRAE 90.1-2001 | Religious Buildings | Fellowship Hall | 0.9 |  | 237
ASHRAE 90.1-2001Retail (not including accent lighting)Sales Area | ASHRAE 90.1-2001 | Retail (not including accent lighting) | Sales Area | 2.1 |  | 238
ASHRAE 90.1-2001Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-2001 | Retail (not including accent lighting) | Mall Concourse | 1.7 |  | 239
ASHRAE 90.1-2001Sports ArenaRing Sports Area | ASHRAE 90.1-2001 | Sports Arena | Ring Sports Area | 2.7 |  | 240
ASHRAE 90.1-2001Sports ArenaCourt Sports Area | ASHRAE 90.1-2001 | Sports Arena | Court Sports Area | 2.3 |  | 241
ASHRAE 90.1-2001Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-2001 | Sports Arena | Indoor Playing Field Area | 1.4 |  | 242
ASHRAE 90.1-2001WarehouseFine Material Storage | ASHRAE 90.1-2001 | Warehouse | Fine Material Storage | 1.4 |  | 243
ASHRAE 90.1-2001WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2001 | Warehouse | Medium/Bulky Material Storage | 0.9 |  | 244
ASHRAE 90.1-2001Parking GarageGarage Area | ASHRAE 90.1-2001 | Parking Garage | Garage Area | 0.2 |  | 245
ASHRAE 90.1-2001TransportationAirport—Concourse | ASHRAE 90.1-2001 | Transportation | Airport—Concourse | 0.6 |  | 246
ASHRAE 90.1-2001TransportationAir/Train/Bus—Baggage Area | ASHRAE 90.1-2001 | Transportation | Air/Train/Bus—Baggage Area | 1 |  | 247
ASHRAE 90.1-2001TransportationTerminal—Ticket Counter | ASHRAE 90.1-2001 | Transportation | Terminal—Ticket Counter | 1.5 |  | 248
ASHRAE 90.1-2001Exterior SpacesGeneral | ASHRAE 90.1-2001 | Exterior Spaces | General | 0 |  | 249
ASHRAE 90.1-2001AtticsGeneral | ASHRAE 90.1-2001 | Attics | General | 0 |  | 250
ASHRAE 90.1-2004Active StorageFor Hospital | ASHRAE 90.1-2004 | Active Storage | For Hospital | 0.9 |  | 321
ASHRAE 90.1-2004Active StorageGeneral | ASHRAE 90.1-2004 | Active Storage | General | 0.8 |  | 320
ASHRAE 90.1-2004AtriumEach Floor over First Three Floors | ASHRAE 90.1-2004 | Atrium | Each Floor over First Three Floors | 0.2 |  | 303
ASHRAE 90.1-2004AtriumFirst Three Floors | ASHRAE 90.1-2004 | Atrium | First Three Floors | 0.6 |  | 302
ASHRAE 90.1-2004AtticsGeneral | ASHRAE 90.1-2004 | Attics | General | 0 |  | 375
ASHRAE 90.1-2004Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2004 | Audience/Seating Area | For Convention Center | 0.7 |  | 295
ASHRAE 90.1-2004Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-2004 | Audience/Seating Area | For Exercise Center | 0.3 |  | 294
ASHRAE 90.1-2004Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2004 | Audience/Seating Area | For Gymnasium | 0.4 |  | 293
ASHRAE 90.1-2004Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2004 | Audience/Seating Area | For Motion Picture Theater | 1.2 |  | 300
ASHRAE 90.1-2004Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2004 | Audience/Seating Area | For Penitentiary | 0.7 |  | 296
ASHRAE 90.1-2004Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-2004 | Audience/Seating Area | For Performing Arts Theater | 2.6 |  | 299
ASHRAE 90.1-2004Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2004 | Audience/Seating Area | For Religious Buildings | 1.7 |  | 297
ASHRAE 90.1-2004Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-2004 | Audience/Seating Area | For Sports Arena | 0.4 |  | 298
ASHRAE 90.1-2004Audience/Seating AreaFor Transportation | ASHRAE 90.1-2004 | Audience/Seating Area | For Transportation | 0.5 |  | 301
ASHRAE 90.1-2004Audience/Seating AreaGeneral | ASHRAE 90.1-2004 | Audience/Seating Area | General | 0.9 |  | 292
ASHRAE 90.1-2004AutomotiveService/Repair | ASHRAE 90.1-2004 | Automotive | Service/Repair | 0.7 |  | 348
ASHRAE 90.1-2004Bank/OfficeBanking Activity Area | ASHRAE 90.1-2004 | Bank/Office | Banking Activity Area | 1.5 |  | 360
ASHRAE 90.1-2004Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2004 | Classroom/Lecture/Training | For Penitentiary | 1.3 |  | 287
ASHRAE 90.1-2004Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2004 | Classroom/Lecture/Training | General | 1.4 |  | 286
ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | 1.3 |  | 285
ASHRAE 90.1-2004Convention CenterExhibit Space | ASHRAE 90.1-2004 | Convention Center | Exhibit Space | 1.3 |  | 332
ASHRAE 90.1-2004Corridor/TransitionFor Hospital | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | 1 |  | 317
ASHRAE 90.1-2004Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-2004 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 318
ASHRAE 90.1-2004Corridor/TransitionGeneral | ASHRAE 90.1-2004 | Corridor/Transition | General | 0.5 |  | 316
ASHRAE 90.1-2004Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-2004 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.9 |  | 327
ASHRAE 90.1-2004Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-2004 | Courthouse/Police Station/Penitentiary | Courtroom | 1.9 |  | 326
ASHRAE 90.1-2004Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-2004 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.3 |  | 328
ASHRAE 90.1-2004Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2004 | Dining Area | For Bar Lounge/Leisure Dining | 1.4 |  | 310
ASHRAE 90.1-2004Dining AreaFor Family Dining | ASHRAE 90.1-2004 | Dining Area | For Family Dining | 2.1 |  | 311
ASHRAE 90.1-2004Dining AreaFor Hotel | ASHRAE 90.1-2004 | Dining Area | For Hotel | 1.3 |  | 308
ASHRAE 90.1-2004Dining AreaFor Motel | ASHRAE 90.1-2004 | Dining Area | For Motel | 1.2 |  | 309
ASHRAE 90.1-2004Dining AreaFor Penitentiary | ASHRAE 90.1-2004 | Dining Area | For Penitentiary | 1.3 |  | 307
ASHRAE 90.1-2004Dining AreaGeneral | ASHRAE 90.1-2004 | Dining Area | General | 0.9 |  | 306
ASHRAE 90.1-2004DormitoryLiving Quarters | ASHRAE 90.1-2004 | Dormitory | Living Quarters | 1.1 |  | 355
ASHRAE 90.1-2004Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-2004 | Dressing/Locker/Fitting Room | General | 0.6 |  | 315
ASHRAE 90.1-2004Electrical/MechanicalGeneral | ASHRAE 90.1-2004 | Electrical/Mechanical | General | 1.5 |  | 358
ASHRAE 90.1-2004Exterior SpacesGeneral | ASHRAE 90.1-2004 | Exterior Spaces | General | 0 |  | 374
ASHRAE 90.1-2004Fire StationsFire Station Engine Room | ASHRAE 90.1-2004 | Fire Stations | Fire Station Engine Room | 0.8 |  | 329
ASHRAE 90.1-2004Fire StationsSleeping Quarters | ASHRAE 90.1-2004 | Fire Stations | Sleeping Quarters | 0.3 |  | 330
ASHRAE 90.1-2004Food PreparationGeneral | ASHRAE 90.1-2004 | Food Preparation | General | 1.2 |  | 312
ASHRAE 90.1-2004Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Exercise Area | 0.9 |  | 325
ASHRAE 90.1-2004Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Playing Area | 1.4 |  | 324
ASHRAE 90.1-2004HospitalEmergency | ASHRAE 90.1-2004 | Hospital | Emergency | 2.7 |  | 336
ASHRAE 90.1-2004HospitalExam/Treatment | ASHRAE 90.1-2004 | Hospital | Exam/Treatment | 1.5 |  | 339
ASHRAE 90.1-2004HospitalLaundry-Washing | ASHRAE 90.1-2004 | Hospital | Laundry-Washing | 0.6 |  | 347
ASHRAE 90.1-2004HospitalMedical Supply | ASHRAE 90.1-2004 | Hospital | Medical Supply | 1.4 |  | 344
ASHRAE 90.1-2004HospitalNurse Station | ASHRAE 90.1-2004 | Hospital | Nurse Station | 1 |  | 338
ASHRAE 90.1-2004HospitalNursery | ASHRAE 90.1-2004 | Hospital | Nursery | 0.6 |  | 343
ASHRAE 90.1-2004HospitalOperating Room | ASHRAE 90.1-2004 | Hospital | Operating Room | 2.2 |  | 342
ASHRAE 90.1-2004HospitalPatient Room | ASHRAE 90.1-2004 | Hospital | Patient Room | 0.7 |  | 341
ASHRAE 90.1-2004HospitalPharmacy | ASHRAE 90.1-2004 | Hospital | Pharmacy | 1.2 |  | 340
ASHRAE 90.1-2004HospitalPhysical Therapy | ASHRAE 90.1-2004 | Hospital | Physical Therapy | 0.9 |  | 345
ASHRAE 90.1-2004HospitalRadiology | ASHRAE 90.1-2004 | Hospital | Radiology | 0.4 |  | 346
ASHRAE 90.1-2004HospitalRecovery | ASHRAE 90.1-2004 | Hospital | Recovery | 0.8 |  | 337
ASHRAE 90.1-2004Hotel/MotelGuest Rooms | ASHRAE 90.1-2004 | Hotel/Motel | Guest Rooms | 1.1 |  | 354
ASHRAE 90.1-2004Inactive storageFor Museum | ASHRAE 90.1-2004 | Inactive storage | For Museum | 0.8 |  | 323
ASHRAE 90.1-2004Inactive storageGeneral | ASHRAE 90.1-2004 | Inactive storage | General | 0.3 |  | 322
ASHRAE 90.1-2004LaboratoryGeneral | ASHRAE 90.1-2004 | Laboratory | General | 1.4 |  | 313
ASHRAE 90.1-2004LibraryCard File and Cataloging | ASHRAE 90.1-2004 | Library | Card File and Cataloging | 1.1 |  | 333
ASHRAE 90.1-2004LibraryReading Area | ASHRAE 90.1-2004 | Library | Reading Area | 1.2 |  | 335
ASHRAE 90.1-2004LibraryStacks | ASHRAE 90.1-2004 | Library | Stacks | 1.7 |  | 334
ASHRAE 90.1-2004LobbyFor Hotel | ASHRAE 90.1-2004 | Lobby | For Hotel | 1.1 |  | 289
ASHRAE 90.1-2004LobbyFor Motion Picture Theater | ASHRAE 90.1-2004 | Lobby | For Motion Picture Theater | 1.1 |  | 291
ASHRAE 90.1-2004LobbyFor Performing Arts Theater | ASHRAE 90.1-2004 | Lobby | For Performing Arts Theater | 3.3 |  | 290
ASHRAE 90.1-2004LobbyGeneral | ASHRAE 90.1-2004 | Lobby | General | 1.3 |  | 288
ASHRAE 90.1-2004Lounge/RecreationFor Hospital | ASHRAE 90.1-2004 | Lounge/Recreation | For Hospital | 0.8 |  | 305
ASHRAE 90.1-2004Lounge/RecreationGeneral | ASHRAE 90.1-2004 | Lounge/Recreation | General | 1.2 |  | 304
ASHRAE 90.1-2004ManufacturingDetailed Manufacturing | ASHRAE 90.1-2004 | Manufacturing | Detailed Manufacturing | 2.1 |  | 351
ASHRAE 90.1-2004ManufacturingGeneral | ASHRAE 90.1-2004 | Manufacturing | General | 0.5 |  | 353
ASHRAE 90.1-2004ManufacturingGeneral | ASHRAE 90.1-2004 | Manufacturing | General | 1.2 |  | 352
ASHRAE 90.1-2004ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-2004 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.7 |  | 350
ASHRAE 90.1-2004ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2004 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.2 |  | 349
ASHRAE 90.1-2004MuseumGeneral Exhibition | ASHRAE 90.1-2004 | Museum | General Exhibition | 1 |  | 356
ASHRAE 90.1-2004MuseumRestoration | ASHRAE 90.1-2004 | Museum | Restoration | 1.7 |  | 357
ASHRAE 90.1-2004Office-EnclosedGeneral | ASHRAE 90.1-2004 | Office-Enclosed | General | 1.1 |  | 283
ASHRAE 90.1-2004Office-Open PlanGeneral | ASHRAE 90.1-2004 | Office-Open Plan | General | 1.1 |  | 284
ASHRAE 90.1-2004Parking GarageGarage Area | ASHRAE 90.1-2004 | Parking Garage | Garage Area | 0.2 |  | 370
ASHRAE 90.1-2004Post OfficeSorting Area | ASHRAE 90.1-2004 | Post Office | Sorting Area | 1.2 |  | 331
ASHRAE 90.1-2004Religious BuildingsFellowship Hall | ASHRAE 90.1-2004 | Religious Buildings | Fellowship Hall | 0.9 |  | 362
ASHRAE 90.1-2004Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2004 | Religious Buildings | Worship Pulpit, Choir | 2.4 |  | 361
ASHRAE 90.1-2004RestroomsGeneral | ASHRAE 90.1-2004 | Restrooms | General | 0.9 |  | 314
ASHRAE 90.1-2004Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Mall Concourse | 1.7 |  | 364
ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | 1.7 |  | 363
ASHRAE 90.1-2004Sports ArenaCourt Sports Area | ASHRAE 90.1-2004 | Sports Arena | Court Sports Area | 2.3 |  | 366
ASHRAE 90.1-2004Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-2004 | Sports Arena | Indoor Playing Field Area | 1.4 |  | 367
ASHRAE 90.1-2004Sports ArenaRing Sports Area | ASHRAE 90.1-2004 | Sports Arena | Ring Sports Area | 2.7 |  | 365
ASHRAE 90.1-2004Stairs-ActiveGeneral | ASHRAE 90.1-2004 | Stairs-Active | General | 0.6 |  | 319
ASHRAE 90.1-2004TransportationAir/Train/Bus—Baggage Area | ASHRAE 90.1-2004 | Transportation | Air/Train/Bus—Baggage Area | 1 |  | 372
ASHRAE 90.1-2004TransportationAirport—Concourse | ASHRAE 90.1-2004 | Transportation | Airport—Concourse | 0.6 |  | 371
ASHRAE 90.1-2004TransportationTerminal—Ticket Counter | ASHRAE 90.1-2004 | Transportation | Terminal—Ticket Counter | 1.5 |  | 373
ASHRAE 90.1-2004WarehouseFine Material Storage | ASHRAE 90.1-2004 | Warehouse | Fine Material Storage | 1.4 |  | 368
ASHRAE 90.1-2004WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2004 | Warehouse | Medium/Bulky Material Storage | 0.9 |  | 369
ASHRAE 90.1-2004Whole BuildingAutomotive Facility | ASHRAE 90.1-2004 | Whole Building | Automotive Facility | 0.9 |  | 251
ASHRAE 90.1-2004Whole BuildingConvention Center | ASHRAE 90.1-2004 | Whole Building | Convention Center | 1.2 |  | 252
ASHRAE 90.1-2004Whole BuildingCourt House | ASHRAE 90.1-2004 | Whole Building | Court House | 1.2 |  | 253
ASHRAE 90.1-2004Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2004 | Whole Building | Dining: Bar Lounge/Leisure | 1.3 |  | 254
ASHRAE 90.1-2004Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2004 | Whole Building | Dining: Cafeteria/Fast Food | 1.4 |  | 255
ASHRAE 90.1-2004Whole BuildingDining: Family | ASHRAE 90.1-2004 | Whole Building | Dining: Family | 1.6 |  | 256
ASHRAE 90.1-2004Whole BuildingDormitory | ASHRAE 90.1-2004 | Whole Building | Dormitory | 1 |  | 257
ASHRAE 90.1-2004Whole BuildingExercise Center | ASHRAE 90.1-2004 | Whole Building | Exercise Center | 1 |  | 258
ASHRAE 90.1-2004Whole BuildingGymnasium | ASHRAE 90.1-2004 | Whole Building | Gymnasium | 1.1 |  | 259
ASHRAE 90.1-2004Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2004 | Whole Building | Health Care-Clinic | 1 |  | 260
ASHRAE 90.1-2004Whole BuildingHospital | ASHRAE 90.1-2004 | Whole Building | Hospital | 1.2 |  | 261
ASHRAE 90.1-2004Whole BuildingHotel | ASHRAE 90.1-2004 | Whole Building | Hotel | 1 |  | 262
ASHRAE 90.1-2004Whole BuildingLibrary | ASHRAE 90.1-2004 | Whole Building | Library | 1.3 |  | 263
ASHRAE 90.1-2004Whole BuildingManufacturing Facility | ASHRAE 90.1-2004 | Whole Building | Manufacturing Facility | 1.3 |  | 264
ASHRAE 90.1-2004Whole BuildingMotel | ASHRAE 90.1-2004 | Whole Building | Motel | 1 |  | 265
ASHRAE 90.1-2004Whole BuildingMotion Picture Theater | ASHRAE 90.1-2004 | Whole Building | Motion Picture Theater | 1.2 |  | 266
ASHRAE 90.1-2004Whole BuildingMulti-Family | ASHRAE 90.1-2004 | Whole Building | Multi-Family | 0.7 |  | 267
ASHRAE 90.1-2004Whole BuildingMuseum | ASHRAE 90.1-2004 | Whole Building | Museum | 1.1 |  | 268
ASHRAE 90.1-2004Whole BuildingOffice | ASHRAE 90.1-2004 | Whole Building | Office | 1 |  | 269
ASHRAE 90.1-2004Whole BuildingParking Garage | ASHRAE 90.1-2004 | Whole Building | Parking Garage | 0.3 |  | 270
ASHRAE 90.1-2004Whole BuildingPenitentiary | ASHRAE 90.1-2004 | Whole Building | Penitentiary | 1 |  | 271
ASHRAE 90.1-2004Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2004 | Whole Building | Performing Arts Theater | 1.6 |  | 272
ASHRAE 90.1-2004Whole BuildingPolice/Fire Station | ASHRAE 90.1-2004 | Whole Building | Police/Fire Station | 1 |  | 273
ASHRAE 90.1-2004Whole BuildingPost Office | ASHRAE 90.1-2004 | Whole Building | Post Office | 1.1 |  | 274
ASHRAE 90.1-2004Whole BuildingReligious Building | ASHRAE 90.1-2004 | Whole Building | Religious Building | 1.3 |  | 275
ASHRAE 90.1-2004Whole BuildingRetail | ASHRAE 90.1-2004 | Whole Building | Retail | 1.5 |  | 276
ASHRAE 90.1-2004Whole BuildingSchool/University | ASHRAE 90.1-2004 | Whole Building | School/University | 1.2 |  | 277
ASHRAE 90.1-2004Whole BuildingSports Arena | ASHRAE 90.1-2004 | Whole Building | Sports Arena | 1.1 |  | 278
ASHRAE 90.1-2004Whole BuildingTown Hall | ASHRAE 90.1-2004 | Whole Building | Town Hall | 1.1 |  | 279
ASHRAE 90.1-2004Whole BuildingTransportation | ASHRAE 90.1-2004 | Whole Building | Transportation | 1 |  | 280
ASHRAE 90.1-2004Whole BuildingWarehouse | ASHRAE 90.1-2004 | Whole Building | Warehouse | 0.8 |  | 281
ASHRAE 90.1-2004Whole BuildingWorkshop | ASHRAE 90.1-2004 | Whole Building | Workshop | 1.4 |  | 282
ASHRAE 90.1-2004WorkshopWorkshop | ASHRAE 90.1-2004 | Workshop | Workshop | 1.9 |  | 359
ASHRAE 90.1-2007Whole BuildingAutomotive Facility | ASHRAE 90.1-2007 | Whole Building | Automotive Facility | 0.9 |  | 376
ASHRAE 90.1-2007Whole BuildingConvention Center | ASHRAE 90.1-2007 | Whole Building | Convention Center | 1.2 |  | 377
ASHRAE 90.1-2007Whole BuildingCourt House | ASHRAE 90.1-2007 | Whole Building | Court House | 1.2 |  | 378
ASHRAE 90.1-2007Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2007 | Whole Building | Dining: Bar Lounge/Leisure | 1.3 |  | 379
ASHRAE 90.1-2007Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2007 | Whole Building | Dining: Cafeteria/Fast Food | 1.4 |  | 380
ASHRAE 90.1-2007Whole BuildingDining: Family | ASHRAE 90.1-2007 | Whole Building | Dining: Family | 1.6 |  | 381
ASHRAE 90.1-2007Whole BuildingDormitory | ASHRAE 90.1-2007 | Whole Building | Dormitory | 1 |  | 382
ASHRAE 90.1-2007Whole BuildingExercise Center | ASHRAE 90.1-2007 | Whole Building | Exercise Center | 1 |  | 383
ASHRAE 90.1-2007Whole BuildingGymnasium | ASHRAE 90.1-2007 | Whole Building | Gymnasium | 1.1 |  | 384
ASHRAE 90.1-2007Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2007 | Whole Building | Health Care-Clinic | 1 |  | 385
ASHRAE 90.1-2007Whole BuildingHospital | ASHRAE 90.1-2007 | Whole Building | Hospital | 1.2 |  | 386
ASHRAE 90.1-2007Whole BuildingHotel | ASHRAE 90.1-2007 | Whole Building | Hotel | 1 |  | 387
ASHRAE 90.1-2007Whole BuildingLibrary | ASHRAE 90.1-2007 | Whole Building | Library | 1.3 |  | 388
ASHRAE 90.1-2007Whole BuildingManufacturing Facility | ASHRAE 90.1-2007 | Whole Building | Manufacturing Facility | 1.3 |  | 389
ASHRAE 90.1-2007Whole BuildingMotel | ASHRAE 90.1-2007 | Whole Building | Motel | 1 |  | 390
ASHRAE 90.1-2007Whole BuildingMotion Picture Theater | ASHRAE 90.1-2007 | Whole Building | Motion Picture Theater | 1.2 |  | 391
ASHRAE 90.1-2007Whole BuildingMulti-Family | ASHRAE 90.1-2007 | Whole Building | Multi-Family | 0.7 |  | 392
ASHRAE 90.1-2007Whole BuildingMuseum | ASHRAE 90.1-2007 | Whole Building | Museum | 1.1 |  | 393
ASHRAE 90.1-2007Whole BuildingOffice | ASHRAE 90.1-2007 | Whole Building | Office | 1 |  | 394
ASHRAE 90.1-2007Whole BuildingParking Garage | ASHRAE 90.1-2007 | Whole Building | Parking Garage | 0.3 |  | 395
ASHRAE 90.1-2007Whole BuildingPenitentiary | ASHRAE 90.1-2007 | Whole Building | Penitentiary | 1 |  | 396
ASHRAE 90.1-2007Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2007 | Whole Building | Performing Arts Theater | 1.6 |  | 397
ASHRAE 90.1-2007Whole BuildingPolice/Fire Station | ASHRAE 90.1-2007 | Whole Building | Police/Fire Station | 1 |  | 398
ASHRAE 90.1-2007Whole BuildingPost Office | ASHRAE 90.1-2007 | Whole Building | Post Office | 1.1 |  | 399
ASHRAE 90.1-2007Whole BuildingReligious Building | ASHRAE 90.1-2007 | Whole Building | Religious Building | 1.3 |  | 400
ASHRAE 90.1-2007Whole BuildingRetail | ASHRAE 90.1-2007 | Whole Building | Retail | 1.5 |  | 401
ASHRAE 90.1-2007Whole BuildingSchool/University | ASHRAE 90.1-2007 | Whole Building | School/University | 1.2 |  | 402
ASHRAE 90.1-2007Whole BuildingSports Arena | ASHRAE 90.1-2007 | Whole Building | Sports Arena | 1.1 |  | 403
ASHRAE 90.1-2007Whole BuildingTown Hall | ASHRAE 90.1-2007 | Whole Building | Town Hall | 1.1 |  | 404
ASHRAE 90.1-2007Whole BuildingTransportation | ASHRAE 90.1-2007 | Whole Building | Transportation | 1 |  | 405
ASHRAE 90.1-2007Whole BuildingWarehouse | ASHRAE 90.1-2007 | Whole Building | Warehouse | 0.8 |  | 406
ASHRAE 90.1-2007Whole BuildingWorkshop | ASHRAE 90.1-2007 | Whole Building | Workshop | 1.4 |  | 407
ASHRAE 90.1-2007Office-EnclosedGeneral | ASHRAE 90.1-2007 | Office-Enclosed | General | 1.1 |  | 408
ASHRAE 90.1-2007Office-Open PlanGeneral | ASHRAE 90.1-2007 | Office-Open Plan | General | 1.1 |  | 409
ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | 1.3 |  | 410
ASHRAE 90.1-2007Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2007 | Classroom/Lecture/Training | General | 1.4 |  | 411
ASHRAE 90.1-2007Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2007 | Classroom/Lecture/Training | For Penitentiary | 1.3 |  | 412
ASHRAE 90.1-2007LobbyGeneral | ASHRAE 90.1-2007 | Lobby | General | 1.3 |  | 413
ASHRAE 90.1-2007LobbyFor Hotel | ASHRAE 90.1-2007 | Lobby | For Hotel | 1.1 |  | 414
ASHRAE 90.1-2007LobbyFor Performing Arts Theater | ASHRAE 90.1-2007 | Lobby | For Performing Arts Theater | 3.3 |  | 415
ASHRAE 90.1-2007LobbyFor Motion Picture Theater | ASHRAE 90.1-2007 | Lobby | For Motion Picture Theater | 1.1 |  | 416
ASHRAE 90.1-2007Audience/Seating AreaGeneral | ASHRAE 90.1-2007 | Audience/Seating Area | General | 0.9 |  | 417
ASHRAE 90.1-2007Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2007 | Audience/Seating Area | For Gymnasium | 0.4 |  | 418
ASHRAE 90.1-2007Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-2007 | Audience/Seating Area | For Exercise Center | 0.3 |  | 419
ASHRAE 90.1-2007Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2007 | Audience/Seating Area | For Convention Center | 0.7 |  | 420
ASHRAE 90.1-2007Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2007 | Audience/Seating Area | For Penitentiary | 0.7 |  | 421
ASHRAE 90.1-2007Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2007 | Audience/Seating Area | For Religious Buildings | 1.7 |  | 422
ASHRAE 90.1-2007Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-2007 | Audience/Seating Area | For Sports Arena | 0.4 |  | 423
ASHRAE 90.1-2007Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-2007 | Audience/Seating Area | For Performing Arts Theater | 2.6 |  | 424
ASHRAE 90.1-2007Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2007 | Audience/Seating Area | For Motion Picture Theater | 1.2 |  | 425
ASHRAE 90.1-2007Audience/Seating AreaFor Transportation | ASHRAE 90.1-2007 | Audience/Seating Area | For Transportation | 0.5 |  | 426
ASHRAE 90.1-2007AtriumFirst Three Floors | ASHRAE 90.1-2007 | Atrium | First Three Floors | 0.6 |  | 427
ASHRAE 90.1-2007AtriumEach Floor over First Three Floors | ASHRAE 90.1-2007 | Atrium | Each Floor over First Three Floors | 0.2 |  | 428
ASHRAE 90.1-2007Lounge/RecreationGeneral | ASHRAE 90.1-2007 | Lounge/Recreation | General | 1.2 |  | 429
ASHRAE 90.1-2007Lounge/RecreationFor Hospital | ASHRAE 90.1-2007 | Lounge/Recreation | For Hospital | 0.8 |  | 430
ASHRAE 90.1-2007Dining AreaGeneral | ASHRAE 90.1-2007 | Dining Area | General | 0.9 |  | 431
ASHRAE 90.1-2007Dining AreaFor Penitentiary | ASHRAE 90.1-2007 | Dining Area | For Penitentiary | 1.3 |  | 432
ASHRAE 90.1-2007Dining AreaFor Hotel | ASHRAE 90.1-2007 | Dining Area | For Hotel | 1.3 |  | 433
ASHRAE 90.1-2007Dining AreaFor Motel | ASHRAE 90.1-2007 | Dining Area | For Motel | 1.2 |  | 434
ASHRAE 90.1-2007Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2007 | Dining Area | For Bar Lounge/Leisure Dining | 1.4 |  | 435
ASHRAE 90.1-2007Dining AreaFor Family Dining | ASHRAE 90.1-2007 | Dining Area | For Family Dining | 2.1 |  | 436
ASHRAE 90.1-2007Food PreparationGeneral | ASHRAE 90.1-2007 | Food Preparation | General | 1.2 |  | 437
ASHRAE 90.1-2007LaboratoryGeneral | ASHRAE 90.1-2007 | Laboratory | General | 1.4 |  | 438
ASHRAE 90.1-2007RestroomsGeneral | ASHRAE 90.1-2007 | Restrooms | General | 0.9 |  | 439
ASHRAE 90.1-2007Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-2007 | Dressing/Locker/Fitting Room | General | 0.6 |  | 440
ASHRAE 90.1-2007Corridor/TransitionGeneral | ASHRAE 90.1-2007 | Corridor/Transition | General | 0.5 |  | 441
ASHRAE 90.1-2007Corridor/TransitionFor Hospital | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | 1 |  | 442
ASHRAE 90.1-2007Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-2007 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 443
ASHRAE 90.1-2007Stairs-ActiveGeneral | ASHRAE 90.1-2007 | Stairs-Active | General | 0.6 |  | 444
ASHRAE 90.1-2007Active StorageGeneral | ASHRAE 90.1-2007 | Active Storage | General | 0.8 |  | 445
ASHRAE 90.1-2007Active StorageFor Hospital | ASHRAE 90.1-2007 | Active Storage | For Hospital | 0.9 |  | 446
ASHRAE 90.1-2007Inactive storageGeneral | ASHRAE 90.1-2007 | Inactive storage | General | 0.3 |  | 447
ASHRAE 90.1-2007Inactive storageFor Museum | ASHRAE 90.1-2007 | Inactive storage | For Museum | 0.8 |  | 448
ASHRAE 90.1-2007Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Playing Area | 1.4 |  | 449
ASHRAE 90.1-2007Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Exercise Area | 0.9 |  | 450
ASHRAE 90.1-2007Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-2007 | Courthouse/Police Station/Penitentiary | Courtroom | 1.9 |  | 451
ASHRAE 90.1-2007Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-2007 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.9 |  | 452
ASHRAE 90.1-2007Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-2007 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.3 |  | 453
ASHRAE 90.1-2007Fire StationsFire Station Engine Room | ASHRAE 90.1-2007 | Fire Stations | Fire Station Engine Room | 0.8 |  | 454
ASHRAE 90.1-2007Fire StationsSleeping Quarters | ASHRAE 90.1-2007 | Fire Stations | Sleeping Quarters | 0.3 |  | 455
ASHRAE 90.1-2007Post OfficeSorting Area | ASHRAE 90.1-2007 | Post Office | Sorting Area | 1.2 |  | 456
ASHRAE 90.1-2007Convention CenterExhibit Space | ASHRAE 90.1-2007 | Convention Center | Exhibit Space | 1.3 |  | 457
ASHRAE 90.1-2007LibraryCard File and Cataloging | ASHRAE 90.1-2007 | Library | Card File and Cataloging | 1.1 |  | 458
ASHRAE 90.1-2007LibraryStacks | ASHRAE 90.1-2007 | Library | Stacks | 1.7 |  | 459
ASHRAE 90.1-2007LibraryReading Area | ASHRAE 90.1-2007 | Library | Reading Area | 1.2 |  | 460
ASHRAE 90.1-2007HospitalEmergency | ASHRAE 90.1-2007 | Hospital | Emergency | 2.7 |  | 461
ASHRAE 90.1-2007HospitalRecovery | ASHRAE 90.1-2007 | Hospital | Recovery | 0.8 |  | 462
ASHRAE 90.1-2007HospitalNurse Station | ASHRAE 90.1-2007 | Hospital | Nurse Station | 1 |  | 463
ASHRAE 90.1-2007HospitalExam/Treatment | ASHRAE 90.1-2007 | Hospital | Exam/Treatment | 1.5 |  | 464
ASHRAE 90.1-2007HospitalPharmacy | ASHRAE 90.1-2007 | Hospital | Pharmacy | 1.2 |  | 465
ASHRAE 90.1-2007HospitalPatient Room | ASHRAE 90.1-2007 | Hospital | Patient Room | 0.7 |  | 466
ASHRAE 90.1-2007HospitalOperating Room | ASHRAE 90.1-2007 | Hospital | Operating Room | 2.2 |  | 467
ASHRAE 90.1-2007HospitalNursery | ASHRAE 90.1-2007 | Hospital | Nursery | 0.6 |  | 468
ASHRAE 90.1-2007HospitalMedical Supply | ASHRAE 90.1-2007 | Hospital | Medical Supply | 1.4 |  | 469
ASHRAE 90.1-2007HospitalPhysical Therapy | ASHRAE 90.1-2007 | Hospital | Physical Therapy | 0.9 |  | 470
ASHRAE 90.1-2007HospitalRadiology | ASHRAE 90.1-2007 | Hospital | Radiology | 0.4 |  | 471
ASHRAE 90.1-2007HospitalLaundry-Washing | ASHRAE 90.1-2007 | Hospital | Laundry-Washing | 0.6 |  | 472
ASHRAE 90.1-2007AutomotiveService/Repair | ASHRAE 90.1-2007 | Automotive | Service/Repair | 0.7 |  | 473
ASHRAE 90.1-2007ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2007 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.2 |  | 474
ASHRAE 90.1-2007ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-2007 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.7 |  | 475
ASHRAE 90.1-2007ManufacturingDetailed Manufacturing | ASHRAE 90.1-2007 | Manufacturing | Detailed Manufacturing | 2.1 |  | 476
ASHRAE 90.1-2007ManufacturingEquipment Room | ASHRAE 90.1-2007 | Manufacturing | Equipment Room | 1.2 |  | 477
ASHRAE 90.1-2007ManufacturingControl Room | ASHRAE 90.1-2007 | Manufacturing | Control Room | 0.5 |  | 478
ASHRAE 90.1-2007Hotel/MotelGuest Rooms | ASHRAE 90.1-2007 | Hotel/Motel | Guest Rooms | 1.1 |  | 479
ASHRAE 90.1-2007DormitoryLiving Quarters | ASHRAE 90.1-2007 | Dormitory | Living Quarters | 1.1 |  | 480
ASHRAE 90.1-2007MuseumGeneral Exhibition | ASHRAE 90.1-2007 | Museum | General Exhibition | 1 |  | 481
ASHRAE 90.1-2007MuseumRestoration | ASHRAE 90.1-2007 | Museum | Restoration | 1.7 |  | 482
ASHRAE 90.1-2007Electrical/MechanicalGeneral | ASHRAE 90.1-2007 | Electrical/Mechanical | General | 1.5 |  | 483
ASHRAE 90.1-2007WorkshopGeneral | ASHRAE 90.1-2007 | Workshop | General | 1.9 |  | 484
ASHRAE 90.1-2007Bank/OfficeBanking Activity Area | ASHRAE 90.1-2007 | Bank/Office | Banking Activity Area | 1.5 |  | 485
ASHRAE 90.1-2007Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2007 | Religious Buildings | Worship Pulpit, Choir | 2.4 |  | 486
ASHRAE 90.1-2007Religious BuildingsFellowship Hall | ASHRAE 90.1-2007 | Religious Buildings | Fellowship Hall | 0.9 |  | 487
ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | 1.7 |  | 488
ASHRAE 90.1-2007Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Mall Concourse | 1.7 |  | 489
ASHRAE 90.1-2007Sports ArenaRing Sports Area | ASHRAE 90.1-2007 | Sports Arena | Ring Sports Area | 2.7 |  | 490
ASHRAE 90.1-2007Sports ArenaCourt Sports Area | ASHRAE 90.1-2007 | Sports Arena | Court Sports Area | 2.3 |  | 491
ASHRAE 90.1-2007Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-2007 | Sports Arena | Indoor Playing Field Area | 1.4 |  | 492
ASHRAE 90.1-2007WarehouseFine Material Storage | ASHRAE 90.1-2007 | Warehouse | Fine Material Storage | 1.4 |  | 493
ASHRAE 90.1-2007WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2007 | Warehouse | Medium/Bulky Material Storage | 0.9 |  | 494
ASHRAE 90.1-2007Parking GarageGarage Area | ASHRAE 90.1-2007 | Parking Garage | Garage Area | 0.2 |  | 495
ASHRAE 90.1-2007TransportationAirport-Concourse | ASHRAE 90.1-2007 | Transportation | Airport-Concourse | 0.6 |  | 496
ASHRAE 90.1-2007TransportationAir/Train/Bus-Baggage Area | ASHRAE 90.1-2007 | Transportation | Air/Train/Bus-Baggage Area | 1 |  | 497
ASHRAE 90.1-2007TransportationTerminal-Ticket Counter | ASHRAE 90.1-2007 | Transportation | Terminal-Ticket Counter | 1.5 |  | 498
ASHRAE 90.1-2007Exterior SpacesGeneral | ASHRAE 90.1-2007 | Exterior Spaces | General | 0 |  | 499
ASHRAE 90.1-2007AtticsGeneral | ASHRAE 90.1-2007 | Attics | General | 0 |  | 500
GGHC v2.2Health CareAnesthesia Storage | GGHC v2.2 | Health Care | Anesthesia Storage | 3 |  | 501
GGHC v2.2Health CareAngiographic-All Other Types | GGHC v2.2 | Health Care | Angiographic-All Other Types | 3 |  | 502
GGHC v2.2Health CareAngiographic-Heart Only | GGHC v2.2 | Health Care | Angiographic-Heart Only | 3 |  | 503
GGHC v2.2Health CareAutopsy | GGHC v2.2 | Health Care | Autopsy | 1.2 |  | 504
GGHC v2.2Health CareBathroom/ Public | GGHC v2.2 | Health Care | Bathroom/ Public | 0.6 |  | 505
GGHC v2.2Health CareBedpan Room | GGHC v2.2 | Health Care | Bedpan Room | 0.5 |  | 506
GGHC v2.2Health CareCast Room | GGHC v2.2 | Health Care | Cast Room | 3 |  | 507
GGHC v2.2Health CareClean Linen Storage | GGHC v2.2 | Health Care | Clean Linen Storage | 0.5 |  | 508
GGHC v2.2Health CareClean Utility / Workroom | GGHC v2.2 | Health Care | Clean Utility / Workroom | 1.2 |  | 509
GGHC v2.2Health CareConference Rooms | GGHC v2.2 | Health Care | Conference Rooms | 1.2 |  | 510
GGHC v2.2Health CareCorridors | GGHC v2.2 | Health Care | Corridors | 0.6 |  | 511
GGHC v2.2Health CareCystoscopy | GGHC v2.2 | Health Care | Cystoscopy | 3 |  | 512
GGHC v2.2Health CareDarkroom | GGHC v2.2 | Health Care | Darkroom | 0.3 |  | 513
GGHC v2.2Health CareDecontamination | GGHC v2.2 | Health Care | Decontamination | 1.2 |  | 514
GGHC v2.2Health CareDelivery Room | GGHC v2.2 | Health Care | Delivery Room | 4.5 |  | 515
GGHC v2.2Health CareDietary Day Storage | GGHC v2.2 | Health Care | Dietary Day Storage | 0.5 |  | 516
GGHC v2.2Health CareDining Room | GGHC v2.2 | Health Care | Dining Room | 1.1 |  | 517
GGHC v2.2Health CareDishwashing | GGHC v2.2 | Health Care | Dishwashing | 1.7 |  | 518
GGHC v2.2Health CareEndoscopy | GGHC v2.2 | Health Care | Endoscopy | 3 |  | 519
GGHC v2.2Health CareHistology | GGHC v2.2 | Health Care | Histology | 4.5 |  | 520
GGHC v2.2Health CareIsolation | GGHC v2.2 | Health Care | Isolation | 0.5 |  | 521
GGHC v2.2Health CareJanitors Closet / Utility | GGHC v2.2 | Health Care | Janitors Closet / Utility | 0.5 |  | 522
GGHC v2.2Health CareKitchen, Food Preparation | GGHC v2.2 | Health Care | Kitchen, Food Preparation | 1.7 |  | 523
GGHC v2.2Health CareLabor/ Delivery/Recovery | GGHC v2.2 | Health Care | Labor/ Delivery/Recovery | 4.5 |  | 524
GGHC v2.2Health CareL / D / R / Post Partum | GGHC v2.2 | Health Care | L / D / R / Post Partum | 0.7 |  | 525
GGHC v2.2Health CareLaboratory | GGHC v2.2 | Health Care | Laboratory | 3 |  | 526
GGHC v2.2Health CareLinen Storage, Clean | GGHC v2.2 | Health Care | Linen Storage, Clean | 0.5 |  | 527
GGHC v2.2Health CareLobby | GGHC v2.2 | Health Care | Lobby | 1.1 |  | 528
GGHC v2.2Health CareLockers | GGHC v2.2 | Health Care | Lockers | 0.7 |  | 529
GGHC v2.2Health CareMammography | GGHC v2.2 | Health Care | Mammography | 3 |  | 530
GGHC v2.2Health CareMechanical Equipment Room | GGHC v2.2 | Health Care | Mechanical Equipment Room | 0.7 |  | 531
GGHC v2.2Health CareMedical Records | GGHC v2.2 | Health Care | Medical Records | 3 |  | 532
GGHC v2.2Health CareNuclear Medicine, Hot Lab | GGHC v2.2 | Health Care | Nuclear Medicine, Hot Lab | 1.2 |  | 533
GGHC v2.2Health CareNursery, General | GGHC v2.2 | Health Care | Nursery, General | 3 |  | 534
GGHC v2.2Health CareNursery, Exam | GGHC v2.2 | Health Care | Nursery, Exam | 0.7 |  | 535
GGHC v2.2Health CareNursing Stations- General | GGHC v2.2 | Health Care | Nursing Stations- General | 1.2 |  | 536
GGHC v2.2Health CareOperating Room | GGHC v2.2 | Health Care | Operating Room | 4.5 |  | 537
GGHC v2.2Health CarePathology | GGHC v2.2 | Health Care | Pathology | 3 |  | 538
GGHC v2.2Health CarePatient Room | GGHC v2.2 | Health Care | Patient Room | 0.5 |  | 539
GGHC v2.2Health CarePharmacy / Medicine Room | GGHC v2.2 | Health Care | Pharmacy / Medicine Room | 3 |  | 540
GGHC v2.2Health CarePhysical Therapy and Hydrotherapy | GGHC v2.2 | Health Care | Physical Therapy and Hydrotherapy | 1.2 |  | 541
GGHC v2.2Health CareRecovery | GGHC v2.2 | Health Care | Recovery | 3 |  | 542
GGHC v2.2Health CareScrub Up Area, Surgical Corridor | GGHC v2.2 | Health Care | Scrub Up Area, Surgical Corridor | 4.5 |  | 543
GGHC v2.2Health CareSoiled Linen, Sorting | GGHC v2.2 | Health Care | Soiled Linen, Sorting | 1.2 |  | 544
GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | 3 |  | 545
GGHC v2.2Health CareSpecial Procedure Room, Invasive | GGHC v2.2 | Health Care | Special Procedure Room, Invasive | 3 |  | 546
GGHC v2.2Health CareStairways | GGHC v2.2 | Health Care | Stairways | 0.6 |  | 547
GGHC v2.2Health CareSterilizer Room | GGHC v2.2 | Health Care | Sterilizer Room | 1.2 |  | 548
GGHC v2.2Health CareSub-Sterile | GGHC v2.2 | Health Care | Sub-Sterile | 0.7 |  | 549
GGHC v2.2Health CareSurgical Supply | GGHC v2.2 | Health Care | Surgical Supply | 1.2 |  | 550
GGHC v2.2Health CareTrash Chute Room | GGHC v2.2 | Health Care | Trash Chute Room | 0.5 |  | 551
GGHC v2.2Health CareTrauma | GGHC v2.2 | Health Care | Trauma | 3 |  | 552
GGHC v2.2Health CareTreatment / Examination | GGHC v2.2 | Health Care | Treatment / Examination | 1.2 |  | 553
GGHC v2.2Health CareUnsterile Supply | GGHC v2.2 | Health Care | Unsterile Supply | 0.5 |  | 554
GGHC v2.2Health CareWaiting Areas/Lounges | GGHC v2.2 | Health Care | Waiting Areas/Lounges | 1.1 |  | 555
GGHC v2.2Health CareX-ray, Diagnostic and Treatment | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | 3 |  | 556
ASHRAE 189.1-2009Whole BuildingAutomotive Facility | ASHRAE 189.1-2009 | Whole Building | Automotive Facility | 0.81
ASHRAE 189.1-2009Whole BuildingConvention Center | ASHRAE 189.1-2009 | Whole Building | Convention Center | 1.08
ASHRAE 189.1-2009Whole BuildingCourt House | ASHRAE 189.1-2009 | Whole Building | Court House | 1.08
ASHRAE 189.1-2009Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 189.1-2009 | Whole Building | Dining: Bar Lounge/Leisure | 1.17
ASHRAE 189.1-2009Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 189.1-2009 | Whole Building | Dining: Cafeteria/Fast Food | 1.26
ASHRAE 189.1-2009Whole BuildingDining: Family | ASHRAE 189.1-2009 | Whole Building | Dining: Family | 1.44
ASHRAE 189.1-2009Whole BuildingDormitory | ASHRAE 189.1-2009 | Whole Building | Dormitory | 0.9
ASHRAE 189.1-2009Whole BuildingExercise Center | ASHRAE 189.1-2009 | Whole Building | Exercise Center | 0.9
ASHRAE 189.1-2009Whole BuildingGymnasium | ASHRAE 189.1-2009 | Whole Building | Gymnasium | 0.99
ASHRAE 189.1-2009Whole BuildingHealth Care-Clinic | ASHRAE 189.1-2009 | Whole Building | Health Care-Clinic | 0.9
ASHRAE 189.1-2009Whole BuildingHospital | ASHRAE 189.1-2009 | Whole Building | Hospital | 1.08
ASHRAE 189.1-2009Whole BuildingHotel | ASHRAE 189.1-2009 | Whole Building | Hotel | 0.9
ASHRAE 189.1-2009Whole BuildingLibrary | ASHRAE 189.1-2009 | Whole Building | Library | 1.17
ASHRAE 189.1-2009Whole BuildingManufacturing Facility | ASHRAE 189.1-2009 | Whole Building | Manufacturing Facility | 1.17
ASHRAE 189.1-2009Whole BuildingMotel | ASHRAE 189.1-2009 | Whole Building | Motel | 0.9
ASHRAE 189.1-2009Whole BuildingMotion Picture Theater | ASHRAE 189.1-2009 | Whole Building | Motion Picture Theater | 1.08
ASHRAE 189.1-2009Whole BuildingMulti-Family | ASHRAE 189.1-2009 | Whole Building | Multi-Family | 0.63
ASHRAE 189.1-2009Whole BuildingMuseum | ASHRAE 189.1-2009 | Whole Building | Museum | 0.99
ASHRAE 189.1-2009Whole BuildingOffice | ASHRAE 189.1-2009 | Whole Building | Office | 0.9
ASHRAE 189.1-2009Whole BuildingParking Garage | ASHRAE 189.1-2009 | Whole Building | Parking Garage | 0.27
ASHRAE 189.1-2009Whole BuildingPenitentiary | ASHRAE 189.1-2009 | Whole Building | Penitentiary | 0.9
ASHRAE 189.1-2009Whole BuildingPerforming Arts Theater | ASHRAE 189.1-2009 | Whole Building | Performing Arts Theater | 1.44
ASHRAE 189.1-2009Whole BuildingPolice/Fire Station | ASHRAE 189.1-2009 | Whole Building | Police/Fire Station | 0.9
ASHRAE 189.1-2009Whole BuildingPost Office | ASHRAE 189.1-2009 | Whole Building | Post Office | 0.99
ASHRAE 189.1-2009Whole BuildingReligious Building | ASHRAE 189.1-2009 | Whole Building | Religious Building | 1.17
ASHRAE 189.1-2009Whole BuildingRetail | ASHRAE 189.1-2009 | Whole Building | Retail | 1.35
ASHRAE 189.1-2009Whole BuildingSchool/University | ASHRAE 189.1-2009 | Whole Building | School/University | 1.08
ASHRAE 189.1-2009Whole BuildingSports Arena | ASHRAE 189.1-2009 | Whole Building | Sports Arena | 0.99
ASHRAE 189.1-2009Whole BuildingTown Hall | ASHRAE 189.1-2009 | Whole Building | Town Hall | 0.99
ASHRAE 189.1-2009Whole BuildingTransportation | ASHRAE 189.1-2009 | Whole Building | Transportation | 0.9
ASHRAE 189.1-2009Whole BuildingWarehouse | ASHRAE 189.1-2009 | Whole Building | Warehouse | 0.72
ASHRAE 189.1-2009Whole BuildingWorkshop | ASHRAE 189.1-2009 | Whole Building | Workshop | 1.26
ASHRAE 189.1-2009Office-EnclosedGeneral | ASHRAE 189.1-2009 | Office-Enclosed | General | 0.99
ASHRAE 189.1-2009Office-Open PlanGeneral | ASHRAE 189.1-2009 | Office-Open Plan | General | 0.99
ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | 1.17
ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | 1.26
ASHRAE 189.1-2009Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 189.1-2009 | Classroom/Lecture/Training | For Penitentiary | 1.17
ASHRAE 189.1-2009LobbyGeneral | ASHRAE 189.1-2009 | Lobby | General | 1.17
ASHRAE 189.1-2009LobbyFor Hotel | ASHRAE 189.1-2009 | Lobby | For Hotel | 0.99
ASHRAE 189.1-2009LobbyFor Performing Arts Theater | ASHRAE 189.1-2009 | Lobby | For Performing Arts Theater | 2.97
ASHRAE 189.1-2009LobbyFor Motion Picture Theater | ASHRAE 189.1-2009 | Lobby | For Motion Picture Theater | 0.99
ASHRAE 189.1-2009Audience/Seating AreaGeneral | ASHRAE 189.1-2009 | Audience/Seating Area | General | 0.81
ASHRAE 189.1-2009Audience/Seating AreaFor Gymnasium | ASHRAE 189.1-2009 | Audience/Seating Area | For Gymnasium | 0.36
ASHRAE 189.1-2009Audience/Seating AreaFor Exercise Center | ASHRAE 189.1-2009 | Audience/Seating Area | For Exercise Center | 0.27
ASHRAE 189.1-2009Audience/Seating AreaFor Convention Center | ASHRAE 189.1-2009 | Audience/Seating Area | For Convention Center | 0.63
ASHRAE 189.1-2009Audience/Seating AreaFor Penitentiary | ASHRAE 189.1-2009 | Audience/Seating Area | For Penitentiary | 0.63
ASHRAE 189.1-2009Audience/Seating AreaFor Religious Buildings | ASHRAE 189.1-2009 | Audience/Seating Area | For Religious Buildings | 1.53
ASHRAE 189.1-2009Audience/Seating AreaFor Sports Arena | ASHRAE 189.1-2009 | Audience/Seating Area | For Sports Arena | 0.36
ASHRAE 189.1-2009Audience/Seating AreaFor Performing Arts Theater | ASHRAE 189.1-2009 | Audience/Seating Area | For Performing Arts Theater | 2.34
ASHRAE 189.1-2009Audience/Seating AreaFor Motion Picture Theater | ASHRAE 189.1-2009 | Audience/Seating Area | For Motion Picture Theater | 1.08
ASHRAE 189.1-2009Audience/Seating AreaFor Transportation | ASHRAE 189.1-2009 | Audience/Seating Area | For Transportation | 0.45
ASHRAE 189.1-2009AtriumFirst Three Floors | ASHRAE 189.1-2009 | Atrium | First Three Floors | 0.54
ASHRAE 189.1-2009AtriumEach Floor over First Three Floors | ASHRAE 189.1-2009 | Atrium | Each Floor over First Three Floors | 0.18
ASHRAE 189.1-2009Lounge/RecreationGeneral | ASHRAE 189.1-2009 | Lounge/Recreation | General | 1.08
ASHRAE 189.1-2009Lounge/RecreationFor Hospital | ASHRAE 189.1-2009 | Lounge/Recreation | For Hospital | 0.72
ASHRAE 189.1-2009Dining AreaGeneral | ASHRAE 189.1-2009 | Dining Area | General | 0.81
ASHRAE 189.1-2009Dining AreaFor Penitentiary | ASHRAE 189.1-2009 | Dining Area | For Penitentiary | 1.17
ASHRAE 189.1-2009Dining AreaFor Hotel | ASHRAE 189.1-2009 | Dining Area | For Hotel | 1.17
ASHRAE 189.1-2009Dining AreaFor Motel | ASHRAE 189.1-2009 | Dining Area | For Motel | 1.08
ASHRAE 189.1-2009Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 189.1-2009 | Dining Area | For Bar Lounge/Leisure Dining | 1.26
ASHRAE 189.1-2009Dining AreaFor Family Dining | ASHRAE 189.1-2009 | Dining Area | For Family Dining | 1.89
ASHRAE 189.1-2009Food PreparationGeneral | ASHRAE 189.1-2009 | Food Preparation | General | 1.08
ASHRAE 189.1-2009LaboratoryGeneral | ASHRAE 189.1-2009 | Laboratory | General | 1.26
ASHRAE 189.1-2009RestroomsGeneral | ASHRAE 189.1-2009 | Restrooms | General | 0.81
ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | 0.54
ASHRAE 189.1-2009Corridor/TransitionGeneral | ASHRAE 189.1-2009 | Corridor/Transition | General | 0.45
ASHRAE 189.1-2009Corridor/TransitionFor Hospital | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | 0.9
ASHRAE 189.1-2009Corridor/TransitionFor Manufacturing Facility | ASHRAE 189.1-2009 | Corridor/Transition | For Manufacturing Facility | 0.45
ASHRAE 189.1-2009Stairs-ActiveGeneral | ASHRAE 189.1-2009 | Stairs-Active | General | 0.54
ASHRAE 189.1-2009Active StorageGeneral | ASHRAE 189.1-2009 | Active Storage | General | 0.72
ASHRAE 189.1-2009Active StorageFor Hospital | ASHRAE 189.1-2009 | Active Storage | For Hospital | 0.81
ASHRAE 189.1-2009Inactive storageGeneral | ASHRAE 189.1-2009 | Inactive storage | General | 0.27
ASHRAE 189.1-2009Inactive storageFor Museum | ASHRAE 189.1-2009 | Inactive storage | For Museum | 0.72
ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | 1.26
ASHRAE 189.1-2009Gymnasium/Exercise CenterExercise Area | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Exercise Area | 0.81
ASHRAE 189.1-2009Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 189.1-2009 | Courthouse/Police Station/Penitentiary | Courtroom | 1.71
ASHRAE 189.1-2009Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 189.1-2009 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.81
ASHRAE 189.1-2009Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 189.1-2009 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.17
ASHRAE 189.1-2009Fire StationsFire Station Engine Room | ASHRAE 189.1-2009 | Fire Stations | Fire Station Engine Room | 0.72
ASHRAE 189.1-2009Fire StationsSleeping Quarters | ASHRAE 189.1-2009 | Fire Stations | Sleeping Quarters | 0.27
ASHRAE 189.1-2009Post OfficeSorting Area | ASHRAE 189.1-2009 | Post Office | Sorting Area | 1.08
ASHRAE 189.1-2009Convention CenterExhibit Space | ASHRAE 189.1-2009 | Convention Center | Exhibit Space | 1.17
ASHRAE 189.1-2009LibraryCard File and Cataloging | ASHRAE 189.1-2009 | Library | Card File and Cataloging | 0.99
ASHRAE 189.1-2009LibraryStacks | ASHRAE 189.1-2009 | Library | Stacks | 1.53
ASHRAE 189.1-2009LibraryReading Area | ASHRAE 189.1-2009 | Library | Reading Area | 1.08
ASHRAE 189.1-2009HospitalEmergency | ASHRAE 189.1-2009 | Hospital | Emergency | 2.43
ASHRAE 189.1-2009HospitalRecovery | ASHRAE 189.1-2009 | Hospital | Recovery | 0.72
ASHRAE 189.1-2009HospitalNurse Station | ASHRAE 189.1-2009 | Hospital | Nurse Station | 0.9
ASHRAE 189.1-2009HospitalExam/Treatment | ASHRAE 189.1-2009 | Hospital | Exam/Treatment | 1.35
ASHRAE 189.1-2009HospitalPharmacy | ASHRAE 189.1-2009 | Hospital | Pharmacy | 1.08
ASHRAE 189.1-2009HospitalPatient Room | ASHRAE 189.1-2009 | Hospital | Patient Room | 0.63
ASHRAE 189.1-2009HospitalOperating Room | ASHRAE 189.1-2009 | Hospital | Operating Room | 1.98
ASHRAE 189.1-2009HospitalNursery | ASHRAE 189.1-2009 | Hospital | Nursery | 0.54
ASHRAE 189.1-2009HospitalMedical Supply | ASHRAE 189.1-2009 | Hospital | Medical Supply | 1.26
ASHRAE 189.1-2009HospitalPhysical Therapy | ASHRAE 189.1-2009 | Hospital | Physical Therapy | 0.81
ASHRAE 189.1-2009HospitalRadiology | ASHRAE 189.1-2009 | Hospital | Radiology | 0.36
ASHRAE 189.1-2009HospitalLaundry-Washing | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | 0.54
ASHRAE 189.1-2009AutomotiveService/Repair | ASHRAE 189.1-2009 | Automotive | Service/Repair | 0.63
ASHRAE 189.1-2009ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 189.1-2009 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.08
ASHRAE 189.1-2009ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 189.1-2009 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.53
ASHRAE 189.1-2009ManufacturingDetailed Manufacturing | ASHRAE 189.1-2009 | Manufacturing | Detailed Manufacturing | 1.89
ASHRAE 189.1-2009ManufacturingEquipment Room | ASHRAE 189.1-2009 | Manufacturing | Equipment Room | 1.08
ASHRAE 189.1-2009ManufacturingControl Room | ASHRAE 189.1-2009 | Manufacturing | Control Room | 0.45
ASHRAE 189.1-2009Hotel/MotelGuest Rooms | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | 0.99
ASHRAE 189.1-2009DormitoryLiving Quarters | ASHRAE 189.1-2009 | Dormitory | Living Quarters | 0.99
ASHRAE 189.1-2009MuseumGeneral Exhibition | ASHRAE 189.1-2009 | Museum | General Exhibition | 0.9
ASHRAE 189.1-2009MuseumRestoration | ASHRAE 189.1-2009 | Museum | Restoration | 1.53
ASHRAE 189.1-2009Electrical/MechanicalGeneral | ASHRAE 189.1-2009 | Electrical/Mechanical | General | 1.35
ASHRAE 189.1-2009WorkshopGeneral | ASHRAE 189.1-2009 | Workshop | General | 1.71
ASHRAE 189.1-2009Bank/OfficeBanking Activity Area | ASHRAE 189.1-2009 | Bank/Office | Banking Activity Area | 1.35
ASHRAE 189.1-2009Religious BuildingsWorship Pulpit, Choir | ASHRAE 189.1-2009 | Religious Buildings | Worship Pulpit, Choir | 2.16
ASHRAE 189.1-2009Religious BuildingsFellowship Hall | ASHRAE 189.1-2009 | Religious Buildings | Fellowship Hall | 0.81
ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | 1.53
ASHRAE 189.1-2009Retail (not including accent lighting)Mall Concourse | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Mall Concourse | 1.53
ASHRAE 189.1-2009Sports ArenaRing Sports Area | ASHRAE 189.1-2009 | Sports Arena | Ring Sports Area | 2.43
ASHRAE 189.1-2009Sports ArenaCourt Sports Area | ASHRAE 189.1-2009 | Sports Arena | Court Sports Area | 2.07
ASHRAE 189.1-2009Sports ArenaIndoor Playing Field Area | ASHRAE 189.1-2009 | Sports Arena | Indoor Playing Field Area | 1.26
ASHRAE 189.1-2009WarehouseFine Material Storage | ASHRAE 189.1-2009 | Warehouse | Fine Material Storage | 1.26
ASHRAE 189.1-2009WarehouseMedium/Bulky Material Storage | ASHRAE 189.1-2009 | Warehouse | Medium/Bulky Material Storage | 0.81
ASHRAE 189.1-2009Parking GarageGarage Area | ASHRAE 189.1-2009 | Parking Garage | Garage Area | 0.18
ASHRAE 189.1-2009TransportationAirport-Concourse | ASHRAE 189.1-2009 | Transportation | Airport-Concourse | 0.54
ASHRAE 189.1-2009TransportationAir/Train/Bus-Baggage Area | ASHRAE 189.1-2009 | Transportation | Air/Train/Bus-Baggage Area | 0.9
ASHRAE 189.1-2009TransportationTerminal-Ticket Counter | ASHRAE 189.1-2009 | Transportation | Terminal-Ticket Counter | 1.35
ASHRAE 189.1-2009Exterior SpacesGeneral | ASHRAE 189.1-2009 | Exterior Spaces | General | 0
ASHRAE 189.1-2009AtticsGeneral | ASHRAE 189.1-2009 | Attics | General | 0

## ConstructionSets
|  |  |  | Exterior Surfaces |  |  | Interior Surfaces |  |  | Ground Contact Surfaces |  |  | Exterior Sub Surfaces | [7 empty] | Interior Sub Surfaces |  |  | Misc Surfaces
Template | Building Type | Space Type | Climate Zone Set | Exterior Wall | Exterior Floor | Exterior Rooofs | Interior Walls | Interior Floors | Interior Ceilings | Ground Contact Walls | Ground Contact Floors | Ground Contact Ceilings | Exterior Fixed Windows | Exterior Operable Windows | Exterior Doors | Exterior Glass Doors | Exterior Overhead Doors | Exterior Skylights | Tubular Daylight Domes | Tubular Daylight Diffusers | Interior Fixed Windows | Interior Operable Windows | Interior Doors | Space Shading | Building Shading | Site Shading | Interior Partitions
ASHRAE 189.1-2009 | Mid-riseApartment |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | StripMall |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeOffice |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | QuickServiceRestaurant |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SecondarySchool |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SmallHotel |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | FullServiceRestaurant |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Retail |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Outpatient |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SuperMarket |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeHotel |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Hospital |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Warehouse |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 1-3 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SmallOffice |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | MediumOffice |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | PrimarySchool |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeHotel |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 |  | Attic | ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | ASHRAE 189.1-2009 AtticFloor ClimateZone 1-8 | ASHRAE 189.1-2009 AtticFloor ClimateZone 1-8 | ASHRAE 189.1-2009 AtticFloor ClimateZone 1-8
ASHRAE 189.1-2009 | SuperMarket |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Hospital |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | StripMall |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Mid-riseApartment |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeHotel |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeOffice |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | MediumOffice |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SmallOffice |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeHotel |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | QuickServiceRestaurant |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Outpatient |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SecondarySchool |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | FullServiceRestaurant |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Warehouse |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 1-3 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Retail |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SmallHotel |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | PrimarySchool |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeOffice |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Retail |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SecondarySchool |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeHotel |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SuperMarket |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | FullServiceRestaurant |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SmallHotel |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | StripMall |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Mid-riseApartment |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeHotel |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | PrimarySchool |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Outpatient |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | MediumOffice |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | QuickServiceRestaurant |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Hospital |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SmallOffice |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Warehouse |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 1-3 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Retail |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SuperMarket |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Hospital |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeOffice |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeHotel |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SmallOffice |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeHotel |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | QuickServiceRestaurant |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SmallHotel |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | StripMall |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SecondarySchool |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Outpatient |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Warehouse |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 4-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Mid-riseApartment |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | MediumOffice |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | FullServiceRestaurant |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | PrimarySchool |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeOffice |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | QuickServiceRestaurant |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Hospital |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SuperMarket |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SmallOffice |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeHotel |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeHotel |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Retail |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Outpatient |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeOffice |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | QuickServiceRestaurant |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 6-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SuperMarket |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | PrimarySchool |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Hospital |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Mid-riseApartment |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SmallHotel |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeHotel |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | MediumOffice |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Retail |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | FullServiceRestaurant |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | StripMall |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeHotel |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SmallOffice |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Warehouse |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 4-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SecondarySchool |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeHotel |  | ClimateZone 7 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Hospital |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeHotel |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | QuickServiceRestaurant |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 6-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Warehouse |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 4-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SuperMarket |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SmallOffice |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Mid-riseApartment |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeOffice |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Retail |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | PrimarySchool |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | Outpatient |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SecondarySchool |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | FullServiceRestaurant |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | MediumOffice |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | StripMall |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | SmallHotel |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
ASHRAE 189.1-2009 | LargeHotel |  | ClimateZone 8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeHotel |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | MediumOffice |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SuperMarket |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | StripMall |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 |  | Attic | ClimateZone 1 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 1 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 1 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 1
CBECS_1980-2004 | Outpatient |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallOffice |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 1 | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Metal ClimateZone 1 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeOffice |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallHotel |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 |  | Attic | ClimateZone 2a | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2a
CBECS_1980-2004 | MediumOffice |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Metal ClimateZone 2a | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SuperMarket |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallOffice |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallHotel |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | StripMall |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 2a | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Outpatient |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeOffice |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeHotel |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 |  | Attic | ClimateZone 2b | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2b
CBECS_1980-2004 | SmallHotel |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | StripMall |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SuperMarket |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 2b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Metal ClimateZone 2b | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Outpatient |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeOffice |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeHotel |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | MediumOffice |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallOffice |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallHotel |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeOffice |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeHotel |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallOffice |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | StripMall |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Outpatient |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | MediumOffice |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SuperMarket |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 |  | Attic | ClimateZone 3a | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3a
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 3a | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Metal ClimateZone 3a | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | StripMall |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeHotel |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SuperMarket |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 3b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Metal ClimateZone 3b LAS | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | MediumOffice |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallOffice |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | MediumOffice |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 |  | Attic | ClimateZone 3b | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAS | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAS | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAS
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeOffice |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeHotel |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallHotel |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallHotel |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 |  | Attic | ClimateZone 3b | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAX | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAX | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAX
CBECS_1980-2004 | SmallOffice |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Outpatient |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Metal ClimateZone 3b LAX | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeOffice |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | StripMall |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SuperMarket |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 3b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Outpatient |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 3c | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeHotel |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeOffice |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Outpatient |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Metal ClimateZone 3c | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | MediumOffice |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallOffice |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | StripMall |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallHotel |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SuperMarket |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Metal ClimateZone 4a | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeHotel |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | MediumOffice |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeOffice |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 |  | Attic | ClimateZone 4a | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4a
CBECS_1980-2004 | StripMall |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Outpatient |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallHotel |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SuperMarket |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 4a | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallOffice |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallOffice |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Metal ClimateZone 4b | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallHotel |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SuperMarket |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeOffice |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Outpatient |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 4b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | StripMall |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeHotel |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 |  | Attic | ClimateZone 4b | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4b
CBECS_1980-2004 | MediumOffice |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SuperMarket |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 4c | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | StripMall |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Outpatient |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeHotel |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallHotel |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 |  | Attic | ClimateZone 4c | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4c | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4c | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4c
CBECS_1980-2004 | SmallOffice |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | MediumOffice |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Metal ClimateZone 4c | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeOffice |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallOffice |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeOffice |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | MediumOffice |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Metal ClimateZone 5 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 |  | Attic | ClimateZone 5a | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a
CBECS_1980-2004 | LargeHotel |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Outpatient |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | StripMall |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 5a | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SuperMarket |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallHotel |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeOffice |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeHotel |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallHotel |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | StripMall |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SuperMarket |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | MediumOffice |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallOffice |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 |  | Attic | ClimateZone 5b | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5b
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Outpatient |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 5b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeHotel |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 |  | Attic | ClimateZone 6a | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6a
CBECS_1980-2004 | SuperMarket |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallHotel |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 6a | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Outpatient |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | StripMall |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallOffice |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Metal ClimateZone 6a | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeOffice |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | MediumOffice |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | StripMall |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallHotel |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 6b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | MediumOffice |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallOffice |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Metal ClimateZone 6b | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeHotel |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 |  | Attic | ClimateZone 6b | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6b
CBECS_1980-2004 | LargeOffice |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SuperMarket |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Outpatient |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Outpatient |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallOffice |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SuperMarket |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | StripMall |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 |  | Attic | ClimateZone 7 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 7 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 7 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 7
CBECS_1980-2004 | MediumOffice |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Metal ClimateZone 7 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 7 | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeOffice |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeHotel |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallHotel |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Hospital |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | StripMall |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Mid-riseApartment |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Warehouse |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Metal ClimateZone 8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SecondarySchool |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeHotel |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Outpatient |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | LargeOffice |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallHotel |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | QuickServiceRestaurant |  | ClimateZone 8 | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | PrimarySchool |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | Retail |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SmallOffice |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | SuperMarket |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | MediumOffice |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 | FullServiceRestaurant |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_1980-2004 |  | Attic | ClimateZone 8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 8
CBECS_Before-1980 | LargeOffice |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeHotel |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Hospital |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Retail |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallOffice |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Warehouse |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Metal ClimateZone 1-2 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SuperMarket |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | QuickServiceRestaurant |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 |  | Attic | ClimateZone 1-3 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 1-3 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 1-3 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 1-3
CBECS_Before-1980 | FullServiceRestaurant |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallHotel |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | MediumOffice |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SecondarySchool |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | StripMall |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Outpatient |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Mid-riseApartment |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | PrimarySchool |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Hospital |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SuperMarket |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeOffice |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallOffice |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | QuickServiceRestaurant |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Retail |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Warehouse |  | ClimateZone 3a | CBECS Before-1980 ExtWall Metal ClimateZone 3a | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeHotel |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Warehouse |  | ClimateZone 3b | CBECS Before-1980 ExtWall Metal ClimateZone 3b | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Hospital |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SuperMarket |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeOffice |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallOffice |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | QuickServiceRestaurant |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeHotel |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Retail |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallOffice |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeHotel |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeOffice |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | MediumOffice |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SuperMarket |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Retail |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | QuickServiceRestaurant |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Mid-riseApartment |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | PrimarySchool |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | StripMall |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Outpatient |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SecondarySchool |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Hospital |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallHotel |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Warehouse |  | ClimateZone 3c | CBECS Before-1980 ExtWall Metal ClimateZone 3c | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | FullServiceRestaurant |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeOffice |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Warehouse |  | ClimateZone 4a | CBECS Before-1980 ExtWall Metal ClimateZone 4a | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallHotel |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallOffice |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeHotel |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | FullServiceRestaurant |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Retail |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SecondarySchool |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SuperMarket |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 |  | Attic | ClimateZone 4a | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4a | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4a | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4a
CBECS_Before-1980 | QuickServiceRestaurant |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Hospital |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | StripMall |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Outpatient |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Mid-riseApartment |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | PrimarySchool |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | MediumOffice |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | QuickServiceRestaurant |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SuperMarket |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallHotel |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Warehouse |  | ClimateZone 4b | CBECS Before-1980 ExtWall Metal ClimateZone 4b | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeOffice |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | PrimarySchool |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 |  | Attic | ClimateZone 4b | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4b | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4b | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4b
CBECS_Before-1980 | Retail |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeHotel |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Hospital |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | FullServiceRestaurant |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallOffice |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | StripMall |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SecondarySchool |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Mid-riseApartment |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Outpatient |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | MediumOffice |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeOffice |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Retail |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeHotel |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | MediumOffice |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Outpatient |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SecondarySchool |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | FullServiceRestaurant |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Warehouse |  | ClimateZone 4c | CBECS Before-1980 ExtWall Metal ClimateZone 4c | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallOffice |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | PrimarySchool |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Hospital |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | QuickServiceRestaurant |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 |  | Attic | ClimateZone 4c | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4c | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4c | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4c
CBECS_Before-1980 | Mid-riseApartment |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallHotel |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | StripMall |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SuperMarket |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SuperMarket |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | MediumOffice |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeHotel |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallHotel |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Warehouse |  | ClimateZone 5a | CBECS Before-1980 ExtWall Metal ClimateZone 5a | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 |  | Attic | ClimateZone 5a | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a
CBECS_Before-1980 | QuickServiceRestaurant |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | StripMall |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SecondarySchool |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Retail |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Outpatient |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Hospital |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | PrimarySchool |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Mid-riseApartment |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeOffice |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | FullServiceRestaurant |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallOffice |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | MediumOffice |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 |  | Attic | ClimateZone 5b | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5b | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5b | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5b
CBECS_Before-1980 | Mid-riseApartment |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Warehouse |  | ClimateZone 5b | CBECS Before-1980 ExtWall Metal ClimateZone 5b | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallOffice |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeOffice |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Retail |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | PrimarySchool |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | QuickServiceRestaurant |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | StripMall |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SecondarySchool |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SuperMarket |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeHotel |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallHotel |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Hospital |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Outpatient |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | FullServiceRestaurant |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeOffice |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallOffice |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | QuickServiceRestaurant |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Hospital |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | PrimarySchool |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Warehouse |  | ClimateZone 6 | CBECS Before-1980 ExtWall Metal ClimateZone 6 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 |  | Attic | ClimateZone 6 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 6 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 6 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 6
CBECS_Before-1980 | MediumOffice |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Outpatient |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SuperMarket |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Retail |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeHotel |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | StripMall |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | FullServiceRestaurant |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SecondarySchool |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallHotel |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Mid-riseApartment |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeOffice |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Hospital |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | PrimarySchool |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallHotel |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 |  | Attic | ClimateZone 7 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 7 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 7 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 7
CBECS_Before-1980 | StripMall |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Mid-riseApartment |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeHotel |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallOffice |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SuperMarket |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | MediumOffice |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Retail |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Outpatient |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SecondarySchool |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | QuickServiceRestaurant |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | FullServiceRestaurant |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Warehouse |  | ClimateZone 7 | CBECS Before-1980 ExtWall Metal ClimateZone 7 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeHotel |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | MediumOffice |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | StripMall |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Retail |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SmallHotel |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | LargeOffice |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 |  | Attic | ClimateZone 8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 8
CBECS_Before-1980 | SmallOffice |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SecondarySchool |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Outpatient |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | PrimarySchool |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Mid-riseApartment |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | QuickServiceRestaurant |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Warehouse |  | ClimateZone 8 | CBECS Before-1980 ExtWall Metal ClimateZone 8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | SuperMarket |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | Hospital |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
CBECS_Before-1980 | FullServiceRestaurant |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Warehouse |  | ClimateZone 1 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 1 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeOffice |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Mid-riseApartment |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Retail |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | PrimarySchool |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | StripMall |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | MediumOffice |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | QuickServiceRestaurant |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SmallHotel |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Outpatient |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SecondarySchool |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | FullServiceRestaurant |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SmallOffice |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Hospital |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SuperMarket |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 |  | Attic | ClimateZone 1-5 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 1-5 | ASHRAE 90.1-2004 AtticFloor ClimateZone 1-5 | ASHRAE 90.1-2004 AtticFloor ClimateZone 1-5
NREL_2004 | Warehouse |  | ClimateZone 2 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 2-3 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 2 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Warehouse |  | ClimateZone 3 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 2-3 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 3-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | MediumOffice |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | StripMall |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeOffice |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Mid-riseApartment |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resA 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resA 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | FullServiceRestaurant |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SecondarySchool |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SuperMarket |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Outpatient |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Retail |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | QuickServiceRestaurant |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SmallOffice |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SmallHotel |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | PrimarySchool |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resH 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resH 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Hospital |  | ClimateZone 3a-b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SmallHotel |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | FullServiceRestaurant |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | MediumOffice |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Hospital |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SmallOffice |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Retail |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeOffice |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Mid-riseApartment |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | QuickServiceRestaurant |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | PrimarySchool |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | StripMall |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Outpatient |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SuperMarket |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SecondarySchool |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SmallOffice |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | StripMall |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | FullServiceRestaurant |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Mid-riseApartment |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 4-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SuperMarket |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Warehouse |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 4 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 3-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeOffice |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | PrimarySchool |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | QuickServiceRestaurant |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | MediumOffice |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SmallHotel |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 4-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SecondarySchool |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Hospital |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Retail |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Outpatient |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Hospital |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Warehouse |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 5 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SuperMarket |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeOffice |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Retail |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 5-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SmallOffice |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SmallHotel |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 4-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | StripMall |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SecondarySchool |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | QuickServiceRestaurant |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | MediumOffice |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | FullServiceRestaurant |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | PrimarySchool |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Outpatient |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Mid-riseApartment |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 4-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 5-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Warehouse |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 6-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeOffice |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Retail |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SmallOffice |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SuperMarket |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Hospital |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 |  | Attic | ClimateZone 6-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 6-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 6-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 6-8
NREL_2004 | Retail |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SecondarySchool |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeOffice |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | FullServiceRestaurant |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | PrimarySchool |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SmallOffice |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | StripMall |  | ClimateZone 7 |  | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Warehouse |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 6-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | MediumOffice |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | QuickServiceRestaurant |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SuperMarket |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Mid-riseApartment |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Hospital |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SmallHotel |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Outpatient |  | ClimateZone 7 |  | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | MediumOffice |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | PrimarySchool |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Outpatient |  | ClimateZone 8 |  | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | FullServiceRestaurant |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SmallHotel |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | QuickServiceRestaurant |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | StripMall |  | ClimateZone 8 |  | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SuperMarket |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SmallOffice |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Retail |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeOffice |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Mid-riseApartment |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | LargeHotel |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Hospital |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | SecondarySchool |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
NREL_2004 | Warehouse |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 6-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition

## Constructions
Constructions |  |  |  |  | Outside |  |  |  |  | Inside
Name | Construction Standard | Climate Zone Set | Intended Surface Type | Standards Construction Type | Material 1 | Material 2 | Material 3 | Material 4 | Material 5 | Material 6
ASHRAE 189.1-2009 AtticFloor ClimateZone 1-8 | ASHRAE 189.1-2009 | ClimateZone 1-8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | ASHRAE 189.1-2009 | ClimateZone 1 | ExteriorRoof | IEAD | Roof Membrane | Roof Insulation [18] | Metal Decking
ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | ASHRAE 189.1-2009 | ClimateZone 2-5 | ExteriorRoof | IEAD | Roof Membrane | Roof Insulation [21] | Metal Decking
ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | ASHRAE 189.1-2009 | ClimateZone 6 | ExteriorRoof | IEAD | Roof Membrane | Roof Insulation [24] | Metal Decking
ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | ASHRAE 189.1-2009 | ClimateZone 7-8 | ExteriorRoof | IEAD | Roof Membrane | Roof Insulation [26] | Metal Decking
ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 1 | ASHRAE 189.1-2009 | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing | Roof Insulation [19]
ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 2-5 | ASHRAE 189.1-2009 | ClimateZone 2-5 | ExteriorRoof | Metal | Metal Roofing | Roof Insulation [22]
ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | ASHRAE 189.1-2009 | ClimateZone 6 | ExteriorRoof | Metal | Metal Roofing | Roof Insulation [25]
ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 7-8 | ASHRAE 189.1-2009 | ClimateZone 7-8 | ExteriorRoof | Metal | Metal Roofing | Roof Insulation [27]
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ASHRAE 189.1-2009 | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [31] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ASHRAE 189.1-2009 | ClimateZone 2 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [35] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ASHRAE 189.1-2009 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [36] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ASHRAE 189.1-2009 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [37] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ASHRAE 189.1-2009 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [40] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ASHRAE 189.1-2009 | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [42] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ASHRAE 189.1-2009 | ClimateZone 7-8 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [44] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 1 | ASHRAE 189.1-2009 | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [35] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 2 | ASHRAE 189.1-2009 | ClimateZone 2 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [36] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 3 | ASHRAE 189.1-2009 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [37] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 4 | ASHRAE 189.1-2009 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [40] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 5 | ASHRAE 189.1-2009 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [42] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 6 | ASHRAE 189.1-2009 | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [44] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 7 | ASHRAE 189.1-2009 | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [44] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 8 | ASHRAE 189.1-2009 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [46] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Metal ClimateZone 1-3 | ASHRAE 189.1-2009 | ClimateZone 1-3 | ExteriorWall | Metal | Metal Siding | Wall Insulation [32] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Metal ClimateZone 4-8 | ASHRAE 189.1-2009 | ClimateZone 4-8 | ExteriorWall | Metal | Metal Siding | Wall Insulation [38] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ASHRAE 189.1-2009 | ClimateZone 1-3 | ExteriorWall | SteelFramed | MAT-SHEATH | Wall Insulation [33] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ASHRAE 189.1-2009 | ClimateZone 4-8 | ExteriorWall | SteelFramed | MAT-SHEATH | Wall Insulation [39] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 1-4 | ASHRAE 189.1-2009 | ClimateZone 1-4 | ExteriorWall | WoodFramed | Wood Siding | Wall Insulation [34] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 5 | ASHRAE 189.1-2009 | ClimateZone 5 | ExteriorWall | WoodFramed | Wood Siding | Wall Insulation [41] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 6-8 | ASHRAE 189.1-2009 | ClimateZone 6-8 | ExteriorWall | WoodFramed | Wood Siding | Wall Insulation [43] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 | ClimateZone 1 | ExteriorWindow |  | Theoretical Glass [167]
ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 | ClimateZone 2 | ExteriorWindow |  | Theoretical Glass [197]
ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 | ClimateZone 3 | ExteriorWindow |  | Theoretical Glass [202]
ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 | ClimateZone 4-5 | ExteriorWindow |  | Theoretical Glass [207]
ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 | ClimateZone 6 | ExteriorWindow |  | Theoretical Glass [216]
ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 | ClimateZone 7-8 | ExteriorWindow |  | Theoretical Glass [221]
ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | ASHRAE 189.1-2009 | ClimateZone 4-5 | ExteriorWindow |  | Theoretical Glass [216]
ASHRAE 90.1-2004 AtticFloor ClimateZone 1-5 | ASHRAE 90.1-2004 | ClimateZone 1-5 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-5.18 | 1/2IN Gypsum
ASHRAE 90.1-2004 AtticFloor ClimateZone 6-8 | ASHRAE 90.1-2004 | ClimateZone 6-8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-6.52 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | ASHRAE 90.1-2004 | ClimateZone 1-4 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.79 | Metal Decking
ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.85 | Metal Decking
ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 1 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.85 | Metal Decking
ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.79 | Metal Decking
ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.72 | Metal Decking
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 1 | ASHRAE 90.1-2004 | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 2 | ASHRAE 90.1-2004 | ClimateZone 2 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-1.05
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 3-4 | ASHRAE 90.1-2004 | ClimateZone 3-4 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-1.81
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 5-6 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-1.87
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-1.81
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.50
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ASHRAE 90.1-2004 | ClimateZone 1-2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ASHRAE 90.1-2004 | ClimateZone 3-4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.17 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ASHRAE 90.1-2004 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.43 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ASHRAE 90.1-2004 | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.69 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.96 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.20 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 1-2 | ASHRAE 90.1-2004 | ClimateZone 1-2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.17 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 3 | ASHRAE 90.1-2004 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.43 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 4 | ASHRAE 90.1-2004 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.69 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 5-6 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.96 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.20 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.48 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Metal ClimateZone 1 | ASHRAE 90.1-2004 | ClimateZone 1 | ExteriorWall | Metal | Metal Siding | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Metal ClimateZone 2-3 | ASHRAE 90.1-2004 | ClimateZone 2-3 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.77 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Metal ClimateZone 4 | ASHRAE 90.1-2004 | ClimateZone 4 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.12 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Metal ClimateZone 5 | ASHRAE 90.1-2004 | ClimateZone 5 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.24 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Metal ClimateZone 6-8 | ASHRAE 90.1-2004 | ClimateZone 6-8 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.37 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ASHRAE 90.1-2004 | ClimateZone 1-4 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.42 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.10 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ASHRAE 90.1-2004 | ClimateZone 7-8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.75 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 3 | ASHRAE 90.1-2004 | ClimateZone 3 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.10 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 4-6 | ASHRAE 90.1-2004 | ClimateZone 4-6 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.75 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-3.21 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ASHRAE 90.1-2004 | ClimateZone 1-7 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.98 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-3.45 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 | ClimateZone 1-2 | ExteriorWindow |  | Fixed Window 5.84/0.25/0.11
ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 | ClimateZone 3a-3b | ExteriorWindow |  | Fixed Window 3.24/0.25/0.16
ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 | ClimateZone 3c | ExteriorWindow |  | Fixed Window 5.84/0.39/0.22
ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 | ClimateZone 4-6 | ExteriorWindow |  | Fixed Window 3.24/0.39/0.31
ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorWindow |  | Fixed Window 3.24/0.49/0.41
ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWindow |  | Fixed Window 2.62/0.30/0.21
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 3c | ASHRAE 90.1-2004 | ClimateZone 3c | ExteriorWindow |  | Fixed Window 5.84/0.61/0.47
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 4-6 | ASHRAE 90.1-2004 | ClimateZone 4-6 | ExteriorWindow |  | Fixed Window 3.81/0.39/0.27
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorWindow |  | Fixed Window 3.81/0.49/0.38
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWindow |  | Fixed Window 2.67/0.30/0.21
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resA 3a-3b | ASHRAE 90.1-2004 | ClimateZone 3a-3b | ExteriorWindow |  | Fixed Window 3.81/0.39/0.27
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resH 3a-3b | ASHRAE 90.1-2004 | ClimateZone 3a-3b | ExteriorWindow |  | Fixed Window 3.24/0.39/0.31
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 | ClimateZone 1-8 | ExteriorWindow |  | Fixed Window 5.84/0.70/0.60
AtticRoof ClimateZone 1-8 |  | ClimateZone 1-8 | AtticRoof | WoodFramed | Roof Membrane | Metal Decking
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 1 |  | ClimateZone 1 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.38 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2a |  | ClimateZone 2a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.67 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2b |  | ClimateZone 2b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.83 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3a |  | ClimateZone 3a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.45 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAS |  | ClimateZone 3b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.67 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAX |  | ClimateZone 3b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-1.76 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4a |  | ClimateZone 4a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.04 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4b |  | ClimateZone 4b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.99 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4c |  | ClimateZone 4c | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.75 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a |  | ClimateZone 5a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.32 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5b |  | ClimateZone 5b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.45 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6a |  | ClimateZone 6a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.91 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6b |  | ClimateZone 6b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.59 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 7 |  | ClimateZone 7 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-4.40 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 8 |  | ClimateZone 8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-5.68 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 |  | ClimateZone 1 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.38 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a |  | ClimateZone 2a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.67 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b |  | ClimateZone 2b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.83 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a |  | ClimateZone 3a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.44 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.66 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-1.76 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c |  | ClimateZone 3c | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.00 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a |  | ClimateZone 4a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.03 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b |  | ClimateZone 4b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.99 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c |  | ClimateZone 4c | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.75 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a |  | ClimateZone 5a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.38 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b |  | ClimateZone 5b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.51 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b 1 |  | ClimateZone 5b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.51 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a |  | ClimateZone 6a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.97 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b |  | ClimateZone 6b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.65 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 |  | ClimateZone 7 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-4.41 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 |  | ClimateZone 8 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-5.75 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 1 |  | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.38
CBECS 1980-2004 ExtRoof Metal ClimateZone 2a |  | ClimateZone 2a | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.67
CBECS 1980-2004 ExtRoof Metal ClimateZone 2b |  | ClimateZone 2b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.83
CBECS 1980-2004 ExtRoof Metal ClimateZone 3a |  | ClimateZone 3a | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.44
CBECS 1980-2004 ExtRoof Metal ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.66
CBECS 1980-2004 ExtRoof Metal ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-1.76
CBECS 1980-2004 ExtRoof Metal ClimateZone 3c |  | ClimateZone 3c | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.00
CBECS 1980-2004 ExtRoof Metal ClimateZone 4a |  | ClimateZone 4a | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.03
CBECS 1980-2004 ExtRoof Metal ClimateZone 4b |  | ClimateZone 4b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.99
CBECS 1980-2004 ExtRoof Metal ClimateZone 4c |  | ClimateZone 4c | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.75
CBECS 1980-2004 ExtRoof Metal ClimateZone 5a |  | ClimateZone 5a | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.38
CBECS 1980-2004 ExtRoof Metal ClimateZone 5b |  | ClimateZone 5b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.38
CBECS 1980-2004 ExtRoof Metal ClimateZone 6a |  | ClimateZone 6a | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.97
CBECS 1980-2004 ExtRoof Metal ClimateZone 6b |  | ClimateZone 6b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.65
CBECS 1980-2004 ExtRoof Metal ClimateZone 7 |  | ClimateZone 7 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-4.41
CBECS 1980-2004 ExtRoof Metal ClimateZone 8 |  | ClimateZone 8 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-5.75
CBECS 1980-2004 ExtWall Mass ClimateZone 1 |  | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 2a |  | ClimateZone 2a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.52 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 2b |  | ClimateZone 2b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.43 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.61 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.61 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.47 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.93 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a |  | ClimateZone 4c-5a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.76 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 5b |  | ClimateZone 5b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.26 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 6a |  | ClimateZone 6a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.48 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 6b |  | ClimateZone 6b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.23 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.89 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-3.75 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 1 |  | ClimateZone 1 | ExteriorWall | Metal | Metal Siding | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 2a |  | ClimateZone 2a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.98 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 2b |  | ClimateZone 2b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.54 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.16 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.91 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.61 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.16 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.79 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.57 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.72 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 5 |  | ClimateZone 5 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.96 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 6a |  | ClimateZone 6a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-2.52 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 6b |  | ClimateZone 6b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-2.25 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-2.85 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-3.72 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 |  | ClimateZone 1 | ExteriorWall | SteelFramed | Wood Siding | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a |  | ClimateZone 2a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.17 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b |  | ClimateZone 2b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.73 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b 1 |  | ClimateZone 2b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.73 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.36 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.10 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.80 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.36 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.98 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.76 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.92 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 |  | ClimateZone 5 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.15 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a |  | ClimateZone 6a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.71 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b |  | ClimateZone 6b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.44 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-3.04 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-3.91 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 1 |  | ClimateZone 1 | ExteriorWall | WoodFramed | Wood Siding | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 2a |  | ClimateZone 2a | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.17 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 2b |  | ClimateZone 2b | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-0.73 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.36 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.10 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-0.80 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.36 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.98 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.76 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.92 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 5 |  | ClimateZone 5 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-2.15 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 6a |  | ClimateZone 6a | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-2.71 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 6b |  | ClimateZone 6b | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-2.44 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-3.04 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-3.91 | 1/2IN Gypsum
CBECS 1980-2004 ExtWindow ClimateZone 1-2 |  | ClimateZone 1-2 | ExteriorWindow |  | Fixed Window 5.84/0.25/0.11
CBECS 1980-2004 ExtWindow ClimateZone 3a |  | ClimateZone 3a | ExteriorWindow |  | Fixed Window 4.09/0.26/0.13
CBECS 1980-2004 ExtWindow ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorWindow |  | Fixed Window 5.84/0.25/0.11
CBECS 1980-2004 ExtWindow ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorWindow |  | Fixed Window 5.84/0.44/0.27
CBECS 1980-2004 ExtWindow ClimateZone 3c |  | ClimateZone 3c | ExteriorWindow |  | Fixed Window 4.09/0.39/0.25
CBECS 1980-2004 ExtWindow ClimateZone 4a |  | ClimateZone 4a | ExteriorWindow |  | Fixed Window 3.35/0.36/0.27
CBECS 1980-2004 ExtWindow ClimateZone 4b |  | ClimateZone 4b | ExteriorWindow |  | Fixed Window 4.09/0.36/0.23
CBECS 1980-2004 ExtWindow ClimateZone 4c |  | ClimateZone 4c | ExteriorWindow |  | Fixed Window 4.09/0.39/0.25
CBECS 1980-2004 ExtWindow ClimateZone 5 |  | ClimateZone 5 | ExteriorWindow |  | Fixed Window 3.35/0.39/0.31
CBECS 1980-2004 ExtWindow ClimateZone 6 |  | ClimateZone 6 | ExteriorWindow |  | Fixed Window 2.96/0.39/0.31
CBECS 1980-2004 ExtWindow ClimateZone 7 |  | ClimateZone 7 | ExteriorWindow |  | Fixed Window 2.96/0.49/0.41
CBECS 1980-2004 ExtWindow ClimateZone 8 |  | ClimateZone 8 | ExteriorWindow |  | Fixed Window 2.96/0.62/0.54
CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 |  | ClimateZone 1-8 | ExteriorWindow |  | Fixed Window 5.84/0.25/0.11
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 1-3 |  | ClimateZone 1-3 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-1.76 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4a |  | ClimateZone 4a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Res Insulation-2.05 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4b |  | ClimateZone 4b | AtticFloor | WoodFramed | 1/2IN Gypsum | IEAD NonRes Roof Insulation-1.98 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4c |  | ClimateZone 4c | AtticFloor | WoodFramed | 1/2IN Gypsum | IEAD NonRes Roof Insulation-2.07 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a |  | ClimateZone 5a | AtticFloor | WoodFramed | 1/2IN Gypsum | IEAD NonRes Roof Insulation-2.50 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5b |  | ClimateZone 5b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Res Insulation-2.37 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 6 |  | ClimateZone 6 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.99 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 7 |  | ClimateZone 7 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Res Insulation-2.93 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 8 |  | ClimateZone 8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.99 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 |  | ClimateZone 1-3 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-1.76 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 4a |  | ClimateZone 4a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.04 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 4b |  | ClimateZone 4b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-1.98 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 4c |  | ClimateZone 4c | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.07 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 5a |  | ClimateZone 5a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.50 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 5b |  | ClimateZone 5b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.37 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 6 |  | ClimateZone 6 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.99 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 7 |  | ClimateZone 7 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.93 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 7 1 |  | ClimateZone 7 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.93 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 8 |  | ClimateZone 8 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.99 | Metal Decking
CBECS Before-1980 ExtWall Mass ClimateZone 1-2 |  | ClimateZone 1-2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.77 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.78 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 3b |  | ClimateZone 3b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.77 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.79 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.99 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.96 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.01 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 5a |  | ClimateZone 5a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.13 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 5b |  | ClimateZone 5b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.09 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 6 |  | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.22 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.30 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.41 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 1-2 |  | ClimateZone 1-2 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.57 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.59 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 3b |  | ClimateZone 3b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.57 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.59 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.80 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.77 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.81 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 5a |  | ClimateZone 5a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.94 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 5b |  | ClimateZone 5b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.90 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 6 |  | ClimateZone 6 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.02 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.10 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.22 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b |  | ClimateZone 1-3b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.77 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.79 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.99 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.96 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.01 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a |  | ClimateZone 5a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.13 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b |  | ClimateZone 5b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.09 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 |  | ClimateZone 6 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.22 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.30 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.41 | 1/2IN Gypsum
CBECS Before-1980 ExtWindow ClimateZone 1-4 |  | ClimateZone 1-4 | ExteriorWindow |  | Fixed Window 5.84/0.54/0.38
CBECS Before-1980 ExtWindow ClimateZone 5-8 |  | ClimateZone 5-8 | ExteriorWindow |  | Fixed Window 3.53/0.41/0.32
CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 |  | ClimateZone 1-8 | ExteriorWindow |  | Fixed Window 5.84/0.54/0.38
Exterior Door |  | ClimateZone 1-8 | ExteriorDoor |  | F08 Metal surface | I01 25mm insulation board
ExtSlab 4in ClimateZone 1-8 |  | ClimateZone 1-8 | ExteriorFloor |  | MAT-CC05 4 HW CONCRETE
ExtSlab 8in ClimateZone 1-8 |  | ClimateZone 1-8 | ExteriorFloor |  | MAT-CC05 8 HW CONCRETE
ExtSlabCarpet 4in ClimateZone 1-8 |  | ClimateZone 1-8 | ExteriorFloor |  | MAT-CC05 4 HW CONCRETE | CP02 CARPET PAD
ExtSlabCarpet 8in ClimateZone 1-8 |  | ClimateZone 1-8 | ExteriorFloor |  | MAT-CC05 8 HW CONCRETE | CP02 CARPET PAD
Interior Ceiling |  | ClimateZone 1-8 | InteriorRoof |  | M11 100mm lightweight concrete | F05 Ceiling air space resistance | F16 Acoustic tile
Interior Door |  | ClimateZone 1-8 | InteriorDoor |  | G05 25mm wood
Interior Floor |  | ClimateZone 1-8 | InteriorFloor |  | F16 Acoustic tile | F05 Ceiling air space resistance | M11 100mm lightweight concrete
Interior Partition |  | ClimateZone 1-8 | InteriorPartition |  | G05 25mm wood
Interior Wall |  | ClimateZone 1-8 | InteriorWall |  | G01a 19mm gypsum board | F04 Wall air space resistance | G01a 19mm gypsum board
Interior Window |  | ClimateZone 1-8 | InteriorWindow |  | Clear 3mm

## Materials
Materials |  | Opaque Material Properties | [8 empty] | Simple Glazing Material Properties |  |  | Detailed Glazing Material Properties
Name | Material Type | Thickness (in) | Conductivity (Btu*in/hr*ft^2*F) | Resistance (hr*ft^2*F/Btu) | Density (lb/ft^3) | Specific Heat (Btu/lbm*F) | Thermal Absorptance | Solar Absorptance | Visible Absorptance | Gas Type | U-Factor (Btu/hr*ft^2*F) | Solar Heat Gain Coefficient | Visible Transmittance | Optical Data Type | Solar Transmittance At Normal Incidence | Front Side Solar Reflectance At Normal Incidence | Back Side Solar Relectance At Normal Incidence | Visible Transmittance At Normal Incidence | Front Side Visible Reflectance At Normal Incidence | Back Side Visible Relectance At Normal Incidence | Infrared Transmittance At Normal Incidence | Front Side Infrared Hemispherical Emissivity | Back Side Infrared Hemispherical Emissivity | Dirt Correction Factor For Solar And Visible Transmittance | Solar Diffusing
1/2IN Gypsum | StandardOpaqueMaterial | 0.5 | 1.1094 | 0.90142 | 48.9997 | 0.19824 | 0.9 | 0.92 | 0.92
1IN Stucco | StandardOpaqueMaterial | 0.99606 | 4.7966 | 0.20848 | 115.9912 | 0.19991 | 0.9 | 0.92 | 0.92
8IN Concrete HW | StandardOpaqueMaterial | 8.0039 | 11.9921 | 0.083388 | 140.0259 | 0.19991 | 0.9 | 0.65 | 0.65
8IN CONCRETE HW RefBldg | StandardOpaqueMaterial | 8 | 9.0898 | 0.11001 | 139.8386 | 0.19987 | 0.9 | 0.7 | 0.7
Air 13mm | AirGap | 0.5 | [7 empty] | Air
AtticFloor Insulation | StandardOpaqueMaterial | 9.3661 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-1.76 | StandardOpaqueMaterial | 2.6224 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-2.38 | StandardOpaqueMaterial | 3.8162 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-2.45 | StandardOpaqueMaterial | 3.9437 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-2.67 | StandardOpaqueMaterial | 4.3727 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-2.75 | StandardOpaqueMaterial | 4.5336 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-2.99 | StandardOpaqueMaterial | 4.9835 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.04 | StandardOpaqueMaterial | 5.0827 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.32 | StandardOpaqueMaterial | 5.7407 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.45 | StandardOpaqueMaterial | 5.9921 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.59 | StandardOpaqueMaterial | 6.264 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.67 | StandardOpaqueMaterial | 6.3031 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.83 | StandardOpaqueMaterial | 6.6109 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.91 | StandardOpaqueMaterial | 6.8803 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-4.40 | StandardOpaqueMaterial | 7.7188 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-5.18 | StandardOpaqueMaterial | 11.9138 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-5.68 | StandardOpaqueMaterial | 10.2901 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-6.52 | StandardOpaqueMaterial | 11.9138 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Res Insulation-2.05 | StandardOpaqueMaterial | 3.1755 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Res Insulation-2.37 | StandardOpaqueMaterial | 3.8007 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Res Insulation-2.93 | StandardOpaqueMaterial | 4.8875 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Clear 3mm | StandardGlazing | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.837 | 0.075 | 0.075 | 0.898 | 0.081 | 0.081 | 0 | 0.84 | 0.84 | 1 | FALSE
CP02 CARPET PAD | MasslessOpaqueMaterial |  | 6.2401 | 0.16025 | 0.0437 | 0.00019108 | 0.9 | 0.7 | 0.8
F04 Wall air space resistance | AirGap |  | 46.2231 | 0.021634
F05 Ceiling air space resistance | AirGap |  | 38.5193 | 0.025961
F08 Metal surface | StandardOpaqueMaterial | 0.031496 | 313.9476 | 0.0031852 | 488.4364 | 0.11942 | 0.9 | 0.7 | 0.7
F16 Acoustic tile | StandardOpaqueMaterial | 0.75197 | 0.41601 | 2.4038 | 22.9735 | 0.14092 | 0.9 | 0.7 | 0.7
Fixed Window 2.62/0.30/0.21 | SimpleGlazing | [9 empty] | 0.45998 | 0.3 | 0.21
Fixed Window 2.67/0.30/0.21 | SimpleGlazing | [9 empty] | 0.46998 | 0.49 | 0.38
Fixed Window 2.96/0.39/0.31 | SimpleGlazing | [9 empty] | 0.51998 | 0.39 | 0.31
Fixed Window 2.96/0.49/0.41 | SimpleGlazing | [9 empty] | 0.51998 | 0.49 | 0.41
Fixed Window 2.96/0.62/0.54 | SimpleGlazing | [9 empty] | 0.51998 | 0.615 | 0.54
Fixed Window 3.24/0.25/0.16 | SimpleGlazing | [9 empty] | 0.56997 | 0.25 | 0.16
Fixed Window 3.24/0.39/0.31 | SimpleGlazing | [9 empty] | 0.56997 | 0.39 | 0.31
Fixed Window 3.24/0.49/0.41 | SimpleGlazing | [9 empty] | 0.56997 | 0.49 | 0.41
Fixed Window 3.35/0.36/0.27 | SimpleGlazing | [9 empty] | 0.58997 | 0.36 | 0.27
Fixed Window 3.35/0.39/0.31 | SimpleGlazing | [9 empty] | 0.58997 | 0.39 | 0.31
Fixed Window 3.53/0.41/0.32 | SimpleGlazing | [9 empty] | 0.61997 | 0.41 | 0.32
Fixed Window 3.81/0.39/0.27 | SimpleGlazing | [9 empty] | 0.51998 | 0.39 | 0.27
Fixed Window 3.81/0.49/0.38 | SimpleGlazing | [9 empty] | 0.51998 | 0.49 | 0.38
Fixed Window 4.09/0.26/0.13 | SimpleGlazing | [9 empty] | 0.71997 | 0.25 | 0.13
Fixed Window 4.09/0.36/0.23 | SimpleGlazing | [9 empty] | 0.71997 | 0.36 | 0.23
Fixed Window 4.09/0.39/0.25 | SimpleGlazing | [9 empty] | 0.71997 | 0.39 | 0.25
Fixed Window 5.84/0.25/0.11 | SimpleGlazing | [9 empty] | 1.0285 | 0.25 | 0.11
Fixed Window 5.84/0.39/0.22 | SimpleGlazing | [9 empty] | 1.0285 | 0.39 | 0.22
Fixed Window 5.84/0.44/0.27 | SimpleGlazing | [9 empty] | 1.0285 | 0.44 | 0.27
Fixed Window 5.84/0.54/0.38 | SimpleGlazing | [9 empty] | 1.0285 | 0.54 | 0.38
Fixed Window 5.84/0.61/0.47 | SimpleGlazing | [9 empty] | 1.0285 | 0.61 | 0.47
Fixed Window 5.84/0.70/0.60 | SimpleGlazing | [9 empty] | 1.0285 | 0.7 | 0.6
G01a 19mm gypsum board | StandardOpaqueMaterial | 0.74803 | 1.1094 | 0.90142 | 49.9424 | 0.26034 | 0.9 | 0.7 | 0.7
G05 25mm wood | StandardOpaqueMaterial | 1 | 1.04 | 0.96152 | 37.9562 | 0.38932 | 0.9 | 0.7 | 0.7
I01 25mm insulation board | StandardOpaqueMaterial | 1 | 0.208 | 4.8076 | 2.6844 | 0.289 | 0.9 | 0.7 | 0.7
I02 50mm insulation board | StandardOpaqueMaterial | 2 | 0.208 | 4.8076 | 2.6844 | 0.289 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-1.76 | StandardOpaqueMaterial | 2.9126 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-1.98 | StandardOpaqueMaterial | 3.3325 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.00 | StandardOpaqueMaterial | 3.3759 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.04 | StandardOpaqueMaterial | 3.4657 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.07 | StandardOpaqueMaterial | 3.5122 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.37 | StandardOpaqueMaterial | 4.0909 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.38 | StandardOpaqueMaterial | 4.1064 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.44 | StandardOpaqueMaterial | 4.2339 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.50 | StandardOpaqueMaterial | 4.3392 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.67 | StandardOpaqueMaterial | 4.6629 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.75 | StandardOpaqueMaterial | 4.8237 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.79 | StandardOpaqueMaterial | 4.908 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.85 | StandardOpaqueMaterial | 5.0133 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.93 | StandardOpaqueMaterial | 5.1777 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.99 | StandardOpaqueMaterial | 5.2736 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.03 | StandardOpaqueMaterial | 5.3729 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.38 | StandardOpaqueMaterial | 6.0309 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.51 | StandardOpaqueMaterial | 6.2823 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.65 | StandardOpaqueMaterial | 6.5542 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.66 | StandardOpaqueMaterial | 6.5933 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.72 | StandardOpaqueMaterial | 6.6986 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.83 | StandardOpaqueMaterial | 6.9011 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.97 | StandardOpaqueMaterial | 7.1705 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-4.41 | StandardOpaqueMaterial | 8.009 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-5.75 | StandardOpaqueMaterial | 10.5803 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
M01 100mm brick | StandardOpaqueMaterial | 4 | 6.1708 | 0.16205 | 119.8617 | 0.18869 | 0.9 | 0.7 | 0.7
M11 100mm lightweight concrete | StandardOpaqueMaterial | 4 | 3.6747 | 0.27213 | 79.9078 | 0.20063 | 0.9 | 0.7 | 0.7
M15 200mm heavyweight concrete | StandardOpaqueMaterial | 8 | 13.5203 | 0.073963 | 139.8386 | 0.21496 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.43 | StandardOpaqueMaterial | 0.017196 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.52 | StandardOpaqueMaterial | 0.18781 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.61 | StandardOpaqueMaterial | 0.3601 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.77 | StandardOpaqueMaterial | 0.66572 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.78 | StandardOpaqueMaterial | 0.69855 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.79 | StandardOpaqueMaterial | 0.70529 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.93 | StandardOpaqueMaterial | 0.97671 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.96 | StandardOpaqueMaterial | 1.035 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.99 | StandardOpaqueMaterial | 1.0973 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.01 | StandardOpaqueMaterial | 1.13 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.09 | StandardOpaqueMaterial | 1.2988 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.13 | StandardOpaqueMaterial | 1.3664 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.17 | StandardOpaqueMaterial | 1.4386 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.22 | StandardOpaqueMaterial | 1.5317 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.26 | StandardOpaqueMaterial | 1.6154 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.30 | StandardOpaqueMaterial | 1.6867 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.41 | StandardOpaqueMaterial | 1.9066 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.43 | StandardOpaqueMaterial | 1.9508 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.47 | StandardOpaqueMaterial | 2.0198 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.69 | StandardOpaqueMaterial | 2.4554 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.76 | StandardOpaqueMaterial | 2.5861 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.96 | StandardOpaqueMaterial | 2.9636 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-2.20 | StandardOpaqueMaterial | 3.4355 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-2.23 | StandardOpaqueMaterial | 3.4892 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-2.48 | StandardOpaqueMaterial | 3.9738 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-2.89 | StandardOpaqueMaterial | 4.7583 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-3.75 | StandardOpaqueMaterial | 6.4174 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
MAT-CC05 4 HW CONCRETE | StandardOpaqueMaterial | 4 | 9.0898 | 0.11001 | 139.8386 | 0.19987 | 0.9 | 0.7 | 0.7
MAT-CC05 8 HW CONCRETE | StandardOpaqueMaterial | 8 | 9.0898 | 0.11001 | 139.8386 | 0.19987 | 0.9 | 0.7 | 0.7
MAT-SHEATH | MasslessOpaqueMaterial |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.54 | StandardOpaqueMaterial | 0.60417 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.57 | StandardOpaqueMaterial | 0.66572 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.59 | StandardOpaqueMaterial | 0.69855 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.61 | StandardOpaqueMaterial | 0.73287 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.77 | StandardOpaqueMaterial | 1.035 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.80 | StandardOpaqueMaterial | 1.0973 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.81 | StandardOpaqueMaterial | 1.13 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.90 | StandardOpaqueMaterial | 1.2988 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.91 | StandardOpaqueMaterial | 1.312 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.94 | StandardOpaqueMaterial | 1.3664 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.98 | StandardOpaqueMaterial | 1.4536 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.02 | StandardOpaqueMaterial | 1.5317 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.10 | StandardOpaqueMaterial | 1.6867 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.12 | StandardOpaqueMaterial | 1.724 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.16 | StandardOpaqueMaterial | 1.802 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.22 | StandardOpaqueMaterial | 1.9066 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.24 | StandardOpaqueMaterial | 1.9508 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.37 | StandardOpaqueMaterial | 2.1952 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.57 | StandardOpaqueMaterial | 2.5861 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.72 | StandardOpaqueMaterial | 2.8815 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.79 | StandardOpaqueMaterial | 3.006 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.96 | StandardOpaqueMaterial | 3.3319 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-2.25 | StandardOpaqueMaterial | 3.9074 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-2.52 | StandardOpaqueMaterial | 4.4155 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-2.85 | StandardOpaqueMaterial | 5.0464 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-3.72 | StandardOpaqueMaterial | 6.7387 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Decking | StandardOpaqueMaterial | 0.059055 | 312.0478 | 0.0032046 | 479.4467 | 0.099933 | 0.9 | 0.7 | 0.3
Metal Roofing | StandardOpaqueMaterial | 0.059055 | 312.0478 | 0.0032046 | 479.4467 | 0.099933 | 0.9 | 0.3 | 0.3
Metal Semi-Cond Roof Insulation-1.05 | StandardOpaqueMaterial | 1.6641 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-1.76 | StandardOpaqueMaterial | 3.0272 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-1.81 | StandardOpaqueMaterial | 3.1322 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-1.87 | StandardOpaqueMaterial | 3.2376 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.00 | StandardOpaqueMaterial | 3.4905 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.38 | StandardOpaqueMaterial | 4.2209 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.44 | StandardOpaqueMaterial | 4.3484 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.50 | StandardOpaqueMaterial | 4.4538 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.67 | StandardOpaqueMaterial | 4.7774 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.75 | StandardOpaqueMaterial | 4.9383 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.99 | StandardOpaqueMaterial | 5.3882 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.03 | StandardOpaqueMaterial | 5.4875 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.38 | StandardOpaqueMaterial | 6.1454 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.65 | StandardOpaqueMaterial | 6.6687 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.66 | StandardOpaqueMaterial | 6.7078 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.83 | StandardOpaqueMaterial | 7.0156 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.97 | StandardOpaqueMaterial | 7.2851 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-4.41 | StandardOpaqueMaterial | 8.1235 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-5.75 | StandardOpaqueMaterial | 10.6948 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Siding | StandardOpaqueMaterial | 0.059055 | 311.7289 | 0.0032079 | 479.9998 | 0.097927 | 0.9 | 0.2 | 0.2
Roof Insulation [18] | StandardOpaqueMaterial | 6.6654 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [19] | StandardOpaqueMaterial | 7.3543 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [21] | StandardOpaqueMaterial | 8.2874 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [22] | StandardOpaqueMaterial | 9.2835 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [24] | StandardOpaqueMaterial | 10.2402 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [25] | StandardOpaqueMaterial | 10.3543 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [26] | StandardOpaqueMaterial | 11.5787 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [27] | StandardOpaqueMaterial | 11.6929 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Membrane | StandardOpaqueMaterial | 0.37402 | 1.1094 | 0.90142 | 69.9998 | 0.34872 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.73 | StandardOpaqueMaterial | 0.79836 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.77 | StandardOpaqueMaterial | 0.85991 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.79 | StandardOpaqueMaterial | 0.89947 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.80 | StandardOpaqueMaterial | 0.92705 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.96 | StandardOpaqueMaterial | 1.2292 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.99 | StandardOpaqueMaterial | 1.2914 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.01 | StandardOpaqueMaterial | 1.3242 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.09 | StandardOpaqueMaterial | 1.493 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.10 | StandardOpaqueMaterial | 1.5062 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.13 | StandardOpaqueMaterial | 1.5606 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.17 | StandardOpaqueMaterial | 1.6477 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.22 | StandardOpaqueMaterial | 1.7259 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.30 | StandardOpaqueMaterial | 1.8809 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.36 | StandardOpaqueMaterial | 1.9962 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.41 | StandardOpaqueMaterial | 2.1008 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.42 | StandardOpaqueMaterial | 2.1227 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.76 | StandardOpaqueMaterial | 2.7803 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.92 | StandardOpaqueMaterial | 3.0757 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.98 | StandardOpaqueMaterial | 3.2002 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-2.10 | StandardOpaqueMaterial | 3.4274 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-2.15 | StandardOpaqueMaterial | 3.5261 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-2.44 | StandardOpaqueMaterial | 4.1015 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-2.71 | StandardOpaqueMaterial | 4.6097 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-2.75 | StandardOpaqueMaterial | 4.6914 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-3.04 | StandardOpaqueMaterial | 5.2406 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-3.21 | StandardOpaqueMaterial | 5.5601 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-3.91 | StandardOpaqueMaterial | 6.9328 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Theoretical Glass [167] | StandardGlazing | 0.11811 | 14.6109 | 0.068442 | [9 empty] | SpectralAverage | 0.2374 | 0.7126 | 0.7126 | 0.2512 | 0.6988 | 0.6988 | 0 | 0.985 | 0.985 | 1 | FALSE
Theoretical Glass [197] | StandardGlazing | 0.11811 | 0.28774 | 3.4754 | [9 empty] | SpectralAverage | 0.2349 | 0.7151 | 0.7151 | 0.2512 | 0.6988 | 0.6988 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [202] | StandardGlazing | 0.11811 | 0.13312 | 7.5119 | [9 empty] | SpectralAverage | 0.2325 | 0.7175 | 0.7175 | 0.3192 | 0.6308 | 0.6308 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [207] | StandardGlazing | 0.11811 | 0.092215 | 10.8442 | [9 empty] | SpectralAverage | 0.3311 | 0.6189 | 0.6189 | 0.44 | 0.51 | 0.51 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [216] | StandardGlazing | 0.11811 | 0.092215 | 10.8442 | [9 empty] | SpectralAverage | 0.3801 | 0.5699 | 0.5699 | 0.5079 | 0.4421 | 0.4421 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [221] | StandardGlazing | 0.11811 | 0.061708 | 16.2054 | [9 empty] | SpectralAverage | 0.4296 | 0.5204 | 0.5204 | 0.4503 | 0.4997 | 0.4997 | 0 | 0.9 | 0.9 | 1 | FALSE
Wall Insulation [31] | StandardOpaqueMaterial | 1.3268 | 0.29953 | 3.3386 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [32] | StandardOpaqueMaterial | 3.5315 | 0.31201 | 3.2051 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [33] | StandardOpaqueMaterial | 3.0748 | 0.31201 | 3.2051 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [34] | StandardOpaqueMaterial | 4.3465 | 0.31201 | 3.2051 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [35] | StandardOpaqueMaterial | 1.7795 | 0.29953 | 3.3386 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [36] | StandardOpaqueMaterial | 2.2283 | 0.29953 | 3.3386 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [37] | StandardOpaqueMaterial | 2.6811 | 0.29953 | 3.3386 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [38] | StandardOpaqueMaterial | 5.4961 | 0.31201 | 3.2051 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [39] | StandardOpaqueMaterial | 4.6614 | 0.31201 | 3.2051 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [40] | StandardOpaqueMaterial | 3.126 | 0.29953 | 3.3386 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [41] | StandardOpaqueMaterial | 5.5315 | 0.31201 | 3.2051 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [42] | StandardOpaqueMaterial | 3.5984 | 0.29953 | 3.3386 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [43] | StandardOpaqueMaterial | 6.2323 | 0.31201 | 3.2051 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [44] | StandardOpaqueMaterial | 4.3465 | 0.29953 | 3.3386 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [46] | StandardOpaqueMaterial | 6.4331 | 0.29953 | 3.3386 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wood Frame NonRes Wall Insulation-0.73 | StandardOpaqueMaterial | 0.79836 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-0.80 | StandardOpaqueMaterial | 0.92705 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.10 | StandardOpaqueMaterial | 1.5062 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.17 | StandardOpaqueMaterial | 1.6477 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.36 | StandardOpaqueMaterial | 1.9962 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.76 | StandardOpaqueMaterial | 2.7803 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.92 | StandardOpaqueMaterial | 3.0757 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.98 | StandardOpaqueMaterial | 3.2002 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-2.15 | StandardOpaqueMaterial | 3.5261 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-2.44 | StandardOpaqueMaterial | 4.1015 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-2.71 | StandardOpaqueMaterial | 4.6097 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-3.04 | StandardOpaqueMaterial | 5.2406 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-3.45 | StandardOpaqueMaterial | 6.0446 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-3.91 | StandardOpaqueMaterial | 6.9328 | 0.33974 | 2.9434 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Siding | StandardOpaqueMaterial | 0.3937 | 0.76268 | 1.3112 | 33.9995 | 0.289 | 0.9 | 0.78 | 0.78

## Lookups
Intended Surface Type | Standards Construction Type
AtticFloor | Mass | Building Type | Space Type | Lighting Standards | Ventilation Standards
AtticWall | SteelFramed |  |  | ASHRAE 90.1-1999 | ASHRAE 62.1-1999
AtticRoof | WoodFramed |  |  | ASHRAE 90.1-2001 | ASHRAE 62.1-2004
DemisingFloor | IEAD Metal |  |  | ASHRAE 90.1-2004 | ASHRAE 62.1-2007
DemisingWall | View |  |  | ASHRAE 90.1-2007 | GGHC v2.2
DemisingRoof | Daylight |  |  | ASHRAE 189.1-2009 | AIA 2001
ExteriorFloor | Swinging
ExteriorWall | NonSwinging
ExteriorRoof | Heated
ExteriorWindow | Unheated
ExteriorDoor | RollUp
GlassDoor | Sliding
GroundContactFloor
GroundContactWall
GroundContactRoof
InteriorFloor
InteriorWall
InteriorCeiling
InteriorPartition
InteriorWindow
InteriorDoor
OverheadDoor
Skylight
TubularDaylightDome
TubularDaylightDiffuser