## Sheet1
| Water Heating (W/person) | Water
|  | Heating | m2/person | People | W/m2 | Btu/h/ft^2 | Watts/ft^2 | kW/ft^2 | kW/m2 | L/s/ft^2 | L/s/m2 | m3/s/m2 | gal (US)/min/ft^2 | gal/hr/ft^2
|  | (Btuh/prsn) |  | /1000 SF | [6 empty] | 0 | 0
- undefined - | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dwelling Unit(s) | 499.9792 | 1706 | 59.9374 | 1.55 | 8.3417 | 2.6443 | 0.77497 | 0.00077497 | 0.0083417 | 4.1657e-06 | 4.4839e-05 | 4.4839e-08 | 6.6027e-05 | 0.0039616
Atrium - H < 13m | 0 | 0 | 10.0003 | 9.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | w/person | btu/h/person | m2/person | ft^2/person | person/ft^2 | *1000
Atrium - H > 13m | 0 | 0 | 10.0003 | 9.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 102.3646 | 5 | 53.8248 | 0.018579 | 18.5788
Audience - auditorium | 29.8932 | 102 | 5.0002 | 18.58 | 5.9785 | 1.8952 | 0.55541 | 0.00055541 | 0.0059785 | 2.9855e-06 | 3.2136e-05 | 3.2136e-08 | 4.7322e-05 | 0.0028393
Audience - performance arts | 29.8932 | 102 | 7.4982 | 12.39 | 3.9867 | 1.2638 | 0.37038 | 0.00037038 | 0.0039867 | 1.9909e-06 | 2.143e-05 | 2.143e-08 | 3.1556e-05 | 0.0018934 |  | 1.9018
Audience - motion picture | 29.8932 | 102 | 5.0002 | 18.58 | 5.9785 | 1.8952 | 0.55541 | 0.00055541 | 0.0059785 | 2.9855e-06 | 3.2136e-05 | 3.2136e-08 | 4.7322e-05 | 0.0028393 |  | 1.9018
Classroom/lecture/training | 65.0618 | 222 | 7.4982 | 12.39 | 8.677 | 2.7506 | 0.80611 | 0.00080611 | 0.008677 | 4.3331e-06 | 4.6641e-05 | 4.6641e-08 | 6.8681e-05 | 0.0041209
Conf./meet./multi-purpose | 45.1329 | 154 | 5.0002 | 18.58 | 9.0263 | 2.8613 | 0.83857 | 0.00083857 | 0.0090263 | 4.5076e-06 | 4.8519e-05 | 4.8519e-08 | 7.1446e-05 | 0.0042868
Corr. >= 2.4m wide | 0 | 0 | 99.8957 | 0.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Corr. < 2.4m wide | 0 | 0 | 99.8957 | 0.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dining - bar lounge/leisure | 89.9728 | 307 | 10.0003 | 9.29 | 8.997 | 2.852 | 0.83584 | 0.00083584 | 0.008997 | 4.4929e-06 | 4.8362e-05 | 4.8362e-08 | 7.1214e-05 | 0.0042729
Dining - family | 119.8661 | 409 | 10.0003 | 9.29 | 11.9862 | 3.7996 | 1.1136 | 0.0011136 | 0.011986 | 5.9857e-06 | 6.443e-05 | 6.443e-08 | 9.4875e-05 | 0.0056925
Dining - other | 119.8661 | 409 | 10.0003 | 9.29 | 11.9862 | 3.7996 | 1.1136 | 0.0011136 | 0.011986 | 5.9857e-06 | 6.443e-05 | 6.443e-08 | 9.4875e-05 | 0.0056925
Dress./fitt. - performance arts | 39.8577 | 136 | 29.9687 | 3.1 | 1.33 | 0.4216 | 0.12356 | 0.00012356 | 0.00133 | 6.6416e-07 | 7.149e-06 | 7.149e-09 | 1.0527e-05 | 0.00063163
Electrical/Mechanical | 0 | 0 | 201.963 | 0.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Food preparation | 119.8661 | 409 | 19.9791 | 4.65 | 5.9996 | 1.9019 | 0.55738 | 0.00055738 | 0.0059996 | 2.9961e-06 | 3.2249e-05 | 3.2249e-08 | 4.7489e-05 | 0.0028493
Lab - classrooms | 179.9456 | 614 | 19.9791 | 4.65 | 9.0067 | 2.8551 | 0.83674 | 0.00083674 | 0.0090067 | 4.4978e-06 | 4.8414e-05 | 4.8414e-08 | 7.1291e-05 | 0.0042775
Lab - research | 179.9456 | 614 | 19.9791 | 4.65 | 9.0067 | 2.8551 | 0.83674 | 0.00083674 | 0.0090067 | 4.4978e-06 | 4.8414e-05 | 4.8414e-08 | 7.1291e-05 | 0.0042775
Lobby - elevator | 0 | 0 | 10.0003 | 9.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lobby - performance arts | 0 | 0 | 10.0003 | 9.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lobby - motion picture | 0 | 0 | 10.0003 | 9.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lobby - other | 0 | 0 | 10.0003 | 9.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locker room | 0 | 0 | 10.0003 | 9.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lounge/recreation | 60.0796 | 205 | 10.0003 | 9.29 | 6.0078 | 1.9044 | 0.55814 | 0.00055814 | 0.0060078 | 3.0002e-06 | 3.2294e-05 | 3.2294e-08 | 4.7554e-05 | 0.0028532
Office - enclosed | 89.9728 | 307 | 19.9791 | 4.65 | 4.5033 | 1.4276 | 0.41837 | 0.00041837 | 0.0045033 | 2.2489e-06 | 2.4207e-05 | 2.4207e-08 | 3.5646e-05 | 0.0021387
Office - open plan | 89.9728 | 307 | 19.9791 | 4.65 | 4.5033 | 1.4276 | 0.41837 | 0.00041837 | 0.0045033 | 2.2489e-06 | 2.4207e-05 | 2.4207e-08 | 3.5646e-05 | 0.0021387
Sales area | 39.8577 | 136 | 29.9687 | 3.1 | 1.33 | 0.4216 | 0.12356 | 0.00012356 | 0.00133 | 6.6416e-07 | 7.149e-06 | 7.149e-09 | 1.0527e-05 | 0.00063163
Stairway | 0 | 0 | 201.963 | 0.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Storage area | 300.1048 | 1024 | 99.8957 | 0.93 | 3.0042 | 0.95232 | 0.2791 | 0.0002791 | 0.0030042 | 1.5002e-06 | 1.6148e-05 | 1.6148e-08 | 2.3779e-05 | 0.0014268
Washroom | 0 | 0 | 29.9687 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Workshop | 89.9728 | 307 | 29.9687 | 3.1 | 3.0022 | 0.9517 | 0.27891 | 0.00027891 | 0.0030022 | 1.4993e-06 | 1.6138e-05 | 1.6138e-08 | 2.3764e-05 | 0.0014258
Automotive - repair | 89.9728 | 307 | 19.9791 | 4.65 | 4.5033 | 1.4276 | 0.41837 | 0.00041837 | 0.0045033 | 2.2489e-06 | 2.4207e-05 | 2.4207e-08 | 3.5646e-05 | 0.0021387
Bank - banking and offices | 60.0796 | 205 | 24.9739 | 3.72 | 2.4057 | 0.7626 | 0.2235 | 0.0002235 | 0.0024057 | 1.2014e-06 | 1.2931e-05 | 1.2931e-08 | 1.9042e-05 | 0.0011425
Convention centre - audience | 29.8932 | 102 | 5.0002 | 18.58 | 5.9785 | 1.8952 | 0.55541 | 0.00055541 | 0.0059785 | 2.9855e-06 | 3.2136e-05 | 3.2136e-08 | 4.7322e-05 | 0.0028393
Convention centre - exhibit | 29.8932 | 102 | 5.0002 | 18.58 | 5.9785 | 1.8952 | 0.55541 | 0.00055541 | 0.0059785 | 2.9855e-06 | 3.2136e-05 | 3.2136e-08 | 4.7322e-05 | 0.0028393
Courthouse - courtroom | 29.8932 | 102 | 5.0002 | 18.58 | 5.9785 | 1.8952 | 0.55541 | 0.00055541 | 0.0059785 | 2.9855e-06 | 3.2136e-05 | 3.2136e-08 | 4.7322e-05 | 0.0028393
Courthouse - cell | 325.0158 | 1109 | 24.9739 | 3.72 | 13.0142 | 4.1255 | 1.2091 | 0.0012091 | 0.013014 | 6.499e-06 | 6.9955e-05 | 6.9955e-08 | 0.00010301 | 0.0061807
Courthouse - chambers | 89.9728 | 307 | 19.9791 | 4.65 | 4.5033 | 1.4276 | 0.41837 | 0.00041837 | 0.0045033 | 2.2489e-06 | 2.4207e-05 | 2.4207e-08 | 3.5646e-05 | 0.0021387
Penitentiary - audience | 29.8932 | 102 | 5.0002 | 18.58 | 5.9785 | 1.8952 | 0.55541 | 0.00055541 | 0.0059785 | 2.9855e-06 | 3.2136e-05 | 3.2136e-08 | 4.7322e-05 | 0.0028393
Penitentiary - classroom | 65.0618 | 222 | 7.4982 | 12.39 | 8.677 | 2.7506 | 0.80611 | 0.00080611 | 0.008677 | 4.3331e-06 | 4.6641e-05 | 4.6641e-08 | 6.8681e-05 | 0.0041209
Penitentiary - dining | 119.8661 | 409 | 10.0003 | 9.29 | 11.9862 | 3.7996 | 1.1136 | 0.0011136 | 0.011986 | 5.9857e-06 | 6.443e-05 | 6.443e-08 | 9.4875e-05 | 0.0056925
Dormitory - living quarters | 499.9792 | 1706 | 24.9739 | 3.72 | 20.0201 | 6.3463 | 1.8599 | 0.0018599 | 0.02002 | 9.9976e-06 | 0.00010761 | 1.0761e-07 | 0.00015847 | 0.009508
Fire station - engine room | 325.0158 | 1109 | 24.9739 | 3.72 | 13.0142 | 4.1255 | 1.2091 | 0.0012091 | 0.013014 | 6.499e-06 | 6.9955e-05 | 6.9955e-08 | 0.00010301 | 0.0061807
Fire station - quarters | 499.9792 | 1706 | 24.9739 | 3.72 | 20.0201 | 6.3463 | 1.8599 | 0.0018599 | 0.02002 | 9.9976e-06 | 0.00010761 | 1.0761e-07 | 0.00015847 | 0.009508
Gym - fitness | 89.9728 | 307 | 5.0002 | 18.58 | 17.994 | 5.7041 | 1.6717 | 0.0016717 | 0.017994 | 8.9858e-06 | 9.6723e-05 | 9.6723e-08 | 0.00014243 | 0.0085457
Gym - audience | 29.8932 | 102 | 5.0002 | 18.58 | 5.9785 | 1.8952 | 0.55541 | 0.00055541 | 0.0059785 | 2.9855e-06 | 3.2136e-05 | 3.2136e-08 | 4.7322e-05 | 0.0028393
Gym - play | 89.9728 | 307 | 5.0002 | 18.58 | 17.994 | 5.7041 | 1.6717 | 0.0016717 | 0.017994 | 8.9858e-06 | 9.6723e-05 | 9.6723e-08 | 0.00014243 | 0.0085457
Hospital corr. >= 2.4m | 0 | 0 | 99.8957 | 0.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital corr. < 2.4m | 0 | 0 | 99.8957 | 0.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital - emergency | 179.9456 | 614 | 19.9791 | 4.65 | 9.0067 | 2.8551 | 0.83674 | 0.00083674 | 0.0090067 | 4.4978e-06 | 4.8414e-05 | 4.8414e-08 | 7.1291e-05 | 0.0042775
Hospital - exam | 89.9728 | 307 | 19.9791 | 4.65 | 4.5033 | 1.4276 | 0.41837 | 0.00041837 | 0.0045033 | 2.2489e-06 | 2.4207e-05 | 2.4207e-08 | 3.5646e-05 | 0.0021387
Hospital - laundry/washing | 60.0796 | 205 | 19.9791 | 4.65 | 3.0071 | 0.95325 | 0.27937 | 0.00027937 | 0.0030071 | 1.5017e-06 | 1.6164e-05 | 1.6164e-08 | 2.3802e-05 | 0.0014281
Hospital - lounge/recreation | 60.0796 | 205 | 10.0003 | 9.29 | 6.0078 | 1.9044 | 0.55814 | 0.00055814 | 0.0060078 | 3.0002e-06 | 3.2294e-05 | 3.2294e-08 | 4.7554e-05 | 0.0028532
Hospital - medical supply | 0 | 0 | 19.9791 | 4.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital - nursery | 89.9728 | 307 | 19.9791 | 4.65 | 4.5033 | 1.4276 | 0.41837 | 0.00041837 | 0.0045033 | 2.2489e-06 | 2.4207e-05 | 2.4207e-08 | 3.5646e-05 | 0.0021387
Hospital - nurses' station | 45.1329 | 154 | 19.9791 | 4.65 | 2.259 | 0.7161 | 0.20987 | 0.00020987 | 0.002259 | 1.1281e-06 | 1.2143e-05 | 1.2143e-08 | 1.7881e-05 | 0.0010728
Hospital - operating room | 300.1048 | 1024 | 19.9791 | 4.65 | 15.0209 | 4.7616 | 1.3955 | 0.0013955 | 0.015021 | 7.5011e-06 | 8.0742e-05 | 8.0742e-08 | 0.0001189 | 0.0071338
Hospital - patient room | 89.9728 | 307 | 19.9791 | 4.65 | 4.5033 | 1.4276 | 0.41837 | 0.00041837 | 0.0045033 | 2.2489e-06 | 2.4207e-05 | 2.4207e-08 | 3.5646e-05 | 0.0021387
Hospital - pharmacy | 45.1329 | 154 | 19.9791 | 4.65 | 2.259 | 0.7161 | 0.20987 | 0.00020987 | 0.002259 | 1.1281e-06 | 1.2143e-05 | 1.2143e-08 | 1.7881e-05 | 0.0010728
Hospital - physical therapy | 45.1329 | 154 | 19.9791 | 4.65 | 2.259 | 0.7161 | 0.20987 | 0.00020987 | 0.002259 | 1.1281e-06 | 1.2143e-05 | 1.2143e-08 | 1.7881e-05 | 0.0010728
Hospital - radiology/imaging | 89.9728 | 307 | 19.9791 | 4.65 | 4.5033 | 1.4276 | 0.41837 | 0.00041837 | 0.0045033 | 2.2489e-06 | 2.4207e-05 | 2.4207e-08 | 3.5646e-05 | 0.0021387
Hospital - recovery | 179.9456 | 614 | 19.9791 | 4.65 | 9.0067 | 2.8551 | 0.83674 | 0.00083674 | 0.0090067 | 4.4978e-06 | 4.8414e-05 | 4.8414e-08 | 7.1291e-05 | 0.0042775
Hotel/Motel - dining | 114.8839 | 392 | 10.0003 | 9.29 | 11.488 | 3.6417 | 1.0673 | 0.0010673 | 0.011488 | 5.7369e-06 | 6.1752e-05 | 6.1752e-08 | 9.0932e-05 | 0.0054559
Hotel/Motel - rooms | 599.9165 | 2047 | 24.9739 | 3.72 | 24.0217 | 7.6148 | 2.2317 | 0.0022317 | 0.024022 | 1.1996e-05 | 0.00012912 | 1.2912e-07 | 0.00019014 | 0.011408
Hotel/Motel - lobby | 29.8932 | 102 | 10.0003 | 9.29 | 2.9892 | 0.94758 | 0.27771 | 0.00027771 | 0.0029892 | 1.4928e-06 | 1.6068e-05 | 1.6068e-08 | 2.3661e-05 | 0.0014196
Hway lodging - dining | 114.8839 | 392 | 10.0003 | 9.29 | 11.488 | 3.6417 | 1.0673 | 0.0010673 | 0.011488 | 5.7369e-06 | 6.1752e-05 | 6.1752e-08 | 9.0932e-05 | 0.0054559
Hway lodging - rooms | 599.9165 | 2047 | 24.9739 | 3.72 | 24.0217 | 7.6148 | 2.2317 | 0.0022317 | 0.024022 | 1.1996e-05 | 0.00012912 | 1.2912e-07 | 0.00019014 | 0.011408
Library - cataloging | 89.9728 | 307 | 19.9791 | 4.65 | 4.5033 | 1.4276 | 0.41837 | 0.00041837 | 0.0045033 | 2.2489e-06 | 2.4207e-05 | 2.4207e-08 | 3.5646e-05 | 0.0021387
Library - reading | 89.9728 | 307 | 19.9791 | 4.65 | 4.5033 | 1.4276 | 0.41837 | 0.00041837 | 0.0045033 | 2.2489e-06 | 2.4207e-05 | 2.4207e-08 | 3.5646e-05 | 0.0021387
Library - stacks | 89.9728 | 307 | 19.9791 | 4.65 | 4.5033 | 1.4276 | 0.41837 | 0.00041837 | 0.0045033 | 2.2489e-06 | 2.4207e-05 | 2.4207e-08 | 3.5646e-05 | 0.0021387
Mfg - corr. >= 2.4m | 0 | 0 | 99.8957 | 0.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mfg - corr. < 2.4m | 0 | 0 | 99.8957 | 0.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mfg - detailed | 89.9728 | 307 | 29.9687 | 3.1 | 3.0022 | 0.9517 | 0.27891 | 0.00027891 | 0.0030022 | 1.4993e-06 | 1.6138e-05 | 1.6138e-08 | 2.3764e-05 | 0.0014258
Mfg - equipment | 89.9728 | 307 | 29.9687 | 3.1 | 3.0022 | 0.9517 | 0.27891 | 0.00027891 | 0.0030022 | 1.4993e-06 | 1.6138e-05 | 1.6138e-08 | 2.3764e-05 | 0.0014258
Mfg - bay H > 15m | 89.9728 | 307 | 29.9687 | 3.1 | 3.0022 | 0.9517 | 0.27891 | 0.00027891 | 0.0030022 | 1.4993e-06 | 1.6138e-05 | 1.6138e-08 | 2.3764e-05 | 0.0014258
Mfg - 7.5 <= bay H <= 15m | 89.9728 | 307 | 29.9687 | 3.1 | 3.0022 | 0.9517 | 0.27891 | 0.00027891 | 0.0030022 | 1.4993e-06 | 1.6138e-05 | 1.6138e-08 | 2.3764e-05 | 0.0014258
Mfg - bay H < 7.5m | 89.9728 | 307 | 29.9687 | 3.1 | 3.0022 | 0.9517 | 0.27891 | 0.00027891 | 0.0030022 | 1.4993e-06 | 1.6138e-05 | 1.6138e-08 | 2.3764e-05 | 0.0014258
Museum - exhibition | 60.0796 | 205 | 5.0002 | 18.58 | 12.0155 | 3.8089 | 1.1163 | 0.0011163 | 0.012016 | 6.0003e-06 | 6.4587e-05 | 6.4587e-08 | 9.5107e-05 | 0.0057064
Museum - restoration | 50.1152 | 171 | 19.9791 | 4.65 | 2.5084 | 0.79515 | 0.23303 | 0.00023303 | 0.0025084 | 1.2526e-06 | 1.3483e-05 | 1.3483e-08 | 1.9855e-05 | 0.0011913
Parking garage | 0 | 0 | 1032.2556 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Post office sorting | 89.9728 | 307 | 19.9791 | 4.65 | 4.5033 | 1.4276 | 0.41837 | 0.00041837 | 0.0045033 | 2.2489e-06 | 2.4207e-05 | 2.4207e-08 | 3.5646e-05 | 0.0021387
Religious - audience | 14.9466 | 51 | 5.0002 | 18.58 | 2.9892 | 0.94758 | 0.27771 | 0.00027771 | 0.0029892 | 1.4928e-06 | 1.6068e-05 | 1.6068e-08 | 2.3661e-05 | 0.0014196
Religious - fellowship hall | 45.1329 | 154 | 5.0002 | 18.58 | 9.0263 | 2.8613 | 0.83857 | 0.00083857 | 0.0090263 | 4.5076e-06 | 4.8519e-05 | 4.8519e-08 | 7.1446e-05 | 0.0042868
Religious - pulpit/choir | 14.9466 | 51 | 5.0002 | 18.58 | 2.9892 | 0.94758 | 0.27771 | 0.00027771 | 0.0029892 | 1.4928e-06 | 1.6068e-05 | 1.6068e-08 | 2.3661e-05 | 0.0014196
Retail - dressing/fitting | 39.8577 | 136 | 29.9687 | 3.1 | 1.33 | 0.4216 | 0.12356 | 0.00012356 | 0.00133 | 6.6416e-07 | 7.149e-06 | 7.149e-09 | 1.0527e-05 | 0.00063163
Retail - mall concourse | 29.8932 | 102 | 19.9791 | 4.65 | 1.4962 | 0.4743 | 0.139 | 0.000139 | 0.0014962 | 7.4718e-07 | 8.0427e-06 | 8.0427e-09 | 1.1843e-05 | 0.00071059
Retail - sales | 39.8577 | 136 | 29.9687 | 3.1 | 1.33 | 0.4216 | 0.12356 | 0.00012356 | 0.00133 | 6.6416e-07 | 7.149e-06 | 7.149e-09 | 1.0527e-05 | 0.00063163
Sports arena - audience | 29.8932 | 102 | 5.0002 | 18.58 | 5.9785 | 1.8952 | 0.55541 | 0.00055541 | 0.0059785 | 2.9855e-06 | 3.2136e-05 | 3.2136e-08 | 4.7322e-05 | 0.0028393
Sports arena - court c4 | 89.9728 | 307 | 5.0002 | 18.58 | 17.994 | 5.7041 | 1.6717 | 0.0016717 | 0.017994 | 8.9858e-06 | 9.6723e-05 | 9.6723e-08 | 0.00014243 | 0.0085457
Sports arena - court c3 | 89.9728 | 307 | 5.0002 | 18.58 | 17.994 | 5.7041 | 1.6717 | 0.0016717 | 0.017994 | 8.9858e-06 | 9.6723e-05 | 9.6723e-08 | 0.00014243 | 0.0085457
Sports arena - court c2 | 89.9728 | 307 | 5.0002 | 18.58 | 17.994 | 5.7041 | 1.6717 | 0.0016717 | 0.017994 | 8.9858e-06 | 9.6723e-05 | 9.6723e-08 | 0.00014243 | 0.0085457
Sports arena - court c1 | 89.9728 | 307 | 5.0002 | 18.58 | 17.994 | 5.7041 | 1.6717 | 0.0016717 | 0.017994 | 8.9858e-06 | 9.6723e-05 | 9.6723e-08 | 0.00014243 | 0.0085457
Sports arena - ring | 89.9728 | 307 | 5.0002 | 18.58 | 17.994 | 5.7041 | 1.6717 | 0.0016717 | 0.017994 | 8.9858e-06 | 9.6723e-05 | 9.6723e-08 | 0.00014243 | 0.0085457
Transp. baggage | 65.0618 | 222 | 19.9791 | 4.65 | 3.2565 | 1.0323 | 0.30254 | 0.00030254 | 0.0032565 | 1.6262e-06 | 1.7505e-05 | 1.7505e-08 | 2.5776e-05 | 0.0015466
Transp. concourse | 65.0618 | 222 | 19.9791 | 4.65 | 3.2565 | 1.0323 | 0.30254 | 0.00030254 | 0.0032565 | 1.6262e-06 | 1.7505e-05 | 1.7505e-08 | 2.5776e-05 | 0.0015466
Transp. seating | 65.0618 | 222 | 10.0003 | 9.29 | 6.506 | 2.0624 | 0.60442 | 0.00060442 | 0.006506 | 3.249e-06 | 3.4972e-05 | 3.4972e-08 | 5.1497e-05 | 0.0030898
Transp. counter | 65.0618 | 222 | 10.0003 | 9.29 | 6.506 | 2.0624 | 0.60442 | 0.00060442 | 0.006506 | 3.249e-06 | 3.4972e-05 | 3.4972e-08 | 5.1497e-05 | 0.0030898
Warehouse - fine | 65.0618 | 222 | 49.9478 | 1.86 | 1.3026 | 0.41292 | 0.12101 | 0.00012101 | 0.0013026 | 6.5049e-07 | 7.0018e-06 | 7.0018e-09 | 1.0311e-05 | 0.00061863
Warehouse - med/blk | 65.0618 | 222 | 99.8957 | 0.93 | 0.6513 | 0.20646 | 0.060507 | 6.0507e-05 | 0.0006513 | 3.2524e-07 | 3.5009e-06 | 3.5009e-09 | 5.1553e-06 | 0.00030932
Warehouse - med/blk2 | 65.0618 | 222 | 99.8957 | 0.93 | 0.6513 | 0.20646 | 0.060507 | 6.0507e-05 | 0.0006513 | 3.2524e-07 | 3.5009e-06 | 3.5009e-09 | 5.1553e-06 | 0.00030932
Automotive facility | 90 | 307.0927 | 20 | 4.6452 | 4.5 | 1.4265 | 0.41806 | 0.00041806 | 0.0045 | 2.2472e-06 | 2.4189e-05 | 2.4189e-08 | 3.5619e-05 | 0.0021371
Convention centre | 30 | 102.3642 | 8 | 11.6129 | 3.75 | 1.1887 | 0.34838 | 0.00034838 | 0.00375 | 1.8727e-06 | 2.0157e-05 | 2.0157e-08 | 2.9683e-05 | 0.001781
Courthouse | 60 | 204.7285 | 15 | 6.1935 | 4 | 1.268 | 0.37161 | 0.00037161 | 0.004 | 1.9975e-06 | 2.1501e-05 | 2.1501e-08 | 3.1661e-05 | 0.0018997
Dining bar lounge/leisure | 115 | 392.3963 | 10 | 9.2903 | 11.5 | 3.6455 | 1.0684 | 0.0010684 | 0.0115 | 5.7429e-06 | 6.1816e-05 | 6.1816e-08 | 9.1027e-05 | 0.0054616
Dining cafeteria/fast food | 115 | 392.3963 | 10 | 9.2903 | 11.5 | 3.6455 | 1.0684 | 0.0010684 | 0.0115 | 5.7429e-06 | 6.1816e-05 | 6.1816e-08 | 9.1027e-05 | 0.0054616
Dining family | 115 | 392.3963 | 10 | 9.2903 | 11.5 | 3.6455 | 1.0684 | 0.0010684 | 0.0115 | 5.7429e-06 | 6.1816e-05 | 6.1816e-08 | 9.1027e-05 | 0.0054616
Dormitory | 500 | 1706.0708 | 30 | 3.0968 | 16.6667 | 5.2833 | 1.5484 | 0.0015484 | 0.016667 | 8.323e-06 | 8.9588e-05 | 8.9588e-08 | 0.00013192 | 0.0079154
Exercise centre | 90 | 307.0927 | 10 | 9.2903 | 9 | 2.853 | 0.83612 | 0.00083612 | 0.009 | 4.4944e-06 | 4.8378e-05 | 4.8378e-08 | 7.1238e-05 | 0.0042743
Fire station | 400 | 1364.8567 | 25 | 3.7161 | 16 | 5.072 | 1.4864 | 0.0014864 | 0.016 | 7.9901e-06 | 8.6005e-05 | 8.6005e-08 | 0.00012665 | 0.0075987
Gymnasium | 90 | 307.0927 | 10 | 9.2903 | 9 | 2.853 | 0.83612 | 0.00083612 | 0.009 | 4.4944e-06 | 4.8378e-05 | 4.8378e-08 | 7.1238e-05 | 0.0042743
Health-care clinic | 90 | 307.0927 | 20 | 4.6452 | 4.5 | 1.4265 | 0.41806 | 0.00041806 | 0.0045 | 2.2472e-06 | 2.4189e-05 | 2.4189e-08 | 3.5619e-05 | 0.0021371
Hospital | 90 | 307.0927 | 20 | 4.6452 | 4.5 | 1.4265 | 0.41806 | 0.00041806 | 0.0045 | 2.2472e-06 | 2.4189e-05 | 2.4189e-08 | 3.5619e-05 | 0.0021371
Hotel | 500 | 1706.0708 | 25 | 3.7161 | 20 | 6.34 | 1.8581 | 0.0018581 | 0.02 | 9.9876e-06 | 0.00010751 | 1.0751e-07 | 0.00015831 | 0.0094984
Library | 90 | 307.0927 | 20 | 4.6452 | 4.5 | 1.4265 | 0.41806 | 0.00041806 | 0.0045 | 2.2472e-06 | 2.4189e-05 | 2.4189e-08 | 3.5619e-05 | 0.0021371
Manufacturing facility | 90 | 307.0927 | 30 | 3.0968 | 3 | 0.95099 | 0.27871 | 0.00027871 | 0.003 | 1.4981e-06 | 1.6126e-05 | 1.6126e-08 | 2.3746e-05 | 0.0014248
Motel | 500 | 1706.0708 | 25 | 3.7161 | 20 | 6.34 | 1.8581 | 0.0018581 | 0.02 | 9.9876e-06 | 0.00010751 | 1.0751e-07 | 0.00015831 | 0.0094984
Motion picture theatre | 30 | 102.3642 | 8 | 11.6129 | 3.75 | 1.1887 | 0.34838 | 0.00034838 | 0.00375 | 1.8727e-06 | 2.0157e-05 | 2.0157e-08 | 2.9683e-05 | 0.001781
Multi-unit residential building | 500 | 1706.0708 | 60 | 1.5484 | 8.3333 | 2.6417 | 0.77419 | 0.00077419 | 0.0083333 | 4.1615e-06 | 4.4794e-05 | 4.4794e-08 | 6.5961e-05 | 0.0039577
Museum | 60 | 204.7285 | 20 | 4.6452 | 3 | 0.95099 | 0.27871 | 0.00027871 | 0.003 | 1.4981e-06 | 1.6126e-05 | 1.6126e-08 | 2.3746e-05 | 0.0014248
Office | 90 | 307.0927 | 25 | 3.7161 | 3.6 | 1.1412 | 0.33445 | 0.00033445 | 0.0036 | 1.7978e-06 | 1.9351e-05 | 1.9351e-08 | 2.8495e-05 | 0.0017097
Parking garage | 0 | 0 | 1000 | 0.092903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Penitentiary | 400 | 1364.8567 | 30 | 3.0968 | 13.3333 | 4.2266 | 1.2387 | 0.0012387 | 0.013333 | 6.6584e-06 | 7.1671e-05 | 7.1671e-08 | 0.00010554 | 0.0063323
Performing arts theatre | 30 | 102.3642 | 8 | 11.6129 | 3.75 | 1.1887 | 0.34838 | 0.00034838 | 0.00375 | 1.8727e-06 | 2.0157e-05 | 2.0157e-08 | 2.9683e-05 | 0.001781
Police station | 90 | 307.0927 | 25 | 3.7161 | 3.6 | 1.1412 | 0.33445 | 0.00033445 | 0.0036 | 1.7978e-06 | 1.9351e-05 | 1.9351e-08 | 2.8495e-05 | 0.0017097
Post office | 90 | 307.0927 | 25 | 3.7161 | 3.6 | 1.1412 | 0.33445 | 0.00033445 | 0.0036 | 1.7978e-06 | 1.9351e-05 | 1.9351e-08 | 2.8495e-05 | 0.0017097
Religious building | 15 | 51.1821 | 5 | 18.5806 | 3 | 0.95099 | 0.27871 | 0.00027871 | 0.003 | 1.4981e-06 | 1.6126e-05 | 1.6126e-08 | 2.3746e-05 | 0.0014248
Retail area | 40 | 136.4857 | 30 | 3.0968 | 1.3333 | 0.42266 | 0.12387 | 0.00012387 | 0.0013333 | 6.6584e-07 | 7.1671e-06 | 7.1671e-09 | 1.0554e-05 | 0.00063323
School/university | 60 | 204.7285 | 8 | 11.6129 | 7.5 | 2.3775 | 0.69677 | 0.00069677 | 0.0075 | 3.7454e-06 | 4.0315e-05 | 4.0315e-08 | 5.9365e-05 | 0.0035619
Sports arena | 90 | 307.0927 | 10 | 9.2903 | 9 | 2.853 | 0.83612 | 0.00083612 | 0.009 | 4.4944e-06 | 4.8378e-05 | 4.8378e-08 | 7.1238e-05 | 0.0042743
Town hall | 90 | 307.0927 | 25 | 3.7161 | 3.6 | 1.1412 | 0.33445 | 0.00033445 | 0.0036 | 1.7978e-06 | 1.9351e-05 | 1.9351e-08 | 2.8495e-05 | 0.0017097
Transportation | 65 | 221.7892 | 15 | 6.1935 | 4.3333 | 1.3737 | 0.40258 | 0.00040258 | 0.0043333 | 2.164e-06 | 2.3293e-05 | 2.3293e-08 | 3.43e-05 | 0.002058
Warehouse | 300 | 1023.6425 | 1500 | 0.061935 | 0.2 | 0.0634 | 0.018581 | 1.8581e-05 | 0.0002 | 9.9876e-08 | 1.0751e-06 | 1.0751e-09 | 1.5831e-06 | 9.4984e-05
Workshop | 90 | 307.0927 | 30 | 3.0968 | 3 | 0.95099 | 0.27871 | 0.00027871 | 0.003 | 1.4981e-06 | 1.6126e-05 | 1.6126e-08 | 2.3746e-05 | 0.0014248

## Sheet2
| Water Heating (W/person) | Water
|  | Heating | m2/person | People | W/m2 | Btu/h/ft^2 | Watts/ft^2 | kW/ft^2 | kW/m2 | L/s/ft^2 | L/s/m2 | m3/s/m2 | gal (US)/min/ft^2 | gal/hr/ft^2
|  | (Btuh/prsn) |  | /1000 SF | [6 empty] | 0 | 0
Automotive facility | 90 |  | 20
Convention centre | 30 |  | 8
Courthouse | 60 |  | 15
Dining bar lounge/leisure | 115 |  | 10
Dining cafeteria/fast food | 115 |  | 10
Dining family | 115 |  | 10
Dormitory | 500 |  | 30
Exercise centre | 90 |  | 10
Fire station | 400 |  | 25
Gymnasium | 90 |  | 10
Health-care clinic | 90 |  | 20
Hospital | 90 |  | 20
Hotel | 500 |  | 25
Library | 90 |  | 20
Manufacturing facility | 90 |  | 30
Motel | 500 |  | 25
Motion picture theatre | 30 |  | 8
Multi-unit residential building | 500 |  | 60
Museum | 60 |  | 20
Office | 90 |  | 25
Parking garage | 0 |  | 1000
Penitentiary | 400 |  | 30
Performing arts theatre | 30 |  | 8
Police station | 90 |  | 25
Post office | 90 |  | 25
Religious building | 15 |  | 5
Retail area | 40 |  | 30
School/university | 60 |  | 8
Sports arena | 90 |  | 10
Town hall | 90 |  | 25
Transportation | 65 |  | 15
Warehouse | 300 |  | 1500
Workshop | 90 |  | 30