## Sheet1
Film Coef Worksheet
Air Films. Prescribed R-values for air films shall be as follows:
R-Value Condition
0.17 All exterior surfaces
0.46 All semi-exterior surfaces
0.61 Interior horizontal surfaces, heat flow up
0.92 Interior horizontal surfaces, heat flow down
0.68 Interior vertical surfaces
Simple Glazing
Assembly Max. U (IP) | R value (IP) | R value to Subtract (IP) | Final R Value (IP) | Final U Value (IP) | Final U Value (SI)
1.2 | 0.83333 | 0 | 0.83333 | 1.2
0.75 | 1.3333 | 0 | 1.3333 | 0.75
0.65 | 1.5385 | 0 | 1.5385 | 0.65
0.55 | 1.8182 | 0 | 1.8182 | 0.55
0.45 | 2.2222 | 0 | 2.2222 | 0.45
0.4 | 2.5 | 0 | 2.5 | 0.4
0.35 | 2.8571 | 0 | 2.8571 | 0.35 | [6 empty] | IP to SI conv. factor
0.17611
IEAD Roof |  |  |  | Roof Membrane | Insulation Layer | Metal Decking | NA |  | IEAD Non Res Roof Insulation |  | used for material name
Assembly Max. U (IP) | R value (IP) | R value to Subtract (IP) | Final R Value (IP) | Mat 1 R Value (IP) | Mat 2 R Value (IP) | Mat 3 R Value (IP) | Mat 4 R Value (IP) | R value left (IP) | Insul. Resistance (IP) | Insul Thickness (IP) | R Value (SI)
0.218 | 4.5872 | 0.78 | 3.8072 | 0.33715 | 0 | 0.00018925 | 0 | 3.4698 | 2.9434 | 1.1788 | 0.61107
0.173 | 5.7803 | 0.78 | 5.0003 | 0.33715 | 0 | 0.00018925 | 0 | 4.663 | 2.9434 | 1.5842 | 0.8212
0.119 | 8.4034 | 0.78 | 7.6234 | 0.33715 | 0 | 0.00018925 | 0 | 7.286 | 2.9434 | 2.4754 | 1.2831
0.093 | 10.7527 | 0.78 | 9.9727 | 0.33715 | 0 | 0.00018925 | 0 | 9.6354 | 2.9434 | 3.2735 | 1.6969
0.063 | 15.873 | 0.78 | 15.093 | 0.33715 | 0 | 0.00018925 | 0 | 14.7557 | 2.9434 | 5.0131 | 2.5986
0.048 | 20.8333 | 0.78 | 20.0533 | 0.33715 | 0 | 0.00018925 | 0 | 19.716 | 2.9434 | 6.6983 | 3.4722
Metal Roof |  |  |  | Metal Roofing | Insulation Layer | Metal Decking | NA |  | Metal Semi-Cond Roof Insulation |  | used for material name
Assembly Max. U (IP) | R value (IP) | R value to Subtract (IP) | Final R Value (IP) | Mat 1 R Value (IP) | Mat 2 R Value (IP) | Mat 3 R Value (IP) | Mat 4 R Value (IP) | R value left (IP) | Insul. Resistance (IP) | Insul Thickness (IP) | R Value (SI)
1.28 | 0.78125 | 0.78 | 0.00125 | 0.00018925 | 0 | 0.00018925 | 0 | 0.0008715 | 2.9434 | 0.00029608 | 0.00015348
0.167 | 5.988 | 0.78 | 5.208 | 0.00018925 | 0 | 0.00018925 | 0 | 5.2076 | 2.9434 | 1.7692 | 0.91712
0.097 | 10.3093 | 0.78 | 9.5293 | 0.00018925 | 0 | 0.00018925 | 0 | 9.5289 | 2.9434 | 3.2373 | 1.6781
0.083 | 12.0482 | 0.78 | 11.2682 | 0.00018925 | 0 | 0.00018925 | 0 | 11.2678 | 2.9434 | 3.8281 | 1.9844
0.072 | 13.8889 | 0.78 | 13.1089 | 0.00018925 | 0 | 0.00018925 | 0 | 13.1085 | 2.9434 | 4.4535 | 2.3085
0.065 | 15.3846 | 0.78 | 14.6046 | 0.00018925 | 0 | 0.00018925 | 0 | 14.6042 | 2.9434 | 4.9616 | 2.572
0.055 | 18.1818 | 0.78 | 17.4018 | 0.00018925 | 0 | 0.00018925 | 0 | 17.4014 | 2.9434 | 5.912 | 3.0646
0.049 | 20.4082 | 0.78 | 19.6282 | 0.00018925 | 0 | 0.00018925 | 0 | 19.6278 | 2.9434 | 6.6683 | 3.4567
0.035 | 28.5714 | 0.78 | 27.7914 | 0.00018925 | 0 | 0.00018925 | 0 | 27.7911 | 2.9434 | 9.4417 | 4.8943
Attic Roof |  |  |  | 1/2IN Gypsum | Insulation Layer | 1/2IN Gypsum | NA |  | AtticFloor NonRes Insulation |  | used for material name
Assembly Max. U (IP) | R value (IP) | R value to Subtract (IP) | Final R Value (IP) | Mat 1 R Value (IP) | Mat 2 R Value (IP) | Mat 3 R Value (IP) | Mat 4 R Value (IP) | R value left (IP) | Insul. Resistance (IP) | Insul Thickness (IP) | R Value (SI)
0.081 | 12.3457 | 1.07 | 11.2757 | 0.45071 | 0 | 0.45071 | 0 | 10.3743 | 2.9434 | 3.5246 | 1.827
0.053 | 18.8679 | 1.07 | 17.7979 | 0.45071 | 0 | 0.45071 | 0 | 16.8965 | 2.9434 | 5.7404 | 2.9756
0.034 | 29.4118 | 1.07 | 28.3418 | 0.45071 | 0 | 0.45071 | 0 | 27.4403 | 2.9434 | 9.3226 | 4.8325
0.027 | 37.037 | 1.07 | 35.967 | 0.45071 | 0 | 0.45071 | 0 | 35.0656 | 2.9434 | 11.9132 | 6.1754
0.021 | 47.619 | 1.07 | 46.549 | 0.45071 | 0 | 0.45071 | 0 | 45.6476 | 2.9434 | 15.5083 | 8.039
Mass Wall |  |  |  | 1IN Stucco | 8IN CONCRETE HW RefBldg | Insulation Layer | 1/2IN Gypsum |  | Mass NonRes Wall Insulation |  | used for material name
Assembly Max. U (IP) | R value (IP) | R value to Subtract (IP) | Final R Value (IP) | Mat 1 R Value (IP) | Mat 2 R Value (IP) | Mat 3 R Value (IP) | Mat 4 R Value (IP) | R value left (IP) | Insul. Resistance (IP) | Insul Thickness (IP) | R Value (SI)
0.58 | 1.7241 | 0.85 | 0.87414 | 0.20766 | 0.88011 | 0 | 0.45071 | -0.66434 | 2.9434 | -0.2257 | -0.117
0.151 | 6.6225 | 0.85 | 5.7725 | 0.20766 | 0.88011 | 0 | 0.45071 | 4.234 | 2.9434 | 1.4385 | 0.74566
0.123 | 8.1301 | 0.85 | 7.2801 | 0.20766 | 0.88011 | 0 | 0.45071 | 5.7416 | 2.9434 | 1.9507 | 1.0112
0.104 | 9.6154 | 0.85 | 8.7654 | 0.20766 | 0.88011 | 0 | 0.45071 | 7.2269 | 2.9434 | 2.4553 | 1.2727
0.09 | 11.1111 | 0.85 | 10.2611 | 0.20766 | 0.88011 | 0 | 0.45071 | 8.7226 | 2.9434 | 2.9634 | 1.5361
0.08 | 12.5 | 0.85 | 11.65 | 0.20766 | 0.88011 | 0 | 0.45071 | 10.1115 | 2.9434 | 3.4353 | 1.7807
0.071 | 14.0845 | 0.85 | 13.2345 | 0.20766 | 0.88011 | 0 | 0.45071 | 11.696 | 2.9434 | 3.9736 | 2.0598
0.052 | 19.2308 | 0.85 | 18.3808 | 0.20766 | 0.88011 | 0 | 0.45071 | 16.8423 | 2.9434 | 5.722 | 2.9661
Metal Building |  |  |  | Metal Siding | Insulation Layer | 1/2IN Gypsum | NA |  | Metal Building Semi-Cond Wall Insulation |  | used for material name
Assembly Max. U (IP) | R value (IP) | R value to Subtract (IP) | Final R Value (IP) | Mat 1 R Value (IP) | Mat 2 R Value (IP) | Mat 3 R Value (IP) | Mat 4 R Value (IP) | R value left (IP) | Insul. Resistance (IP) | Insul Thickness (IP) | R Value (SI)
1.18 | 0.84746 | 0.85 | -0.0025424 | 0.00018944 | 0 | 0.45071 | 0 | -0.45344 | 2.9434 | -0.15405 | -0.079856
0.184 | 5.4348 | 0.85 | 4.5848 | 0.00018944 | 0 | 0.45071 | 0 | 4.1339 | 2.9434 | 1.4044 | 0.72802
0.134 | 7.4627 | 0.85 | 6.6127 | 0.00018944 | 0 | 0.45071 | 0 | 6.1618 | 2.9434 | 2.0934 | 1.0852
0.123 | 8.1301 | 0.85 | 7.2801 | 0.00018944 | 0 | 0.45071 | 0 | 6.8292 | 2.9434 | 2.3201 | 1.2027
0.113 | 8.8496 | 0.85 | 7.9996 | 0.00018944 | 0 | 0.45071 | 0 | 7.5487 | 2.9434 | 2.5646 | 1.3294
0.093 | 10.7527 | 0.85 | 9.9027 | 0.00018944 | 0 | 0.45071 | 0 | 9.4518 | 2.9434 | 3.2112 | 1.6646
0.084 | 11.9048 | 0.85 | 11.0548 | 0.00018944 | 0 | 0.45071 | 0 | 10.6039 | 2.9434 | 3.6026 | 1.8674
0.069 | 14.4928 | 0.85 | 13.6428 | 0.00018944 | 0 | 0.45071 | 0 | 13.1919 | 2.9434 | 4.4818 | 2.3232
0.057 | 17.5439 | 0.85 | 16.6939 | 0.00018944 | 0 | 0.45071 | 0 | 16.243 | 2.9434 | 5.5184 | 2.8606
Steel Framed |  |  |  | Wood Siding | Insulation Layer | 1/2IN Gypsum | NA |  | Steel Frame NonRes Wall Insulation |  | used for material name
Assembly Max. U (IP) | R value (IP) | R value to Subtract (IP) | Final R Value (IP) | Mat 1 R Value (IP) | Mat 2 R Value (IP) | Mat 3 R Value (IP) | Mat 4 R Value (IP) | R value left (IP) | Insul. Resistance (IP) | Insul Thickness (IP) | R Value (SI)
0.352 | 2.8409 | 0.85 | 1.9909 | 0.51621 | 0 | 0.45071 | 0 | 1.024 | 2.9434 | 0.34789 | 0.18034
0.124 | 8.0645 | 0.85 | 7.2145 | 0.51621 | 0 | 0.45071 | 0 | 6.2476 | 2.9434 | 2.1226 | 1.1003
0.084 | 11.9048 | 0.85 | 11.0548 | 0.51621 | 0 | 0.45071 | 0 | 10.0878 | 2.9434 | 3.4272 | 1.7766
0.064 | 15.625 | 0.85 | 14.775 | 0.51621 | 0 | 0.45071 | 0 | 13.8081 | 2.9434 | 4.6912 | 2.4317
0.042 | 23.8095 | 0.85 | 22.9595 | 0.51621 | 0 | 0.45071 | 0 | 21.9926 | 2.9434 | 7.4718 | 3.8731
0.037 | 27.027 | 0.85 | 26.177 | 0.51621 | 0 | 0.45071 | 0 | 25.2101 | 2.9434 | 8.5649 | 4.4398
Wood Framed |  |  |  | Wood Siding | Insulation Layer | 1/2IN Gypsum | NA |  | Wood Frame NonRes Wall Insulation |  | used for material name
Assembly Max. U (IP) | R value (IP) | R value to Subtract (IP) | Final R Value (IP) | Mat 1 R Value (IP) | Mat 2 R Value (IP) | Mat 3 R Value (IP) | Mat 4 R Value (IP) | R value left (IP) | Insul. Resistance (IP) | Insul Thickness (IP) | R Value (SI)
0.292 | 3.4247 | 0.85 | 2.5747 | 0.51621 | 0 | 0.45071 | 0 | 1.6077 | 2.9434 | 0.54621 | 0.28314
0.089 | 11.236 | 0.85 | 10.386 | 0.51621 | 0 | 0.45071 | 0 | 9.419 | 2.9434 | 3.2 | 1.6588
0.064 | 15.625 | 0.85 | 14.775 | 0.51621 | 0 | 0.45071 | 0 | 13.8081 | 2.9434 | 4.6912 | 2.4317
0.051 | 19.6078 | 0.85 | 18.7578 | 0.51621 | 0 | 0.45071 | 0 | 17.7909 | 2.9434 | 6.0443 | 3.1332
0.036 | 27.7778 | 0.85 | 26.9278 | 0.51621 | 0 | 0.45071 | 0 | 25.9609 | 2.9434 | 8.8199 | 4.572