## Templates
Templates combine standards and prototype data to create space types and construction sets, templates for each building type are exported to OSM format
0 | 1
Name | Notes
DOE Ref Pre-1980 | Numbers taken from the DOE Pre-1980 reference buildings, with values mapped back to the original data source (standards, etc) where possible. The infiltration numbers were taken from the reference buildings but converted to cfm/ft^2 of exterior surface area. Color scheme is based on redder for more public spaces, bluer for more private spaces. Occupancy from ventilation standards was not used by reference buildings because numbers were generally found to be too high for modeling, representing very conservative design scenarios.
DOE Ref 1980-2004 | Numbers taken from the DOE 1980-2004 reference buildings, with values mapped back to the original data source (standards, etc) where possible. The infiltration numbers were taken from the reference buildings but converted to cfm/ft^2 of exterior surface area. Color scheme is based on redder for more public spaces, bluer for more private spaces. Occupancy from ventilation standards was not used by reference buildings because numbers were generally found to be too high for modeling, representing very conservative design scenarios.
90.1-2004 | Numbers taken from the DOE 2004 reference buildings, with values mapped back to the original data source (standards, etc) where possible. The infiltration numbers were taken from the reference buildings but converted to cfm/ft^2 of exterior surface area. Color scheme is based on redder for more public spaces, bluer for more private spaces. Occupancy from ventilation standards was not used by reference buildings because numbers were generally found to be too high for modeling, representing very conservative design scenarios.
189.1-2009 | Lighting, equipment, infiltration, and ventilation taken from the EnergyPlus example file generator low-energy case. Schedules and occupancy taken from DOE Ref 2004 template.
90.1-2007 | Lighting and ventilation taken from 90.1-2007. Equipment and infiltration taken from 189.1-2009 template. Schedules and occupancy taken from DOE Ref 2004 template.
90.1-2010 | Lighting and ventilation taken from 90.1-2010. Equipment and infiltration taken from 189.1-2009 template. Schedules and occupancy taken from DOE Ref 2004 template.

## Standards
Standards are actual standards documents issued by a standards organization
Name
AIA 2001
ASHRAE 169-2006
ASHRAE 189.1-2009
ASHRAE 62.1-1999
ASHRAE 62.1-2004
ASHRAE 62.1-2007
ASHRAE 90.1-1999
ASHRAE 90.1-2001
ASHRAE 90.1-2004
ASHRAE 90.1-2007
ASHRAE 90.1-2010
ASHRAE 90.1-2013
GGHC v2.2
CEC Title24-2005
CEC Title24-2008
CEC Title24-2013

## Climate Zones
A climate zone is a geographic area defined in a standards document
0 | 1 | 2 | 3
Name | Standard | Representative City | BCL Weather Component ID
ASHRAE 169-2006-1A | ASHRAE 169-2006
ASHRAE 169-2006-1B | ASHRAE 169-2006
ASHRAE 169-2006-2A | ASHRAE 169-2006
ASHRAE 169-2006-2B | ASHRAE 169-2006
ASHRAE 169-2006-3A | ASHRAE 169-2006
ASHRAE 169-2006-3B | ASHRAE 169-2006
ASHRAE 169-2006-3C | ASHRAE 169-2006
ASHRAE 169-2006-4A | ASHRAE 169-2006
ASHRAE 169-2006-4B | ASHRAE 169-2006
ASHRAE 169-2006-4C | ASHRAE 169-2006
ASHRAE 169-2006-5A | ASHRAE 169-2006
ASHRAE 169-2006-5B | ASHRAE 169-2006
ASHRAE 169-2006-5C | ASHRAE 169-2006
ASHRAE 169-2006-6A | ASHRAE 169-2006
ASHRAE 169-2006-6B | ASHRAE 169-2006
ASHRAE 169-2006-7A | ASHRAE 169-2006
ASHRAE 169-2006-7B | ASHRAE 169-2006
ASHRAE 169-2006-8A | ASHRAE 169-2006
ASHRAE 169-2006-8B | ASHRAE 169-2006
CEC 2005-1 | CEC Title24-2005
CEC 2005-2 | CEC Title24-2005
CEC 2005-3 | CEC Title24-2005
CEC 2005-4 | CEC Title24-2005
CEC 2005-5 | CEC Title24-2005
CEC 2005-6 | CEC Title24-2005
CEC 2005-7 | CEC Title24-2005
CEC 2005-8 | CEC Title24-2005
CEC 2005-9 | CEC Title24-2005
CEC 2005-10 | CEC Title24-2005
CEC 2008-1 | CEC Title24-2008
CEC 2008-2 | CEC Title24-2008
CEC 2008-3 | CEC Title24-2008
CEC 2008-4 | CEC Title24-2008
CEC 2008-5 | CEC Title24-2008
CEC 2008-6 | CEC Title24-2008
CEC 2008-7 | CEC Title24-2008
CEC 2008-8 | CEC Title24-2008
CEC 2008-9 | CEC Title24-2008
CEC 2008-10 | CEC Title24-2008

## Climate Zone Sets
A climate zone set is a group of climate zones
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39
Name | Climate Zone | Climate Zone2 | Climate Zone3 | Climate Zone4 | Climate Zone5 | Climate Zone6 | Climate Zone7 | Climate Zone8 | Climate Zone9 | Climate Zone10 | Climate Zone11 | Climate Zone12 | Climate Zone13 | Climate Zone14 | Climate Zone15 | Climate Zone16 | Climate Zone17 | Climate Zone18 | Climate Zone19 | Climate Zone20 | Climate Zone21 | Climate Zone22 | Climate Zone23 | Climate Zone24 | Climate Zone25 | Climate Zone26 | Climate Zone27 | Climate Zone28 | Climate Zone29 | Climate Zone30 | Climate Zone31 | Climate Zone32 | Climate Zone33 | Climate Zone34 | Climate Zone35 | Climate Zone36 | Climate Zone37 | Climate Zone38 | Climate Zone39
All Climates | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B | CEC 2005-1 | CEC 2005-2 | CEC 2005-3 | CEC 2005-4 | CEC 2005-5 | CEC 2005-6 | CEC 2005-7 | CEC 2005-8 | CEC 2005-9 | CEC 2005-10 | CEC 2008-1 | CEC 2008-2 | CEC 2008-3 | CEC 2008-4 | CEC 2008-5 | CEC 2008-6 | CEC 2008-7 | CEC 2008-8 | CEC 2008-9 | CEC 2008-10
ClimateZone 1 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B
ClimateZone 1-2 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B
ClimateZone 1-3 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C
ClimateZone 1-3 + 8 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 1-3b | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B
ClimateZone 1-4 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C
ClimateZone 1-5 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C
ClimateZone 1-6 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B
ClimateZone 1-7 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B
ClimateZone 1-8 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 1a | ASHRAE 169-2006-1A
ClimateZone 1b | ASHRAE 169-2006-1B
ClimateZone 2 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B
ClimateZone 2-3 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C
ClimateZone 2-4 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C
ClimateZone 2-5 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C
ClimateZone 2-6 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B
ClimateZone 2-7 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B
ClimateZone 2-8 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 2a | ASHRAE 169-2006-2A
ClimateZone 2b | ASHRAE 169-2006-2B
ClimateZone 3 | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C
ClimateZone 3-4 | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C
ClimateZone 3-5 | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C
ClimateZone 3-6 | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B
ClimateZone 3-7 | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B
ClimateZone 3-8 | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 3a | ASHRAE 169-2006-3A
ClimateZone 3a-3b | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B
ClimateZone 3b | ASHRAE 169-2006-3B
ClimateZone 3c | ASHRAE 169-2006-3C
ClimateZone 4 | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C
ClimateZone 4-5 | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C
ClimateZone 4-6 | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B
ClimateZone 4-7 | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B
ClimateZone 4-8 | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 4a | ASHRAE 169-2006-4A
ClimateZone 4b | ASHRAE 169-2006-4B
ClimateZone 4c | ASHRAE 169-2006-4C
ClimateZone 4c-5a | ASHRAE 169-2006-4C | ASHRAE 169-2006-5A
ClimateZone 5 | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C
ClimateZone 5-6 | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B
ClimateZone 5-7 | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B
ClimateZone 5-8 | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 5a | ASHRAE 169-2006-5A
ClimateZone 5b | ASHRAE 169-2006-5B
ClimateZone 5c | ASHRAE 169-2006-5C
ClimateZone 6 | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B
ClimateZone 6-7 | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B
ClimateZone 6-8 | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 6a | ASHRAE 169-2006-6A
ClimateZone 6b | ASHRAE 169-2006-6B
ClimateZone 7 | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B
ClimateZone 7-8 | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 7a | ASHRAE 169-2006-7A
ClimateZone 7b | ASHRAE 169-2006-7B
ClimateZone 8 | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
ClimateZone 8a | ASHRAE 169-2006-8A
ClimateZone 8b | ASHRAE 169-2006-8B

## Space Types
A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building
|  |  |  | Color | Lighting | [12 empty] | Ventilation | [6 empty] | Occupancy |  |  | Infiltration |  |  | Gas Equipment |  |  |  |  | Electric Plug Loads |  |  |  |  | Thermostats - not currently part of a space type |  | Service Hot Water - not currently part of a space type | [6 empty] | Exhaust - Not currently part of a space type
Template | Climate Zone Set | Building Type | Space Type | RGB | Lighting Standard | Lighting Primary Space Type | Lighting Secondary Space Type | LookupColumn | OSM Lighting per Person(W/person) | OSM Lighting per Area (W/ft) | Lighting per Area (W/ft^2) | Lighting per Person (W/person) | Lighting per Length (W/ft) | Lighting Fraction to Return Air | Lighting Fraction Radiant | Lighting Fraction Visible | Lighting Schedule | Ventilation Standard | Ventilation Primary Space Type | Ventilation Secondary Space Type | Lookup | Ventilation per Area (ft^3/min*ft^2) | Ventilation per Person (ft^3/min*person) | Ventilation Air Changes (ach) | Occupancy per Area (people/1000 ft^2) | Occupancy Schedule | Occupancy Activity Schedule | Infiltration per Exterior Area (ft^3/min*ft^2 ext) | Infiltration per Exterior Wall Area (ft^3/min*ft^2 ext) | Infiltration Schedule | Gas Equipment per Area (Btu/hr*ft^2) | Gas Equipment Fraction Latent | Gas Equipment Fraction Radiant | Gas Equipment Fraction Lost | Gas Equipment Schedule | Electric Equipment per Area (W/ft^2) | Electric Equipment Fraction Latent | Electric Equipment Fraction Radiant | Electric Equipment Fraction Lost | Electric Equipment Schedule | Heating Setpoint Schedule | Cooling Setpoint Schedule | Service Water Heating Peak Flow Rate (gal/h) | Service Water Heating Area (ft^2) | Service Water Heating Peak Flow per Area (gal/h*ft^2) | Service Water Heating Target Temperature (C) | Service Water Heating Fraction Sensible | Service Water Heating Fraction Latent | Service Water Heating Schedule | Exhaust per Area (cfm/ft2) | Exhaust per Unit (cfm) | Exhaust Fan Efficiency | Exhaust Fan Pressure Rise (in.w.g.) | Exhaust Fan Power (W) | Exhaust Fan Power per Area (W/ft^2) | Exhaust Schedule
90.1-2004 | ClimateZone 1-8 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | RestaurantSitDown BLDG_OCC_SCH | RestaurantSitDown ACTIVITY_SCH | 0.0595 |  | RestaurantSitDown INFIL_HALF_ON_SCH | 378.75 | 0.1 | 0.2 | 0.7 | RestaurantSitDown Rest_GAS_EQUIP_SCH | 35 | 0.25 | 0.3 | 0.2 | RestaurantSitDown BLDG_EQUIP_SCH | RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | RestaurantSitDown BLDG_SWH_SCH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | RestaurantSitDown Kitchen_Exhaust_SCH
90.1-2007 | ClimateZone 1-8 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | RestaurantSitDown BLDG_OCC_SCH | RestaurantSitDown ACTIVITY_SCH | 0.0446 |  | RestaurantSitDown INFIL_HALF_ON_SCH | 276.72 | 0.1 | 0.2 | 0.7 | RestaurantSitDown Rest_GAS_EQUIP_SCH | 25.5 | 0.25 | 0.3 | 0.2 | RestaurantSitDown BLDG_EQUIP_SCH | RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | RestaurantSitDown BLDG_SWH_SCH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | RestaurantSitDown Kitchen_Exhaust_SCH
90.1-2010 | ClimateZone 1-8 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | RestaurantSitDown BLDG_OCC_SCH | RestaurantSitDown ACTIVITY_SCH | 0.0446 |  | RestaurantSitDown INFIL_HALF_ON_SCH | 276.72 | 0.1 | 0.2 | 0.7 | RestaurantSitDown Rest_GAS_EQUIP_SCH | 25.5 | 0.25 | 0.3 | 0.2 | RestaurantSitDown BLDG_EQUIP_SCH | RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | RestaurantSitDown BLDG_SWH_SCH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | RestaurantSitDown Kitchen_Exhaust_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | FullServiceRestaurant | Kitchen | 78_222_133 | [6 empty] | 1.52 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity |  | 0.2232 | FullServiceRestaurant Infil Half On | 378.75 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant Gas Equip | 35 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp Kitchen | FullServiceRestaurant ClgSetp Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant Kitchen Exhaust
189.1-2009 | ClimateZone 1-3 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0595 |  | FullServiceRestaurant Infil Half On | 276.72 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant Gas Equip | 25.5 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp Kitchen | FullServiceRestaurant ClgSetp Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant Kitchen Exhaust
189.1-2009 | ClimateZone 4-8 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0446 |  | FullServiceRestaurant Infil Half On | 276.72 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant Gas Equip | 25.5 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp Kitchen | FullServiceRestaurant ClgSetp Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant Kitchen Exhaust
DOE Ref Pre-1980 | ClimateZone 1-8 | FullServiceRestaurant | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity |  | 0.2232 | FullServiceRestaurant Infil Half On | 378.75 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant Gas Equip | 35 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp Kitchen | FullServiceRestaurant ClgSetp Kitchen | 133 | 1501 | 0.088608 | 49 | 0.2 | 0.05 | FullServiceRestaurant SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | FullServiceRestaurant Kitchen Exhaust
90.1-2004 | ClimateZone 1-8 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | For Family Dining | ASHRAE 90.1-2004Dining AreaFor Family Dining |  |  | 2.1 |  |  | 0 | 0.7 | 0.2 | RestaurantSitDown BLDG_LIGHT_DINING_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 67 | RestaurantSitDown BLDG_OCC_SCH | RestaurantSitDown ACTIVITY_SCH | 0.0595 |  | RestaurantSitDown INFIL_HALF_ON_SCH | [5 empty] | 5.6 | 0.25 | 0.3 | 0 | RestaurantSitDown BLDG_EQUIP_SCH | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | For Family Dining | ASHRAE 90.1-2007Dining AreaFor Family Dining |  |  | 2.1 |  |  | 0 | 0.7 | 0.2 | RestaurantSitDown BLDG_LIGHT_DINING_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Restaurant dining rooms | ASHRAE 62.1-2004Food and Beverage ServiceRestaurant dining rooms | 0.18 | 7.5 | 0 | 67 | RestaurantSitDown BLDG_OCC_SCH | RestaurantSitDown ACTIVITY_SCH | 0.0446 |  | RestaurantSitDown INFIL_HALF_ON_SCH | [5 empty] | 4.08 | 0.25 | 0.3 | 0 | RestaurantSitDown BLDG_EQUIP_SCH | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | For Family Dining | ASHRAE 90.1-2010Dining AreaFor Family Dining |  |  | 0.89 |  |  | 0 | 0.7 | 0.2 | RestaurantSitDown BLDG_LIGHT_DINING_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Restaurant dining rooms | ASHRAE 62.1-2007Food and Beverage ServiceRestaurant dining rooms | 0.18 | 7.5 | 0 | 67 | RestaurantSitDown BLDG_OCC_SCH | RestaurantSitDown ACTIVITY_SCH | 0.0446 |  | RestaurantSitDown INFIL_HALF_ON_SCH | [5 empty] | 4.08 | 0.25 | 0.3 | 0 | RestaurantSitDown BLDG_EQUIP_SCH | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | FullServiceRestaurant | Dining | 31_169_34 | [6 empty] | 2.54 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 67 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity |  | 0.2232 | FullServiceRestaurant Infil Half On | [5 empty] | 5.6 | 0.25 | 0.3 | 0 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp
189.1-2009 | ClimateZone 1-3 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Family Dining | ASHRAE 189.1-2009Dining AreaFor Family Dining |  |  | 1.89 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 67 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0595 |  | FullServiceRestaurant Infil Half On | [5 empty] | 4.08 | 0.25 | 0.3 | 0 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp
189.1-2009 | ClimateZone 4-8 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Family Dining | ASHRAE 189.1-2009Dining AreaFor Family Dining |  |  | 1.89 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 67 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0446 |  | FullServiceRestaurant Infil Half On | [5 empty] | 4.08 | 0.25 | 0.3 | 0 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | FullServiceRestaurant | Dining | 31_169_34 | [6 empty] | 2.77 |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 67 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity |  | 0.2232 | FullServiceRestaurant Infil Half On | [5 empty] | 5.6 | 0.25 | 0.3 | 0 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp
90.1-2004 | ClimateZone 1-8 | Hospital | Radiology | 136_78_222 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_RADIOLOGY_SCH | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 10 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | Radiology | 136_78_222 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_RADIOLOGY_SCH | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 7.28 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | Radiology | 136_78_222 | ASHRAE 90.1-2010 | Hospital | Radiology/Imaging | ASHRAE 90.1-2010HospitalRadiology/Imaging |  |  | 1.32 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_RADIOLOGY_SCH | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 7.28 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | Radiology | 136_78_222 | [6 empty] | 2.21 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 10 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital SWH Extd
189.1-2009 | ClimateZone 1-3 | Hospital | Radiology | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 7.28 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital SWH Extd
189.1-2009 | ClimateZone 4-8 | Hospital | Radiology | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 7.28 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital SWH Extd
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | Radiology | 136_78_222 | [6 empty] | 3.3 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 10 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5250 | 0.00019048 | 49 | 0.2 | 0.05 | Hospital SWH Extd
90.1-2004 | ClimateZone 1-8 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 90.1-2004 | Hospital | Physical Therapy | ASHRAE 90.1-2004HospitalPhysical Therapy |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 90.1-2007 | Hospital | Physical Therapy | ASHRAE 90.1-2007HospitalPhysical Therapy |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 90.1-2010 | Hospital | Physical Therapy | ASHRAE 90.1-2010HospitalPhysical Therapy |  |  | 0.91 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | PhysTherapy | 154_230_120 | [6 empty] | 2.5 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital SWH
189.1-2009 | ClimateZone 1-3 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 189.1-2009 | Hospital | Physical Therapy | ASHRAE 189.1-2009HospitalPhysical Therapy |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital SWH
189.1-2009 | ClimateZone 4-8 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 189.1-2009 | Hospital | Physical Therapy | ASHRAE 189.1-2009HospitalPhysical Therapy |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital SWH
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | PhysTherapy | 154_230_120 | [6 empty] | 2.51 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5280 | 0.00018939 | 49 | 0.2 | 0.05 | Hospital SWH
90.1-2004 | ClimateZone 1-8 | Hospital | PatRoom | 78_167_222 | ASHRAE 90.1-2004 | Hospital | Patient Room | ASHRAE 90.1-2004HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | PatRoom | 78_167_222 | ASHRAE 90.1-2007 | Hospital | Patient Room | ASHRAE 90.1-2007HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | PatRoom | 78_167_222 | ASHRAE 90.1-2010 | Hospital | Patient Room | ASHRAE 90.1-2010HospitalPatient Room |  |  | 0.62 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | PatRoom | 78_167_222 | [6 empty] | 2.19 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital SWH Extd
189.1-2009 | ClimateZone 1-3 | Hospital | PatRoom | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital SWH Extd
189.1-2009 | ClimateZone 4-8 | Hospital | PatRoom | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital SWH Extd
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | PatRoom | 78_167_222 | [6 empty] | 1.85 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 1 | 280 | 0.0035714 | 49 | 0.2 | 0.05 | Hospital SWH Extd
90.1-2004 | ClimateZone 1-8 | Hospital | PatCorridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | ASHRAE 90.1-2004Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | PatCorridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | ASHRAE 90.1-2007Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 1 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | PatCorridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | For Hospital | ASHRAE 90.1-2010Corridor/TransitionFor Hospital |  |  | 0.89 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 1 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | PatCorridor | 169_31_31 | [6 empty] | 1.36 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp
189.1-2009 | ClimateZone 1-3 | Hospital | PatCorridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp
189.1-2009 | ClimateZone 4-8 | Hospital | PatCorridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | PatCorridor | 169_31_31 | [6 empty] | 1.32 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp
90.1-2004 | ClimateZone 1-8 | Hospital | OR | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Operating Room | ASHRAE 90.1-2004HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 5 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | OR | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Operating Room | ASHRAE 90.1-2007HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | OR | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Operating Room | ASHRAE 90.1-2010HospitalOperating Room |  |  | 1.89 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | OR | 169_31_159 | [6 empty] | 9.75 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH
189.1-2009 | ClimateZone 1-3 | Hospital | OR | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital Critical Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH
189.1-2009 | ClimateZone 4-8 | Hospital | OR | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | OR | 169_31_159 | [6 empty] | 10 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 2 | 600 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH
90.1-2004 | ClimateZone 1-8 | Hospital | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 6.99 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 6.99 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 6.99 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | Office | 120_230_199 | [6 empty] | 2.4 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 6.99 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
189.1-2009 | ClimateZone 1-3 | Hospital | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 6.99 | Hospital Bldg Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
189.1-2009 | ClimateZone 4-8 | Hospital | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 6.99 | Hospital Bldg Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | Office | 120_230_199 | [6 empty] | 1.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 6.99 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
90.1-2004 | ClimateZone 1-8 | Hospital | NurseStn | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_NURSEFLR234_SCH | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 7.14 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.04 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | NurseStn | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_NURSEFLR234_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 7.14 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.76 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | NurseStn | 31_162_169 | ASHRAE 90.1-2010 | Hospital | Nurse Station | ASHRAE 90.1-2010HospitalNurse Station |  |  | 0.87 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_NURSEFLR234_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 7.14 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.76 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | NurseStn | 31_162_169 | [6 empty] | 1.46 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1.04 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
189.1-2009 | ClimateZone 1-3 | Hospital | NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 0.76 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
189.1-2009 | ClimateZone 4-8 | Hospital | NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 0.76 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | NurseStn | 31_162_169 | [6 empty] | 1.53 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1.04 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
90.1-2004 | ClimateZone 1-8 | Hospital | Lobby | 31_162_169 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 7.14 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.1 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | Lobby | 31_162_169 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2004Office BuildingsMain entry lobbies | 0.06 | 5 | 0 | 7.14 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.07 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | Lobby | 31_162_169 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2007Office BuildingsMain entry lobbies | 0.06 | 5 | 0 | 7.14 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.07 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | Lobby | 31_162_169 | [6 empty] | 1.46 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 0.1 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
189.1-2009 | ClimateZone 1-3 | Hospital | Lobby | 31_162_169 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
189.1-2009 | ClimateZone 4-8 | Hospital | Lobby | 31_162_169 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | Lobby | 31_162_169 | [6 empty] | 1.49 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 7.14 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 0.1 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
90.1-2004 | ClimateZone 1-8 | Hospital | Lab | 204_120_230 | ASHRAE 90.1-2004 | Laboratory | General | ASHRAE 90.1-2004LaboratoryGeneral |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 | 0 | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | Lab | 204_120_230 | ASHRAE 90.1-2007 | Laboratory | General | ASHRAE 90.1-2007LaboratoryGeneral |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Educational Facilities | Science laboratories | ASHRAE 62.1-2004Educational FacilitiesScience laboratories | 0.18 | 10 | 0 | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 3.22 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | Lab | 204_120_230 | ASHRAE 90.1-2010 | Laboratory | For Medical/Industrial/Research | ASHRAE 90.1-2010LaboratoryFor Medical/Industrial/Research |  |  | 1.81 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Educational Facilities | Science laboratories | ASHRAE 62.1-2007Educational FacilitiesScience laboratories | 0.18 | 10 | 0 | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 3.22 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | Lab | 204_120_230 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 | 0 | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital SWH
189.1-2009 | ClimateZone 1-3 | Hospital | Lab | 204_120_230 | ASHRAE 189.1-2009 | Laboratory | General | ASHRAE 189.1-2009LaboratoryGeneral |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 3.22 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital SWH
189.1-2009 | ClimateZone 4-8 | Hospital | Lab | 204_120_230 | ASHRAE 189.1-2009 | Laboratory | General | ASHRAE 189.1-2009LaboratoryGeneral |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 3.22 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital SWH
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | Lab | 204_120_230 | [6 empty] | 1.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 | 0 | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 2 | 2850 | 0.00070175 | 49 | 0.2 | 0.05 | Hospital SWH
90.1-2004 | ClimateZone 1-8 | Hospital | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | 96.7 | 0.1 | 0.2 | 0.7 | Hospital BLDG_EQUIP_SCH | 7.5 | 0.2 | 0.5 | 0.1 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital Kitchen_Exhaust_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | 70.46 | 0.1 | 0.2 | 0.7 | Hospital BLDG_EQUIP_SCH | 5.47 | 0.2 | 0.5 | 0.1 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital Kitchen_Exhaust_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | 70.46 | 0.1 | 0.2 | 0.7 | Hospital BLDG_EQUIP_SCH | 5.47 | 0.2 | 0.5 | 0.1 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital Kitchen_Exhaust_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | Kitchen | 78_222_133 | [6 empty] | 1.42 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | 96.7 | 0.1 | 0.2 | 0.7 | Hospital Kitchen Gas | 7.5 | 0.2 | 0.5 | 0.1 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital SWH Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital Kitchen Exhaust
189.1-2009 | ClimateZone 1-3 | Hospital | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | 70.46 | 0.1 | 0.2 | 0.7 | Hospital Kitchen Gas | 5.47 | 0.2 | 0.5 | 0.1 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital SWH Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital Kitchen Exhaust
189.1-2009 | ClimateZone 4-8 | Hospital | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | 70.46 | 0.1 | 0.2 | 0.7 | Hospital Kitchen Gas | 5.47 | 0.2 | 0.5 | 0.1 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital SWH Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital Kitchen Exhaust
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | 96.7 | 0.1 | 0.2 | 0.7 | Hospital Kitchen Gas | 7.5 | 0.2 | 0.5 | 0.1 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital SWH Extd | 0.7 | 5300 | 0.338 | 0.50241 | 924.6539 | 0.12212 | Hospital Kitchen Exhaust
90.1-2004 | ClimateZone 1-8 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 90.1-2004 | Hospital | Patient Room | ASHRAE 90.1-2004HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 90.1-2007 | Hospital | Patient Room | ASHRAE 90.1-2007HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 90.1-2010 | Hospital | Patient Room | ASHRAE 90.1-2010HospitalPatient Room |  |  | 0.62 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | ICU_PatRm | 78_167_222 | [6 empty] | 3.84 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
189.1-2009 | ClimateZone 1-3 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
189.1-2009 | ClimateZone 4-8 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | ICU_PatRm | 78_167_222 | [6 empty] | 4.22 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
90.1-2004 | ClimateZone 1-8 | Hospital | ICU_Open | 78_167_222 | ASHRAE 90.1-2004 | Hospital | Recovery | ASHRAE 90.1-2004HospitalRecovery |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | ICU_Open | 78_167_222 | ASHRAE 90.1-2007 | Hospital | Recovery | ASHRAE 90.1-2007HospitalRecovery |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | ICU_Open | 78_167_222 | ASHRAE 90.1-2010 | Hospital | Recovery | ASHRAE 90.1-2010HospitalRecovery |  |  | 1.15 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | ICU_Open | 78_167_222 | [6 empty] | 3.84 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
189.1-2009 | ClimateZone 1-3 | Hospital | ICU_Open | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Recovery | ASHRAE 189.1-2009HospitalRecovery |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
189.1-2009 | ClimateZone 4-8 | Hospital | ICU_Open | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Recovery | ASHRAE 189.1-2009HospitalRecovery |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | ICU_Open | 78_167_222 | [6 empty] | 4.22 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
90.1-2004 | ClimateZone 1-8 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 90.1-2010 | Hospital | Nurse Station | ASHRAE 90.1-2010HospitalNurse Station |  |  | 0.87 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | ICU_NurseStn | 31_162_169 | [6 empty] | 1.71 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
189.1-2009 | ClimateZone 1-3 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
189.1-2009 | ClimateZone 4-8 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | ICU_NurseStn | 31_162_169 | [6 empty] | 1.64 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care | 0 | 0 | 2 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
90.1-2004 | ClimateZone 1-8 | Hospital | ER_Triage | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | ER_Triage | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.97 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | ER_Triage | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Emergency | ASHRAE 90.1-2010HospitalEmergency |  |  | 2.26 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.97 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | ER_Triage | 169_31_159 | [6 empty] | 3.84 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
189.1-2009 | ClimateZone 1-3 | Hospital | ER_Triage | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 1.97 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
189.1-2009 | ClimateZone 4-8 | Hospital | ER_Triage | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 1.97 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | ER_Triage | 169_31_159 | [6 empty] | 5 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
90.1-2004 | ClimateZone 1-8 | Hospital | ER_Trauma | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | ER_Trauma | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | ER_Trauma | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Emergency | ASHRAE 90.1-2010HospitalEmergency |  |  | 2.26 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | ER_Trauma | 169_31_159 | [6 empty] | 3.84 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
189.1-2009 | ClimateZone 1-3 | Hospital | ER_Trauma | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
189.1-2009 | ClimateZone 4-8 | Hospital | ER_Trauma | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | ER_Trauma | 169_31_159 | [6 empty] | 5 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
90.1-2004 | ClimateZone 1-8 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_NURSEFLR1_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.36 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_NURSEFLR1_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.99 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 90.1-2010 | Hospital | Nurse Station | ASHRAE 90.1-2010HospitalNurse Station |  |  | 0.87 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_NURSEFLR1_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.99 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | ER_NurseStn | 31_162_169 | [6 empty] | 1.66 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1.36 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
189.1-2009 | ClimateZone 1-3 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital Critical Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 0.99 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
189.1-2009 | ClimateZone 4-8 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital Critical Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 0.99 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | ER_NurseStn | 31_162_169 | [6 empty] | 1.64 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 6.25 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1.36 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
90.1-2004 | ClimateZone 1-8 | Hospital | ER_Exam | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | ER_Exam | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | ER_Exam | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Emergency | ASHRAE 90.1-2010HospitalEmergency |  |  | 2.26 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | ER_Exam | 169_31_159 | [6 empty] | 3.84 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
189.1-2009 | ClimateZone 1-3 | Hospital | ER_Exam | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
189.1-2009 | ClimateZone 4-8 | Hospital | ER_Exam | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | ER_Exam | 169_31_159 | [6 empty] | 5 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room | 0 | 0 | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.0033333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
90.1-2004 | ClimateZone 1-8 | Hospital | Dining | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 10 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | Dining | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 10 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | Dining | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | General | ASHRAE 90.1-2010Dining AreaGeneral |  |  | 0.65 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 10 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | Dining | 31_169_34 | [6 empty] | 2.58 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 10 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
189.1-2009 | ClimateZone 1-3 | Hospital | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 10 | Hospital Critical Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
189.1-2009 | ClimateZone 4-8 | Hospital | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 10 | Hospital Critical Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | Dining | 31_169_34 | [6 empty] | 2.77 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 | 0 | 10 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
90.1-2004 | ClimateZone 1-8 | Hospital | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | ASHRAE 90.1-2004Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | ClimateZone 1-8 | Hospital | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | ASHRAE 90.1-2007Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 1 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | Hospital | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | For Hospital | ASHRAE 90.1-2010Corridor/TransitionFor Hospital |  |  | 0.89 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 1 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Hospital | Corridor | 169_31_31 | [6 empty] | 1.36 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
189.1-2009 | ClimateZone 1-3 | Hospital | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity | 0.0595 |  | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
189.1-2009 | ClimateZone 4-8 | Hospital | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity | 0.0446 |  | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Hospital | Corridor | 169_31_31 | [6 empty] | 1.32 |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Hospital Critical Occ | Hospital Activity |  | 0.2232 | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
90.1-2004 | ClimateZone 1-8 | LargeHotel | Storage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 2 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0595 |  | HotelLarge INFIL_SCH | [5 empty] | 0.25 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2007 | ClimateZone 1-8 | LargeHotel | Storage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 2 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 0.13 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | LargeHotel | Storage | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 2 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 0.13 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | LargeHotel | Storage | 120_149_230 | [6 empty] | 0.37 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 2 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 0.25 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | ClimateZone 1-3 | LargeHotel | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 2 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 |  | LargeHotel Infil Quarter On | [5 empty] | 0.13 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | ClimateZone 4-8 | LargeHotel | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 2 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  | LargeHotel Infil Quarter On | [5 empty] | 0.13 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | LargeHotel | Storage | 120_149_230 | [6 empty] | 0.62 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 2 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 0.25 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
90.1-2004 | ClimateZone 1-8 | LargeHotel | Retail | 171_222_78 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0595 |  | HotelLarge INFIL_SCH | [5 empty] | 1 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2007 | ClimateZone 1-8 | LargeHotel | Retail | 171_222_78 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Retail | General Sales | ASHRAE 62.1-2004RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 0.51 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | LargeHotel | Retail | 171_222_78 | ASHRAE 90.1-2010 | Sales Area | General | ASHRAE 90.1-2010Sales AreaGeneral |  |  | 1.68 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 0.51 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | LargeHotel | Retail | 171_222_78 | [6 empty] | 3.54 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | ClimateZone 1-3 | LargeHotel | Retail | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 |  | LargeHotel Infil Quarter On | [5 empty] | 0.51 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | ClimateZone 4-8 | LargeHotel | Retail | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  | LargeHotel Infil Quarter On | [5 empty] | 0.51 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | LargeHotel | Retail | 171_222_78 | [6 empty] | 5.04 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
90.1-2004 | ClimateZone 1-8 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0595 |  | HotelLarge INFIL_SCH | [5 empty] | 0.5 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2007 | ClimateZone 1-8 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 0.26 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral |  |  | 0.95 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 0.26 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | LargeHotel | Mechanical | 41_31_169 | [6 empty] | 0.8 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 0.5 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | ClimateZone 1-3 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 |  | LargeHotel Infil Quarter On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | ClimateZone 4-8 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  | LargeHotel Infil Quarter On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | LargeHotel | Mechanical | 41_31_169 | [6 empty] | 0.6 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 0.5 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
90.1-2004 | ClimateZone 1-8 | LargeHotel | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | For Hotel | ASHRAE 90.1-2004LobbyFor Hotel |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | HotelLarge Lobby_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0595 |  | HotelLarge INFIL_SCH | [5 empty] | 0.75 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2007 | ClimateZone 1-8 | LargeHotel | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | For Hotel | ASHRAE 90.1-2007LobbyFor Hotel |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 | 0 | 30 | HotelLarge Lobby_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 0.38 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | LargeHotel | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | For Hotel | ASHRAE 90.1-2010LobbyFor Hotel |  |  | 1.06 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 | 0 | 30 | HotelLarge Lobby_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 0.38 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | LargeHotel | Lobby | 230_157_120 | [6 empty] | 1.88 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 0.75 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | ClimateZone 1-3 | LargeHotel | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | For Hotel | ASHRAE 189.1-2009LobbyFor Hotel |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 |  | LargeHotel Infil Quarter On | [5 empty] | 0.38 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | ClimateZone 4-8 | LargeHotel | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | For Hotel | ASHRAE 189.1-2009LobbyFor Hotel |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  | LargeHotel Infil Quarter On | [5 empty] | 0.38 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | LargeHotel | Lobby | 230_157_120 | [6 empty] | 1.45 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 0.75 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
90.1-2004 | ClimateZone 1-8 | LargeHotel | Laundry | 120_149_230 | ASHRAE 90.1-2004 | Hospital | Laundry-Washing | ASHRAE 90.1-2004HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 4 | HotelLarge LaundryRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0595 |  | HotelLarge INFIL_SCH | 170 | 0 | 0.5 | 0 | HotelLarge LaundryRoom_Eqp_Gas_Sch | 5.73 | 0 | 0.5 | 0 | HotelLarge LaundryRoom_Eqp_Elec_Sch | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | HotelLarge LaundryRoom_SWH_Sch | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | OutPatientHealthCare Hours_of_operation
90.1-2007 | ClimateZone 1-8 | LargeHotel | Laundry | 120_149_230 | ASHRAE 90.1-2007 | Hospital | Laundry-Washing | ASHRAE 90.1-2007HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Retail | Coinoperated laundries | ASHRAE 62.1-2004RetailCoinoperated laundries | 0.06 | 7.5 | 0 | 4 | HotelLarge LaundryRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | 123.8 | 0 | 0.5 | 0 | HotelLarge LaundryRoom_Eqp_Gas_Sch | 2.93 | 0 | 0.5 | 0 | HotelLarge LaundryRoom_Eqp_Elec_Sch | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | HotelLarge LaundryRoom_SWH_Sch | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | OutPatientHealthCare Hours_of_operation
90.1-2010 | ClimateZone 1-8 | LargeHotel | Laundry | 120_149_230 | ASHRAE 90.1-2010 | Hospital | Laundry-Washing | ASHRAE 90.1-2010HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | ASHRAE 62.1-2007RetailCoinoperated laundries | 0.06 | 7.5 | 0 | 4 | HotelLarge LaundryRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | 123.8 | 0 | 0.5 | 0 | HotelLarge LaundryRoom_Eqp_Gas_Sch | 2.93 | 0 | 0.5 | 0 | HotelLarge LaundryRoom_Eqp_Elec_Sch | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | HotelLarge LaundryRoom_SWH_Sch | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | OutPatientHealthCare Hours_of_operation
DOE Ref 1980-2004 | ClimateZone 1-8 | LargeHotel | Laundry | 120_149_230 | [6 empty] | 1.14 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 4 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | 170 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Gas | 5.73 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Equip | LargeHotel HtgSetp | LargeHotel ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel SWH Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel Laundry Exhaust_Always On
189.1-2009 | ClimateZone 1-3 | LargeHotel | Laundry | 120_149_230 | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | ASHRAE 189.1-2009HospitalLaundry-Washing |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 4 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 |  | LargeHotel Infil Quarter On | 123.8 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Gas | 2.93 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Equip | LargeHotel HtgSetp | LargeHotel ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel SWH Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel Laundry Exhaust_Always On
189.1-2009 | ClimateZone 4-8 | LargeHotel | Laundry | 120_149_230 | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | ASHRAE 189.1-2009HospitalLaundry-Washing |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 4 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  | LargeHotel Infil Quarter On | 123.8 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Gas | 2.93 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Equip | LargeHotel HtgSetp | LargeHotel ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel SWH Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel Laundry Exhaust_Always On
DOE Ref Pre-1980 | ClimateZone 1-8 | LargeHotel | Laundry | 120_149_230 | [6 empty] | 0.7 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 4 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | 170 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Gas | 5.73 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Equip | LargeHotel HtgSetp | LargeHotel ClgSetp | 156.6 | 840 | 0.18643 | 60 | 0.2 | 0.05 | LargeHotel SWH Laundry | 0.59523 | 500 | 0.338 | 0.50241 | 87.2315 | 0.10385 | LargeHotel Laundry Exhaust_Always On
90.1-2004 | ClimateZone 1-8 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0595 |  | HotelLarge INFIL_SCH | 511 | 0.1 | 0.2 | 0.7 | HotelLarge Kitchen_Gas_Equip_SCH | 47.22 | 0.2 | 0.5 | 0.1 | HotelLarge Kitchen_Elec_Equip_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | HotelLarge BLDG_SWH_SCH | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | HotelLarge Kitchen_Exhaust_SCH
90.1-2007 | ClimateZone 1-8 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | 373.8 | 0.1 | 0.2 | 0.7 | HotelLarge Kitchen_Gas_Equip_SCH | 24.16 | 0.2 | 0.5 | 0.1 | HotelLarge Kitchen_Elec_Equip_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | HotelLarge BLDG_SWH_SCH | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | HotelLarge Kitchen_Exhaust_SCH
90.1-2010 | ClimateZone 1-8 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | 373.8 | 0.1 | 0.2 | 0.7 | HotelLarge Kitchen_Gas_Equip_SCH | 24.16 | 0.2 | 0.5 | 0.1 | HotelLarge Kitchen_Elec_Equip_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | HotelLarge BLDG_SWH_SCH | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | HotelLarge Kitchen_Exhaust_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | LargeHotel | Kitchen | 78_222_133 | [6 empty] | 1.56 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | 511 | 0.1 | 0.2 | 0.7 | LargeHotel Kitchen Gas | 47.22 | 0.2 | 0.5 | 0.1 | LargeHotel Kitchen Equip | LargeHotel Kitchen HtgSetp | LargeHotel Kitchen ClgSetp | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel SWH Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel Kitchen Exhaust
189.1-2009 | ClimateZone 1-3 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 |  | LargeHotel Infil Quarter On | 373.8 | 0.1 | 0.2 | 0.7 | LargeHotel Kitchen Gas | 24.16 | 0.2 | 0.5 | 0.1 | LargeHotel Kitchen Equip | LargeHotel Kitchen HtgSetp | LargeHotel Kitchen ClgSetp | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel SWH Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel Kitchen Exhaust
189.1-2009 | ClimateZone 4-8 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  | LargeHotel Infil Quarter On | 373.8 | 0.1 | 0.2 | 0.7 | LargeHotel Kitchen Gas | 24.16 | 0.2 | 0.5 | 0.1 | LargeHotel Kitchen Equip | LargeHotel Kitchen HtgSetp | LargeHotel Kitchen ClgSetp | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel SWH Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel Kitchen Exhaust
DOE Ref Pre-1980 | ClimateZone 1-8 | LargeHotel | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | 511 | 0.1 | 0.2 | 0.7 | LargeHotel Kitchen Gas | 47.22 | 0.2 | 0.5 | 0.1 | LargeHotel Kitchen Equip | LargeHotel Kitchen HtgSetp | LargeHotel Kitchen ClgSetp | 133 | 1112 | 0.1196 | 49 | 0.2 | 0.05 | LargeHotel SWH Kitchen | 0.7 | 4000 | 0.338 | 0.50241 | 697.852 | 0.12212 | LargeHotel Kitchen Exhaust
90.1-2004 | ClimateZone 1-8 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2004 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2004Hotel/MotelGuest Rooms |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 3.57 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0595 |  | HotelLarge INFIL_SCH | [5 empty] | 1.33 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Base | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
90.1-2007 | ClimateZone 1-8 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2007 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2007Hotel/MotelGuest Rooms |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 | 0 | 3.57 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 0.68 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Base | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
90.1-2010 | ClimateZone 1-8 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Hotel | ASHRAE 90.1-2010Guest RoomFor Hotel |  |  | 1.11 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 | 0 | 3.57 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 0.68 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Base | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
DOE Ref 1980-2004 | ClimateZone 1-8 | LargeHotel | GuestRoom | 78_167_222 | [6 empty] | 1.77 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
189.1-2009 | ClimateZone 1-3 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | ASHRAE 189.1-2009Hotel/MotelGuest Rooms |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity | 0.0595 |  | LargeHotel Infil Quarter On | [5 empty] | 0.68 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
189.1-2009 | ClimateZone 4-8 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | ASHRAE 189.1-2009Hotel/MotelGuest Rooms |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity | 0.0446 |  | LargeHotel Infil Quarter On | [5 empty] | 0.68 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
DOE Ref Pre-1980 | ClimateZone 1-8 | LargeHotel | GuestRoom | 78_167_222 | [6 empty] | 1.4 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.0029762 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
DOE Ref 1980-2004 | ClimateZone 1-8 | LargeHotel | Corridor | 169_31_31 | [6 empty] | 1.22 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel Corridor HtgSetp | LargeHotel Corridor ClgSetp
189.1-2009 | ClimateZone 1-3 | LargeHotel | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 |  | LargeHotel Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel Corridor HtgSetp | LargeHotel Corridor ClgSetp
189.1-2009 | ClimateZone 4-8 | LargeHotel | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  | LargeHotel Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel Corridor HtgSetp | LargeHotel Corridor ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | LargeHotel | Corridor | 169_31_31 | [6 empty] | 0.6 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel Corridor HtgSetp | LargeHotel Corridor ClgSetp
90.1-2004 | ClimateZone 1-8 | LargeHotel | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0595 |  | HotelLarge INFIL_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2007 | ClimateZone 1-8 | LargeHotel | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 1 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | LargeHotel | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral |  |  | 0.66 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 1 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | LargeHotel | Cafe | 31_169_34 | [6 empty] | 1.46 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 0.5 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | ClimateZone 1-3 | LargeHotel | Cafe | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Hotel | ASHRAE 189.1-2009Dining AreaFor Hotel |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 |  | LargeHotel Infil Quarter On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | ClimateZone 4-8 | LargeHotel | Cafe | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Hotel | ASHRAE 189.1-2009Dining AreaFor Hotel |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  | LargeHotel Infil Quarter On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | LargeHotel | Cafe | 31_169_34 | [6 empty] | 3.7 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 0.5 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
90.1-2007 | ClimateZone 1-8 | LargeHotel | Cafe | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | For Hotel | ASHRAE 90.1-2007Dining AreaFor Hotel |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 67 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 0.26 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2004 | ClimateZone 1-8 | LargeHotel | Cafe | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | For Hotel | ASHRAE 90.1-2004Dining AreaFor Hotel |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 67 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0595 |  | HotelLarge INFIL_SCH | [5 empty] | 0.5 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | LargeHotel | Cafe | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | For Hotel | ASHRAE 90.1-2010Dining AreaFor Hotel |  |  | 0.82 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 67 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 0.26 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | LargeHotel | Banquet | 230_196_120 | [6 empty] | 2.56 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 6.3 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | ClimateZone 1-3 | LargeHotel | Banquet | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0595 |  | LargeHotel Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | ClimateZone 4-8 | LargeHotel | Banquet | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  | LargeHotel Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | LargeHotel | Banquet | 230_196_120 | [6 empty] | 2.77 |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 67 | LargeHotel Bldg Occ | LargeHotel Activity |  | 0.2232 | LargeHotel Infil Quarter On | [5 empty] | 6.3 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
90.1-2007 | ClimateZone 1-8 | LargeHotel | Banquet | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | 0.06 | 5 | 0 | 67 | HotelLarge MeetingRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 3 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2004 | ClimateZone 1-8 | LargeHotel | Banquet | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 67 | HotelLarge MeetingRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0595 |  | HotelLarge INFIL_SCH | [5 empty] | 6.3 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | ClimateZone 1-8 | LargeHotel | Banquet | 230_196_120 | ASHRAE 90.1-2010 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2010Conference/Meeting/MultipurposeGeneral |  |  | 1.23 |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | 0.06 | 5 | 0 | 67 | HotelLarge MeetingRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0446 |  | HotelLarge INFIL_SCH | [5 empty] | 3 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2004 | ClimateZone 1-8 | MidriseApartment | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | ApartmentMidRise LTG_OFF_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 2.11 | ApartmentMidRise OCC_OFF_SCH | ApartmentMidRise Activity Schedule | 0.0595 |  | ApartmentMidRise INF_OFF_SCH | [5 empty] | 1.2 | 0 | 0.5 | 0 | ApartmentMidRise EQP_OFF_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH
90.1-2007 | ClimateZone 1-8 | MidriseApartment | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | ApartmentMidRise LTG_OFF_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 2.11 | ApartmentMidRise OCC_OFF_SCH | ApartmentMidRise Activity Schedule | 0.0446 |  | ApartmentMidRise INF_OFF_SCH | [5 empty] | 0.87 | 0 | 0.5 | 0 | ApartmentMidRise EQP_OFF_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH
90.1-2010 | ClimateZone 1-8 | MidriseApartment | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.7 | 0.2 | ApartmentMidRise LTG_OFF_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 2.11 | ApartmentMidRise OCC_OFF_SCH | ApartmentMidRise Activity Schedule | 0.0446 |  | ApartmentMidRise INF_OFF_SCH | [5 empty] | 0.87 | 0 | 0.5 | 0 | ApartmentMidRise EQP_OFF_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | MidriseApartment | Office | 120_230_199 | [6 empty] | 2.04 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 2.11 | MidriseApartment Office Occ | MidriseApartment Activity |  | 0.2232 | MidriseApartment Infil | [5 empty] | 1.2 | 0 | 0.5 | 0 | MidriseApartment Office Equip | MidriseApartment Office HtgSetp | MidriseApartment Office ClgSetp
189.1-2009 | ClimateZone 1-3 | MidriseApartment | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 2.11 | MidriseApartment Office Occ | MidriseApartment Activity | 0.0595 |  | MidriseApartment Infil | [5 empty] | 0.87 | 0 | 0.5 | 0 | MidriseApartment Office Equip | MidriseApartment Office HtgSetp | MidriseApartment Office ClgSetp
189.1-2009 | ClimateZone 4-8 | MidriseApartment | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 2.11 | MidriseApartment Office Occ | MidriseApartment Activity | 0.0446 |  | MidriseApartment Infil | [5 empty] | 0.87 | 0 | 0.5 | 0 | MidriseApartment Office Equip | MidriseApartment Office HtgSetp | MidriseApartment Office ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | MidriseApartment | Office | 120_230_199 | [6 empty] | 2.04 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 2.11 | MidriseApartment Office Occ | MidriseApartment Activity |  | 0.2232 | MidriseApartment Infil | [5 empty] | 1.2 | 0 | 0.5 | 0 | MidriseApartment Office Equip | MidriseApartment Office HtgSetp | MidriseApartment Office ClgSetp
DOE Ref 1980-2004 | ClimateZone 1-8 | MidriseApartment | Corridor | 169_31_31 | [6 empty] | 0.92 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Corridor Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  |  |  | 0.2232 | MidriseApartment Infil | [5 empty] | 0 | 0 | 0.5 | 0 |  | MidriseApartment Corridor HtgSetp | MidriseApartment Corridor ClgSetp
189.1-2009 | ClimateZone 1-3 | MidriseApartment | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Corridor Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  |  | 0.0595 |  | MidriseApartment Infil | [5 empty] | 0 | 0 | 0.5 | 0 |  | MidriseApartment Corridor HtgSetp | MidriseApartment Corridor ClgSetp
189.1-2009 | ClimateZone 4-8 | MidriseApartment | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Corridor Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  |  | 0.0446 |  | MidriseApartment Infil | [5 empty] | 0 | 0 | 0.5 | 0 |  | MidriseApartment Corridor HtgSetp | MidriseApartment Corridor ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | MidriseApartment | Corridor | 169_31_31 | [6 empty] | 0.92 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Corridor Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  |  |  | 0.2232 | MidriseApartment Infil | [5 empty] | 0 | 0 | 0.5 | 0 |  | MidriseApartment Corridor HtgSetp | MidriseApartment Corridor ClgSetp
90.1-2007 | ClimateZone 1-8 | MidriseApartment | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | ApartmentMidRise LTG_COR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | ApartmentMidRise All Off |  | 0.0446 |  | ApartmentMidRise INF_COR_SCH | [5 empty] | 0 | 0 | 0.5 | 0 |  | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH
90.1-2004 | ClimateZone 1-8 | MidriseApartment | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | ApartmentMidRise LTG_COR_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | ApartmentMidRise All Off |  | 0.0595 |  | ApartmentMidRise INF_COR_SCH | [5 empty] | 0 | 0 | 0.5 | 0 |  | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH
90.1-2010 | ClimateZone 1-8 | MidriseApartment | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral |  |  | 0.66 |  |  | 0 | 0.7 | 0.2 | ApartmentMidRise LTG_COR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | ApartmentMidRise All Off |  | 0.0446 |  | ApartmentMidRise INF_COR_SCH | [5 empty] | 0 | 0 | 0.5 | 0 |  | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | MidriseApartment | Apartment | 78_167_222 | [6 empty] | 0.36 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Apartment Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 0 | 0 | 2.63 | MidriseApartment Apartment Occ | MidriseApartment Activity |  | 0.2232 | MidriseApartment Infil | [5 empty] | 0.5 | 0 | 0.5 | 0 | MidriseApartment Apartment Equip | MidriseApartment Apartment HtgSetp | MidriseApartment Apartment ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | MidriseApartment DHW
189.1-2009 | ClimateZone 1-3 | MidriseApartment | Apartment | 78_167_222 | ASHRAE 189.1-2009 | Dormitory | Living Quarters | ASHRAE 189.1-2009DormitoryLiving Quarters |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Apartment Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 0 | 0 | 2.63 | MidriseApartment Apartment Occ | MidriseApartment Activity | 0.0595 |  | MidriseApartment Infil | [5 empty] | 0.36 | 0 | 0.5 | 0 | MidriseApartment Apartment Equip | MidriseApartment Apartment HtgSetp | MidriseApartment Apartment ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | MidriseApartment DHW
189.1-2009 | ClimateZone 4-8 | MidriseApartment | Apartment | 78_167_222 | ASHRAE 189.1-2009 | Dormitory | Living Quarters | ASHRAE 189.1-2009DormitoryLiving Quarters |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Apartment Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 0 | 0 | 2.63 | MidriseApartment Apartment Occ | MidriseApartment Activity | 0.0446 |  | MidriseApartment Infil | [5 empty] | 0.36 | 0 | 0.5 | 0 | MidriseApartment Apartment Equip | MidriseApartment Apartment HtgSetp | MidriseApartment Apartment ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | MidriseApartment DHW
DOE Ref Pre-1980 | ClimateZone 1-8 | MidriseApartment | Apartment | 78_167_222 | [6 empty] | 0.36 |  |  | 0 | 0.7 | 0.2 | MidriseApartment Apartment Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 0 | 0 | 2.63 | MidriseApartment Apartment Occ | MidriseApartment Activity |  | 0.223 | MidriseApartment Infil | [5 empty] | 0.5 | 0 | 0.5 | 0 | MidriseApartment Apartment Equip | MidriseApartment Apartment HtgSetp | MidriseApartment Apartment ClgSetp | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | MidriseApartment DHW
90.1-2007 | ClimateZone 1-8 | MidriseApartment | Apartment | 78_167_222 | ASHRAE 90.1-2007 | Dormitory | Living Quarters | ASHRAE 90.1-2007DormitoryLiving Quarters |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | ApartmentMidRise LTG_APT_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2004Hotels, Motels, Resorts, Dormitories Bedroom/living Room | 0 | 0 | 0 | 2.63 | ApartmentMidRise OCC_APT_SCH | ApartmentMidRise Activity Schedule | 0.0446 |  | ApartmentMidRise INF_APT_SCH | [5 empty] | 0.36 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
90.1-2004 | ClimateZone 1-8 | MidriseApartment | Apartment | 78_167_222 | ASHRAE 90.1-2004 | Dormitory | Living Quarters | ASHRAE 90.1-2004DormitoryLiving Quarters |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | ApartmentMidRise LTG_APT_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 0 | 0 | 2.63 | ApartmentMidRise OCC_APT_SCH | ApartmentMidRise Activity Schedule | 0.0595 |  | ApartmentMidRise INF_APT_SCH | [5 empty] | 0.5 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
90.1-2010 | ClimateZone 1-8 | MidriseApartment | Apartment | 78_167_222 | ASHRAE 90.1-2010 | Dormitory | Living Quarters | ASHRAE 90.1-2010DormitoryLiving Quarters |  |  | 0.38 |  |  | 0 | 0.7 | 0.2 | ApartmentMidRise LTG_APT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 | 0 | 2.63 | ApartmentMidRise OCC_APT_SCH | ApartmentMidRise Activity Schedule | 0.0446 |  | ApartmentMidRise INF_APT_SCH | [5 empty] | 0.36 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH | 3.5 | 950 | 0.0036842 | 43.3 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
90.1-2004 | ClimateZone 1-8 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 90.1-2004 | Whole Building | Office | ASHRAE 90.1-2004Whole BuildingOffice |  |  | 1 |  |  | 0 | 0.7 | 0.2 | OfficeSmall BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | OfficeSmall BLDG_OCC_SCH | OfficeSmall ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | OfficeSmall BLDG_EQUIP_SCH | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_OPTIMUM | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | OfficeSmall BLDG_SWH_SCH
90.1-2010 | ClimateZone 1-8 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 90.1-2010 | Whole Building | Office | ASHRAE 90.1-2010Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | OfficeSmall BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 5 | OfficeSmall BLDG_OCC_SCH | OfficeSmall ACTIVITY_SCH | 0.112 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.63 | 0 | 0.5 | 0 | OfficeSmall BLDG_EQUIP_SCH | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_OPTIMUM | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | OfficeSmall BLDG_SWH_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | WholeBuilding - Sm Office | 120_230_199 | [6 empty] | 1.81 |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | Small Office Bldg Occ | Small Office Activity |  | 0.2232 | Small Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Small Office Bldg Equip | Small Office HtgSetp | Small Office ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | Office SWH
189.1-2009 | ClimateZone 1-3 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | Small Office Bldg Occ | Small Office Activity | 0.0595 |  | Small Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Small Office Bldg Equip | Small Office HtgSetp | Small Office ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | Office SWH
189.1-2009 | ClimateZone 4-8 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | Small Office Bldg Occ | Small Office Activity | 0.0446 |  | Small Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Small Office Bldg Equip | Small Office HtgSetp | Small Office ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | Office SWH
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | WholeBuilding - Sm Office | 120_230_199 | [6 empty] | 1.81 |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | Small Office Bldg Occ | Small Office Activity |  | 0.2232 | Small Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Small Office Bldg Equip | Small Office HtgSetp | Small Office ClgSetp | 3 | 5502 | 0.00054526 | 43.3 | 0.2 | 0.05 | Office SWH
90.1-2004 | ClimateZone 1-8 | Office | WholeBuilding - Md Office | 120_230_199 | ASHRAE 90.1-2004 | Whole Building | Office | ASHRAE 90.1-2004Whole BuildingOffice |  |  | 1 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | OfficeMedium BLDG_SWH_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | WholeBuilding - Md Office | 120_230_199 | [6 empty] | 1.57 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | Medium Office Bldg Occ | Medium Office Activity |  | 0.2232 | Medium Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | Office SWH
189.1-2009 | ClimateZone 1-3 | Office | WholeBuilding - Md Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | Medium Office Bldg Occ | Medium Office Activity | 0.0595 |  | Medium Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | Office SWH
189.1-2009 | ClimateZone 4-8 | Office | WholeBuilding - Md Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 |  | Medium Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | Office SWH
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | WholeBuilding - Md Office | 120_230_199 | [6 empty] | 1.9 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | Medium Office Bldg Occ | Medium Office Activity |  | 0.2232 | Medium Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | Office SWH
90.1-2004 | ClimateZone 1-8 | Office | WholeBuilding - Lg Office | 120_230_199 | ASHRAE 90.1-2004 | Whole Building | Office | ASHRAE 90.1-2004Whole BuildingOffice |  |  | 1 |  |  | 0.4 | 0.4 | 0.2 | OfficeLarge BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | OfficeLarge BLDG_OCC_SCH | OfficeLarge ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | OfficeLarge BLDG_EQUIP_SCH | OfficeLarge HTGSETP_DC_SCH | OfficeLarge CLGSETP_DC_SCH | 27.7 | 53628 | 0.00051652 | 43.3 | 0.2 | 0.05 | OfficeLarge BLDG_SWH_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | WholeBuilding - Lg Office | 120_230_199 | [6 empty] | 1.5 |  |  | 0 | 0.7 | 0.2 | Large Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | Large Office Bldg Occ | Large Office Activity |  | 0.2232 | Large Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Large Office Bldg Equip | Large Office HtgSetp | Large Office ClgSetp | 63.9 | 498588 | 0.00012816 | 43.3 | 0.2 | 0.05 | Office SWH
189.1-2009 | ClimateZone 1-3 | Office | WholeBuilding - Lg Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Large Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | Large Office Bldg Occ | Large Office Activity | 0.0595 |  | Large Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Large Office Bldg Equip | Large Office HtgSetp | Large Office ClgSetp | 63.9 | 498588 | 0.00012816 | 43.3 | 0.2 | 0.05 | Office SWH
189.1-2009 | ClimateZone 4-8 | Office | WholeBuilding - Lg Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Large Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | Large Office Bldg Occ | Large Office Activity | 0.0446 |  | Large Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Large Office Bldg Equip | Large Office HtgSetp | Large Office ClgSetp | 63.9 | 498588 | 0.00012816 | 43.3 | 0.2 | 0.05 | Office SWH
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | WholeBuilding - Lg Office | 120_230_199 | [6 empty] | 1.9 |  |  | 0 | 0.7 | 0.2 | Large Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | Large Office Bldg Occ | Large Office Activity |  | 0.2232 | Large Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Large Office Bldg Equip | Large Office HtgSetp | Large Office ClgSetp | 63.9 | 498588 | 0.00012816 | 43.3 | 0.2 | 0.05 | Office SWH
90.1-2004 | ClimateZone 1-8 | Office | Vending | 230_157_120 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 3.85 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Office | Vending | 230_157_120 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 1 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 3.85 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Office | Vending | 230_157_120 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral |  |  | 0.66 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 1 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 3.85 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Vending | 230_157_120 | [6 empty] | 1.57 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Misc Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 3.85 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 1-3 | Office | Vending | 230_157_120 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Misc Occ | Office Activity | 0.0595 |  | Office Infil Quarter On | [5 empty] | 3.85 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 4-8 | Office | Vending | 230_157_120 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Misc Occ | Office Activity | 0.0446 |  | Office Infil Quarter On | [5 empty] | 3.85 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Vending | 230_157_120 | [6 empty] | 0.95 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Misc Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 3.85 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
90.1-2004 | ClimateZone 1-8 | Office | Storage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Office | Storage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Office | Storage | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Storage | 120_149_230 | [6 empty] | 1.27 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 1-3 | Office | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0595 |  | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 4-8 | Office | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0446 |  | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Storage | 120_149_230 | [6 empty] | 1.539 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
90.1-2004 | ClimateZone 1-8 | Office | Stair | 230_157_120 | ASHRAE 90.1-2004 | Stairs-Active | General | ASHRAE 90.1-2004Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Office | Stair | 230_157_120 | ASHRAE 90.1-2007 | Stairs-Active | General | ASHRAE 90.1-2007Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Office | Stair | 230_157_120 | ASHRAE 90.1-2010 | Stairway | General | ASHRAE 90.1-2010StairwayGeneral |  |  | 0.69 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Stair | 230_157_120 | [6 empty] | 0.942 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 1-3 | Office | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0595 |  | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 4-8 | Office | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity | 0.0446 |  | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Stair | 230_157_120 | [6 empty] | 1.14 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
90.1-2004 | ClimateZone 1-8 | Office | Restroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | OfficeMedium BLDG_SWH_SCH
90.1-2007 | ClimateZone 1-8 | Office | Restroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.07 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | OfficeMedium BLDG_SWH_SCH
90.1-2010 | ClimateZone 1-8 | Office | Restroom | 169_169_31 | ASHRAE 90.1-2010 | Restrooms | General | ASHRAE 90.1-2010RestroomsGeneral |  |  | 0.98 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.07 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | OfficeMedium BLDG_SWH_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Restroom | 169_169_31 | [6 empty] | 1.41 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 10 | Office Misc Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office Bldg Occ
189.1-2009 | ClimateZone 1-3 | Office | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0595 |  | Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office Bldg Occ
189.1-2009 | ClimateZone 4-8 | Office | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0446 |  | Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office Bldg Occ
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Restroom | 169_169_31 | [6 empty] | 1.71 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 10 | Office Misc Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp |  |  | 0.027628 | 43.3 | 0.2 | 0.05 | Medium Office Bldg Occ
90.1-2004 | ClimateZone 1-8 | Office | PrintRoom | 41_31_169 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 5.4 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Office | PrintRoom | 41_31_169 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 2.79 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Office | PrintRoom | 41_31_169 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 2.79 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | PrintRoom | 41_31_169 | [6 empty] | 1.55 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 10 | Office Misc Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 5.4 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 1-3 | Office | PrintRoom | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0595 |  | Office Infil Quarter On | [5 empty] | 2.79 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 4-8 | Office | PrintRoom | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 10 | Office Misc Occ | Office Activity | 0.0446 |  | Office Infil Quarter On | [5 empty] | 2.79 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | PrintRoom | 41_31_169 | [6 empty] | 1.881 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 10 | Office Misc Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 5.4 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
90.1-2004 | ClimateZone 1-8 | Office | OpenOffice | 120_230_199 | ASHRAE 90.1-2004 | Office-Open Plan | General | ASHRAE 90.1-2004Office-Open PlanGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5.25 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.96 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Office | OpenOffice | 120_230_199 | ASHRAE 90.1-2007 | Office-Open Plan | General | ASHRAE 90.1-2007Office-Open PlanGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 5.25 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.71 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Office | OpenOffice | 120_230_199 | ASHRAE 90.1-2010 | Office-Open Plan | General | ASHRAE 90.1-2010Office-Open PlanGeneral |  |  | 0.98 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 5.25 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.71 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | OpenOffice | 120_230_199 | [6 empty] | 1.73 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5.25 | Office Work Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0.96 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 1-3 | Office | OpenOffice | 120_230_199 | ASHRAE 189.1-2009 | Office-Open Plan | General | ASHRAE 189.1-2009Office-Open PlanGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5.25 | Office Work Occ | Office Activity | 0.0595 |  | Office Infil Quarter On | [5 empty] | 0.71 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 4-8 | Office | OpenOffice | 120_230_199 | ASHRAE 189.1-2009 | Office-Open Plan | General | ASHRAE 189.1-2009Office-Open PlanGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5.25 | Office Work Occ | Office Activity | 0.0446 |  | Office Infil Quarter On | [5 empty] | 0.71 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | OpenOffice | 120_230_199 | [6 empty] | 2.09 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5.25 | Office Work Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0.96 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
90.1-2004 | ClimateZone 1-8 | Office | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral |  |  | 1.3 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Office | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral |  |  | 1.3 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2004Office BuildingsMain entry lobbies | 0.06 | 5 | 0 | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.07 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Office | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral |  |  | 0.9 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2007Office BuildingsMain entry lobbies | 0.06 | 5 | 0 | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.07 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Lobby | 230_157_120 | [6 empty] | 2.04 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 10 | Office Misc Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 1-3 | Office | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 10 | Office Misc Occ | Office Activity | 0.0595 |  | Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 4-8 | Office | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 10 | Office Misc Occ | Office Activity | 0.0446 |  | Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Lobby | 230_157_120 | [6 empty] | 2.47 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 10 | Office Misc Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
90.1-2004 | ClimateZone 1-8 | Office | IT_Room | 41_31_169 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 5 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 2 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Office | IT_Room | 41_31_169 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Telephone/data entry | ASHRAE 62.1-2004Office BuildingsTelephone/data entry | 0.06 | 5 | 0 | 5 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 1.56 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Office | IT_Room | 41_31_169 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | ASHRAE 62.1-2007Office BuildingsTelephone/data entry | 0.06 | 5 | 0 | 5 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 1.56 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | IT_Room | 41_31_169 | [6 empty] | 1.55 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 5 | Office Misc Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 1-3 | Office | IT_Room | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 5 | Office Misc Occ | Office Activity | 0.0595 |  | Office Infil Quarter On | [5 empty] | 1.56 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 4-8 | Office | IT_Room | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 5 | Office Misc Occ | Office Activity | 0.0446 |  | Office Infil Quarter On | [5 empty] | 1.56 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | IT_Room | 41_31_169 | [6 empty] | 2.09 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 5 | Office Misc Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Elec/MechRoom | 41_31_169 | [6 empty] | 2.355 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 0 |  | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 1-3 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 0 |  | Office Activity | 0.0595 |  | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 4-8 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 0 |  | Office Activity | 0.0446 |  | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Elec/MechRoom | 41_31_169 | [6 empty] | 2.85 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 0 |  | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
90.1-2007 | ClimateZone 1-8 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral |  |  | 0.95 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Corridor | 169_31_31 | [6 empty] | 0.785 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Work Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0.29 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 1-3 | Office | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Work Occ | Office Activity | 0.0595 |  | Office Infil Quarter On | [5 empty] | 0.16 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 4-8 | Office | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Work Occ | Office Activity | 0.0446 |  | Office Infil Quarter On | [5 empty] | 0.16 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Corridor | 169_31_31 | [6 empty] | 0.95 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | Office Work Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0.29 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
90.1-2007 | ClimateZone 1-8 | Office | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 1 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.16 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | Office | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 1 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.29 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Office | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral |  |  | 0.66 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 1 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.16 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Conference | 230_196_120 | [6 empty] | 1.84 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 | 0 | 50 | Office Misc Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 1-3 | Office | Conference | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 | 0 | 50 | Office Misc Occ | Office Activity | 0.0595 |  | Office Infil Quarter On | [5 empty] | 0.37 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 4-8 | Office | Conference | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 | 0 | 50 | Office Misc Occ | Office Activity | 0.0446 |  | Office Infil Quarter On | [5 empty] | 0.37 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Conference | 230_196_120 | [6 empty] | 2.47 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 | 0 | 50 | Office Misc Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
90.1-2007 | ClimateZone 1-8 | Office | Conference | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Conference/meeting | ASHRAE 62.1-2004GeneralConference/meeting | 0.06 | 5 | 0 | 50 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | Office | Conference | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 | 0 | 50 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Office | Conference | 230_196_120 | ASHRAE 90.1-2010 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2010Conference/Meeting/MultipurposeGeneral |  |  | 1.23 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 | 0 | 50 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | ClosedOffice | 120_230_199 | [6 empty] | 1.727 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.75 | Office Work Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0.87 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 1-3 | Office | ClosedOffice | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.75 | Office Work Occ | Office Activity | 0.0595 |  | Office Infil Quarter On | [5 empty] | 0.64 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 4-8 | Office | ClosedOffice | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.75 | Office Work Occ | Office Activity | 0.0446 |  | Office Infil Quarter On | [5 empty] | 0.64 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | ClosedOffice | 120_230_199 | [6 empty] | 2.09 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.75 | Office Work Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 0.87 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
90.1-2007 | ClimateZone 1-8 | Office | ClosedOffice | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 4.75 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.64 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | Office | ClosedOffice | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.75 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.87 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Office | ClosedOffice | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 4.75 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.64 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | BreakRoom | 230_157_120 | [6 empty] | 1.884 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 50 | Office Misc Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 5.63 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 1-3 | Office | BreakRoom | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 50 | Office Misc Occ | Office Activity | 0.0595 |  | Office Infil Quarter On | [5 empty] | 4.46 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | ClimateZone 4-8 | Office | BreakRoom | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 50 | Office Misc Occ | Office Activity | 0.0446 |  | Office Infil Quarter On | [5 empty] | 4.46 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | BreakRoom | 230_157_120 | [6 empty] | 2.28 |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 50 | Office Misc Occ | Office Activity |  | 0.2232 | Office Infil Quarter On | [5 empty] | 5.63 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
90.1-2007 | ClimateZone 1-8 | Office | BreakRoom | 230_157_120 | ASHRAE 90.1-2007 | Lounge/Recreation | General | ASHRAE 90.1-2007Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Conference/meeting | ASHRAE 62.1-2004GeneralConference/meeting | 0.06 | 5 | 0 | 50 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 4.46 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | Office | BreakRoom | 230_157_120 | ASHRAE 90.1-2004 | Lounge/Recreation | General | ASHRAE 90.1-2004Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 | 0 | 50 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 5.58 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Office | BreakRoom | 230_157_120 | ASHRAE 90.1-2010 | Lounge/Recreation | General | ASHRAE 90.1-2010Lounge/RecreationGeneral |  |  | 0.73 |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 | 0 | 50 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 4.46 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | Office | Attic | 120_149_230 | [23 empty] | 0.0595 |  | OfficeMedium INFIL_SCH_PNNL
90.1-2010 | ClimateZone 1-8 | Office | Attic | 120_149_230 | [23 empty] | 0.112 |  | OfficeMedium INFIL_SCH_PNNL
DOE Ref 1980-2004 | ClimateZone 1-8 | Office | Attic | 120_149_230 | [24 empty] | 0.2232 | Small Office Infil Quarter On
189.1-2009 | ClimateZone 1-3 | Office | Attic | 120_149_230 | [23 empty] | 0.0595 |  | Small Office Infil Quarter On
189.1-2009 | ClimateZone 4-8 | Office | Attic | 120_149_230 | [23 empty] | 0.0446 |  | Small Office Infil Quarter On
DOE Ref Pre-1980 | ClimateZone 1-8 | Office | Attic | 120_149_230 | [24 empty] | 0.2232 | Small Office Infil Quarter On
90.1-2004 | ClimateZone 1-8 | Outpatient | Xray | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.3 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2007 | ClimateZone 1-8 | Outpatient | Xray | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.95 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2010 | ClimateZone 1-8 | Outpatient | Xray | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Radiology/Imaging | ASHRAE 90.1-2010HospitalRadiology/Imaging |  |  | 1.32 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.95 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Xray | 169_31_159 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | ClimateZone 1-3 | Outpatient | Xray | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 0.95 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | ClimateZone 4-8 | Outpatient | Xray | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 0.95 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Xray | 169_31_159 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 900 | 0.0011111 | 43.3 | 0.2 | 0.05 | Outpatient SWH
90.1-2004 | ClimateZone 1-8 | Outpatient | Toilet | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.4 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | OutPatientHealthCare Hours_of_operation
90.1-2007 | ClimateZone 1-8 | Outpatient | Toilet | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.29 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | OutPatientHealthCare Hours_of_operation
90.1-2010 | ClimateZone 1-8 | Outpatient | Toilet | 169_169_31 | ASHRAE 90.1-2010 | Restrooms | General | ASHRAE 90.1-2010RestroomsGeneral |  |  | 0.98 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.29 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | OutPatientHealthCare Hours_of_operation
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Toilet | 169_169_31 | [6 empty] | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 0.4 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
189.1-2009 | ClimateZone 1-3 | Outpatient | Toilet | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 0.29 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
189.1-2009 | ClimateZone 4-8 | Outpatient | Toilet | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 0.29 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Toilet | 169_169_31 | [6 empty] | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 0.4 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 90 | 0.31 | 1 | 34.0754 | 0.63103 | Outpatient_FirstFlr_Exhaust
90.1-2004 | ClimateZone 1-8 | Outpatient | Stair | 230_157_120 | ASHRAE 90.1-2004 | Stairs-Active | General | ASHRAE 90.1-2004Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Outpatient | Stair | 230_157_120 | ASHRAE 90.1-2007 | Stairs-Active | General | ASHRAE 90.1-2007Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | Stair | 230_157_120 | ASHRAE 90.1-2010 | Stairway | General | ASHRAE 90.1-2010StairwayGeneral |  |  | 0.69 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Stair | 230_157_120 | [6 empty] | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Stair | 230_157_120 | [6 empty] | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2004 | ClimateZone 1-8 | Outpatient | Soil Work | 204_120_230 | ASHRAE 90.1-2004 | Hospital | Medical Supply | ASHRAE 90.1-2004HospitalMedical Supply |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | OutPatientHealthCare Hours_of_operation
90.1-2007 | ClimateZone 1-8 | Outpatient | Soil Work | 204_120_230 | ASHRAE 90.1-2007 | Hospital | Medical Supply | ASHRAE 90.1-2007HospitalMedical Supply |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | OutPatientHealthCare Hours_of_operation
90.1-2010 | ClimateZone 1-8 | Outpatient | Soil Work | 204_120_230 | ASHRAE 90.1-2010 | Hospital | Medical Supply | ASHRAE 90.1-2010HospitalMedical Supply |  |  | 1.27 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | OutPatientHealthCare Hours_of_operation
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Soil Work | 204_120_230 | [6 empty] | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
189.1-2009 | ClimateZone 1-3 | Outpatient | Soil Work | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Medical Supply | ASHRAE 189.1-2009HospitalMedical Supply |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
189.1-2009 | ClimateZone 4-8 | Outpatient | Soil Work | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Medical Supply | ASHRAE 189.1-2009HospitalMedical Supply |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Soil Work | 204_120_230 | [6 empty] | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 210 | 0.31 | 1 | 79.5093 | 0.63103 | Outpatient_FirstFlr_Exhaust
90.1-2004 | ClimateZone 1-8 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 3 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2007 | ClimateZone 1-8 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency |  |  | 2.7 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2010 | ClimateZone 1-8 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Emergency | ASHRAE 90.1-2010HospitalEmergency |  |  | 2.26 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | ProcedureRoom | 169_31_159 | [6 empty] | 1.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | ClimateZone 1-3 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | ClimateZone 4-8 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency |  |  | 2.43 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | ProcedureRoom | 169_31_159 | [6 empty] | 1.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 285 | 0.0035088 | 43.3 | 0.2 | 0.05 | Outpatient SWH
90.1-2004 | ClimateZone 1-8 | Outpatient | PreOp | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Patient Room | ASHRAE 90.1-2004HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2007 | ClimateZone 1-8 | Outpatient | PreOp | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Patient Room | ASHRAE 90.1-2007HospitalPatient Room |  |  | 0.7 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2010 | ClimateZone 1-8 | Outpatient | PreOp | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Patient Room | ASHRAE 90.1-2010HospitalPatient Room |  |  | 0.62 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | PreOp | 169_31_159 | [6 empty] | 1.4 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | ClimateZone 1-3 | Outpatient | PreOp | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | ClimateZone 4-8 | Outpatient | PreOp | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | PreOp | 169_31_159 | [6 empty] | 1.4 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 | 0 | 0 | 9.29 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 263.5 | 0.0037951 | 43.3 | 0.2 | 0.05 | Outpatient SWH
90.1-2004 | ClimateZone 1-8 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 90.1-2004 | Hospital | Physical Therapy | ASHRAE 90.1-2004HospitalPhysical Therapy |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.5 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2007 | ClimateZone 1-8 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 90.1-2007 | Hospital | Physical Therapy | ASHRAE 90.1-2007HospitalPhysical Therapy |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.09 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2010 | ClimateZone 1-8 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 90.1-2010 | Hospital | Physical Therapy | ASHRAE 90.1-2010HospitalPhysical Therapy |  |  | 0.91 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.09 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | PhysicalTherapy | 154_230_120 | [6 empty] | 1.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.5 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | ClimateZone 1-3 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 189.1-2009 | Hospital | Physical Therapy | ASHRAE 189.1-2009HospitalPhysical Therapy |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 1.09 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | ClimateZone 4-8 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 189.1-2009 | Hospital | Physical Therapy | ASHRAE 189.1-2009HospitalPhysical Therapy |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 1.09 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | PhysicalTherapy | 154_230_120 | [6 empty] | 1.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.5 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 946 | 0.0010571 | 43.3 | 0.2 | 0.05 | Outpatient SWH
90.1-2004 | ClimateZone 1-8 | Outpatient | PACU | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Recovery | ASHRAE 90.1-2004HospitalRecovery |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 3 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2007 | ClimateZone 1-8 | Outpatient | PACU | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Recovery | ASHRAE 90.1-2007HospitalRecovery |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2010 | ClimateZone 1-8 | Outpatient | PACU | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Recovery | ASHRAE 90.1-2010HospitalRecovery |  |  | 1.15 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | PACU | 169_31_159 | [6 empty] | 2.3 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | ClimateZone 1-3 | Outpatient | PACU | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Recovery | ASHRAE 189.1-2009HospitalRecovery |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | ClimateZone 4-8 | Outpatient | PACU | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Recovery | ASHRAE 189.1-2009HospitalRecovery |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | PACU | 169_31_159 | [6 empty] | 2.3 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH
90.1-2004 | ClimateZone 1-8 | Outpatient | OR | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Operating Room | ASHRAE 90.1-2004HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | 23.9 | 0 | 0 | 0.5 | OutPatientHealthCare BLDG_EQUIP_SCH | 4 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare OR_HTGSETP_SCH | OutPatientHealthCare OR_CLGSETP_SCH | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2007 | ClimateZone 1-8 | Outpatient | OR | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Operating Room | ASHRAE 90.1-2007HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | 17.4 | 0 | 0 | 0.5 | OutPatientHealthCare BLDG_EQUIP_SCH | 2.92 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare OR_HTGSETP_SCH | OutPatientHealthCare OR_CLGSETP_SCH | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2010 | ClimateZone 1-8 | Outpatient | OR | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Operating Room | ASHRAE 90.1-2010HospitalOperating Room |  |  | 1.89 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | 17.4 | 0 | 0 | 0.5 | OutPatientHealthCare BLDG_EQUIP_SCH | 2.92 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare OR_HTGSETP_SCH | OutPatientHealthCare OR_CLGSETP_SCH | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | OR | 169_31_159 | [6 empty] | 7 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | 23.9 | 0 | 0 | 0.5 | Outpatient Bldg Equip | 4 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient OR HtgSetp | Outpatient OR ClgSetp | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | ClimateZone 1-3 | Outpatient | OR | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | 17.4 | 0 | 0 | 0.5 | Outpatient Bldg Equip | 2.92 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient OR HtgSetp | Outpatient OR ClgSetp | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | ClimateZone 4-8 | Outpatient | OR | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | 17.4 | 0 | 0 | 0.5 | Outpatient Bldg Equip | 2.92 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient OR HtgSetp | Outpatient OR ClgSetp | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | OR | 169_31_159 | [6 empty] | 7 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | 0 | 0 | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | 23.9 | 0 | 0 | 0.5 | Outpatient Bldg Equip | 4 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient OR HtgSetp | Outpatient OR ClgSetp | 6 | 470 | 0.012766 | 43.3 | 0.2 | 0.05 | Outpatient SWH
90.1-2004 | ClimateZone 1-8 | Outpatient | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Outpatient | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Office | 120_230_199 | [6 empty] | 1.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Office | 120_230_199 | [6 empty] | 1.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2004 | ClimateZone 1-8 | Outpatient | NurseStation | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Outpatient | NurseStation | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station |  |  | 1 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | NurseStation | 31_162_169 | ASHRAE 90.1-2010 | Hospital | Nurse Station | ASHRAE 90.1-2010HospitalNurse Station |  |  | 0.87 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | NurseStation | 31_162_169 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | NurseStation | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | NurseStation | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | NurseStation | 31_162_169 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2004 | ClimateZone 1-8 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | OutPatientHealthCare Hours_of_operation
90.1-2007 | ClimateZone 1-8 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | OutPatientHealthCare Hours_of_operation
90.1-2010 | ClimateZone 1-8 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 90.1-2010 | Hospital | Radiology/Imaging | ASHRAE 90.1-2010HospitalRadiology/Imaging |  |  | 1.32 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | OutPatientHealthCare Hours_of_operation
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | MRI_Control | 136_78_222 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
189.1-2009 | ClimateZone 1-3 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
189.1-2009 | ClimateZone 4-8 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | MRI_Control | 136_78_222 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 168 | 0.0059524 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 168 | 0.31 | 1 | 63.6075 | 0.37862 | Outpatient_FirstFlr_Exhaust
90.1-2004 | ClimateZone 1-8 | Outpatient | MRI | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 53.06 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | OutPatientHealthCare Hours_of_operation
90.1-2007 | ClimateZone 1-8 | Outpatient | MRI | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology |  |  | 0.4 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 38.63 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | OutPatientHealthCare Hours_of_operation
90.1-2010 | ClimateZone 1-8 | Outpatient | MRI | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Radiology/Imaging | ASHRAE 90.1-2010HospitalRadiology/Imaging |  |  | 1.32 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 38.63 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | OutPatientHealthCare Hours_of_operation
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | MRI | 169_31_159 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 53.06 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
189.1-2009 | ClimateZone 1-3 | Outpatient | MRI | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 38.63 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
189.1-2009 | ClimateZone 4-8 | Outpatient | MRI | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology |  |  | 0.36 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 38.63 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | MRI | 169_31_159 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 53.06 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 440 | 0.0022727 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 440 | 0.31 | 1 | 166.5909 | 0.37862 | Outpatient_FirstFlr_Exhaust
90.1-2004 | ClimateZone 1-8 | Outpatient | MedGas | 204_120_230 | ASHRAE 90.1-2004 | Active Storage | For Hospital | ASHRAE 90.1-2004Active StorageFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Outpatient | MedGas | 204_120_230 | ASHRAE 90.1-2007 | Active Storage | For Hospital | ASHRAE 90.1-2007Active StorageFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.07 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | MedGas | 204_120_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.07 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | MedGas | 204_120_230 | [6 empty] | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 0.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | MedGas | 204_120_230 | ASHRAE 189.1-2009 | Active Storage | For Hospital | ASHRAE 189.1-2009Active StorageFor Hospital |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | MedGas | 204_120_230 | ASHRAE 189.1-2009 | Active Storage | For Hospital | ASHRAE 189.1-2009Active StorageFor Hospital |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | MedGas | 204_120_230 | [6 empty] | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 0.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2004 | ClimateZone 1-8 | Outpatient | Lounge | 230_157_120 | ASHRAE 90.1-2004 | Lounge/Recreation | For Hospital | ASHRAE 90.1-2004Lounge/RecreationFor Hospital |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 13.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 3 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Outpatient | Lounge | 230_157_120 | ASHRAE 90.1-2007 | Lounge/Recreation | For Hospital | ASHRAE 90.1-2007Lounge/RecreationFor Hospital |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 | 0 | 13.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | Lounge | 230_157_120 | ASHRAE 90.1-2010 | Lounge/Recreation | For Hospital | ASHRAE 90.1-2010Lounge/RecreationFor Hospital |  |  | 1.07 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 | 0 | 13.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Lounge | 230_157_120 | [6 empty] | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | Lounge | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | For Hospital | ASHRAE 189.1-2009Lounge/RecreationFor Hospital |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | Lounge | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | For Hospital | ASHRAE 189.1-2009Lounge/RecreationFor Hospital |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Lounge | 230_157_120 | [6 empty] | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2004 | ClimateZone 1-8 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 90.1-2004 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2004Dressing/Locker/Fitting RoomGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 3 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 90.1-2007 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2007Dressing/Locker/Fitting RoomGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 90.1-2010 | Locker Room | General | ASHRAE 90.1-2010Locker RoomGeneral |  |  | 0.75 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | LockerRoom | 169_169_31 | [6 empty] | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | LockerRoom | 169_169_31 | [6 empty] | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 | 0 | 0 | 13.94 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2004 | ClimateZone 1-8 | Outpatient | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 27.87 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Outpatient | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2004Office BuildingsMain entry lobbies | 0.06 | 5 | 0 | 27.87 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2007Office BuildingsMain entry lobbies | 0.06 | 5 | 0 | 27.87 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Lobby | 230_157_120 | [6 empty] | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 27.87 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 27.87 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 27.87 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Lobby | 230_157_120 | [6 empty] | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 27.87 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Janitor | 120_149_230 | [6 empty] | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | Janitor | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | Janitor | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Janitor | 120_149_230 | [6 empty] | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2004 | ClimateZone 1-8 | Outpatient | Janitor | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Outpatient | Janitor | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | Janitor | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | IT_Room | 41_31_169 | [6 empty] | 1.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | 0 | 20 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | IT_Room | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | 0 | 20 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | IT_Room | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | 0 | 20 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | IT_Room | 41_31_169 | [6 empty] | 1.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | 0 | 20 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2007 | ClimateZone 1-8 | Outpatient | IT_Room | 41_31_169 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Telephone/data entry | ASHRAE 62.1-2004Office BuildingsTelephone/data entry | 0.06 | 5 | 0 | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | Outpatient | IT_Room | 41_31_169 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | 0 | 20 | 0 | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | IT_Room | 41_31_169 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | ASHRAE 62.1-2007Office BuildingsTelephone/data entry | 0.06 | 5 | 0 | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Hall | 169_31_31 | [6 empty] | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 0.4 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | Hall | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 0.29 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | Hall | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 0.29 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Hall | 169_31_31 | [6 empty] | 0.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 0.4 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2007 | ClimateZone 1-8 | Outpatient | Hall | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | ASHRAE 90.1-2007Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.29 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | Outpatient | Hall | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | ASHRAE 90.1-2004Corridor/TransitionFor Hospital |  |  | 1 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.4 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | Hall | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | For Hospital | ASHRAE 90.1-2010Corridor/TransitionFor Hospital |  |  | 0.89 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.29 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Exam | 136_78_222 | [6 empty] | 1.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | Exam | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Exam/Treatment | ASHRAE 189.1-2009HospitalExam/Treatment |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | Exam | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Exam/Treatment | ASHRAE 189.1-2009HospitalExam/Treatment |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Exam | 136_78_222 | [6 empty] | 1.6 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2004 | ClimateZone 1-8 | Outpatient | Exam | 136_78_222 | ASHRAE 90.1-2004 | Hospital | Exam/Treatment | ASHRAE 90.1-2004HospitalExam/Treatment |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Outpatient | Exam | 136_78_222 | ASHRAE 90.1-2007 | Hospital | Exam/Treatment | ASHRAE 90.1-2007HospitalExam/Treatment |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | Exam | 136_78_222 | ASHRAE 90.1-2010 | Hospital | Exam/Treatment | ASHRAE 90.1-2010HospitalExam/Treatment |  |  | 1.66 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Elec/MechRoom | 41_31_169 | [6 empty] | 0.7 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 5 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 3.64 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 3.64 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Elec/MechRoom | 41_31_169 | [6 empty] | 0.7 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 5 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2004 | ClimateZone 1-8 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 5 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 3.64 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral |  |  | 0.95 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 3.64 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | DressingRoom | 136_78_222 | [6 empty] | 1.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | DressingRoom | 136_78_222 | [6 empty] | 1.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 4.65 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2007 | ClimateZone 1-8 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 90.1-2007 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2007Dressing/Locker/Fitting RoomGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Patient rooms | ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPatient rooms | 0 | 25 | 0 | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 90.1-2004 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2004Dressing/Locker/Fitting RoomGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 90.1-2010 | Dressing/Fitting Room | For Retail | ASHRAE 90.1-2010Dressing/Fitting RoomFor Retail |  |  | 0.87 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Patient rooms | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPatient rooms | 0 | 25 | 0 | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Conference | 230_196_120 | [6 empty] | 1.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 46.45 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | Conference | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 46.45 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | Conference | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 46.45 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Conference | 230_196_120 | [6 empty] | 1.8 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 46.45 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2007 | ClimateZone 1-8 | Outpatient | Conference | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Conference/meeting | ASHRAE 62.1-2004GeneralConference/meeting | 0.06 | 5 | 0 | 46.45 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.73 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | Outpatient | Conference | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 46.45 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | Conference | 230_196_120 | ASHRAE 90.1-2010 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2010Conference/Meeting/MultipurposeGeneral |  |  | 1.23 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 | 0 | 46.45 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.73 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | CleanWork | 204_120_230 | [6 empty] | 1.3 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | CleanWork | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Medical Supply | ASHRAE 189.1-2009HospitalMedical Supply |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | CleanWork | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Medical Supply | ASHRAE 189.1-2009HospitalMedical Supply |  |  | 1.26 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | CleanWork | 204_120_230 | [6 empty] | 1.3 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2004 | ClimateZone 1-8 | Outpatient | CleanWork | 204_120_230 | ASHRAE 90.1-2004 | Hospital | Medical Supply | ASHRAE 90.1-2004HospitalMedical Supply |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Outpatient | CleanWork | 204_120_230 | ASHRAE 90.1-2007 | Hospital | Medical Supply | ASHRAE 90.1-2007HospitalMedical Supply |  |  | 1.4 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | CleanWork | 204_120_230 | ASHRAE 90.1-2010 | Hospital | Medical Supply | ASHRAE 90.1-2010HospitalMedical Supply |  |  | 1.27 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 | 0 | 0 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Cafe | 31_169_34 | [6 empty] | 1.3 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 92.94 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | Cafe | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 92.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | Cafe | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 92.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Cafe | 31_169_34 | [6 empty] | 1.3 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 92.94 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2007 | ClimateZone 1-8 | Outpatient | Cafe | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 92.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.73 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | Outpatient | Cafe | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 92.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | Cafe | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | General | ASHRAE 90.1-2010Dining AreaGeneral |  |  | 0.65 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 92.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.73 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | BioHazard | 204_120_230 | [6 empty] | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 0.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 1-3 | Outpatient | BioHazard | 204_120_230 | ASHRAE 189.1-2009 | Active Storage | For Hospital | ASHRAE 189.1-2009Active StorageFor Hospital |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | ClimateZone 4-8 | Outpatient | BioHazard | 204_120_230 | ASHRAE 189.1-2009 | Active Storage | For Hospital | ASHRAE 189.1-2009Active StorageFor Hospital |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | BioHazard | 204_120_230 | [6 empty] | 1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 0.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
90.1-2004 | ClimateZone 1-8 | Outpatient | BioHazard | 204_120_230 | ASHRAE 90.1-2004 | Active Storage | For Hospital | ASHRAE 90.1-2004Active StorageFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Outpatient | BioHazard | 204_120_230 | ASHRAE 90.1-2007 | Active Storage | For Hospital | ASHRAE 90.1-2007Active StorageFor Hospital |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.07 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Outpatient | BioHazard | 204_120_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.07 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Outpatient | Anesthesia | 204_120_230 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
189.1-2009 | ClimateZone 1-3 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0595 |  | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
189.1-2009 | ClimateZone 4-8 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room |  |  | 1.98 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
DOE Ref Pre-1980 | ClimateZone 1-8 | Outpatient | Anesthesia | 204_120_230 | [6 empty] | 2.1 |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | Outpatient_FirstFlr_Exhaust
90.1-2004 | ClimateZone 1-8 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 90.1-2004 | Hospital | Operating Room | ASHRAE 90.1-2004HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | OutPatientHealthCare Hours_of_operation
90.1-2007 | ClimateZone 1-8 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 90.1-2007 | Hospital | Operating Room | ASHRAE 90.1-2007HospitalOperating Room |  |  | 2.2 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | OutPatientHealthCare Hours_of_operation
90.1-2010 | ClimateZone 1-8 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 90.1-2010 | Hospital | Operating Room | ASHRAE 90.1-2010HospitalOperating Room |  |  | 1.89 |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 | 0 | 0 | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 108 | 0.0092593 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1.3333 | 144 | 0.31 | 1 | 54.5207 | 0.50482 | OutPatientHealthCare Hours_of_operation
90.1-2004 | ClimateZone 1-8 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_BATH_SCH | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | SchoolPrimary BLDG_LIGHT_BATH_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | SchoolPrimary BLDG_SWH_SCH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
90.1-2007 | ClimateZone 1-8 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_BATH_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | SchoolPrimary BLDG_LIGHT_BATH_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | SchoolPrimary BLDG_SWH_SCH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
90.1-2010 | ClimateZone 1-8 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2010 | Restrooms | General | ASHRAE 90.1-2010RestroomsGeneral |  |  | 0.98 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_BATH_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | SchoolPrimary BLDG_LIGHT_BATH_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | SchoolPrimary BLDG_SWH_SCH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
DOE Ref 1980-2004 | ClimateZone 1-8 | PrimarySchool | Restroom | 169_169_31 | [6 empty] | 0.9 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
189.1-2009 | ClimateZone 1-3 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 |  | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
189.1-2009 | ClimateZone 4-8 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
DOE Ref Pre-1980 | ClimateZone 1-8 | PrimarySchool | Restroom | 169_169_31 | [6 empty] | 0.9 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 56.5 | 2045 | 0.027628 | 43.3 | 0.2 | 0.05 | PrimarySchool SWH | 0.29338 | 600 | 0.338 | 0.5 | 104.1753 | 0.050938
DOE Ref 1980-2004 | ClimateZone 1-8 | PrimarySchool | Office | 120_230_199 | [6 empty] | 1.89 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.65 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 1 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | ClimateZone 1-3 | PrimarySchool | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.65 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 |  | PrimarySchool Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | ClimateZone 4-8 | PrimarySchool | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.65 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  | PrimarySchool Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | PrimarySchool | Office | 120_230_199 | [6 empty] | 1.89 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.65 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 1 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
90.1-2004 | ClimateZone 1-8 | PrimarySchool | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | SchoolPrimary BLDG_LIGHT_OFFICE_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | PrimarySchool | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 5 | SchoolPrimary BLDG_LIGHT_OFFICE_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.73 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | PrimarySchool | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 5 | SchoolPrimary BLDG_LIGHT_OFFICE_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.73 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | PrimarySchool | Mechanical | 41_31_169 | [6 empty] | 0.77 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
189.1-2009 | ClimateZone 1-3 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 |  | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
189.1-2009 | ClimateZone 4-8 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | PrimarySchool | Mechanical | 41_31_169 | [6 empty] | 0.77 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
90.1-2004 | ClimateZone 1-8 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SchoolPrimary BLDG_LIGHT_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0 | SchoolPrimary BLDG_LIGHT_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral |  |  | 0.95 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0 | SchoolPrimary BLDG_LIGHT_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | PrimarySchool | Lobby | 230_157_120 | [6 empty] | 1.14 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | ClimateZone 1-3 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 |  | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | ClimateZone 4-8 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | PrimarySchool | Lobby | 230_157_120 | [6 empty] | 1.3 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
90.1-2007 | ClimateZone 1-8 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | PrimarySchool | Library | 230_196_120 | [6 empty] | 2.11 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 | 0 | 21.36 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 1.39 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | ClimateZone 1-3 | PrimarySchool | Library | 230_196_120 | ASHRAE 189.1-2009 | Library | Reading Area | ASHRAE 189.1-2009LibraryReading Area |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 | 0 | 21.36 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 |  | PrimarySchool Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | ClimateZone 4-8 | PrimarySchool | Library | 230_196_120 | ASHRAE 189.1-2009 | Library | Reading Area | ASHRAE 189.1-2009LibraryReading Area |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 | 0 | 21.36 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  | PrimarySchool Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | PrimarySchool | Library | 230_196_120 | [6 empty] | 2.11 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 | 0 | 21.36 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 1.39 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
90.1-2007 | ClimateZone 1-8 | PrimarySchool | Library | 230_196_120 | ASHRAE 90.1-2007 | Library | Reading Area | ASHRAE 90.1-2007LibraryReading Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | ASHRAE 62.1-2004 | Educational Facilities | Media center | ASHRAE 62.1-2004Educational FacilitiesMedia center | 0.12 | 10 | 0 | 10 | SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1.02 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | PrimarySchool | Library | 230_196_120 | ASHRAE 90.1-2004 | Library | Reading Area | ASHRAE 90.1-2004LibraryReading Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 | 0 | 10 | SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  | SchoolPrimary INFIL_SCH_PNNL | 0 |  |  |  |  | 1.39 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | PrimarySchool | Library | 230_196_120 | ASHRAE 90.1-2010 | Library | Reading Area | ASHRAE 90.1-2010LibraryReading Area |  |  | 0.93 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | ASHRAE 62.1-2007 | Educational Facilities | Media center | ASHRAE 62.1-2007Educational FacilitiesMedia center | 0.12 | 10 | 0 | 10 | SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1.02 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | PrimarySchool | Kitchen | 78_222_133 | [6 empty] | 1.6 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 13.93 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | 302.6 | 0.1 | 0.2 | 0.7 | PrimarySchool Kitchen Gas | 17.7 | 0.25 | 0.3 | 0.2 | PrimarySchool Kitchen Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool Kitchen Exhaust
189.1-2009 | ClimateZone 1-3 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 13.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 |  | PrimarySchool Infil | 220.5 | 0.1 | 0.2 | 0.7 | PrimarySchool Kitchen Gas | 13.13 | 0.25 | 0.3 | 0.2 | PrimarySchool Kitchen Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool Kitchen Exhaust
189.1-2009 | ClimateZone 4-8 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 13.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  | PrimarySchool Infil | 220.5 | 0.1 | 0.2 | 0.7 | PrimarySchool Kitchen Gas | 13.13 | 0.25 | 0.3 | 0.2 | PrimarySchool Kitchen Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool Kitchen Exhaust
DOE Ref Pre-1980 | ClimateZone 1-8 | PrimarySchool | Kitchen | 78_222_133 | [6 empty] | 1.6 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 13.93 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | 302.6 | 0.1 | 0.2 | 0.7 | PrimarySchool Kitchen Gas | 17.7 | 0.25 | 0.3 | 0.2 | PrimarySchool Kitchen Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | PrimarySchool SWH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | PrimarySchool Kitchen Exhaust
90.1-2007 | ClimateZone 1-8 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 13.93 | SchoolPrimary BLDG_LIGHT_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | 220.5 | 0.1 | 0.2 | 0.7 | SchoolPrimary KITCHEN_GAS_EQUIP_SCH | 17.7 | 0.25 | 0.3 | 0.2 | SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | SchoolPrimary BLDG_SWH_SCH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | SchoolPrimary Kitchen_Exhaust_SCH
90.1-2004 | ClimateZone 1-8 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 13.93 | SchoolPrimary BLDG_LIGHT_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  | SchoolPrimary INFIL_SCH_PNNL | 302.6 | 0.1 | 0.2 | 0.7 | SchoolPrimary KITCHEN_GAS_EQUIP_SCH | 17.7 | 0.25 | 0.3 | 0.2 | SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | SchoolPrimary BLDG_SWH_SCH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | SchoolPrimary Kitchen_Exhaust_SCH
90.1-2010 | ClimateZone 1-8 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 13.93 | SchoolPrimary BLDG_LIGHT_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | 220.5 | 0.1 | 0.2 | 0.7 | SchoolPrimary KITCHEN_GAS_EQUIP_SCH | 17.7 | 0.25 | 0.3 | 0.2 | SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | 100 | 1808 | 0.05531 | 49 | 0.2 | 0.05 | SchoolPrimary BLDG_SWH_SCH | 0.7 | 3300 | 0.338 | 0.5 | 572.9644 | 0.12154 | SchoolPrimary Kitchen_Exhaust_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | PrimarySchool | Gym | 154_230_120 | [6 empty] | 1.07 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 21.2 | 0 | 27.9 | PrimarySchool Gym Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | ClimateZone 1-3 | PrimarySchool | Gym | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 21.2 | 0 | 27.9 | PrimarySchool Gym Occ | PrimarySchool Activity | 0.0595 |  | PrimarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | ClimateZone 4-8 | PrimarySchool | Gym | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 21.2 | 0 | 27.9 | PrimarySchool Gym Occ | PrimarySchool Activity | 0.0446 |  | PrimarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | PrimarySchool | Gym | 154_230_120 | [6 empty] | 0.8 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 21.2 | 0 | 27.9 | PrimarySchool Gym Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
90.1-2007 | ClimateZone 1-8 | PrimarySchool | Gym | 154_230_120 | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Playing Area | ASHRAE 90.1-2007Gymnasium/Exercise CenterPlaying Area |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_GYM_SCH | ASHRAE 62.1-2004 | Sports and Entertainment | Gym, stadium (play area) | ASHRAE 62.1-2004Sports and EntertainmentGym, stadium (play area) | 0.3 | 0 | 0 | 30 | SchoolPrimary BLDG_LIGHT_GYM_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.34 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | PrimarySchool | Gym | 154_230_120 | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Playing Area | ASHRAE 90.1-2004Gymnasium/Exercise CenterPlaying Area |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_GYM_SCH | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 21.2 | 0 | 30 | SchoolPrimary BLDG_LIGHT_GYM_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.46 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | PrimarySchool | Gym | 154_230_120 | ASHRAE 90.1-2010 | Gymnasium/Fitness Center | Playing Area | ASHRAE 90.1-2010Gymnasium/Fitness CenterPlaying Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_GYM_SCH | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) | ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | 0.3 | 0 | 0 | 30 | SchoolPrimary BLDG_LIGHT_GYM_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.34 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | PrimarySchool | Corridor | 169_31_31 | [6 empty] | 0.9 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
189.1-2009 | ClimateZone 1-3 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 |  | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
189.1-2009 | ClimateZone 4-8 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | PrimarySchool | Corridor | 169_31_31 | [6 empty] | 2 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
90.1-2007 | ClimateZone 1-8 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral |  |  | 0.66 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | PrimarySchool | Classroom | 120_230_199 | [6 empty] | 2 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 | 0 | 23.22 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 1.39 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | ClimateZone 1-3 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 | 0 | 23.22 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0595 |  | PrimarySchool Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | ClimateZone 4-8 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 | 0 | 23.22 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  | PrimarySchool Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | PrimarySchool | Classroom | 120_230_199 | [6 empty] | 2 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 | 0 | 23.22 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 1.39 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
90.1-2007 | ClimateZone 1-8 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2007 | Classroom/Lecture/Training | General | ASHRAE 90.1-2007Classroom/Lecture/TrainingGeneral |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (ages 5-8) | ASHRAE 62.1-2004Educational FacilitiesClassrooms (ages 5-8) | 0.12 | 10 | 0 | 25 | SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1.02 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2004 | Classroom/Lecture/Training | General | ASHRAE 90.1-2004Classroom/Lecture/TrainingGeneral |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 | 0 | 25 | SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1.39 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2010 | Classroom/Lecture/Training | General | ASHRAE 90.1-2010Classroom/Lecture/TrainingGeneral |  |  | 1.24 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (ages 5-8) | ASHRAE 62.1-2007Educational FacilitiesClassrooms (ages 5-8) | 0.12 | 10 | 0 | 25 | SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1.02 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | PrimarySchool | Cafeteria | 31_169_34 | [6 empty] | 1.4 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 66.67 | PrimarySchool Cafeteria Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 2.36 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | ClimateZone 1-3 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 66.67 | PrimarySchool Cafeteria Occ | PrimarySchool Activity | 0.0595 |  | PrimarySchool Infil | [5 empty] | 1.72 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | ClimateZone 4-8 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 66.67 | PrimarySchool Cafeteria Occ | PrimarySchool Activity | 0.0446 |  | PrimarySchool Infil | [5 empty] | 1.72 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | PrimarySchool | Cafeteria | 31_169_34 | [6 empty] | 1.4 |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 66.67 | PrimarySchool Cafeteria Occ | PrimarySchool Activity |  | 0.2232 | PrimarySchool Infil | [5 empty] | 2.36 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
90.1-2007 | ClimateZone 1-8 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 100 | SchoolPrimary BLDG_OCC_SCH_Cafeteria | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1.72 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 100 | SchoolPrimary BLDG_OCC_SCH_Cafeteria | SchoolPrimary ACTIVITY_SCH | 0.0595 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 2.36 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | General | ASHRAE 90.1-2010Dining AreaGeneral |  |  | 0.65 |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 100 | SchoolPrimary BLDG_OCC_SCH_Cafeteria | SchoolPrimary ACTIVITY_SCH | 0.0446 |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1.72 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | [6 empty] | 1.55 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity |  | 0.2232 | QuickServiceRestaurant Infil Half On | 409.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant Gas Equip | 28 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp Kitchen | QuickServiceRestaurant ClgSetp Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant Kitchen Exhaust
189.1-2009 | ClimateZone 1-3 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0595 |  | QuickServiceRestaurant Infil Half On | 298.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant Gas Equip | 20.4 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp Kitchen | QuickServiceRestaurant ClgSetp Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant Kitchen Exhaust
189.1-2009 | ClimateZone 4-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0446 |  | QuickServiceRestaurant Infil Half On | 298.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant Gas Equip | 20.4 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp Kitchen | QuickServiceRestaurant ClgSetp Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant Kitchen Exhaust
DOE Ref Pre-1980 | ClimateZone 1-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity |  | 0.2232 | QuickServiceRestaurant Infil Half On | 409.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant Gas Equip | 28 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp Kitchen | QuickServiceRestaurant ClgSetp Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant SWH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | QuickServiceRestaurant Kitchen Exhaust
90.1-2007 | ClimateZone 1-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | RestaurantFastFood BLDG_OCC_SCH | RestaurantFastFood ACTIVITY_SCH | 0.0446 |  | RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | 298.6 | 0.1 | 0.2 | 0.7 | RestaurantFastFood FF_GAS_EQUIP_SCH | 20.4 | 0.25 | 0.3 | 0.3 | RestaurantFastFood BLDG_EQUIP_SCH | RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | RestaurantFastFood BLDG_SWH_SCH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | RestaurantFastFood Hours_of_operation
90.1-2004 | ClimateZone 1-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 5 | RestaurantFastFood BLDG_OCC_SCH | RestaurantFastFood ACTIVITY_SCH | 0.0595 |  | RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | 409.6 | 0.1 | 0.2 | 0.7 | RestaurantFastFood FF_GAS_EQUIP_SCH | 28 | 0.25 | 0.3 | 0.3 | RestaurantFastFood BLDG_EQUIP_SCH | RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | RestaurantFastFood BLDG_SWH_SCH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | RestaurantFastFood Hours_of_operation
90.1-2010 | ClimateZone 1-8 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 5 | RestaurantFastFood BLDG_OCC_SCH | RestaurantFastFood ACTIVITY_SCH | 0.0446 |  | RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | 298.6 | 0.1 | 0.2 | 0.7 | RestaurantFastFood FF_GAS_EQUIP_SCH | 20.4 | 0.25 | 0.3 | 0.3 | RestaurantFastFood BLDG_EQUIP_SCH | RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | RestaurantFastFood BLDG_SWH_SCH | 0.7 | 3300 | 0.338 | 0.50241 | 575.7279 | 0.12212 | RestaurantFastFood Hours_of_operation
DOE Ref 1980-2004 | ClimateZone 1-8 | QuickServiceRestaurant | Dining | 31_169_34 | [6 empty] | 1.44 |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 67 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity |  | 0.2232 | QuickServiceRestaurant Infil Half On | [5 empty] | 12 | 0.25 | 0.3 | 0 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp
189.1-2009 | ClimateZone 1-3 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Family Dining | ASHRAE 189.1-2009Dining AreaFor Family Dining |  |  | 1.89 |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 67 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0595 |  | QuickServiceRestaurant Infil Half On | [5 empty] | 8.74 | 0.25 | 0.3 | 0 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp
189.1-2009 | ClimateZone 4-8 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Family Dining | ASHRAE 189.1-2009Dining AreaFor Family Dining |  |  | 1.89 |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 67 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0446 |  | QuickServiceRestaurant Infil Half On | [5 empty] | 8.74 | 0.25 | 0.3 | 0 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | QuickServiceRestaurant | Dining | 31_169_34 | [6 empty] | 3.7 |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 67 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity |  | 0.2232 | QuickServiceRestaurant Infil Half On | [5 empty] | 12 | 0.25 | 0.3 | 0 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp
90.1-2007 | ClimateZone 1-8 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | For Family Dining | ASHRAE 90.1-2007Dining AreaFor Family Dining |  |  | 2.1 |  |  | 0 | 0.37 | 0.2 | RestaurantFastFood BLDG_LIGHT_DINING_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 67 | RestaurantFastFood BLDG_OCC_SCH | RestaurantFastFood ACTIVITY_SCH | 0.0446 |  | RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | [5 empty] | 8.74 | 0.25 | 0.3 | 0 | RestaurantFastFood BLDG_EQUIP_SCH | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | For Family Dining | ASHRAE 90.1-2004Dining AreaFor Family Dining |  |  | 2.1 |  |  | 0 | 0.37 | 0.2 | RestaurantFastFood BLDG_LIGHT_DINING_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 67 | RestaurantFastFood BLDG_OCC_SCH | RestaurantFastFood ACTIVITY_SCH | 0.0595 |  | RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | [5 empty] | 12 | 0.25 | 0.3 | 0 | RestaurantFastFood BLDG_EQUIP_SCH | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | For Family Dining | ASHRAE 90.1-2010Dining AreaFor Family Dining |  |  | 0.89 |  |  | 0 | 0.37 | 0.2 | RestaurantFastFood BLDG_LIGHT_DINING_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 67 | RestaurantFastFood BLDG_OCC_SCH | RestaurantFastFood ACTIVITY_SCH | 0.0446 |  | RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | [5 empty] | 8.74 | 0.25 | 0.3 | 0 | RestaurantFastFood BLDG_EQUIP_SCH | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | Retail | Retail | 171_222_78 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | 0.3 | 0 | 0 | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0595 |  | RetailStandalone INFIL_SCH | [5 empty] | 0.3 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Retail | Retail | 171_222_78 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Retail | General Sales | ASHRAE 62.1-2004RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0446 |  | RetailStandalone INFIL_SCH | [5 empty] | 0.22 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Retail | Retail | 171_222_78 | ASHRAE 90.1-2010 | Sales Area | General | ASHRAE 90.1-2010Sales AreaGeneral |  |  | 1.68 |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0446 |  | RetailStandalone INFIL_SCH | [5 empty] | 0.22 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Retail | Retail | 171_222_78 | [6 empty] | 3.37 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity |  | 0.2232 | Retail Infil Half On | [5 empty] | 0.3 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
189.1-2009 | ClimateZone 1-3 | Retail | Retail | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0595 |  | Retail Infil Half On | [5 empty] | 0.22 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
189.1-2009 | ClimateZone 4-8 | Retail | Retail | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0446 |  | Retail Infil Half On | [5 empty] | 0.22 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Retail | Retail | 171_222_78 | [6 empty] | 5.04 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity |  | 0.2232 | Retail Infil Half On | [5 empty] | 0.3 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
90.1-2004 | ClimateZone 1-8 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_FRONT_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0595 |  | RetailStandalone INFIL_SCH | [5 empty] | 2 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | ClimateZone 1-8 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_FRONT_SCH | ASHRAE 62.1-2004 | Retail | General Sales | ASHRAE 62.1-2004RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0446 |  | RetailStandalone INFIL_SCH | [5 empty] | 1.45 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 90.1-2010 | Sales Area | General | ASHRAE 90.1-2010Sales AreaGeneral |  |  | 1.68 |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_FRONT_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0446 |  | RetailStandalone INFIL_SCH | [5 empty] | 1.45 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Retail | Point_of_Sale | 171_222_78 | [6 empty] | 3.37 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity |  | 0.2232 | Retail Infil Half On | [5 empty] | 2 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
189.1-2009 | ClimateZone 1-3 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0595 |  | Retail Infil Half On | [5 empty] | 1.45 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
189.1-2009 | ClimateZone 4-8 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0446 |  | Retail Infil Half On | [5 empty] | 1.45 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Retail | Point_of_Sale | 171_222_78 | [6 empty] | 5.04 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity |  | 0.2232 | Retail Infil Half On | [5 empty] | 2 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
DOE Ref 1980-2004 | ClimateZone 1-8 | Retail | Entry | 169_31_31 | [6 empty] | 3.37 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity |  | 0.2232 | Retail Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
189.1-2009 | ClimateZone 1-3 | Retail | Entry | 169_31_31 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Mall Concourse | ASHRAE 189.1-2009Retail (not including accent lighting)Mall Concourse |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0595 |  | Retail Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
189.1-2009 | ClimateZone 4-8 | Retail | Entry | 169_31_31 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Mall Concourse | ASHRAE 189.1-2009Retail (not including accent lighting)Mall Concourse |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity | 0.0446 |  | Retail Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Retail | Entry | 169_31_31 | [6 empty] | 5.04 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | Retail Bldg Occ | Retail Activity |  | 0.2232 | Retail Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
90.1-2007 | ClimateZone 1-8 | Retail | Entry | 169_31_31 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Mall Concourse | ASHRAE 90.1-2007Retail (not including accent lighting)Mall Concourse |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_ENTRY_SCH | ASHRAE 62.1-2004 | Retail | General Sales | ASHRAE 62.1-2004RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0446 |  | RetailStandalone INFIL_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | Retail | Entry | 169_31_31 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Mall Concourse | ASHRAE 90.1-2004Retail (not including accent lighting)Mall Concourse |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_ENTRY_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0595 |  | RetailStandalone INFIL_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Retail | Entry | 169_31_31 | ASHRAE 90.1-2010 | Retail | Mall Concourse | ASHRAE 90.1-2010RetailMall Concourse |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_ENTRY_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 | 0 | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0446 |  | RetailStandalone INFIL_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | ClimateZone 1-8 | Retail | Back_Space | 120_149_230 | [6 empty] | 1.17 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 3.33 | Retail Bldg Occ | Retail Activity |  | 0.2232 | Retail Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
189.1-2009 | ClimateZone 1-3 | Retail | Back_Space | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 3.33 | Retail Bldg Occ | Retail Activity | 0.0595 |  | Retail Infil Half On | [5 empty] | 0.546 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
189.1-2009 | ClimateZone 4-8 | Retail | Back_Space | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 3.33 | Retail Bldg Occ | Retail Activity | 0.0446 |  | Retail Infil Half On | [5 empty] | 0.546 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Retail | Back_Space | 120_149_230 | [6 empty] | 0.77 |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 3.33 | Retail Bldg Occ | Retail Activity |  | 0.2232 | Retail Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
90.1-2007 | ClimateZone 1-8 | Retail | Back_Space | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_BACK_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 3.33 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0446 |  | RetailStandalone INFIL_SCH | [5 empty] | 0.546 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | Retail | Back_Space | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_BACK_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 | 0 | 3.33 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0595 |  | RetailStandalone INFIL_SCH | [5 empty] | 0.75 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | Retail | Back_Space | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_BACK_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 3.33 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0446 |  | RetailStandalone INFIL_SCH | [5 empty] | 0.546 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_BATH_SCH | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0595 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
90.1-2007 | ClimateZone 1-8 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_BATH_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
90.1-2010 | ClimateZone 1-8 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2010 | Restrooms | General | ASHRAE 90.1-2010RestroomsGeneral |  |  | 0.98 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_BATH_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
DOE Ref 1980-2004 | ClimateZone 1-8 | SecondarySchool | Restroom | 169_169_31 | [6 empty] | 0.89 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
189.1-2009 | ClimateZone 1-3 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 |  | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
189.1-2009 | ClimateZone 4-8 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
DOE Ref Pre-1980 | ClimateZone 1-8 | SecondarySchool | Restroom | 169_169_31 | [6 empty] | 1.08 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 9.29 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 52.2 | 2260 | 0.023097 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH | 0.28122 | 635.6646 | 0.338 | 0.5 | 110.3676 | 0.048826
DOE Ref 1980-2004 | ClimateZone 1-8 | SecondarySchool | Office | 120_230_199 | [6 empty] | 1.87 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.65 | SecondarySchool Office Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 1 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | ClimateZone 1-3 | SecondarySchool | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.65 | SecondarySchool Office Occ | SecondarySchool Activity | 0.0595 |  | SecondarySchool Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | ClimateZone 4-8 | SecondarySchool | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.65 | SecondarySchool Office Occ | SecondarySchool Activity | 0.0446 |  | SecondarySchool Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SecondarySchool | Office | 120_230_199 | [6 empty] | 2.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 4.65 | SecondarySchool Office Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 1 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
90.1-2007 | ClimateZone 1-8 | SecondarySchool | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 5 | SchoolSecondary BLDG_OCC_SCH_Offices | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.73 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | SecondarySchool | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | SchoolSecondary BLDG_OCC_SCH_Offices | SchoolSecondary ACTIVITY_SCH | 0.0595 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | SecondarySchool | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 5 | SchoolSecondary BLDG_OCC_SCH_Offices | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.73 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
DOE Ref 1980-2004 | ClimateZone 1-8 | SecondarySchool | Mechanical | 41_31_169 | [6 empty] | 0.75 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
189.1-2009 | ClimateZone 1-3 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 |  | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | SecondarySchool BathCorrMechKitchen HtgSetp |  | #VALUE!
189.1-2009 | ClimateZone 4-8 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
DOE Ref Pre-1980 | ClimateZone 1-8 | SecondarySchool | Mechanical | 41_31_169 | [6 empty] | 0.6 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0.93 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
90.1-2007 | ClimateZone 1-8 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0595 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral |  |  | 0.95 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
DOE Ref 1980-2004 | ClimateZone 1-8 | SecondarySchool | Lobby | 230_157_120 | [6 empty] | 1.12 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | ClimateZone 1-3 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 |  | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | ClimateZone 4-8 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral |  |  | 1.17 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SecondarySchool | Lobby | 230_157_120 | [6 empty] | 1.32 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
90.1-2007 | ClimateZone 1-8 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral |  |  | 1.3 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0595 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
DOE Ref 1980-2004 | ClimateZone 1-8 | SecondarySchool | Library | 230_196_120 | [6 empty] | 1.52 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 | 0 | 21.34 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.93 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | ClimateZone 1-3 | SecondarySchool | Library | 230_196_120 | ASHRAE 189.1-2009 | Library | Reading Area | ASHRAE 189.1-2009LibraryReading Area |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 | 0 | 21.34 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 |  | SecondarySchool Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | ClimateZone 4-8 | SecondarySchool | Library | 230_196_120 | ASHRAE 189.1-2009 | Library | Reading Area | ASHRAE 189.1-2009LibraryReading Area |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 | 0 | 21.34 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  | SecondarySchool Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SecondarySchool | Library | 230_196_120 | [6 empty] | 2.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 | 0 | 21.34 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.93 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
90.1-2007 | ClimateZone 1-8 | SecondarySchool | Library | 230_196_120 | ASHRAE 90.1-2007 | Library | Reading Area | ASHRAE 90.1-2007LibraryReading Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | ASHRAE 62.1-2004 | Educational Facilities | Media center | ASHRAE 62.1-2004Educational FacilitiesMedia center | 0.12 | 10 | 0 | 10 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.68 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | SecondarySchool | Library | 230_196_120 | ASHRAE 90.1-2004 | Library | Reading Area | ASHRAE 90.1-2004LibraryReading Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 | 0 | 10 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0595 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.93 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | SecondarySchool | Library | 230_196_120 | ASHRAE 90.1-2010 | Library | Reading Area | ASHRAE 90.1-2010LibraryReading Area |  |  | 0.93 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | ASHRAE 62.1-2007 | Educational Facilities | Media center | ASHRAE 62.1-2007Educational FacilitiesMedia center | 0.12 | 10 | 0 | 10 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.68 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
DOE Ref 1980-2004 | ClimateZone 1-8 | SecondarySchool | Kitchen | 78_222_133 | [6 empty] | 1.56 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 15.48 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | 354.9 | 0.1 | 0.2 | 0.7 | SecondarySchool Kitchen Gas | 20.65 | 0.25 | 0.3 | 0.2 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool Kitchen Exhaust
189.1-2009 | ClimateZone 1-3 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 15.48 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 |  | SecondarySchool Infil | 258.6 | 0.1 | 0.2 | 0.7 | SecondarySchool Kitchen Gas | 15.05 | 0.25 | 0.3 | 0.2 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool Kitchen Exhaust
189.1-2009 | ClimateZone 4-8 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral |  |  | 1.08 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 15.48 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  | SecondarySchool Infil | 258.6 | 0.1 | 0.2 | 0.7 | SecondarySchool Kitchen Gas | 15.05 | 0.25 | 0.3 | 0.2 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool Kitchen Exhaust
DOE Ref Pre-1980 | ClimateZone 1-8 | SecondarySchool | Kitchen | 78_222_133 | [6 empty] | 2.24 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 15.48 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | 354.9 | 0.1 | 0.2 | 0.7 | SecondarySchool Kitchen Gas | 20.65 | 0.25 | 0.3 | 0.2 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SecondarySchool SWH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SecondarySchool Kitchen Exhaust
90.1-2007 | ClimateZone 1-8 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 15.23 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | 258.6 | 0.1 | 0.2 | 0.7 | SchoolSecondary KITCHEN_GAS_EQUIP_SCH | 20.65 | 0.25 | 0.3 | 0.2 | SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SchoolSecondary Kitchen_Exhaust_SCH
90.1-2004 | ClimateZone 1-8 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 16.95 | 0 | 15.23 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0595 |  | SchoolSecondary INFIL_SCH_PNNL | 354.9 | 0.1 | 0.2 | 0.7 | SchoolSecondary KITCHEN_GAS_EQUIP_SCH | 20.65 | 0.25 | 0.3 | 0.2 | SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SchoolSecondary Kitchen_Exhaust_SCH
90.1-2010 | ClimateZone 1-8 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral |  |  | 0.99 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 15.23 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | 258.6 | 0.1 | 0.2 | 0.7 | SchoolSecondary KITCHEN_GAS_EQUIP_SCH | 20.65 | 0.25 | 0.3 | 0.2 | SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK | 133 | 2325 | 0.057204 | 49 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH | 0.7 | 4000 | 0.338 | 0.5 | 694.5023 | 0.12154 | SchoolSecondary Kitchen_Exhaust_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | SecondarySchool | Gym | 154_230_120 | [6 empty] | 1.06 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 21.2 | 0 | 92.94 | SecondarySchool Gym Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
189.1-2009 | ClimateZone 1-3 | SecondarySchool | Gym | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 21.2 | 0 | 92.94 | SecondarySchool Gym Occ | SecondarySchool Activity | 0.0595 |  | SecondarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
189.1-2009 | ClimateZone 4-8 | SecondarySchool | Gym | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 21.2 | 0 | 92.94 | SecondarySchool Gym Occ | SecondarySchool Activity | 0.0446 |  | SecondarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
DOE Ref Pre-1980 | ClimateZone 1-8 | SecondarySchool | Gym | 154_230_120 | [6 empty] | 0.8 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 21.2 | 0 | 92.94 | SecondarySchool Gym Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
90.1-2007 | ClimateZone 1-8 | SecondarySchool | Gym | 154_230_120 | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Playing Area | ASHRAE 90.1-2007Gymnasium/Exercise CenterPlaying Area |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_GYM_SCH | ASHRAE 62.1-2004 | Sports and Entertainment | Gym, stadium (play area) | ASHRAE 62.1-2004Sports and EntertainmentGym, stadium (play area) | 0.3 | 0 | 0 | 30 | SchoolSecondary BLDG_OCC_SCH_Gym | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.34 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH
90.1-2004 | ClimateZone 1-8 | SecondarySchool | Gym | 154_230_120 | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Playing Area | ASHRAE 90.1-2004Gymnasium/Exercise CenterPlaying Area |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_GYM_SCH | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 21.2 | 0 | 30 | SchoolSecondary BLDG_OCC_SCH_Gym | SchoolSecondary ACTIVITY_SCH | 0.0595 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.46 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH
90.1-2010 | ClimateZone 1-8 | SecondarySchool | Gym | 154_230_120 | ASHRAE 90.1-2010 | Gymnasium/Fitness Center | Playing Area | ASHRAE 90.1-2010Gymnasium/Fitness CenterPlaying Area |  |  | 1.2 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_GYM_SCH | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) | ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | 0.3 | 0 | 0 | 30 | SchoolSecondary BLDG_OCC_SCH_Gym | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.34 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK | 159.5 | 21269 | 0.0074992 | 43.3 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH
DOE Ref 1980-2004 | ClimateZone 1-8 | SecondarySchool | Corridor | 169_31_31 | [6 empty] | 0.86 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.31 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
189.1-2009 | ClimateZone 1-3 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.31 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 |  | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
189.1-2009 | ClimateZone 4-8 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.31 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
DOE Ref Pre-1980 | ClimateZone 1-8 | SecondarySchool | Corridor | 169_31_31 | [6 empty] | 0.7 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 9.31 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
90.1-2007 | ClimateZone 1-8 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 | 0 | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0595 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral |  |  | 0.66 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
DOE Ref 1980-2004 | ClimateZone 1-8 | SecondarySchool | Classroom | 120_230_199 | [6 empty] | 2 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 | 0 | 23.22 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.93 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | ClimateZone 1-3 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 | 0 | 23.22 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 |  | SecondarySchool Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | ClimateZone 4-8 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral |  |  | 1.26 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 | 0 | 23.22 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  | SecondarySchool Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SecondarySchool | Classroom | 120_230_199 | [6 empty] | 2.9 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 | 0 | 23.22 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.93 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
90.1-2007 | ClimateZone 1-8 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2007 | Classroom/Lecture/Training | General | ASHRAE 90.1-2007Classroom/Lecture/TrainingGeneral |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (age 9 plus) | ASHRAE 62.1-2004Educational FacilitiesClassrooms (age 9 plus) | 0.12 | 10 | 0 | 35 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.68 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2004 | Classroom/Lecture/Training | General | ASHRAE 90.1-2004Classroom/Lecture/TrainingGeneral |  |  | 1.4 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 | 0 | 35 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0595 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.93 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2010 | Classroom/Lecture/Training | General | ASHRAE 90.1-2010Classroom/Lecture/TrainingGeneral |  |  | 1.24 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (age 9 plus) | ASHRAE 62.1-2007Educational FacilitiesClassrooms (age 9 plus) | 0.12 | 10 | 0 | 35 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.68 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
DOE Ref 1980-2004 | ClimateZone 1-8 | SecondarySchool | Cafeteria | 31_169_34 | [6 empty] | 1.34 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 66.84 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 1.79 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | ClimateZone 1-3 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 66.84 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0595 |  | SecondarySchool Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | ClimateZone 4-8 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 66.84 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  | SecondarySchool Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SecondarySchool | Cafeteria | 31_169_34 | [6 empty] | 3.7 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 66.84 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 1.79 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
90.1-2007 | ClimateZone 1-8 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 100 | SchoolSecondary BLDG_OCC_SCH_Cafeteria | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 1.3 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 21.2 | 0 | 100 | SchoolSecondary BLDG_OCC_SCH_Cafeteria | SchoolSecondary ACTIVITY_SCH | 0.0595 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 1.79 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | General | ASHRAE 90.1-2010Dining AreaGeneral |  |  | 0.65 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 | 0 | 100 | SchoolSecondary BLDG_OCC_SCH_Cafeteria | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 1.3 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
DOE Ref 1980-2004 | ClimateZone 1-8 | SecondarySchool | Auditorium | 230_196_120 | [6 empty] | 1.12 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Auditorium | ASHRAE 62.1-1999EducationAuditorium | 0 | 15 | 0 | 92.94 | SecondarySchool Auditorium Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | ClimateZone 1-3 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 189.1-2009 | Audience/Seating Area | General | ASHRAE 189.1-2009Audience/Seating AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Auditorium | ASHRAE 62.1-1999EducationAuditorium | 0 | 15 | 0 | 92.94 | SecondarySchool Auditorium Occ | SecondarySchool Activity | 0.0595 |  | SecondarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | ClimateZone 4-8 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 189.1-2009 | Audience/Seating Area | General | ASHRAE 189.1-2009Audience/Seating AreaGeneral |  |  | 0.81 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Auditorium | ASHRAE 62.1-1999EducationAuditorium | 0 | 15 | 0 | 92.94 | SecondarySchool Auditorium Occ | SecondarySchool Activity | 0.0446 |  | SecondarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SecondarySchool | Auditorium | 230_196_120 | [6 empty] | 1.45 |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Auditorium | ASHRAE 62.1-1999EducationAuditorium | 0 | 15 | 0 | 92.94 | SecondarySchool Auditorium Occ | SecondarySchool Activity |  | 0.2232 | SecondarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
90.1-2007 | ClimateZone 1-8 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 90.1-2007 | Audience/Seating Area | General | ASHRAE 90.1-2007Audience/Seating AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Educational Facilities | Music/theater/dance | ASHRAE 62.1-2004Educational FacilitiesMusic/theater/dance | 0.06 | 10 | 0 | 150 | SchoolSecondary BLDG_OCC_SCH_Auditorium | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.34 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | ClimateZone 1-8 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 90.1-2004 | Audience/Seating Area | General | ASHRAE 90.1-2004Audience/Seating AreaGeneral |  |  | 0.9 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Education | Auditorium | ASHRAE 62.1-1999EducationAuditorium | 0 | 15 | 0 | 150 | SchoolSecondary BLDG_OCC_SCH_Auditorium | SchoolSecondary ACTIVITY_SCH | 0.0595 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.46 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | ClimateZone 1-8 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 90.1-2010 | Audience/Seating Area | For Auditorium | ASHRAE 90.1-2010Audience/Seating AreaFor Auditorium |  |  | 0.79 |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Educational Facilities | Music/theater/dance | ASHRAE 62.1-2007Educational FacilitiesMusic/theater/dance | 0.06 | 10 | 0 | 150 | SchoolSecondary BLDG_OCC_SCH_Auditorium | SchoolSecondary ACTIVITY_SCH | 0.0446 |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.34 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2004 | ClimateZone 1-8 | SmallHotel | Storage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0595 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2007 | ClimateZone 1-8 | SmallHotel | Storage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2010 | ClimateZone 1-8 | SmallHotel | Storage | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | Storage | 120_149_230 | [6 empty] | 0.45 |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 1-3 | SmallHotel | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 |  | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 4-8 | SmallHotel | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 |  | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | Storage | 120_149_230 | [6 empty] | 0.45 |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | Stair | 230_157_120 | [6 empty] | 0.82 |  |  | 0 | 0.7 | 0.2 | Always On | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 1-3 | SmallHotel | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 |  | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 4-8 | SmallHotel | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 |  | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | Stair | 230_157_120 | [6 empty] | 0.82 |  |  | 0 | 0.7 | 0.2 | Always On | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
90.1-2004 | ClimateZone 1-8 | SmallHotel | Stair | 230_157_120 | ASHRAE 90.1-2004 | Stairs-Active | General | ASHRAE 90.1-2004Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STAIR_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0595 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2007 | ClimateZone 1-8 | SmallHotel | Stair | 230_157_120 | ASHRAE 90.1-2007 | Stairs-Active | General | ASHRAE 90.1-2007Stairs-ActiveGeneral |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STAIR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2010 | ClimateZone 1-8 | SmallHotel | Stair | 230_157_120 | ASHRAE 90.1-2010 | Stairway | General | ASHRAE 90.1-2010StairwayGeneral |  |  | 0.69 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STAIR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | StaffLounge | 31_169_34 | [6 empty] | 1.65 |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel StaffLounge Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 7.17 | 0 | 0.5 | 0 | SmallHotel StaffLounge Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 1-3 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel StaffLounge Occ | SmallHotel Activity | 0.0595 |  | SmallHotel Infil Half On | [5 empty] | 3.67 | 0 | 0.5 | 0 | SmallHotel StaffLounge Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 4-8 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel StaffLounge Occ | SmallHotel Activity | 0.0446 |  | SmallHotel Infil Half On | [5 empty] | 3.67 | 0 | 0.5 | 0 | SmallHotel StaffLounge Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | StaffLounge | 31_169_34 | [6 empty] | 1.65 |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel StaffLounge Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 7.17 | 0 | 0.5 | 0 | SmallHotel StaffLounge Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
90.1-2004 | ClimateZone 1-8 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 90.1-2004 | Lounge/Recreation | General | ASHRAE 90.1-2004Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | HotelSmall EmployeeLounge_Occ_Sch | HotelSmall Activity_Sch | 0.0595 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 7.17 | 0 | 0.5 | 0 | HotelSmall EmployeeLounge_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2007 | ClimateZone 1-8 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 90.1-2007 | Lounge/Recreation | General | ASHRAE 90.1-2007Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | ASHRAE 62.1-2004 | General | Conference/meeting | ASHRAE 62.1-2004GeneralConference/meeting | 0.06 | 5 | 0 | 30 | HotelSmall EmployeeLounge_Occ_Sch | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 3.67 | 0 | 0.5 | 0 | HotelSmall EmployeeLounge_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2010 | ClimateZone 1-8 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 90.1-2010 | Lounge/Recreation | General | ASHRAE 90.1-2010Lounge/RecreationGeneral |  |  | 0.73 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 | 0 | 30 | HotelSmall EmployeeLounge_Occ_Sch | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 3.67 | 0 | 0.5 | 0 | HotelSmall EmployeeLounge_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | PublicRestroom | 169_169_31 | [6 empty] | 1.1 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 2.85 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
189.1-2009 | ClimateZone 1-3 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 2.85 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 |  | SmallHotel Infil Half On | [5 empty] | 0.51 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
189.1-2009 | ClimateZone 4-8 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 2.85 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 |  | SmallHotel Infil Half On | [5 empty] | 0.51 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | PublicRestroom | 169_169_31 | [6 empty] | 1.1 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 2.85 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
90.1-2007 | ClimateZone 1-8 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_RESTROOM_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 2.85 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0.51 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
90.1-2004 | ClimateZone 1-8 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_RESTROOM_SCH | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 | 0 | 2.85 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0595 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 1 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
90.1-2010 | ClimateZone 1-8 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 90.1-2010 | Restrooms | General | ASHRAE 90.1-2010RestroomsGeneral |  |  | 0.98 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_RESTROOM_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 2.85 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0.51 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [7 empty] | 1.1396 | 400 | 0.338 | 0.5 | 69.4502 | 0.19786
DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | Office | 120_230_199 | [6 empty] | 2.01 |  |  | 0 | 0.7 | 0.2 | SmallHotel Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 7.14 | SmallHotel Office Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1.2 | 0 | 0.5 | 0 | SmallHotel Office Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 1-3 | SmallHotel | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SmallHotel Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 7.14 | SmallHotel Office Occ | SmallHotel Activity | 0.0595 |  | SmallHotel Infil Half On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel Office Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 4-8 | SmallHotel | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SmallHotel Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 7.14 | SmallHotel Office Occ | SmallHotel Activity | 0.0446 |  | SmallHotel Infil Half On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel Office Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | Office | 120_230_199 | [6 empty] | 2.01 |  |  | 0 | 0.7 | 0.2 | SmallHotel Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 7.14 | SmallHotel Office Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1.2 | 0 | 0.5 | 0 | SmallHotel Office Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
90.1-2007 | ClimateZone 1-8 | SmallHotel | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 7.14 | HotelSmall Office_Occ_Sch | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0.61 | 0 | 0.5 | 0 | HotelSmall OFF_EQUIP_SCH | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2004 | ClimateZone 1-8 | SmallHotel | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 7.14 | HotelSmall Office_Occ_Sch | HotelSmall Activity_Sch | 0.0595 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 1.2 | 0 | 0.5 | 0 | HotelSmall OFF_EQUIP_SCH | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2010 | ClimateZone 1-8 | SmallHotel | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 7.14 | HotelSmall Office_Occ_Sch | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0.61 | 0 | 0.5 | 0 | HotelSmall OFF_EQUIP_SCH | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | Meeting | 230_196_120 | [6 empty] | 2.13 |  |  | 0 | 0.7 | 0.2 | SmallHotel Meeting Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 50 | SmallHotel Meeting Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1.2 | 0 | 0.5 | 0 | SmallHotel Meeting Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 1-3 | SmallHotel | Meeting | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | SmallHotel Meeting Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 50 | SmallHotel Meeting Occ | SmallHotel Activity | 0.0595 |  | SmallHotel Infil Half On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel Meeting Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 4-8 | SmallHotel | Meeting | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral |  |  | 1.17 |  |  | 0 | 0.7 | 0.2 | SmallHotel Meeting Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 50 | SmallHotel Meeting Occ | SmallHotel Activity | 0.0446 |  | SmallHotel Infil Half On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel Meeting Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | Meeting | 230_196_120 | [6 empty] | 2.13 |  |  | 0 | 0.7 | 0.2 | SmallHotel Meeting Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 50 | SmallHotel Meeting Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1.2 | 0 | 0.5 | 0 | SmallHotel Meeting Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
90.1-2007 | ClimateZone 1-8 | SmallHotel | Meeting | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | ASHRAE 62.1-2004 | General | Conference/meeting | ASHRAE 62.1-2004GeneralConference/meeting | 0.06 | 5 | 0 | 50 | HotelSmall MeetingRoom_Occ_Sch | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0.61 | 0 | 0.5 | 0 | HotelSmall MeetingRoom_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2004 | ClimateZone 1-8 | SmallHotel | Meeting | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral |  |  | 1.3 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 | 0 | 50 | HotelSmall MeetingRoom_Occ_Sch | HotelSmall Activity_Sch | 0.0595 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 1.2 | 0 | 0.5 | 0 | HotelSmall MeetingRoom_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2010 | ClimateZone 1-8 | SmallHotel | Meeting | 230_196_120 | ASHRAE 90.1-2010 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2010Conference/Meeting/MultipurposeGeneral |  |  | 1.23 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 | 0 | 50 | HotelSmall MeetingRoom_Occ_Sch | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0.61 | 0 | 0.5 | 0 | HotelSmall MeetingRoom_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | Mechanical | 41_31_169 | [6 empty] | 0.96 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 1-3 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 |  | SmallHotel Infil Half On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 4-8 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 |  | SmallHotel Infil Half On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | Mechanical | 41_31_169 | [6 empty] | 0.96 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
90.1-2007 | ClimateZone 1-8 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_MECHROOM_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | HotelSmall OFF_EQUIP_SCH | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2004 | ClimateZone 1-8 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_MECHROOM_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0595 |  | HotelSmall CommonArea_Infil_Sch |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2010 | ClimateZone 1-8 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral |  |  | 0.95 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_MECHROOM_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | Laundry | 120_149_230 | [6 empty] | 1.04 |  |  | 0 | 0.7 | 0.2 | SmallHotel Laundry Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 10 | SmallHotel Laundry Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | 58.4 |  |  |  | SmallHotel Laundry Gas | 2.03 | 0 | 0.5 | 0 | SmallHotel Laundry Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel SWH Laundry
189.1-2009 | ClimateZone 1-3 | SmallHotel | Laundry | 120_149_230 | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | ASHRAE 189.1-2009HospitalLaundry-Washing |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | SmallHotel Laundry Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 10 | SmallHotel Laundry Occ | SmallHotel Activity | 0.0595 |  | SmallHotel Infil Half On | 42.6 |  |  |  | SmallHotel Laundry Gas | 1.04 | 0 | 0.5 | 0 | SmallHotel Laundry Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel SWH Laundry
189.1-2009 | ClimateZone 4-8 | SmallHotel | Laundry | 120_149_230 | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | ASHRAE 189.1-2009HospitalLaundry-Washing |  |  | 0.54 |  |  | 0 | 0.7 | 0.2 | SmallHotel Laundry Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 10 | SmallHotel Laundry Occ | SmallHotel Activity | 0.0446 |  | SmallHotel Infil Half On | 42.6 |  |  |  | SmallHotel Laundry Gas | 1.04 | 0 | 0.5 | 0 | SmallHotel Laundry Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel SWH Laundry
DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | Laundry | 120_149_230 | [6 empty] | 1.04 |  |  | 0 | 0.7 | 0.2 | SmallHotel Laundry Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 10 | SmallHotel Laundry Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | 58.4 |  |  |  | SmallHotel Laundry Gas | 2.03 | 0 | 0.5 | 0 | SmallHotel Laundry Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | SmallHotel SWH Laundry
90.1-2007 | ClimateZone 1-8 | SmallHotel | Laundry | 120_149_230 | ASHRAE 90.1-2007 | Hospital | Laundry-Washing | ASHRAE 90.1-2007HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_LAUNDRY_SCH | ASHRAE 62.1-2004 | Retail | Coinoperated laundries | ASHRAE 62.1-2004RetailCoinoperated laundries | 0.06 | 7.5 | 0 | 10 | HotelSmall LaundryRoom_Occ_Sch | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | 42.6 |  |  |  | HotelSmall LaundryRoom_Eqp_Gas_Sch | 1.04 | 0 | 0.5 | 0 | HotelSmall LaundryRoom_Eqp_Elec_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | HotelSmall LaundryRoom_SHW_Sch
90.1-2004 | ClimateZone 1-8 | SmallHotel | Laundry | 120_149_230 | ASHRAE 90.1-2004 | Hospital | Laundry-Washing | ASHRAE 90.1-2004HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_LAUNDRY_SCH | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 | 0 | 10 | HotelSmall LaundryRoom_Occ_Sch | HotelSmall Activity_Sch | 0.0595 |  | HotelSmall CommonArea_Infil_Sch | 58.4 |  |  |  | HotelSmall LaundryRoom_Eqp_Gas_Sch | 2.03 | 0 | 0.5 | 0 | HotelSmall LaundryRoom_Eqp_Elec_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | HotelSmall LaundryRoom_SHW_Sch
90.1-2010 | ClimateZone 1-8 | SmallHotel | Laundry | 120_149_230 | ASHRAE 90.1-2010 | Hospital | Laundry-Washing | ASHRAE 90.1-2010HospitalLaundry-Washing |  |  | 0.6 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_LAUNDRY_SCH | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | ASHRAE 62.1-2007RetailCoinoperated laundries | 0.06 | 7.5 | 0 | 10 | HotelSmall LaundryRoom_Occ_Sch | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | 42.6 |  |  |  | HotelSmall LaundryRoom_Eqp_Gas_Sch | 1.04 | 0 | 0.5 | 0 | HotelSmall LaundryRoom_Eqp_Elec_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | 67.5 | 1053 | 0.064103 | 60 | 0.2 | 0.05 | HotelSmall LaundryRoom_SHW_Sch
DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | GuestRoom | 78_167_222 | [6 empty] | 1.74 |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 4.27 | SmallHotel GuestRoom Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1.33 | 0 | 0.5 | 0 | SmallHotel GuestRoom Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel SWH GuestRoom
189.1-2009 | ClimateZone 1-3 | SmallHotel | GuestRoom | 78_167_222 | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | ASHRAE 189.1-2009Hotel/MotelGuest Rooms |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 4.27 | SmallHotel GuestRoom Occ | SmallHotel Activity | 0.0595 |  | SmallHotel Infil Half On | [5 empty] | 0.68 | 0 | 0.5 | 0 | SmallHotel GuestRoom Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel SWH GuestRoom
189.1-2009 | ClimateZone 4-8 | SmallHotel | GuestRoom | 78_167_222 | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | ASHRAE 189.1-2009Hotel/MotelGuest Rooms |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 4.27 | SmallHotel GuestRoom Occ | SmallHotel Activity | 0.0446 |  | SmallHotel Infil Half On | [5 empty] | 0.68 | 0 | 0.5 | 0 | SmallHotel GuestRoom Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel SWH GuestRoom
DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | GuestRoom | 78_167_222 | [6 empty] | 1.74 |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 4.27 | SmallHotel GuestRoom Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1.33 | 0 | 0.5 | 0 | SmallHotel GuestRoom Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | SmallHotel SWH GuestRoom
90.1-2007 | ClimateZone 1-8 | SmallHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2007 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2007Hotel/MotelGuest Rooms |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_GUESTROOM_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 | 0 | 4.27 | HotelSmall GuestRoom_Occ_Sch | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 0.68 | 0 | 0.5 | 0 | HotelSmall GuestRoom_Eqp_Sch_Base | HotelSmall Base_OccGuestRoom_HtgSP_Sch | HotelSmall Base_OccGuestRoom_ClgSP_Sch | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | HotelSmall GuestRoom_SHW_Sch
90.1-2004 | ClimateZone 1-8 | SmallHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2004 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2004Hotel/MotelGuest Rooms |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_GUESTROOM_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 | 0 | 4.27 | HotelSmall GuestRoom_Occ_Sch | HotelSmall Activity_Sch | 0.0595 |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.33 | 0 | 0.5 | 0 | HotelSmall GuestRoom_Eqp_Sch_Base | HotelSmall Base_OccGuestRoom_HtgSP_Sch | HotelSmall Base_OccGuestRoom_ClgSP_Sch | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | HotelSmall GuestRoom_SHW_Sch
90.1-2010 | ClimateZone 1-8 | SmallHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Highway Lodging | ASHRAE 90.1-2010Guest RoomFor Highway Lodging |  |  | 0.75 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_GUESTROOM_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 | 0 | 4.27 | HotelSmall GuestRoom_Occ_Sch | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 0.68 | 0 | 0.5 | 0 | HotelSmall GuestRoom_Eqp_Sch_Base | HotelSmall Base_OccGuestRoom_HtgSP_Sch | HotelSmall Base_OccGuestRoom_ClgSP_Sch | 1.75 | 351 | 0.0049858 | 43.3 | 0.2 | 0.05 | HotelSmall GuestRoom_SHW_Sch
DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | GuestLounge | 230_157_120 | [6 empty] | 1.31 |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1.43 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 1-3 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 |  | SmallHotel Infil Half On | [5 empty] | 0.73 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 4-8 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral |  |  | 1.08 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 |  | SmallHotel Infil Half On | [5 empty] | 0.73 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | GuestLounge | 230_157_120 | [6 empty] | 1.31 |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1.43 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
90.1-2007 | ClimateZone 1-8 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 90.1-2007 | Lounge/Recreation | General | ASHRAE 90.1-2007Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 | 0 | 30 | HotelSmall Lobby_Occ_Sch | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0.73 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2004 | ClimateZone 1-8 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 90.1-2004 | Lounge/Recreation | General | ASHRAE 90.1-2004Lounge/RecreationGeneral |  |  | 1.2 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 | 0 | 30 | HotelSmall Lobby_Occ_Sch | HotelSmall Activity_Sch | 0.0595 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 1.43 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2010 | ClimateZone 1-8 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 90.1-2010 | Lounge/Recreation | General | ASHRAE 90.1-2010Lounge/RecreationGeneral |  |  | 0.73 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 | 0 | 30 | HotelSmall Lobby_Occ_Sch | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0.73 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | Exercise | 154_230_120 | [6 empty] | 1.37 |  |  | 0 | 0.7 | 0.2 | SmallHotel Exercise Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 21.2 | 0 | 30 | SmallHotel Exercise Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1.07 | 0 | 0.5 | 0 | SmallHotel Exercise Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 1-3 | SmallHotel | Exercise | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterExercise Area |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | SmallHotel Exercise Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 21.2 | 0 | 30 | SmallHotel Exercise Occ | SmallHotel Activity | 0.0595 |  | SmallHotel Infil Half On | [5 empty] | 0.55 | 0 | 0.5 | 0 | SmallHotel Exercise Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 4-8 | SmallHotel | Exercise | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterExercise Area |  |  | 0.81 |  |  | 0 | 0.7 | 0.2 | SmallHotel Exercise Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 21.2 | 0 | 30 | SmallHotel Exercise Occ | SmallHotel Activity | 0.0446 |  | SmallHotel Infil Half On | [5 empty] | 0.55 | 0 | 0.5 | 0 | SmallHotel Exercise Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | Exercise | 154_230_120 | [6 empty] | 1.37 |  |  | 0 | 0.7 | 0.2 | SmallHotel Exercise Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 21.2 | 0 | 30 | SmallHotel Exercise Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 1.07 | 0 | 0.5 | 0 | SmallHotel Exercise Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
90.1-2007 | ClimateZone 1-8 | SmallHotel | Exercise | 154_230_120 | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 90.1-2007Gymnasium/Exercise CenterExercise Area |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_EXERCENTER_SCH | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/weight rooms | ASHRAE 62.1-2004Sports and EntertainmentHealth club/weight rooms | 0.06 | 20 | 0 | 30 | HotelSmall ExerciseCenter_Occ_Sch | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0.55 | 0 | 0.5 | 0 | HotelSmall ExerciseCenter_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2004 | ClimateZone 1-8 | SmallHotel | Exercise | 154_230_120 | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 90.1-2004Gymnasium/Exercise CenterExercise Area |  |  | 0.9 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_EXERCENTER_SCH | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 21.2 | 0 | 30 | HotelSmall ExerciseCenter_Occ_Sch | HotelSmall Activity_Sch | 0.0595 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 1.07 | 0 | 0.5 | 0 | HotelSmall ExerciseCenter_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2010 | ClimateZone 1-8 | SmallHotel | Exercise | 154_230_120 | ASHRAE 90.1-2010 | Gymnasium/Fitness Center | Fitness Area | ASHRAE 90.1-2010Gymnasium/Fitness CenterFitness Area |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_EXERCENTER_SCH | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/weight rooms | ASHRAE 62.1-2007Sports and EntertainmentHealth club/weight rooms | 0.06 | 20 | 0 | 30 | HotelSmall ExerciseCenter_Occ_Sch | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0.55 | 0 | 0.5 | 0 | HotelSmall ExerciseCenter_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | Elec/MechRoom | 41_31_169 | [13 empty] | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  |  |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 198.2 | 0 | 0.5 | 0 | SmallHotel BLDG ELEVATORS
189.1-2009 | ClimateZone 1-3 | SmallHotel | Elec/MechRoom | 41_31_170 | [13 empty] | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  |  | 0.223 |  | SmallHotel Infil Half On | [5 empty] | 198.2 | 0 | 0.5 | 0 | SmallHotel BLDG ELEVATORS
189.1-2009 | ClimateZone 4-8 | SmallHotel | Elec/MechRoom | 41_31_171 | [13 empty] | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  |  | 0.223 |  | SmallHotel Infil Half On | [5 empty] | 198.2 | 0 | 0.5 | 0 | SmallHotel BLDG ELEVATORS
DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | Elec/MechRoom | 41_31_172 | [13 empty] | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  |  |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 198.2 | 0 | 0.5 | 0 | SmallHotel BLDG ELEVATORS
90.1-2007 | ClimateZone 1-8 | SmallHotel | Elec/MechRoom | 41_31_173 | [13 empty] | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 0 |  |  | 0.202 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 198.2 | 0 | 0.5 | 0 | HotelSmall BLDG_ELEVATORS
90.1-2004 | ClimateZone 1-8 | SmallHotel | Elec/MechRoom | 41_31_174 | [13 empty] | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 |  |  | 0.202 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 198.2 | 0 | 0.5 | 0 | HotelSmall BLDG_ELEVATORS
90.1-2010 | ClimateZone 1-8 | SmallHotel | Elec/MechRoom | 41_31_175 | [13 empty] | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 0 |  |  | 0.202 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 198.2 | 0 | 0.5 | 0 | HotelSmall BLDG_ELEVATORS
DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | Corridor | 169_31_31 | [6 empty] | 0.86 |  |  | 0 | 0.7 | 0.2 | Always On | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 1-3 | SmallHotel | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0595 |  | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | ClimateZone 4-8 | SmallHotel | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral |  |  | 0.45 |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 |  | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | Corridor | 169_31_31 | [6 empty] | 0.86 |  |  | 0 | 0.7 | 0.2 | Always On | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
90.1-2007 | ClimateZone 1-8 | SmallHotel | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 | 0 | 0 | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2004 | ClimateZone 1-8 | SmallHotel | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral |  |  | 0.5 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 | 0 | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0595 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
90.1-2010 | ClimateZone 1-8 | SmallHotel | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral |  |  | 0.66 |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 | 0 | 0 | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0446 |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
DOE Ref 1980-2004 | ClimateZone 1-8 | SmallHotel | Attic | 120_149_230 | [24 empty] | 0.2232 | Always On
189.1-2009 | ClimateZone 1-3 | SmallHotel | Attic | 120_149_230 | [23 empty] | 0.0751 |  | Always On
189.1-2009 | ClimateZone 4-8 | SmallHotel | Attic | 120_149_230 | [23 empty] | 0.0751 |  | Always On
DOE Ref Pre-1980 | ClimateZone 1-8 | SmallHotel | Attic | 120_149_230 | [24 empty] | 0.2232 | Always On
90.1-2004 | ClimateZone 1-8 | StripMall | WholeBuilding | 171_222_78 | ASHRAE 90.1-2004 | Whole Building | Retail | ASHRAE 90.1-2004Whole BuildingRetail |  |  | 1.5 |  |  | 0 | 0.7 | 0.2 | RetailStripmall Type1_LIGHT_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | RetailStripmall Type1_OCC_SCH | HotelSmall Activity_Sch | 0.0595 |  | RetailStripmall Type1_Infil_SCH | [5 empty] | 0.4 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch
DOE Ref 1980-2004 | ClimateZone 1-8 | StripMall | WholeBuilding | 171_222_78 | [6 empty] | 3.58 |  |  | 0 | 0.7 | 0.2 | StripMall Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | StripMall Bldg Occ | StripMall Activity |  | 0.2232 | StripMall Infil Half On | [5 empty] | 0.4 | 0 | 0.5 | 0 | StripMall Bldg Equip | StripMall HtgSetp | StripMall ClgSetp
189.1-2009 | ClimateZone 1-3 | StripMall | WholeBuilding | 171_222_78 | ASHRAE 189.1-2009 | Whole Building | Retail | ASHRAE 189.1-2009Whole BuildingRetail |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | StripMall Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | StripMall Bldg Occ | StripMall Activity | 0.0595 |  | StripMall Infil Half On | [5 empty] | 0.29 | 0 | 0.5 | 0 | StripMall Bldg Equip | StripMall HtgSetp | StripMall ClgSetp
189.1-2009 | ClimateZone 4-8 | StripMall | WholeBuilding | 171_222_78 | ASHRAE 189.1-2009 | Whole Building | Retail | ASHRAE 189.1-2009Whole BuildingRetail |  |  | 1.35 |  |  | 0 | 0.7 | 0.2 | StripMall Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | StripMall Bldg Occ | StripMall Activity | 0.0446 |  | StripMall Infil Half On | [5 empty] | 0.29 | 0 | 0.5 | 0 | StripMall Bldg Equip | StripMall HtgSetp | StripMall ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | StripMall | WholeBuilding | 171_222_78 | [6 empty] | 4.81 |  |  | 0 | 0.7 | 0.2 | StripMall Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 | 0 | 15 | StripMall Bldg Occ | StripMall Activity |  | 0.2232 | StripMall Infil Half On | [5 empty] | 0.4 | 0 | 0.5 | 0 | StripMall Bldg Equip | StripMall HtgSetp | StripMall ClgSetp
DOE Ref 1980-2004 | ClimateZone 1-8 | SuperMarket | Sales/Produce | 230_196_120 | [6 empty] | 2.78 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 | SuperMarket Infil Half On | [5 empty] | 0.5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
189.1-2009 | ClimateZone 1-3 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 |  | SuperMarket Infil Half On | [5 empty] | 0.36 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
189.1-2009 | ClimateZone 4-8 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  | SuperMarket Infil Half On | [5 empty] | 0.36 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SuperMarket | Sales/Produce | 230_196_120 | [6 empty] | 5.04 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 | SuperMarket Infil Half On | [5 empty] | 0.5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2007 | ClimateZone 1-8 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2004 | Retail | Supermarket | ASHRAE 62.1-2004RetailSupermarket | 0.06 | 7.5 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  | SuperMarket Infil Half On | [5 empty] | 0.36 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2004 | ClimateZone 1-8 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 |  | SuperMarket Infil Half On | [5 empty] | 0.5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2010 | ClimateZone 1-8 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 90.1-2010 | Sales Area | General | ASHRAE 90.1-2010Sales AreaGeneral |  |  | 1.68 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | Retail | Supermarket | ASHRAE 62.1-2007RetailSupermarket | 0.06 | 7.5 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  | SuperMarket Infil Half On | [5 empty] | 0.36 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
DOE Ref 1980-2004 | ClimateZone 1-8 | SuperMarket | Office | 120_230_199 | [6 empty] | 1.98 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 | SuperMarket Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
189.1-2009 | ClimateZone 1-3 | SuperMarket | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
189.1-2009 | ClimateZone 4-8 | SuperMarket | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SuperMarket | Office | 120_230_199 | [6 empty] | 2.9 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 | SuperMarket Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2007 | ClimateZone 1-8 | SuperMarket | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 5 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2004 | ClimateZone 1-8 | SuperMarket | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 5 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 |  | SuperMarket Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2010 | ClimateZone 1-8 | SuperMarket | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 5 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
DOE Ref 1980-2004 | ClimateZone 1-8 | SuperMarket | DryStorage | 120_149_230 | [6 empty] | 1.1 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 | SuperMarket Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
189.1-2009 | ClimateZone 1-3 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
189.1-2009 | ClimateZone 4-8 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral |  |  | 0.72 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | SuperMarket | DryStorage | 120_149_230 | [6 empty] | 0.77 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 | SuperMarket Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2007 | ClimateZone 1-8 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 | 0 | 0 | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2004 | ClimateZone 1-8 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral |  |  | 0.8 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 | 0 | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 |  | SuperMarket Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2010 | ClimateZone 1-8 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral |  |  | 0.63 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 | 0 | 0 | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
DOE Ref 1980-2004 | ClimateZone 1-8 | SuperMarket | Deli/Bakery | 31_169_34 | [6 empty] | 2.78 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 | SuperMarket Infil Half On | 8.53 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
189.1-2009 | ClimateZone 1-3 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 |  | SuperMarket Infil Half On | 6.25 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 3.64 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
189.1-2009 | ClimateZone 4-8 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area |  |  | 1.53 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  | SuperMarket Infil Half On | 6.25 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 3.64 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
DOE Ref Pre-1980 | ClimateZone 1-8 | SuperMarket | Deli/Bakery | 31_169_34 | [6 empty] | 5.04 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 | SuperMarket Infil Half On | 8.53 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
90.1-2007 | ClimateZone 1-8 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2004 | Retail | Supermarket | ASHRAE 62.1-2004RetailSupermarket | 0.06 | 7.5 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  | SuperMarket Infil Half On | 6.25 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 3.64 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
90.1-2004 | ClimateZone 1-8 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area |  |  | 1.7 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 |  | SuperMarket Infil Half On | 8.53 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
90.1-2010 | ClimateZone 1-8 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 90.1-2010 | Sales Area | General | ASHRAE 90.1-2010Sales AreaGeneral |  |  | 1.68 |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | Retail | Supermarket | ASHRAE 62.1-2007RetailSupermarket | 0.06 | 7.5 | 0 | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  | SuperMarket Infil Half On | 6.25 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 3.64 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.0021418 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.338 | 0.5 | 520.8767 | 0.21534 | SuperMarket_Deli_Exhaust
DOE Ref 1980-2004 | ClimateZone 1-8 | Warehouse | Office | 120_230_199 | [6 empty] | 2.02 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 1.96 | Warehouse Bldg Occ | Warehouse Activity |  | 0.2232 | Always On | [5 empty] | 0.75 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp | Warehouse ClgSetp
189.1-2009 | ClimateZone 1-3 | Warehouse | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 1.96 | Warehouse Bldg Occ | Warehouse Activity | 0.0595 |  | Always On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp | Warehouse ClgSetp
189.1-2009 | ClimateZone 4-8 | Warehouse | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral |  |  | 0.99 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 1.96 | Warehouse Bldg Occ | Warehouse Activity | 0.0446 |  | Always On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp | Warehouse ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Warehouse | Office | 120_230_199 | [6 empty] | 2.9 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 1.96 | Warehouse Bldg Occ | Warehouse Activity |  | 0.2232 | Always On | [5 empty] | 0.75 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp | Warehouse ClgSetp
90.1-2007 | ClimateZone 1-8 | Warehouse | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 | 0 | 1.96 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0446 |  | Warehouse ALWAYS_ON | [5 empty] | 0.54 | 0 | 0.5 | 0 | Warehouse Office_Plug_SCH | Warehouse HtgSetp | Warehouse ClgSetp
90.1-2004 | ClimateZone 1-8 | Warehouse | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral |  |  | 1.1 |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 21.2 | 0 | 1.96 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0595 |  | Warehouse ALWAYS_ON | [5 empty] | 0.75 | 0 | 0.5 | 0 | Warehouse Office_Plug_SCH | Warehouse HtgSetp | Warehouse ClgSetp
90.1-2010 | ClimateZone 1-8 | Warehouse | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral |  |  | 1.11 |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 | 0 | 1.96 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0446 |  | Warehouse ALWAYS_ON | [5 empty] | 0.54 | 0 | 0.5 | 0 | Warehouse Office_Plug_SCH | Warehouse HtgSetp | Warehouse ClgSetp
DOE Ref 1980-2004 | ClimateZone 1-8 | Warehouse | Fine | 120_149_230 | [6 empty] | 1.08 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity |  | 0.2232 | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp FineStorage | Warehouse ClgSetp FineStorage
189.1-2009 | ClimateZone 1-3 | Warehouse | Fine | 120_149_230 | ASHRAE 189.1-2009 | Warehouse | Fine Material Storage | ASHRAE 189.1-2009WarehouseFine Material Storage |  |  | 1.26 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0595 |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp FineStorage | Warehouse ClgSetp FineStorage
189.1-2009 | ClimateZone 4-8 | Warehouse | Fine | 120_149_230 | ASHRAE 189.1-2009 | Warehouse | Fine Material Storage | ASHRAE 189.1-2009WarehouseFine Material Storage |  |  | 1.26 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0446 |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp FineStorage | Warehouse ClgSetp FineStorage
DOE Ref Pre-1980 | ClimateZone 1-8 | Warehouse | Fine | 120_149_230 | [6 empty] | 1.08 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity |  | 0.2232 | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp FineStorage | Warehouse ClgSetp FineStorage
90.1-2007 | ClimateZone 1-8 | Warehouse | Fine | 120_149_230 | ASHRAE 90.1-2007 | Warehouse | Fine Material Storage | ASHRAE 90.1-2007WarehouseFine Material Storage |  |  | 1.4 |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2004 | Miscellaneous Spaces | Warehouses | ASHRAE 62.1-2004Miscellaneous SpacesWarehouses | 0.06 | 0 | 0 | 0 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0446 |  | Warehouse ALWAYS_ON | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse ALWAYS_OFF | Warehouse Fine Storage Heating Setpoint Schedule | Warehouse Fine Storage Cooling Setpoint Schedule
90.1-2004 | ClimateZone 1-8 | Warehouse | Fine | 120_149_230 | ASHRAE 90.1-2004 | Warehouse | Fine Material Storage | ASHRAE 90.1-2004WarehouseFine Material Storage |  |  | 1.4 |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0595 |  | Warehouse ALWAYS_ON | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse ALWAYS_OFF | Warehouse Fine Storage Heating Setpoint Schedule | Warehouse Fine Storage Cooling Setpoint Schedule
90.1-2010 | ClimateZone 1-8 | Warehouse | Fine | 120_149_230 | ASHRAE 90.1-2010 | Warehouse | Fine Material Storage | ASHRAE 90.1-2010WarehouseFine Material Storage |  |  | 0.95 |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses | ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | 0.06 | 0 | 0 | 0 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0446 |  | Warehouse ALWAYS_ON | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse ALWAYS_OFF | Warehouse Fine Storage Heating Setpoint Schedule | Warehouse Fine Storage Cooling Setpoint Schedule
DOE Ref 1980-2004 | ClimateZone 1-8 | Warehouse | Bulk | 41_31_169 | [6 empty] | 0.31 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity |  | 0.2232 | Always On | [5 empty] | 0.25 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp BulkStorage | Warehouse ClgSetp
189.1-2009 | ClimateZone 1-3 | Warehouse | Bulk | 41_31_169 | ASHRAE 189.1-2009 | Warehouse | Medium/Bulky Material Storage | ASHRAE 189.1-2009WarehouseMedium/Bulky Material Storage |  |  | 0.81 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0595 |  | Always On | [5 empty] | 0.17 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp BulkStorage | Warehouse ClgSetp
189.1-2009 | ClimateZone 4-8 | Warehouse | Bulk | 41_31_169 | ASHRAE 189.1-2009 | Warehouse | Medium/Bulky Material Storage | ASHRAE 189.1-2009WarehouseMedium/Bulky Material Storage |  |  | 0.81 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0446 |  | Always On | [5 empty] | 0.17 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp BulkStorage | Warehouse ClgSetp
DOE Ref Pre-1980 | ClimateZone 1-8 | Warehouse | Bulk | 41_31_169 | [6 empty] | 0.62 |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse Bldg Occ | Warehouse Activity |  | 0.2232 | Always On | [5 empty] | 0.25 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp BulkStorage | Warehouse ClgSetp
90.1-2007 | ClimateZone 1-8 | Warehouse | Bulk | 41_31_169 | ASHRAE 90.1-2007 | Warehouse | Medium/Bulky Material Storage | ASHRAE 90.1-2007WarehouseMedium/Bulky Material Storage |  |  | 0.9 |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2004 | Miscellaneous Spaces | Warehouses | ASHRAE 62.1-2004Miscellaneous SpacesWarehouses | 0.06 | 0 | 0 | 0 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0446 |  | Warehouse ALWAYS_ON | [5 empty] | 0.17 | 0 | 0.5 | 0 | Warehouse ALWAYS_OFF | Warehouse Bulk Storage Heating Setpoint Schedule | Warehouse ClgSetp
90.1-2004 | ClimateZone 1-8 | Warehouse | Bulk | 41_31_169 | ASHRAE 90.1-2004 | Warehouse | Medium/Bulky Material Storage | ASHRAE 90.1-2004WarehouseMedium/Bulky Material Storage |  |  | 0.9 |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 | 0 | 0 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0595 |  | Warehouse ALWAYS_ON | [5 empty] | 0.25 | 0 | 0.5 | 0 | Warehouse ALWAYS_OFF | Warehouse Bulk Storage Heating Setpoint Schedule | Warehouse ClgSetp
90.1-2010 | ClimateZone 1-8 | Warehouse | Bulk | 41_31_169 | ASHRAE 90.1-2010 | Warehouse | Medium/Bulky Material Storage | ASHRAE 90.1-2010WarehouseMedium/Bulky Material Storage |  |  | 0.58 |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses | ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | 0.06 | 0 | 0 | 0 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0446 |  | Warehouse ALWAYS_ON | [5 empty] | 0.17 | 0 | 0.5 | 0 | Warehouse ALWAYS_OFF | Warehouse Bulk Storage Heating Setpoint Schedule | Warehouse ClgSetp
Note on AS32: NREL: average size across 8 rooms
Note on AS33: NREL: average size across 8 rooms
Note on AS34: NREL: average size across 8 rooms
Note on AS35: NREL: average size across 8 rooms
Note on AS36: NREL: average size across 8 rooms
Note on AS37: NREL: average size across 8 rooms
Note on AS38: NREL: average size across 8 rooms
Note on AS46: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AS47: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AS48: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AS49: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AS50: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AS51: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AS52: NREL: There is also a 2400 OR with 4x as many people that still shows 2gal/hr.
Note on AS81: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AS82: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AS83: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AS84: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AS85: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AS86: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on AS87: NREL: This is huge. I wonder if space type should be kitchen/dining
Note on D404: NREL: Step down and Recovery same as this
Note on BE545: NREL: Typical - ref has different schedule for 2nd and 3rd floor than first
Note on BE555: NREL: Don’t see an elec object for this in ref building model like I do for other exhaust fans
Note on D612: NREL: Not adjusted for special computer classrroom with slightly higher plug loads
Note on BE667: NREL: Don’t see an elec object for this in ref building model like I do for other exhaust fans
Note on BE762: NREL: Don’t see an elec object for this in ref building model like I do for other exhaust fans
Note on AY861: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AY862: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AY863: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AY864: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AY865: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AY866: NREL: This is for Deli. Bakery only has 0.33 cfm/sf
Note on AY867: NREL: This is for Deli. Bakery only has 0.33 cfm/sf

## Ventilation
Each row represents ventilation requirements for a particular space type in a particular standard. Values are referenced on Space Types tab.
|  |  |  | ventilation | ventilation | ventilation
VlookupColumn | Ventilation Standard | Primary Space Type | Secondary Space Type | ft^3/min*person | ft^3/min*ft^2 | ach | Notes
AIA 2001AncillaryX-Ray (Surgical/Critical Care and Catheterization) | AIA 2001 | Ancillary | X-Ray (Surgical/Critical Care and Catheterization) |  |  | 3
ASHRAE 62.1-1999Correctional FacilitiesCell | ASHRAE 62.1-1999 | Correctional Facilities | Cell | 20 | 0
ASHRAE 62.1-1999Correctional FacilitiesDining halls | ASHRAE 62.1-1999 | Correctional Facilities | Dining halls | 15 | 0
ASHRAE 62.1-1999Correctional FacilitiesGuard stations | ASHRAE 62.1-1999 | Correctional Facilities | Guard stations | 15 | 0
ASHRAE 62.1-2004Correctional FacilitiesDay room | ASHRAE 62.1-2004 | Correctional Facilities | Day room | 5 | 0.06
ASHRAE 62.1-2004Correctional FacilitiesGuard stations | ASHRAE 62.1-2004 | Correctional Facilities | Guard stations | 5 | 0.06
ASHRAE 62.1-2004Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2004 | Correctional Facilities | Booking/waiting | 7.5 | 0.06
ASHRAE 62.1-2007Correctional FacilitiesDay room | ASHRAE 62.1-2007 | Correctional Facilities | Day room | 5 | 0.06
ASHRAE 62.1-2007Correctional FacilitiesGuard stations | ASHRAE 62.1-2007 | Correctional Facilities | Guard stations | 5 | 0.06
ASHRAE 62.1-2007Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2007 | Correctional Facilities | Booking/waiting | 7.5 | 0.06
ASHRAE 62.1-2004Correctional FacilitiesCell | ASHRAE 62.1-2004 | Correctional Facilities | Cell | 5 | 0.12
ASHRAE 62.1-2007Correctional FacilitiesCell | ASHRAE 62.1-2007 | Correctional Facilities | Cell | 5 | 0.12
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial laundry | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial laundry | 25 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial dry cleaner | 30 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesStorage, pick up | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Storage, pick up | 35 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated laundries | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated laundries | 15 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated dry cleaner | 15 | 0
ASHRAE 62.1-1999EducationClassroom | ASHRAE 62.1-1999 | Education | Classroom | 16.95 | 0
ASHRAE 62.1-1999EducationLaboratories | ASHRAE 62.1-1999 | Education | Laboratories | 20 | 0
ASHRAE 62.1-1999EducationTraining shop | ASHRAE 62.1-1999 | Education | Training shop | 20 | 0
ASHRAE 62.1-1999EducationMusic rooms | ASHRAE 62.1-1999 | Education | Music rooms | 15 | 0
ASHRAE 62.1-1999EducationLibraries | ASHRAE 62.1-1999 | Education | Libraries | 16.95 | 0
ASHRAE 62.1-1999EducationAuditorium | ASHRAE 62.1-1999 | Education | Auditorium | 15 | 0
ASHRAE 62.1-1999EducationSmoking lounges | ASHRAE 62.1-1999 | Education | Smoking lounges | 60 | 0
ASHRAE 62.1-1999EducationCorridors | ASHRAE 62.1-1999 | Education | Corridors | 0 | 0.1
ASHRAE 62.1-1999EducationLocker rooms | ASHRAE 62.1-1999 | Education | Locker rooms | 0 | 0.5
ASHRAE 62.1-2004Educational FacilitiesLecture classroom | ASHRAE 62.1-2004 | Educational Facilities | Lecture classroom | 7.5 | 0.06
ASHRAE 62.1-2004Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2004 | Educational Facilities | Lecture hall (fixed seats) | 7.5 | 0.06
ASHRAE 62.1-2004Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2004 | Educational Facilities | Music/theater/dance | 10 | 0.06
ASHRAE 62.1-2004Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2004 | Educational Facilities | Multiuse assembly | 7.5 | 0.06
ASHRAE 62.1-2007Educational FacilitiesLecture classroom | ASHRAE 62.1-2007 | Educational Facilities | Lecture classroom | 7.5 | 0.06
ASHRAE 62.1-2007Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2007 | Educational Facilities | Lecture hall (fixed seats) | 7.5 | 0.06
ASHRAE 62.1-2007Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2007 | Educational Facilities | Music/theater/dance | 10 | 0.06
ASHRAE 62.1-2007Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2007 | Educational Facilities | Multiuse assembly | 7.5 | 0.06
ASHRAE 62.1-2004Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (ages 5-8) | 10 | 0.12
ASHRAE 62.1-2004Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (age 9 plus) | 10 | 0.12
ASHRAE 62.1-2004Educational FacilitiesComputer lab | ASHRAE 62.1-2004 | Educational Facilities | Computer lab | 10 | 0.12
ASHRAE 62.1-2004Educational FacilitiesMedia center | ASHRAE 62.1-2004 | Educational Facilities | Media center | 10 | 0.12 |  | A
ASHRAE 62.1-2007Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (ages 5-8) | 10 | 0.12
ASHRAE 62.1-2007Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (age 9 plus) | 10 | 0.12
ASHRAE 62.1-2007Educational FacilitiesComputer lab | ASHRAE 62.1-2007 | Educational Facilities | Computer lab | 10 | 0.12
ASHRAE 62.1-2007Educational FacilitiesMedia center | ASHRAE 62.1-2007 | Educational Facilities | Media center | 10 | 0.12 |  | A
ASHRAE 62.1-2004Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2004 | Educational Facilities | Daycare (through age 4) | 10 | 0.18
ASHRAE 62.1-2004Educational FacilitiesArt classroom | ASHRAE 62.1-2004 | Educational Facilities | Art classroom | 10 | 0.18
ASHRAE 62.1-2004Educational FacilitiesScience laboratories | ASHRAE 62.1-2004 | Educational Facilities | Science laboratories | 10 | 0.18 |  | E
ASHRAE 62.1-2004Educational FacilitiesWood/metal shop | ASHRAE 62.1-2004 | Educational Facilities | Wood/metal shop | 10 | 0.18
ASHRAE 62.1-2007Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2007 | Educational Facilities | Daycare (through age 4) | 10 | 0.18
ASHRAE 62.1-2007Educational FacilitiesArt classroom | ASHRAE 62.1-2007 | Educational Facilities | Art classroom | 10 | 0.18
ASHRAE 62.1-2007Educational FacilitiesScience laboratories | ASHRAE 62.1-2007 | Educational Facilities | Science laboratories | 10 | 0.18 |  | E
ASHRAE 62.1-2007Educational FacilitiesWood/metal shop | ASHRAE 62.1-2007 | Educational Facilities | Wood/metal shop | 10 | 0.18
ASHRAE 62.1-1999Food and Beverage ServiceDining rooms | ASHRAE 62.1-1999 | Food and Beverage Service | Dining rooms | 20 | 0
ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | 21.2 | 0
ASHRAE 62.1-1999Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-1999 | Food and Beverage Service | Bars, cocktail lounges | 30 | 0
ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | 16.95 | 0 |  | Exhaust >= 1.5 cfm/ft2, 7.5 L/s m2
ASHRAE 62.1-2004Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2004 | Food and Beverage Service | Restaurant dining rooms | 7.5 | 0.18
ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | 7.5 | 0.18
ASHRAE 62.1-2004Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2004 | Food and Beverage Service | Bars, cocktail lounges | 7.5 | 0.18
ASHRAE 62.1-2007Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2007 | Food and Beverage Service | Restaurant dining rooms | 7.5 | 0.18
ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | 7.5 | 0.18
ASHRAE 62.1-2007Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2007 | Food and Beverage Service | Bars, cocktail lounges | 7.5 | 0.18
ASHRAE 62.1-1999Garages, Repair, Service StationsEnclosed parking garage | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Enclosed parking garage | 0 | 1.5
ASHRAE 62.1-1999Garages, Repair, Service StationsAuto repair rooms | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Auto repair rooms | 0 | 1.5
ASHRAE 62.1-2004GeneralConference/meeting | ASHRAE 62.1-2004 | General | Conference/meeting | 5 | 0.06
ASHRAE 62.1-2004GeneralCorridors | ASHRAE 62.1-2004 | General | Corridors |  | 0.06
ASHRAE 62.1-2007GeneralConference/meeting | ASHRAE 62.1-2007 | General | Conference/meeting | 5 | 0.06
ASHRAE 62.1-2007GeneralCorridors | ASHRAE 62.1-2007 | General | Corridors |  | 0.06
ASHRAE 62.1-2004GeneralStorage rooms | ASHRAE 62.1-2004 | General | Storage rooms |  | 0.12 |  | B
ASHRAE 62.1-2007GeneralStorage rooms | ASHRAE 62.1-2007 | General | Storage rooms |  | 0.12 |  | B
GGHC v2.2Health CareBathroom/ Public | GGHC v2.2 | Health Care | Bathroom/ Public |  | 0.15
GGHC v2.2Health CareBedpan Room | GGHC v2.2 | Health Care | Bedpan Room |  | 0.15
GGHC v2.2Health CareLobby | GGHC v2.2 | Health Care | Lobby |  | 0.15
GGHC v2.2Health CareLockers | GGHC v2.2 | Health Care | Lockers |  | 0.15
GGHC v2.2Health CareMechanical Equipment Room | GGHC v2.2 | Health Care | Mechanical Equipment Room |  | 0.15
GGHC v2.2Health CareMedical Records | GGHC v2.2 | Health Care | Medical Records |  | 0.15
GGHC v2.2Health CareNursing Stations- General | GGHC v2.2 | Health Care | Nursing Stations- General |  | 0.15
GGHC v2.2Health CareStairways | GGHC v2.2 | Health Care | Stairways |  | 0.15
GGHC v2.2Health CareWaiting Areas/Lounges | GGHC v2.2 | Health Care | Waiting Areas/Lounges |  | 0.15
GGHC v2.2Health CareAngiographic-All Other Types | GGHC v2.2 | Health Care | Angiographic-All Other Types |  | 0.3
GGHC v2.2Health CareAutopsy | GGHC v2.2 | Health Care | Autopsy |  | 0.3
GGHC v2.2Health CareCast Room | GGHC v2.2 | Health Care | Cast Room |  | 0.3
GGHC v2.2Health CareClean Linen Storage | GGHC v2.2 | Health Care | Clean Linen Storage |  | 0.3
GGHC v2.2Health CareClean Utility / Workroom | GGHC v2.2 | Health Care | Clean Utility / Workroom |  | 0.3
GGHC v2.2Health CareCorridors | GGHC v2.2 | Health Care | Corridors |  | 0.3
GGHC v2.2Health CareDarkroom | GGHC v2.2 | Health Care | Darkroom |  | 0.3
GGHC v2.2Health CareDecontamination | GGHC v2.2 | Health Care | Decontamination |  | 0.3
GGHC v2.2Health CareDietary Day Storage | GGHC v2.2 | Health Care | Dietary Day Storage |  | 0.3
GGHC v2.2Health CareDishwashing | GGHC v2.2 | Health Care | Dishwashing |  | 0.3
GGHC v2.2Health CareEndoscopy | GGHC v2.2 | Health Care | Endoscopy |  | 0.3
GGHC v2.2Health CareHistology | GGHC v2.2 | Health Care | Histology |  | 0.3
GGHC v2.2Health CareIsolation | GGHC v2.2 | Health Care | Isolation |  | 0.3
GGHC v2.2Health CareKitchen, Food Preparation | GGHC v2.2 | Health Care | Kitchen, Food Preparation |  | 0.3
GGHC v2.2Health CareLabor/ Delivery/Recovery | GGHC v2.2 | Health Care | Labor/ Delivery/Recovery |  | 0.3
GGHC v2.2Health CareL / D / R / Post Partum | GGHC v2.2 | Health Care | L / D / R / Post Partum |  | 0.3
GGHC v2.2Health CareLaboratory | GGHC v2.2 | Health Care | Laboratory |  | 0.3
GGHC v2.2Health CareLinen Storage, Clean | GGHC v2.2 | Health Care | Linen Storage, Clean |  | 0.3
GGHC v2.2Health CareMammography | GGHC v2.2 | Health Care | Mammography |  | 0.3
GGHC v2.2Health CareNuclear Medicine, Hot Lab | GGHC v2.2 | Health Care | Nuclear Medicine, Hot Lab |  | 0.3
GGHC v2.2Health CarePathology | GGHC v2.2 | Health Care | Pathology |  | 0.3
GGHC v2.2Health CarePatient Room | GGHC v2.2 | Health Care | Patient Room |  | 0.3
GGHC v2.2Health CarePharmacy / Medicine Room | GGHC v2.2 | Health Care | Pharmacy / Medicine Room |  | 0.3
GGHC v2.2Health CarePhysical Therapy and Hydrotherapy | GGHC v2.2 | Health Care | Physical Therapy and Hydrotherapy |  | 0.3
GGHC v2.2Health CareRecovery | GGHC v2.2 | Health Care | Recovery |  | 0.3
GGHC v2.2Health CareScrub Up Area, Surgical Corridor | GGHC v2.2 | Health Care | Scrub Up Area, Surgical Corridor |  | 0.3
GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic |  | 0.3
GGHC v2.2Health CareSub-Sterile | GGHC v2.2 | Health Care | Sub-Sterile |  | 0.3
GGHC v2.2Health CareSurgical Supply | GGHC v2.2 | Health Care | Surgical Supply |  | 0.3
GGHC v2.2Health CareTreatment / Examination | GGHC v2.2 | Health Care | Treatment / Examination |  | 0.3
GGHC v2.2Health CareUnsterile Supply | GGHC v2.2 | Health Care | Unsterile Supply |  | 0.3
GGHC v2.2Health CareX-ray, Diagnostic and Treatment | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment |  | 0.3
GGHC v2.2Health CareNursery, General | GGHC v2.2 | Health Care | Nursery, General |  | 0.45
GGHC v2.2Health CareNursery, Exam | GGHC v2.2 | Health Care | Nursery, Exam |  | 0.45
GGHC v2.2Health CareConference Rooms | GGHC v2.2 | Health Care | Conference Rooms |  | 0.5
GGHC v2.2Health CareAngiographic-Heart Only | GGHC v2.2 | Health Care | Angiographic-Heart Only |  | 0.75
GGHC v2.2Health CareCystoscopy | GGHC v2.2 | Health Care | Cystoscopy |  | 0.75
GGHC v2.2Health CareDelivery Room | GGHC v2.2 | Health Care | Delivery Room |  | 0.75
GGHC v2.2Health CareOperating Room | GGHC v2.2 | Health Care | Operating Room |  | 0.75
GGHC v2.2Health CareSpecial Procedure Room, Invasive | GGHC v2.2 | Health Care | Special Procedure Room, Invasive |  | 0.75
GGHC v2.2Health CareTrauma | GGHC v2.2 | Health Care | Trauma |  | 0.75
GGHC v2.2Health CareAnesthesia Storage | GGHC v2.2 | Health Care | Anesthesia Storage |  | 1.2
GGHC v2.2Health CareDining Room | GGHC v2.2 | Health Care | Dining Room |  | 1.5
GGHC v2.2Health CareJanitors Closet / Utility | GGHC v2.2 | Health Care | Janitors Closet / Utility |  | 1.5
GGHC v2.2Health CareSoiled Linen, Sorting | GGHC v2.2 | Health Care | Soiled Linen, Sorting |  | 1.5
GGHC v2.2Health CareSterilizer Room | GGHC v2.2 | Health Care | Sterilizer Room |  | 1.5
GGHC v2.2Health CareTrash Chute Room | GGHC v2.2 | Health Care | Trash Chute Room |  | 1.5
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 25 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 15 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 30 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 15 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 15 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 0 | 0.5
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 25 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 30 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms |  | 0.5 |  | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 15
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 25 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 30 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms |  | 0.5 |  | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 15
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBedrooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Bedrooms | 0 | -9999 |  | 30 cfm/room, 15 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLiving rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Living rooms | 0 | -9999 |  | 30 cfm/room, 15 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBaths | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Baths | 0 | -9999 |  | 35 cfm/room, 18 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | 15 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | 20 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesAssembly rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Assembly rooms | 15 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | 15 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesGambling casinos | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Gambling casinos | 30 | 0
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 5 | 0.06
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 5 | 0.06
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 7.5 | 0.06
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 5 | 0.06
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 5 | 0.06
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 5 | 0.06
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 7.5 | 0.06
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2004 | Miscellaneous Spaces | Bank vaults/safe deposit | 5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Computer (not printing) | 5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2004 | Miscellaneous Spaces | Transportation waiting | 7.5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesWarehouses | ASHRAE 62.1-2004 | Miscellaneous Spaces | Warehouses |  | 0.06 |  | B
ASHRAE 62.1-2007Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2007 | Miscellaneous Spaces | Bank vaults/safe deposit | 5 | 0.06
ASHRAE 62.1-2007Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Computer (not printing) | 5 | 0.06
ASHRAE 62.1-2007Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2007 | Miscellaneous Spaces | Transportation waiting | 7.5 | 0.06
ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses |  | 0.06 |  | B
ASHRAE 62.1-2004Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2004 | Miscellaneous Spaces | Photo studios | 5 | 0.12
ASHRAE 62.1-2004Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2004 | Miscellaneous Spaces | Shipping/receiving |  | 0.12 |  | B
ASHRAE 62.1-2007Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2007 | Miscellaneous Spaces | Photo studios | 5 | 0.12
ASHRAE 62.1-2007Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2007 | Miscellaneous Spaces | Shipping/receiving |  | 0.12 |  | B
ASHRAE 62.1-2004Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Pharmacy (prep. area) | 5 | 0.18
ASHRAE 62.1-2007Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Pharmacy (prep. area) | 5 | 0.18
AIA 2001NursingPatient Room | AIA 2001 | Nursing | Patient Room |  |  | 2
AIA 2001NursingNewborn Nursery Suite | AIA 2001 | Nursing | Newborn Nursery Suite |  |  | 2
AIA 2001NursingProtective Environment Room | AIA 2001 | Nursing | Protective Environment Room |  |  | 2
AIA 2001NursingAirborne Infection Isolation Room | AIA 2001 | Nursing | Airborne Infection Isolation Room |  |  | 2
AIA 2001NursingLabor/Delivery/Recovery | AIA 2001 | Nursing | Labor/Delivery/Recovery |  |  | 2
AIA 2001NursingLabor/Delivery/Recovery/Postpartum | AIA 2001 | Nursing | Labor/Delivery/Recovery/Postpartum |  |  | 2
ASHRAE 62.1-2004Office BuildingsOffice space | ASHRAE 62.1-2004 | Office Buildings | Office space | 5 | 0.06
ASHRAE 62.1-2004Office BuildingsReception areas | ASHRAE 62.1-2004 | Office Buildings | Reception areas | 5 | 0.06
ASHRAE 62.1-2004Office BuildingsTelephone/data entry | ASHRAE 62.1-2004 | Office Buildings | Telephone/data entry | 5 | 0.06
ASHRAE 62.1-2004Office BuildingsMain entry lobbies | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsOffice space | ASHRAE 62.1-2007 | Office Buildings | Office space | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsReception areas | ASHRAE 62.1-2007 | Office Buildings | Reception areas | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsTelephone/data entry | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsMain entry lobbies | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | 5 | 0.06
ASHRAE 62.1-1999OfficesOffice space | ASHRAE 62.1-1999 | Offices | Office space | 21.2 | 0
ASHRAE 62.1-1999OfficesReception areas | ASHRAE 62.1-1999 | Offices | Reception areas | 15 | 0
ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | 20 | 0
ASHRAE 62.1-1999OfficesConference rooms | ASHRAE 62.1-1999 | Offices | Conference rooms | 20 | 0
ASHRAE 62.1-2004Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2004 | Public Assembly Spaces | Auditorium seating area | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2004 | Public Assembly Spaces | Places of religious worship | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesCourtrooms | ASHRAE 62.1-2004 | Public Assembly Spaces | Courtrooms | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2004 | Public Assembly Spaces | Legislative chambers | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesLobbies | ASHRAE 62.1-2004 | Public Assembly Spaces | Lobbies | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums/galleries | 7.5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2007 | Public Assembly Spaces | Auditorium seating area | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2007 | Public Assembly Spaces | Places of religious worship | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesCourtrooms | ASHRAE 62.1-2007 | Public Assembly Spaces | Courtrooms | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2007 | Public Assembly Spaces | Legislative chambers | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesLobbies | ASHRAE 62.1-2007 | Public Assembly Spaces | Lobbies | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums/galleries | 7.5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesLibraries | ASHRAE 62.1-2004 | Public Assembly Spaces | Libraries | 5 | 0.12
ASHRAE 62.1-2004Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums (children’s) | 7.5 | 0.12
ASHRAE 62.1-2007Public Assembly SpacesLibraries | ASHRAE 62.1-2007 | Public Assembly Spaces | Libraries | 5 | 0.12
ASHRAE 62.1-2007Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums (children’s) | 7.5 | 0.12
ASHRAE 62.1-1999Public SpacesSmoking lounge | ASHRAE 62.1-1999 | Public Spaces | Smoking lounge | 60 | 0
ASHRAE 62.1-1999Public SpacesCorridors and utilities | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | 0 | 0.05
ASHRAE 62.1-1999Public SpacesLocker and dressing rooms | ASHRAE 62.1-1999 | Public Spaces | Locker and dressing rooms | 0 | 0.5
ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | 0 | 0.96 |  | 50 cfm/wc or urinal, 25 L/s wc or urinal
ASHRAE 62.1-1999Public SpacesElevators | ASHRAE 62.1-1999 | Public Spaces | Elevators | 0 | 1
ASHRAE 62.1-2004RetailMall common areas | ASHRAE 62.1-2004 | Retail | Mall common areas | 7.5 | 0.06
ASHRAE 62.1-2004RetailBarber shop | ASHRAE 62.1-2004 | Retail | Barber shop | 7.5 | 0.06
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 7.5 | 0.06
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 7.5 | 0.06
ASHRAE 62.1-2004RetailCoinoperated laundries | ASHRAE 62.1-2004 | Retail | Coinoperated laundries | 7.5 | 0.06
ASHRAE 62.1-2007RetailMall common areas | ASHRAE 62.1-2007 | Retail | Mall common areas | 7.5 | 0.06
ASHRAE 62.1-2007RetailBarber shop | ASHRAE 62.1-2007 | Retail | Barber shop | 7.5 | 0.06
ASHRAE 62.1-2007RetailSupermarket | ASHRAE 62.1-2007 | Retail | Supermarket | 7.5 | 0.06
ASHRAE 62.1-2007RetailCoinoperated laundries | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | 7.5 | 0.06
ASHRAE 62.1-2004RetailGeneral Sales | ASHRAE 62.1-2004 | Retail | General Sales | 7.5 | 0.12
ASHRAE 62.1-2004RetailBeauty and nail salons | ASHRAE 62.1-2004 | Retail | Beauty and nail salons | 20 | 0.12
ASHRAE 62.1-2007RetailGeneral Sales | ASHRAE 62.1-2007 | Retail | General Sales | 7.5 | 0.12
ASHRAE 62.1-2007RetailBeauty and nail salons | ASHRAE 62.1-2007 | Retail | Beauty and nail salons | 20 | 0.12
ASHRAE 62.1-2004RetailPet shops (animal areas) | ASHRAE 62.1-2004 | Retail | Pet shops (animal areas) | 7.5 | 0.18
ASHRAE 62.1-2007RetailPet shops (animal areas) | ASHRAE 62.1-2007 | Retail | Pet shops (animal areas) | 7.5 | 0.18
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsSmoking lounge | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Smoking lounge | 60 | 0
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | 0 | 0.05
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | 0 | 0.15
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | 0 | 0.15
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsUpper floors | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Upper floors | 0 | 0.2
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsDressing rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Dressing rooms | 0 | 0.2
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsMalls and arcades | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Malls and arcades | 0 | 0.2
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | 0 | 0.3
ASHRAE 62.1-1999Specialty ShopsBarber | ASHRAE 62.1-1999 | Specialty Shops | Barber | 15 | 0
ASHRAE 62.1-1999Specialty ShopsBeauty | ASHRAE 62.1-1999 | Specialty Shops | Beauty | 25 | 0
ASHRAE 62.1-1999Specialty ShopsReducing salons | ASHRAE 62.1-1999 | Specialty Shops | Reducing salons | 15 | 0
ASHRAE 62.1-1999Specialty ShopsFlorists | ASHRAE 62.1-1999 | Specialty Shops | Florists | 15 | 0
ASHRAE 62.1-1999Specialty ShopsHardware, drugs, fabric | ASHRAE 62.1-1999 | Specialty Shops | Hardware, drugs, fabric | 15 | 0
ASHRAE 62.1-1999Specialty ShopsSupermarket | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | 15 | 0
ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | 0 | 0.3
ASHRAE 62.1-1999Specialty ShopsPet shops | ASHRAE 62.1-1999 | Specialty Shops | Pet shops | 0 | 1
ASHRAE 62.1-1999Sports and AmusementSpectator areas | ASHRAE 62.1-1999 | Sports and Amusement | Spectator areas | 15 | 0
ASHRAE 62.1-1999Sports and AmusementGame rooms | ASHRAE 62.1-1999 | Sports and Amusement | Game rooms | 25 | 0
ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | 21.2 | 0
ASHRAE 62.1-1999Sports and AmusementBallrooms and discos | ASHRAE 62.1-1999 | Sports and Amusement | Ballrooms and discos | 25 | 0
ASHRAE 62.1-1999Sports and AmusementBowling alleys (seating areas) | ASHRAE 62.1-1999 | Sports and Amusement | Bowling alleys (seating areas) | 25 | 0
ASHRAE 62.1-1999Sports and AmusementIce arenas (playing areas) | ASHRAE 62.1-1999 | Sports and Amusement | Ice arenas (playing areas) | 0 | 0.5 |  | Higher may be needed if internal combustion engines are operated for maintenance
ASHRAE 62.1-1999Sports and AmusementSwimming pools (pool and deck areas) | ASHRAE 62.1-1999 | Sports and Amusement | Swimming pools (pool and deck areas) | 0 | 0.5 |  | Higher may be needed for humidity control
ASHRAE 62.1-2004Sports and EntertainmentSpectator areas | ASHRAE 62.1-2004 | Sports and Entertainment | Spectator areas | 7.5 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2004 | Sports and Entertainment | Disco/dance floors | 20 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/aerobics room | 20 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/weight rooms | 20 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentStages, studios | ASHRAE 62.1-2004 | Sports and Entertainment | Stages, studios | 10 | 0.06 |  | D
ASHRAE 62.1-2007Sports and EntertainmentSpectator areas | ASHRAE 62.1-2007 | Sports and Entertainment | Spectator areas | 7.5 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2007 | Sports and Entertainment | Disco/dance floors | 20 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/aerobics room | 20 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/weight rooms | 20 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentStages, studios | ASHRAE 62.1-2007 | Sports and Entertainment | Stages, studios | 10 | 0.06 |  | D
ASHRAE 62.1-2004Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2004 | Sports and Entertainment | Bowling alley (seating) | 10 | 0.12
ASHRAE 62.1-2007Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2007 | Sports and Entertainment | Bowling alley (seating) | 10 | 0.12
ASHRAE 62.1-2004Sports and EntertainmentGambling casinos | ASHRAE 62.1-2004 | Sports and Entertainment | Gambling casinos | 7.5 | 0.18
ASHRAE 62.1-2004Sports and EntertainmentGame arcades | ASHRAE 62.1-2004 | Sports and Entertainment | Game arcades | 7.5 | 0.18
ASHRAE 62.1-2007Sports and EntertainmentGambling casinos | ASHRAE 62.1-2007 | Sports and Entertainment | Gambling casinos | 7.5 | 0.18
ASHRAE 62.1-2007Sports and EntertainmentGame arcades | ASHRAE 62.1-2007 | Sports and Entertainment | Game arcades | 7.5 | 0.18
ASHRAE 62.1-2004Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Sports arena (play area) |  | 0.3
ASHRAE 62.1-2004Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Gym, stadium (play area) |  | 0.3
ASHRAE 62.1-2007Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Sports arena (play area) |  | 0.3
ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) |  | 0.3
ASHRAE 62.1-2004Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2004 | Sports and Entertainment | Swimming (pool & deck) |  | 0.48 |  | C
ASHRAE 62.1-2007Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2007 | Sports and Entertainment | Swimming (pool & deck) |  | 0.48 |  | C
AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms |  |  | 3
AIA 2001Surgery and Critical CareDelivery Room | AIA 2001 | Surgery and Critical Care | Delivery Room |  |  | 3
AIA 2001Surgery and Critical CareRecovery Room | AIA 2001 | Surgery and Critical Care | Recovery Room |  |  | 2
AIA 2001Surgery and Critical CareCritical and Intensive Care | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care |  |  | 2
AIA 2001Surgery and Critical CareNewborn Intensive Care | AIA 2001 | Surgery and Critical Care | Newborn Intensive Care |  |  | 2
AIA 2001Surgery and Critical CareTrauma Room | AIA 2001 | Surgery and Critical Care | Trauma Room |  |  | 3
AIA 2001Surgery and Critical CareEndoscopy | AIA 2001 | Surgery and Critical Care | Endoscopy |  |  | 2
AIA 2001Surgery and Critical CareBronchoscopy | AIA 2001 | Surgery and Critical Care | Bronchoscopy |  |  | 2
AIA 2001Surgery and Critical CareER Waiting Room | AIA 2001 | Surgery and Critical Care | ER Waiting Room |  |  | 2
AIA 2001Surgery and Critical CareTriage | AIA 2001 | Surgery and Critical Care | Triage |  |  | 2
AIA 2001Surgery and Critical CareRadiology Waiting Rooms | AIA 2001 | Surgery and Critical Care | Radiology Waiting Rooms |  |  | 2
AIA 2001Surgery and Critical CareProcedure Room | AIA 2001 | Surgery and Critical Care | Procedure Room |  |  | 3
ASHRAE 62.1-1999TheatersTicket booths | ASHRAE 62.1-1999 | Theaters | Ticket booths | 20 | 0
ASHRAE 62.1-1999TheatersLobbies | ASHRAE 62.1-1999 | Theaters | Lobbies | 20 | 0
ASHRAE 62.1-1999TheatersAuditorium | ASHRAE 62.1-1999 | Theaters | Auditorium | 15 | 0
ASHRAE 62.1-1999TheatersStages, studios | ASHRAE 62.1-1999 | Theaters | Stages, studios | 15 | 0
ASHRAE 62.1-1999TransportationWaiting rooms | ASHRAE 62.1-1999 | Transportation | Waiting rooms | 15 | 0
ASHRAE 62.1-1999TransportationPlatforms | ASHRAE 62.1-1999 | Transportation | Platforms | 15 | 0
ASHRAE 62.1-1999TransportationVehicles | ASHRAE 62.1-1999 | Transportation | Vehicles | 15 | 0
ASHRAE 62.1-1999WorkroomsMeat processing | ASHRAE 62.1-1999 | Workrooms | Meat processing | 15 | 0
ASHRAE 62.1-1999WorkroomsPhoto studios | ASHRAE 62.1-1999 | Workrooms | Photo studios | 15 | 0
ASHRAE 62.1-1999WorkroomsPharmacy | ASHRAE 62.1-1999 | Workrooms | Pharmacy | 15 | 0
ASHRAE 62.1-1999WorkroomsBank vaults | ASHRAE 62.1-1999 | Workrooms | Bank vaults | 15 | 0
ASHRAE 62.1-1999WorkroomsDarkrooms | ASHRAE 62.1-1999 | Workrooms | Darkrooms | 0 | 0.5
ASHRAE 62.1-1999WorkroomsDuplicating, printing | ASHRAE 62.1-1999 | Workrooms | Duplicating, printing | 0 | 0.5

## Occupancy
Each row represents typical design occupancy for a particular space type in a particular standard. Values may be referenced on Space Types tab.
occupancy
VlookupColumn | Ventilation Standard | Primary Space Type | Secondary Space Type | people/1000 ft^2 | Notes
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial laundry | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial laundry | 10
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial dry cleaner | 30
ASHRAE 62.1-1999Dry Cleaners, LaundriesStorage, pick up | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Storage, pick up | 30
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated laundries | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated laundries | 20
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated dry cleaner | 20
ASHRAE 62.1-1999Food and Beverage ServiceDining rooms | ASHRAE 62.1-1999 | Food and Beverage Service | Dining rooms | 70
ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | 100
ASHRAE 62.1-1999Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-1999 | Food and Beverage Service | Bars, cocktail lounges | 100
ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | 20 | Exhaust >= 1.5 cfm/ft2, 7.5 L/s m2
ASHRAE 62.1-1999Garages, Repair, Service StationsEnclosed parking garage | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Enclosed parking garage | 0
ASHRAE 62.1-1999Garages, Repair, Service StationsAuto repair rooms | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Auto repair rooms | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBedrooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Bedrooms | 0 | 30 cfm/room, 15 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLiving rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Living rooms | 0 | 30 cfm/room, 15 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBaths | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Baths | 0 | 35 cfm/room, 18 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | 30
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | 50
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesAssembly rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Assembly rooms | 120
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | 20
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesGambling casinos | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Gambling casinos | 120
ASHRAE 62.1-1999OfficesOffice space | ASHRAE 62.1-1999 | Offices | Office space | 7
ASHRAE 62.1-1999OfficesReception areas | ASHRAE 62.1-1999 | Offices | Reception areas | 60
ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | 60
ASHRAE 62.1-1999OfficesConference rooms | ASHRAE 62.1-1999 | Offices | Conference rooms | 50
ASHRAE 62.1-1999Public SpacesCorridors and utilities | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | 0
ASHRAE 62.1-1999Public SpacesPublic restrooms | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | 0 | (Assume 12 toilet/625 ft^2) 50 cfm/wc or urinal, 25 L/s wc or urinal
ASHRAE 62.1-1999Public SpacesLocker and dressing rooms | ASHRAE 62.1-1999 | Public Spaces | Locker and dressing rooms | 0
ASHRAE 62.1-1999Public SpacesSmoking lounge | ASHRAE 62.1-1999 | Public Spaces | Smoking lounge | 70
ASHRAE 62.1-1999Public SpacesElevators | ASHRAE 62.1-1999 | Public Spaces | Elevators | 0
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | 30
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsUpper floors | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Upper floors | 20
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | 15
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsDressing rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Dressing rooms | 0
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsMalls and arcades | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Malls and arcades | 20
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | 10
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | 5
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsSmoking lounge | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Smoking lounge | 70
ASHRAE 62.1-1999Specialty ShopsBarber | ASHRAE 62.1-1999 | Specialty Shops | Barber | 25
ASHRAE 62.1-1999Specialty ShopsBeauty | ASHRAE 62.1-1999 | Specialty Shops | Beauty | 25
ASHRAE 62.1-1999Specialty ShopsReducing salons | ASHRAE 62.1-1999 | Specialty Shops | Reducing salons | 20
ASHRAE 62.1-1999Specialty ShopsFlorists | ASHRAE 62.1-1999 | Specialty Shops | Florists | 8
ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | 0
ASHRAE 62.1-1999Specialty ShopsHardware, drugs, fabric | ASHRAE 62.1-1999 | Specialty Shops | Hardware, drugs, fabric | 8
ASHRAE 62.1-1999Specialty ShopsSupermarket | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | 8
ASHRAE 62.1-1999Specialty ShopsPet shops | ASHRAE 62.1-1999 | Specialty Shops | Pet shops | 0
ASHRAE 62.1-1999Sports and AmusementSpectator areas | ASHRAE 62.1-1999 | Sports and Amusement | Spectator areas | 150
ASHRAE 62.1-1999Sports and AmusementGame rooms | ASHRAE 62.1-1999 | Sports and Amusement | Game rooms | 70
ASHRAE 62.1-1999Sports and AmusementIce arenas (playing areas) | ASHRAE 62.1-1999 | Sports and Amusement | Ice arenas (playing areas) | 0 | Higher may be needed if internal combustion engines are operated for maintenance
ASHRAE 62.1-1999Sports and AmusementSwimming pools (pool and deck areas) | ASHRAE 62.1-1999 | Sports and Amusement | Swimming pools (pool and deck areas) | 0 | Higher may be needed for humidity control
ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | 30
ASHRAE 62.1-1999Sports and AmusementBallrooms and discos | ASHRAE 62.1-1999 | Sports and Amusement | Ballrooms and discos | 100
ASHRAE 62.1-1999Sports and AmusementBowling alleys (seating areas) | ASHRAE 62.1-1999 | Sports and Amusement | Bowling alleys (seating areas) | 70
ASHRAE 62.1-1999TheatersTicket booths | ASHRAE 62.1-1999 | Theaters | Ticket booths | 60
ASHRAE 62.1-1999TheatersLobbies | ASHRAE 62.1-1999 | Theaters | Lobbies | 150
ASHRAE 62.1-1999TheatersAuditorium | ASHRAE 62.1-1999 | Theaters | Auditorium | 150
ASHRAE 62.1-1999TheatersStages, studios | ASHRAE 62.1-1999 | Theaters | Stages, studios | 70
ASHRAE 62.1-1999TransportationWaiting rooms | ASHRAE 62.1-1999 | Transportation | Waiting rooms | 100
ASHRAE 62.1-1999TransportationPlatforms | ASHRAE 62.1-1999 | Transportation | Platforms | 100
ASHRAE 62.1-1999TransportationVehicles | ASHRAE 62.1-1999 | Transportation | Vehicles | 150
ASHRAE 62.1-1999WorkroomsMeat processing | ASHRAE 62.1-1999 | Workrooms | Meat processing | 10
ASHRAE 62.1-1999WorkroomsPhoto studios | ASHRAE 62.1-1999 | Workrooms | Photo studios | 10
ASHRAE 62.1-1999WorkroomsDarkrooms | ASHRAE 62.1-1999 | Workrooms | Darkrooms | 10
ASHRAE 62.1-1999WorkroomsPharmacy | ASHRAE 62.1-1999 | Workrooms | Pharmacy | 20
ASHRAE 62.1-1999WorkroomsBank vaults | ASHRAE 62.1-1999 | Workrooms | Bank vaults | 5
ASHRAE 62.1-1999WorkroomsDuplicating, printing | ASHRAE 62.1-1999 | Workrooms | Duplicating, printing | 0
ASHRAE 62.1-1999EducationClassroom | ASHRAE 62.1-1999 | Education | Classroom | 50
ASHRAE 62.1-1999EducationLaboratories | ASHRAE 62.1-1999 | Education | Laboratories | 30
ASHRAE 62.1-1999EducationTraining shop | ASHRAE 62.1-1999 | Education | Training shop | 30
ASHRAE 62.1-1999EducationMusic rooms | ASHRAE 62.1-1999 | Education | Music rooms | 50
ASHRAE 62.1-1999EducationLibraries | ASHRAE 62.1-1999 | Education | Libraries | 20
ASHRAE 62.1-1999EducationLocker rooms | ASHRAE 62.1-1999 | Education | Locker rooms | 0
ASHRAE 62.1-1999EducationCorridors | ASHRAE 62.1-1999 | Education | Corridors | 0
ASHRAE 62.1-1999EducationAuditorium | ASHRAE 62.1-1999 | Education | Auditorium | 150
ASHRAE 62.1-1999EducationSmoking lounges | ASHRAE 62.1-1999 | Education | Smoking lounges | 70
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 10
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 20
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 20
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 20
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 20
ASHRAE 62.1-1999Correctional FacilitiesCell | ASHRAE 62.1-1999 | Correctional Facilities | Cell | 20
ASHRAE 62.1-1999Correctional FacilitiesDining halls | ASHRAE 62.1-1999 | Correctional Facilities | Dining halls | 100
ASHRAE 62.1-1999Correctional FacilitiesGuard stations | ASHRAE 62.1-1999 | Correctional Facilities | Guard stations | 40
ASHRAE 62.1-2004Correctional FacilitiesCell | ASHRAE 62.1-2004 | Correctional Facilities | Cell | 25
ASHRAE 62.1-2004Correctional FacilitiesDay room | ASHRAE 62.1-2004 | Correctional Facilities | Day room | 30
ASHRAE 62.1-2004Correctional FacilitiesGuard stations | ASHRAE 62.1-2004 | Correctional Facilities | Guard stations | 15
ASHRAE 62.1-2004Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2004 | Correctional Facilities | Booking/waiting | 50
ASHRAE 62.1-2004Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2004 | Educational Facilities | Daycare (through age 4) | 25
ASHRAE 62.1-2004Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (ages 5-8) | 25
ASHRAE 62.1-2004Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (age 9 plus) | 35
ASHRAE 62.1-2004Educational FacilitiesLecture classroom | ASHRAE 62.1-2004 | Educational Facilities | Lecture classroom | 65
ASHRAE 62.1-2004Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2004 | Educational Facilities | Lecture hall (fixed seats) | 150
ASHRAE 62.1-2004Educational FacilitiesArt classroom | ASHRAE 62.1-2004 | Educational Facilities | Art classroom | 20
ASHRAE 62.1-2004Educational FacilitiesScience laboratories | ASHRAE 62.1-2004 | Educational Facilities | Science laboratories | 25 | E
ASHRAE 62.1-2004Educational FacilitiesWood/metal shop | ASHRAE 62.1-2004 | Educational Facilities | Wood/metal shop | 20
ASHRAE 62.1-2004Educational FacilitiesComputer lab | ASHRAE 62.1-2004 | Educational Facilities | Computer lab | 25
ASHRAE 62.1-2004Educational FacilitiesMedia center | ASHRAE 62.1-2004 | Educational Facilities | Media center | 25 | A
ASHRAE 62.1-2004Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2004 | Educational Facilities | Music/theater/dance | 35
ASHRAE 62.1-2004Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2004 | Educational Facilities | Multiuse assembly | 100
ASHRAE 62.1-2004Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2004 | Food and Beverage Service | Restaurant dining rooms | 70
ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | 100
ASHRAE 62.1-2004Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2004 | Food and Beverage Service | Bars, cocktail lounges | 100
ASHRAE 62.1-2004GeneralConference/meeting | ASHRAE 62.1-2004 | General | Conference/meeting | 50
ASHRAE 62.1-2004GeneralCorridors | ASHRAE 62.1-2004 | General | Corridors | 0
ASHRAE 62.1-2004GeneralStorage rooms | ASHRAE 62.1-2004 | General | Storage rooms | 0 | B
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 10
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 20
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 30
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 120
ASHRAE 62.1-2004Office BuildingsOffice space | ASHRAE 62.1-2004 | Office Buildings | Office space | 5
ASHRAE 62.1-2004Office BuildingsReception areas | ASHRAE 62.1-2004 | Office Buildings | Reception areas | 30
ASHRAE 62.1-2004Office BuildingsTelephone/data entry | ASHRAE 62.1-2004 | Office Buildings | Telephone/data entry | 60
ASHRAE 62.1-2004Office BuildingsMain entry lobbies | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | 10
ASHRAE 62.1-2004Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2004 | Miscellaneous Spaces | Bank vaults/safe deposit | 5
ASHRAE 62.1-2004Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Computer (not printing) | 4
ASHRAE 62.1-2004Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Pharmacy (prep. area) | 10
ASHRAE 62.1-2004Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2004 | Miscellaneous Spaces | Photo studios | 10
ASHRAE 62.1-2004Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2004 | Miscellaneous Spaces | Shipping/receiving | 0 | B
ASHRAE 62.1-2004Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2004 | Miscellaneous Spaces | Transportation waiting | 100
ASHRAE 62.1-2004Miscellaneous SpacesWarehouses | ASHRAE 62.1-2004 | Miscellaneous Spaces | Warehouses | 0 | B
ASHRAE 62.1-2004Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2004 | Public Assembly Spaces | Auditorium seating area | 150
ASHRAE 62.1-2004Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2004 | Public Assembly Spaces | Places of religious worship | 120
ASHRAE 62.1-2004Public Assembly SpacesCourtrooms | ASHRAE 62.1-2004 | Public Assembly Spaces | Courtrooms | 70
ASHRAE 62.1-2004Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2004 | Public Assembly Spaces | Legislative chambers | 50
ASHRAE 62.1-2004Public Assembly SpacesLibraries | ASHRAE 62.1-2004 | Public Assembly Spaces | Libraries | 10
ASHRAE 62.1-2004Public Assembly SpacesLobbies | ASHRAE 62.1-2004 | Public Assembly Spaces | Lobbies | 150
ASHRAE 62.1-2004Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums (children’s) | 40
ASHRAE 62.1-2004Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums/galleries | 40
ASHRAE 62.1-2004RetailGeneral Sales | ASHRAE 62.1-2004 | Retail | General Sales | 15
ASHRAE 62.1-2004RetailMall common areas | ASHRAE 62.1-2004 | Retail | Mall common areas | 40
ASHRAE 62.1-2004RetailBarber shop | ASHRAE 62.1-2004 | Retail | Barber shop | 25
ASHRAE 62.1-2004RetailBeauty and nail salons | ASHRAE 62.1-2004 | Retail | Beauty and nail salons | 25
ASHRAE 62.1-2004RetailPet shops (animal areas) | ASHRAE 62.1-2004 | Retail | Pet shops (animal areas) | 10
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 8
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 8
ASHRAE 62.1-2004RetailCoinoperated laundries | ASHRAE 62.1-2004 | Retail | Coinoperated laundries | 20
ASHRAE 62.1-2004Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Sports arena (play area) | 0
ASHRAE 62.1-2004Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Gym, stadium (play area) | 30
ASHRAE 62.1-2004Sports and EntertainmentSpectator areas | ASHRAE 62.1-2004 | Sports and Entertainment | Spectator areas | 150
ASHRAE 62.1-2004Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2004 | Sports and Entertainment | Swimming (pool & deck) | 0 | C
ASHRAE 62.1-2004Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2004 | Sports and Entertainment | Disco/dance floors | 100
ASHRAE 62.1-2004Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/aerobics room | 40
ASHRAE 62.1-2004Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/weight rooms | 10
ASHRAE 62.1-2004Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2004 | Sports and Entertainment | Bowling alley (seating) | 40
ASHRAE 62.1-2004Sports and EntertainmentGambling casinos | ASHRAE 62.1-2004 | Sports and Entertainment | Gambling casinos | 120
ASHRAE 62.1-2004Sports and EntertainmentGame arcades | ASHRAE 62.1-2004 | Sports and Entertainment | Game arcades | 20
ASHRAE 62.1-2004Sports and EntertainmentStages, studios | ASHRAE 62.1-2004 | Sports and Entertainment | Stages, studios | 70 | D
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 10 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 20 | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 20
ASHRAE 62.1-2007Correctional FacilitiesCell | ASHRAE 62.1-2007 | Correctional Facilities | Cell | 25
ASHRAE 62.1-2007Correctional FacilitiesDay room | ASHRAE 62.1-2007 | Correctional Facilities | Day room | 30
ASHRAE 62.1-2007Correctional FacilitiesGuard stations | ASHRAE 62.1-2007 | Correctional Facilities | Guard stations | 15
ASHRAE 62.1-2007Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2007 | Correctional Facilities | Booking/waiting | 50
ASHRAE 62.1-2007Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2007 | Educational Facilities | Daycare (through age 4) | 25
ASHRAE 62.1-2007Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (ages 5-8) | 25
ASHRAE 62.1-2007Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (age 9 plus) | 35
ASHRAE 62.1-2007Educational FacilitiesLecture classroom | ASHRAE 62.1-2007 | Educational Facilities | Lecture classroom | 65
ASHRAE 62.1-2007Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2007 | Educational Facilities | Lecture hall (fixed seats) | 150
ASHRAE 62.1-2007Educational FacilitiesArt classroom | ASHRAE 62.1-2007 | Educational Facilities | Art classroom | 20
ASHRAE 62.1-2007Educational FacilitiesScience laboratories | ASHRAE 62.1-2007 | Educational Facilities | Science laboratories | 25 | E
ASHRAE 62.1-2007Educational FacilitiesWood/metal shop | ASHRAE 62.1-2007 | Educational Facilities | Wood/metal shop | 20
ASHRAE 62.1-2007Educational FacilitiesComputer lab | ASHRAE 62.1-2007 | Educational Facilities | Computer lab | 25
ASHRAE 62.1-2007Educational FacilitiesMedia center | ASHRAE 62.1-2007 | Educational Facilities | Media center | 25 | A
ASHRAE 62.1-2007Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2007 | Educational Facilities | Music/theater/dance | 35
ASHRAE 62.1-2007Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2007 | Educational Facilities | Multiuse assembly | 100
ASHRAE 62.1-2007Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2007 | Food and Beverage Service | Restaurant dining rooms | 70
ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | 100
ASHRAE 62.1-2007Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2007 | Food and Beverage Service | Bars, cocktail lounges | 100
ASHRAE 62.1-2007GeneralConference/meeting | ASHRAE 62.1-2007 | General | Conference/meeting | 50
ASHRAE 62.1-2007GeneralCorridors | ASHRAE 62.1-2007 | General | Corridors | 0
ASHRAE 62.1-2007GeneralStorage rooms | ASHRAE 62.1-2007 | General | Storage rooms | 0 | B
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 10
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 20
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 30
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 120
ASHRAE 62.1-2007Office BuildingsOffice space | ASHRAE 62.1-2007 | Office Buildings | Office space | 5
ASHRAE 62.1-2007Office BuildingsReception areas | ASHRAE 62.1-2007 | Office Buildings | Reception areas | 30
ASHRAE 62.1-2007Office BuildingsTelephone/data entry | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | 60
ASHRAE 62.1-2007Office BuildingsMain entry lobbies | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | 10
ASHRAE 62.1-2007Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2007 | Miscellaneous Spaces | Bank vaults/safe deposit | 5
ASHRAE 62.1-2007Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Computer (not printing) | 4
ASHRAE 62.1-2007Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Pharmacy (prep. area) | 10
ASHRAE 62.1-2007Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2007 | Miscellaneous Spaces | Photo studios | 10
ASHRAE 62.1-2007Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2007 | Miscellaneous Spaces | Shipping/receiving | 0 | B
ASHRAE 62.1-2007Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2007 | Miscellaneous Spaces | Transportation waiting | 100
ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses | 0 | B
ASHRAE 62.1-2007Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2007 | Public Assembly Spaces | Auditorium seating area | 150
ASHRAE 62.1-2007Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2007 | Public Assembly Spaces | Places of religious worship | 120
ASHRAE 62.1-2007Public Assembly SpacesCourtrooms | ASHRAE 62.1-2007 | Public Assembly Spaces | Courtrooms | 70
ASHRAE 62.1-2007Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2007 | Public Assembly Spaces | Legislative chambers | 50
ASHRAE 62.1-2007Public Assembly SpacesLibraries | ASHRAE 62.1-2007 | Public Assembly Spaces | Libraries | 10
ASHRAE 62.1-2007Public Assembly SpacesLobbies | ASHRAE 62.1-2007 | Public Assembly Spaces | Lobbies | 150
ASHRAE 62.1-2007Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums (children’s) | 40
ASHRAE 62.1-2007Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums/galleries | 40
ASHRAE 62.1-2007RetailGeneral Sales | ASHRAE 62.1-2007 | Retail | General Sales | 15
ASHRAE 62.1-2007RetailMall common areas | ASHRAE 62.1-2007 | Retail | Mall common areas | 40
ASHRAE 62.1-2007RetailBarber shop | ASHRAE 62.1-2007 | Retail | Barber shop | 25
ASHRAE 62.1-2007RetailBeauty and nail salons | ASHRAE 62.1-2007 | Retail | Beauty and nail salons | 25
ASHRAE 62.1-2007RetailPet shops (animal areas) | ASHRAE 62.1-2007 | Retail | Pet shops (animal areas) | 10
ASHRAE 62.1-2007RetailSupermarket | ASHRAE 62.1-2007 | Retail | Supermarket | 8
ASHRAE 62.1-2007RetailCoinoperated laundries | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | 20
ASHRAE 62.1-2007Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Sports arena (play area) | 0
ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) | 30
ASHRAE 62.1-2007Sports and EntertainmentSpectator areas | ASHRAE 62.1-2007 | Sports and Entertainment | Spectator areas | 150
ASHRAE 62.1-2007Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2007 | Sports and Entertainment | Swimming (pool & deck) | 0 | C
ASHRAE 62.1-2007Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2007 | Sports and Entertainment | Disco/dance floors | 100
ASHRAE 62.1-2007Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/aerobics room | 40
ASHRAE 62.1-2007Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/weight rooms | 10
ASHRAE 62.1-2007Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2007 | Sports and Entertainment | Bowling alley (seating) | 40
ASHRAE 62.1-2007Sports and EntertainmentGambling casinos | ASHRAE 62.1-2007 | Sports and Entertainment | Gambling casinos | 120
ASHRAE 62.1-2007Sports and EntertainmentGame arcades | ASHRAE 62.1-2007 | Sports and Entertainment | Game arcades | 20
ASHRAE 62.1-2007Sports and EntertainmentStages, studios | ASHRAE 62.1-2007 | Sports and Entertainment | Stages, studios | 70 | D
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 10 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 20 | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 20
GGHC v2.2Health CareAnesthesia Storage | GGHC v2.2 | Health Care | Anesthesia Storage | 5
GGHC v2.2Health CareAngiographic-All Other Types | GGHC v2.2 | Health Care | Angiographic-All Other Types | 5
GGHC v2.2Health CareAngiographic-Heart Only | GGHC v2.2 | Health Care | Angiographic-Heart Only | 5
GGHC v2.2Health CareAutopsy | GGHC v2.2 | Health Care | Autopsy | 5
GGHC v2.2Health CareBathroom/ Public | GGHC v2.2 | Health Care | Bathroom/ Public | 3.3
GGHC v2.2Health CareBedpan Room | GGHC v2.2 | Health Care | Bedpan Room | 5
GGHC v2.2Health CareCast Room | GGHC v2.2 | Health Care | Cast Room | 5
GGHC v2.2Health CareClean Linen Storage | GGHC v2.2 | Health Care | Clean Linen Storage | 1
GGHC v2.2Health CareClean Utility / Workroom | GGHC v2.2 | Health Care | Clean Utility / Workroom | 5
GGHC v2.2Health CareConference Rooms | GGHC v2.2 | Health Care | Conference Rooms | 20
GGHC v2.2Health CareCorridors | GGHC v2.2 | Health Care | Corridors | 10
GGHC v2.2Health CareCystoscopy | GGHC v2.2 | Health Care | Cystoscopy | 5
GGHC v2.2Health CareDarkroom | GGHC v2.2 | Health Care | Darkroom | 5
GGHC v2.2Health CareDecontamination | GGHC v2.2 | Health Care | Decontamination | 5
GGHC v2.2Health CareDelivery Room | GGHC v2.2 | Health Care | Delivery Room | 5
GGHC v2.2Health CareDietary Day Storage | GGHC v2.2 | Health Care | Dietary Day Storage | 2
GGHC v2.2Health CareDining Room | GGHC v2.2 | Health Care | Dining Room | 10
GGHC v2.2Health CareDishwashing | GGHC v2.2 | Health Care | Dishwashing | 5
GGHC v2.2Health CareEndoscopy | GGHC v2.2 | Health Care | Endoscopy | 5
GGHC v2.2Health CareHistology | GGHC v2.2 | Health Care | Histology | 5
GGHC v2.2Health CareIsolation | GGHC v2.2 | Health Care | Isolation | 5
GGHC v2.2Health CareJanitors Closet / Utility | GGHC v2.2 | Health Care | Janitors Closet / Utility | 1
GGHC v2.2Health CareKitchen, Food Preparation | GGHC v2.2 | Health Care | Kitchen, Food Preparation | 5
GGHC v2.2Health CareLabor/ Delivery/Recovery | GGHC v2.2 | Health Care | Labor/ Delivery/Recovery | 5
GGHC v2.2Health CareL / D / R / Post Partum | GGHC v2.2 | Health Care | L / D / R / Post Partum | 5
GGHC v2.2Health CareLaboratory | GGHC v2.2 | Health Care | Laboratory | 5
GGHC v2.2Health CareLinen Storage, Clean | GGHC v2.2 | Health Care | Linen Storage, Clean | 2
GGHC v2.2Health CareLobby | GGHC v2.2 | Health Care | Lobby | 10
GGHC v2.2Health CareLockers | GGHC v2.2 | Health Care | Lockers | 10
GGHC v2.2Health CareMammography | GGHC v2.2 | Health Care | Mammography | 5
GGHC v2.2Health CareMechanical Equipment Room | GGHC v2.2 | Health Care | Mechanical Equipment Room | 0.5
GGHC v2.2Health CareMedical Records | GGHC v2.2 | Health Care | Medical Records | 2
GGHC v2.2Health CareNuclear Medicine, Hot Lab | GGHC v2.2 | Health Care | Nuclear Medicine, Hot Lab | 5
GGHC v2.2Health CareNursery, General | GGHC v2.2 | Health Care | Nursery, General | 5
GGHC v2.2Health CareNursery, Exam | GGHC v2.2 | Health Care | Nursery, Exam | 5
GGHC v2.2Health CareNursing Stations- General | GGHC v2.2 | Health Care | Nursing Stations- General | 5
GGHC v2.2Health CareOperating Room | GGHC v2.2 | Health Care | Operating Room | 5
GGHC v2.2Health CarePathology | GGHC v2.2 | Health Care | Pathology | 5
GGHC v2.2Health CarePatient Room | GGHC v2.2 | Health Care | Patient Room | 5
GGHC v2.2Health CarePharmacy / Medicine Room | GGHC v2.2 | Health Care | Pharmacy / Medicine Room | 5
GGHC v2.2Health CarePhysical Therapy and Hydrotherapy | GGHC v2.2 | Health Care | Physical Therapy and Hydrotherapy | 5
GGHC v2.2Health CareRecovery | GGHC v2.2 | Health Care | Recovery | 5
GGHC v2.2Health CareScrub Up Area, Surgical Corridor | GGHC v2.2 | Health Care | Scrub Up Area, Surgical Corridor | 5
GGHC v2.2Health CareSoiled Linen, Sorting | GGHC v2.2 | Health Care | Soiled Linen, Sorting | 5
GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | 5
GGHC v2.2Health CareSpecial Procedure Room, Invasive | GGHC v2.2 | Health Care | Special Procedure Room, Invasive | 5
GGHC v2.2Health CareStairways | GGHC v2.2 | Health Care | Stairways | 1
GGHC v2.2Health CareSterilizer Room | GGHC v2.2 | Health Care | Sterilizer Room | 5
GGHC v2.2Health CareSub-Sterile | GGHC v2.2 | Health Care | Sub-Sterile | 5
GGHC v2.2Health CareSurgical Supply | GGHC v2.2 | Health Care | Surgical Supply | 5
GGHC v2.2Health CareTrash Chute Room | GGHC v2.2 | Health Care | Trash Chute Room | 0.5
GGHC v2.2Health CareTrauma | GGHC v2.2 | Health Care | Trauma | 5
GGHC v2.2Health CareTreatment / Examination | GGHC v2.2 | Health Care | Treatment / Examination | 5
GGHC v2.2Health CareUnsterile Supply | GGHC v2.2 | Health Care | Unsterile Supply | 2
GGHC v2.2Health CareWaiting Areas/Lounges | GGHC v2.2 | Health Care | Waiting Areas/Lounges | 10
GGHC v2.2Health CareX-ray, Diagnostic and Treatment | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | 5

## Interior Lighting
Each row represents interior lighting power limits for a particular space type in a particular standard. Values are referenced on Space Types tab.
VLookupColumn | Lighting Standard | Primary Space Type | Secondary Space Type | W/ft^2 | W/ft | Import Order
ASHRAE 90.1-1999Whole BuildingAutomotive Facility | ASHRAE 90.1-1999 | Whole Building | Automotive Facility | 1.5 |  | 1
ASHRAE 90.1-1999Whole BuildingConvention Center | ASHRAE 90.1-1999 | Whole Building | Convention Center | 1.4 |  | 2
ASHRAE 90.1-1999Whole BuildingCourt House | ASHRAE 90.1-1999 | Whole Building | Court House | 1.4 |  | 3
ASHRAE 90.1-1999Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-1999 | Whole Building | Dining: Bar Lounge/Leisure | 1.5 |  | 4
ASHRAE 90.1-1999Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-1999 | Whole Building | Dining: Cafeteria/Fast Food | 1.8 |  | 5
ASHRAE 90.1-1999Whole BuildingDining: Family | ASHRAE 90.1-1999 | Whole Building | Dining: Family | 1.9 |  | 6
ASHRAE 90.1-1999Whole BuildingDormitory | ASHRAE 90.1-1999 | Whole Building | Dormitory | 1.5 |  | 7
ASHRAE 90.1-1999Whole BuildingExercise Center | ASHRAE 90.1-1999 | Whole Building | Exercise Center | 1.4 |  | 8
ASHRAE 90.1-1999Whole BuildingGymnasium | ASHRAE 90.1-1999 | Whole Building | Gymnasium | 1.7 |  | 9
ASHRAE 90.1-1999Whole BuildingHealth Care-Clinic | ASHRAE 90.1-1999 | Whole Building | Health Care-Clinic | 1.6 |  | 10
ASHRAE 90.1-1999Whole BuildingHospital | ASHRAE 90.1-1999 | Whole Building | Hospital | 1.6 |  | 11
ASHRAE 90.1-1999Whole BuildingHotel | ASHRAE 90.1-1999 | Whole Building | Hotel | 1.7 |  | 12
ASHRAE 90.1-1999Whole BuildingLibrary | ASHRAE 90.1-1999 | Whole Building | Library | 1.5 |  | 13
ASHRAE 90.1-1999Whole BuildingManufacturing Facility | ASHRAE 90.1-1999 | Whole Building | Manufacturing Facility | 2.2 |  | 14
ASHRAE 90.1-1999Whole BuildingMotel | ASHRAE 90.1-1999 | Whole Building | Motel | 2 |  | 15
ASHRAE 90.1-1999Whole BuildingMotion Picture Theater | ASHRAE 90.1-1999 | Whole Building | Motion Picture Theater | 1.6 |  | 16
ASHRAE 90.1-1999Whole BuildingMulti-Family | ASHRAE 90.1-1999 | Whole Building | Multi-Family | 1 |  | 17
ASHRAE 90.1-1999Whole BuildingMuseum | ASHRAE 90.1-1999 | Whole Building | Museum | 1.6 |  | 18
ASHRAE 90.1-1999Whole BuildingOffice | ASHRAE 90.1-1999 | Whole Building | Office | 1.3 |  | 19
ASHRAE 90.1-1999Whole BuildingParking Garage | ASHRAE 90.1-1999 | Whole Building | Parking Garage | 0.3 |  | 20
ASHRAE 90.1-1999Whole BuildingPenitentiary | ASHRAE 90.1-1999 | Whole Building | Penitentiary | 1.2 |  | 21
ASHRAE 90.1-1999Whole BuildingPerforming Arts Theater | ASHRAE 90.1-1999 | Whole Building | Performing Arts Theater | 1.5 |  | 22
ASHRAE 90.1-1999Whole BuildingPolice/Fire Station | ASHRAE 90.1-1999 | Whole Building | Police/Fire Station | 1.3 |  | 23
ASHRAE 90.1-1999Whole BuildingPost Office | ASHRAE 90.1-1999 | Whole Building | Post Office | 1.6 |  | 24
ASHRAE 90.1-1999Whole BuildingReligious Building | ASHRAE 90.1-1999 | Whole Building | Religious Building | 2.2 |  | 25
ASHRAE 90.1-1999Whole BuildingRetail | ASHRAE 90.1-1999 | Whole Building | Retail | 1.9 |  | 26
ASHRAE 90.1-1999Whole BuildingSchool/University | ASHRAE 90.1-1999 | Whole Building | School/University | 1.5 |  | 27
ASHRAE 90.1-1999Whole BuildingSports Arena | ASHRAE 90.1-1999 | Whole Building | Sports Arena | 1.5 |  | 28
ASHRAE 90.1-1999Whole BuildingTown Hall | ASHRAE 90.1-1999 | Whole Building | Town Hall | 1.4 |  | 29
ASHRAE 90.1-1999Whole BuildingTransportation | ASHRAE 90.1-1999 | Whole Building | Transportation | 1.2 |  | 30
ASHRAE 90.1-1999Whole BuildingWarehouse | ASHRAE 90.1-1999 | Whole Building | Warehouse | 1.2 |  | 31
ASHRAE 90.1-1999Whole BuildingWorkshop | ASHRAE 90.1-1999 | Whole Building | Workshop | 1.7 |  | 32
ASHRAE 90.1-1999Office-EnclosedGeneral | ASHRAE 90.1-1999 | Office-Enclosed | General | 1.5 |  | 33
ASHRAE 90.1-1999Office-Open PlanGeneral | ASHRAE 90.1-1999 | Office-Open Plan | General | 1.3 |  | 34
ASHRAE 90.1-1999Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-1999 | Conference/Meeting/Multipurpose | General | 1.5 |  | 35
ASHRAE 90.1-1999Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-1999 | Classroom/Lecture/Training | General | 1.6 |  | 36
ASHRAE 90.1-1999Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-1999 | Classroom/Lecture/Training | For Penitentiary | 1.4 |  | 37
ASHRAE 90.1-1999LobbyGeneral | ASHRAE 90.1-1999 | Lobby | General | 1.8 |  | 38
ASHRAE 90.1-1999LobbyFor Hotel | ASHRAE 90.1-1999 | Lobby | For Hotel | 1.8 |  | 39
ASHRAE 90.1-1999LobbyFor Performing Arts Theater | ASHRAE 90.1-1999 | Lobby | For Performing Arts Theater | 1.2 |  | 40
ASHRAE 90.1-1999LobbyFor Motion Picture Theater | ASHRAE 90.1-1999 | Lobby | For Motion Picture Theater | 0.8 |  | 41
ASHRAE 90.1-1999Audience/Seating AreaGeneral | ASHRAE 90.1-1999 | Audience/Seating Area | General | 0.5 |  | 42
ASHRAE 90.1-1999Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-1999 | Audience/Seating Area | For Gymnasium | 0.5 |  | 43
ASHRAE 90.1-1999Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-1999 | Audience/Seating Area | For Exercise Center | 0.5 |  | 44
ASHRAE 90.1-1999Audience/Seating AreaFor Convention Center | ASHRAE 90.1-1999 | Audience/Seating Area | For Convention Center | 0.5 |  | 45
ASHRAE 90.1-1999Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-1999 | Audience/Seating Area | For Penitentiary | 1.9 |  | 46
ASHRAE 90.1-1999Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-1999 | Audience/Seating Area | For Religious Buildings | 3.2 |  | 47
ASHRAE 90.1-1999Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-1999 | Audience/Seating Area | For Sports Arena | 0.5 |  | 48
ASHRAE 90.1-1999Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-1999 | Audience/Seating Area | For Performing Arts Theater | 1.8 |  | 49
ASHRAE 90.1-1999Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-1999 | Audience/Seating Area | For Motion Picture Theater | 1.3 |  | 50
ASHRAE 90.1-1999Audience/Seating AreaFor Transportation | ASHRAE 90.1-1999 | Audience/Seating Area | For Transportation | 1 |  | 51
ASHRAE 90.1-1999AtriumFirst Three Floors | ASHRAE 90.1-1999 | Atrium | First Three Floors | 1.3 |  | 52
ASHRAE 90.1-1999AtriumEach Floor over First Three Floors | ASHRAE 90.1-1999 | Atrium | Each Floor over First Three Floors | 0.2 |  | 53
ASHRAE 90.1-1999Lounge/RecreationGeneral | ASHRAE 90.1-1999 | Lounge/Recreation | General | 1.4 |  | 54
ASHRAE 90.1-1999Lounge/RecreationFor Hospital | ASHRAE 90.1-1999 | Lounge/Recreation | For Hospital | 1.4 |  | 55
ASHRAE 90.1-1999Dining AreaGeneral | ASHRAE 90.1-1999 | Dining Area | General | 1.4 |  | 56
ASHRAE 90.1-1999Dining AreaFor Penitentiary | ASHRAE 90.1-1999 | Dining Area | For Penitentiary | 1.4 |  | 57
ASHRAE 90.1-1999Dining AreaFor Hotel | ASHRAE 90.1-1999 | Dining Area | For Hotel | 1 |  | 58
ASHRAE 90.1-1999Dining AreaFor Motel | ASHRAE 90.1-1999 | Dining Area | For Motel | 1.2 |  | 59
ASHRAE 90.1-1999Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-1999 | Dining Area | For Bar Lounge/Leisure Dining | 1.2 |  | 60
ASHRAE 90.1-1999Dining AreaFor Family Dining | ASHRAE 90.1-1999 | Dining Area | For Family Dining | 2.2 |  | 61
ASHRAE 90.1-1999Food PreparationGeneral | ASHRAE 90.1-1999 | Food Preparation | General | 2.2 |  | 62
ASHRAE 90.1-1999LaboratoryGeneral | ASHRAE 90.1-1999 | Laboratory | General | 1.8 |  | 63
ASHRAE 90.1-1999RestroomsGeneral | ASHRAE 90.1-1999 | Restrooms | General | 1 |  | 64
ASHRAE 90.1-1999Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-1999 | Dressing/Locker/Fitting Room | General | 0.8 |  | 65
ASHRAE 90.1-1999Corridor/TransitionGeneral | ASHRAE 90.1-1999 | Corridor/Transition | General | 0.7 |  | 66
ASHRAE 90.1-1999Corridor/TransitionFor Hospital | ASHRAE 90.1-1999 | Corridor/Transition | For Hospital | 1.6 |  | 67
ASHRAE 90.1-1999Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-1999 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 68
ASHRAE 90.1-1999Stairs—ActiveGeneral | ASHRAE 90.1-1999 | Stairs—Active | General | 0.9 |  | 69
ASHRAE 90.1-1999Active StorageGeneral | ASHRAE 90.1-1999 | Active Storage | General | 1.1 |  | 70
ASHRAE 90.1-1999Active StorageFor Hospital | ASHRAE 90.1-1999 | Active Storage | For Hospital | 2.9 |  | 71
ASHRAE 90.1-1999Inactive storageGeneral | ASHRAE 90.1-1999 | Inactive storage | General | 0.3 |  | 72
ASHRAE 90.1-1999Inactive storageFor Museum | ASHRAE 90.1-1999 | Inactive storage | For Museum | 1.4 |  | 73
ASHRAE 90.1-1999Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-1999 | Gymnasium/Exercise Center | Playing Area | 1.9 |  | 74
ASHRAE 90.1-1999Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-1999 | Gymnasium/Exercise Center | Exercise Area | 1.1 |  | 75
ASHRAE 90.1-1999Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-1999 | Courthouse/Police Station/Penitentiary | Courtroom | 2.1 |  | 76
ASHRAE 90.1-1999Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-1999 | Courthouse/Police Station/Penitentiary | Confinement Cells | 1.1 |  | 77
ASHRAE 90.1-1999Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-1999 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.1 |  | 78
ASHRAE 90.1-1999Fire StationsFire Station Engine Room | ASHRAE 90.1-1999 | Fire Stations | Fire Station Engine Room | 0.9 |  | 79
ASHRAE 90.1-1999Fire StationsSleeping Quarters | ASHRAE 90.1-1999 | Fire Stations | Sleeping Quarters | 1.1 |  | 80
ASHRAE 90.1-1999Post OfficeSorting Area | ASHRAE 90.1-1999 | Post Office | Sorting Area | 1.7 |  | 81
ASHRAE 90.1-1999Convention CenterExhibit Space | ASHRAE 90.1-1999 | Convention Center | Exhibit Space | 3.3 |  | 82
ASHRAE 90.1-1999LibraryCard File and Cataloging | ASHRAE 90.1-1999 | Library | Card File and Cataloging | 1.4 |  | 83
ASHRAE 90.1-1999LibraryStacks | ASHRAE 90.1-1999 | Library | Stacks | 1.9 |  | 84
ASHRAE 90.1-1999LibraryReading Area | ASHRAE 90.1-1999 | Library | Reading Area | 1.8 |  | 85
ASHRAE 90.1-1999HospitalEmergency | ASHRAE 90.1-1999 | Hospital | Emergency | 2.8 |  | 86
ASHRAE 90.1-1999HospitalRecovery | ASHRAE 90.1-1999 | Hospital | Recovery | 2.6 |  | 87
ASHRAE 90.1-1999HospitalNurse Station | ASHRAE 90.1-1999 | Hospital | Nurse Station | 1.8 |  | 88
ASHRAE 90.1-1999HospitalExam/Treatment | ASHRAE 90.1-1999 | Hospital | Exam/Treatment | 1.6 |  | 89
ASHRAE 90.1-1999HospitalPharmacy | ASHRAE 90.1-1999 | Hospital | Pharmacy | 2.3 |  | 90
ASHRAE 90.1-1999HospitalPatient Room | ASHRAE 90.1-1999 | Hospital | Patient Room | 1.2 |  | 91
ASHRAE 90.1-1999HospitalOperating Room | ASHRAE 90.1-1999 | Hospital | Operating Room | 7.6 |  | 92
ASHRAE 90.1-1999HospitalNursery | ASHRAE 90.1-1999 | Hospital | Nursery | 1 |  | 93
ASHRAE 90.1-1999HospitalMedical Supply | ASHRAE 90.1-1999 | Hospital | Medical Supply | 3 |  | 94
ASHRAE 90.1-1999HospitalPhysical Therapy | ASHRAE 90.1-1999 | Hospital | Physical Therapy | 1.9 |  | 95
ASHRAE 90.1-1999HospitalRadiology | ASHRAE 90.1-1999 | Hospital | Radiology | 0.4 |  | 96
ASHRAE 90.1-1999HospitalLaundry—Washing | ASHRAE 90.1-1999 | Hospital | Laundry—Washing | 0.7 |  | 97
ASHRAE 90.1-1999AutomotiveService/Repair | ASHRAE 90.1-1999 | Automotive | Service/Repair | 1.4 |  | 98
ASHRAE 90.1-1999ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-1999 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 2.1 |  | 99
ASHRAE 90.1-1999ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-1999 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 3 |  | 100
ASHRAE 90.1-1999ManufacturingDetailed Manufacturing | ASHRAE 90.1-1999 | Manufacturing | Detailed Manufacturing | 6.2 |  | 101
ASHRAE 90.1-1999ManufacturingEquipment Room | ASHRAE 90.1-1999 | Manufacturing | Equipment Room | 0.8 |  | 102
ASHRAE 90.1-1999ManufacturingControl Room | ASHRAE 90.1-1999 | Manufacturing | Control Room | 0.5 |  | 103
ASHRAE 90.1-1999Hotel/MotelGuest Rooms | ASHRAE 90.1-1999 | Hotel/Motel | Guest Rooms | 2.5 |  | 104
ASHRAE 90.1-1999DormitoryLiving Quarters | ASHRAE 90.1-1999 | Dormitory | Living Quarters | 1.9 |  | 105
ASHRAE 90.1-1999MuseumGeneral Exhibition | ASHRAE 90.1-1999 | Museum | General Exhibition | 1.6 |  | 106
ASHRAE 90.1-1999MuseumRestoration | ASHRAE 90.1-1999 | Museum | Restoration | 2.5 |  | 107
ASHRAE 90.1-1999Electrical/MechanicalGeneral | ASHRAE 90.1-1999 | Electrical/Mechanical | General | 1.3 |  | 108
ASHRAE 90.1-1999WorkshopGeneral | ASHRAE 90.1-1999 | Workshop | General | 2.5 |  | 109
ASHRAE 90.1-1999Bank/OfficeBanking Activity Area | ASHRAE 90.1-1999 | Bank/Office | Banking Activity Area | 2.4 |  | 110
ASHRAE 90.1-1999Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-1999 | Religious Buildings | Worship Pulpit, Choir | 5.2 |  | 111
ASHRAE 90.1-1999Religious BuildingsFellowship Hall | ASHRAE 90.1-1999 | Religious Buildings | Fellowship Hall | 2.3 |  | 112
ASHRAE 90.1-1999Retail (not including accent lighting)Sales Area | ASHRAE 90.1-1999 | Retail (not including accent lighting) | Sales Area | 2.1 |  | 113
ASHRAE 90.1-1999Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-1999 | Retail (not including accent lighting) | Mall Concourse | 1.8 |  | 114
ASHRAE 90.1-1999Sports ArenaRing Sports Area | ASHRAE 90.1-1999 | Sports Arena | Ring Sports Area | 3.8 |  | 115
ASHRAE 90.1-1999Sports ArenaCourt Sports Area | ASHRAE 90.1-1999 | Sports Arena | Court Sports Area | 4.3 |  | 116
ASHRAE 90.1-1999Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-1999 | Sports Arena | Indoor Playing Field Area | 1.9 |  | 117
ASHRAE 90.1-1999WarehouseFine Material Storage | ASHRAE 90.1-1999 | Warehouse | Fine Material Storage | 1.6 |  | 118
ASHRAE 90.1-1999WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-1999 | Warehouse | Medium/Bulky Material Storage | 1.1 |  | 119
ASHRAE 90.1-1999Parking GarageGarage Area | ASHRAE 90.1-1999 | Parking Garage | Garage Area | 0.2 |  | 120
ASHRAE 90.1-1999TransportationAirport—Concourse | ASHRAE 90.1-1999 | Transportation | Airport—Concourse | 0.7 |  | 121
ASHRAE 90.1-1999TransportationAir/Train/Bus—Baggage Area | ASHRAE 90.1-1999 | Transportation | Air/Train/Bus—Baggage Area | 1.3 |  | 122
ASHRAE 90.1-1999TransportationTerminal—Ticket Counter | ASHRAE 90.1-1999 | Transportation | Terminal—Ticket Counter | 1.8 |  | 123
ASHRAE 90.1-1999Exterior SpacesGeneral | ASHRAE 90.1-1999 | Exterior Spaces | General | 0 |  | 124
ASHRAE 90.1-1999AtticsGeneral | ASHRAE 90.1-1999 | Attics | General | 0 |  | 125
ASHRAE 90.1-2001Whole BuildingAutomotive Facility | ASHRAE 90.1-2001 | Whole Building | Automotive Facility | 0.9 |  | 126
ASHRAE 90.1-2001Whole BuildingConvention Center | ASHRAE 90.1-2001 | Whole Building | Convention Center | 1.2 |  | 127
ASHRAE 90.1-2001Whole BuildingCourt House | ASHRAE 90.1-2001 | Whole Building | Court House | 1.2 |  | 128
ASHRAE 90.1-2001Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2001 | Whole Building | Dining: Bar Lounge/Leisure | 1.3 |  | 129
ASHRAE 90.1-2001Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2001 | Whole Building | Dining: Cafeteria/Fast Food | 1.4 |  | 130
ASHRAE 90.1-2001Whole BuildingDining: Family | ASHRAE 90.1-2001 | Whole Building | Dining: Family | 1.6 |  | 131
ASHRAE 90.1-2001Whole BuildingDormitory | ASHRAE 90.1-2001 | Whole Building | Dormitory | 1 |  | 132
ASHRAE 90.1-2001Whole BuildingExercise Center | ASHRAE 90.1-2001 | Whole Building | Exercise Center | 1 |  | 133
ASHRAE 90.1-2001Whole BuildingGymnasium | ASHRAE 90.1-2001 | Whole Building | Gymnasium | 1.1 |  | 134
ASHRAE 90.1-2001Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2001 | Whole Building | Health Care-Clinic | 1 |  | 135
ASHRAE 90.1-2001Whole BuildingHospital | ASHRAE 90.1-2001 | Whole Building | Hospital | 1.2 |  | 136
ASHRAE 90.1-2001Whole BuildingHotel | ASHRAE 90.1-2001 | Whole Building | Hotel | 1 |  | 137
ASHRAE 90.1-2001Whole BuildingLibrary | ASHRAE 90.1-2001 | Whole Building | Library | 1.3 |  | 138
ASHRAE 90.1-2001Whole BuildingManufacturing Facility | ASHRAE 90.1-2001 | Whole Building | Manufacturing Facility | 1.3 |  | 139
ASHRAE 90.1-2001Whole BuildingMotel | ASHRAE 90.1-2001 | Whole Building | Motel | 1 |  | 140
ASHRAE 90.1-2001Whole BuildingMotion Picture Theater | ASHRAE 90.1-2001 | Whole Building | Motion Picture Theater | 1.2 |  | 141
ASHRAE 90.1-2001Whole BuildingMulti-Family | ASHRAE 90.1-2001 | Whole Building | Multi-Family | 0.7 |  | 142
ASHRAE 90.1-2001Whole BuildingMuseum | ASHRAE 90.1-2001 | Whole Building | Museum | 1.1 |  | 143
ASHRAE 90.1-2001Whole BuildingOffice | ASHRAE 90.1-2001 | Whole Building | Office | 1 |  | 144
ASHRAE 90.1-2001Whole BuildingParking Garage | ASHRAE 90.1-2001 | Whole Building | Parking Garage | 0.3 |  | 145
ASHRAE 90.1-2001Whole BuildingPenitentiary | ASHRAE 90.1-2001 | Whole Building | Penitentiary | 1 |  | 146
ASHRAE 90.1-2001Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2001 | Whole Building | Performing Arts Theater | 1.6 |  | 147
ASHRAE 90.1-2001Whole BuildingPolice/Fire Station | ASHRAE 90.1-2001 | Whole Building | Police/Fire Station | 1 |  | 148
ASHRAE 90.1-2001Whole BuildingPost Office | ASHRAE 90.1-2001 | Whole Building | Post Office | 1.1 |  | 149
ASHRAE 90.1-2001Whole BuildingReligious Building | ASHRAE 90.1-2001 | Whole Building | Religious Building | 1.3 |  | 150
ASHRAE 90.1-2001Whole BuildingRetail | ASHRAE 90.1-2001 | Whole Building | Retail | 1.5 |  | 151
ASHRAE 90.1-2001Whole BuildingSchool/University | ASHRAE 90.1-2001 | Whole Building | School/University | 1.2 |  | 152
ASHRAE 90.1-2001Whole BuildingSports Arena | ASHRAE 90.1-2001 | Whole Building | Sports Arena | 1.1 |  | 153
ASHRAE 90.1-2001Whole BuildingTown Hall | ASHRAE 90.1-2001 | Whole Building | Town Hall | 1.1 |  | 154
ASHRAE 90.1-2001Whole BuildingTransportation | ASHRAE 90.1-2001 | Whole Building | Transportation | 1 |  | 155
ASHRAE 90.1-2001Whole BuildingWarehouse | ASHRAE 90.1-2001 | Whole Building | Warehouse | 0.8 |  | 156
ASHRAE 90.1-2001Whole BuildingWorkshop | ASHRAE 90.1-2001 | Whole Building | Workshop | 1.4 |  | 157
ASHRAE 90.1-2001Office-EnclosedGeneral | ASHRAE 90.1-2001 | Office-Enclosed | General | 1.1 |  | 158
ASHRAE 90.1-2001Office-Open PlanGeneral | ASHRAE 90.1-2001 | Office-Open Plan | General | 1.1 |  | 159
ASHRAE 90.1-2001Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2001 | Conference/Meeting/Multipurpose | General | 1.3 |  | 160
ASHRAE 90.1-2001Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2001 | Classroom/Lecture/Training | General | 1.4 |  | 161
ASHRAE 90.1-2001Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2001 | Classroom/Lecture/Training | For Penitentiary | 1.3 |  | 162
ASHRAE 90.1-2001LobbyGeneral | ASHRAE 90.1-2001 | Lobby | General | 1.3 |  | 163
ASHRAE 90.1-2001LobbyFor Hotel | ASHRAE 90.1-2001 | Lobby | For Hotel | 1.1 |  | 164
ASHRAE 90.1-2001LobbyFor Performing Arts Theater | ASHRAE 90.1-2001 | Lobby | For Performing Arts Theater | 3.3 |  | 165
ASHRAE 90.1-2001LobbyFor Motion Picture Theater | ASHRAE 90.1-2001 | Lobby | For Motion Picture Theater | 1.1 |  | 166
ASHRAE 90.1-2001Audience/Seating AreaGeneral | ASHRAE 90.1-2001 | Audience/Seating Area | General | 0.9 |  | 167
ASHRAE 90.1-2001Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2001 | Audience/Seating Area | For Gymnasium | 0.4 |  | 168
ASHRAE 90.1-2001Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-2001 | Audience/Seating Area | For Exercise Center | 0.3 |  | 169
ASHRAE 90.1-2001Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2001 | Audience/Seating Area | For Convention Center | 0.7 |  | 170
ASHRAE 90.1-2001Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2001 | Audience/Seating Area | For Penitentiary | 0.7 |  | 171
ASHRAE 90.1-2001Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2001 | Audience/Seating Area | For Religious Buildings | 1.7 |  | 172
ASHRAE 90.1-2001Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-2001 | Audience/Seating Area | For Sports Arena | 0.4 |  | 173
ASHRAE 90.1-2001Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-2001 | Audience/Seating Area | For Performing Arts Theater | 2.6 |  | 174
ASHRAE 90.1-2001Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2001 | Audience/Seating Area | For Motion Picture Theater | 1.2 |  | 175
ASHRAE 90.1-2001Audience/Seating AreaFor Transportation | ASHRAE 90.1-2001 | Audience/Seating Area | For Transportation | 0.5 |  | 176
ASHRAE 90.1-2001AtriumFirst Three Floors | ASHRAE 90.1-2001 | Atrium | First Three Floors | 0.6 |  | 177
ASHRAE 90.1-2001AtriumEach Floor over First Three Floors | ASHRAE 90.1-2001 | Atrium | Each Floor over First Three Floors | 0.2 |  | 178
ASHRAE 90.1-2001Lounge/RecreationGeneral | ASHRAE 90.1-2001 | Lounge/Recreation | General | 1.2 |  | 179
ASHRAE 90.1-2001Lounge/RecreationFor Hospital | ASHRAE 90.1-2001 | Lounge/Recreation | For Hospital | 0.8 |  | 180
ASHRAE 90.1-2001Dining AreaGeneral | ASHRAE 90.1-2001 | Dining Area | General | 0.9 |  | 181
ASHRAE 90.1-2001Dining AreaFor Penitentiary | ASHRAE 90.1-2001 | Dining Area | For Penitentiary | 1.3 |  | 182
ASHRAE 90.1-2001Dining AreaFor Hotel | ASHRAE 90.1-2001 | Dining Area | For Hotel | 1.3 |  | 183
ASHRAE 90.1-2001Dining AreaFor Motel | ASHRAE 90.1-2001 | Dining Area | For Motel | 1.2 |  | 184
ASHRAE 90.1-2001Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2001 | Dining Area | For Bar Lounge/Leisure Dining | 1.4 |  | 185
ASHRAE 90.1-2001Dining AreaFor Family Dining | ASHRAE 90.1-2001 | Dining Area | For Family Dining | 2.1 |  | 186
ASHRAE 90.1-2001Food PreparationGeneral | ASHRAE 90.1-2001 | Food Preparation | General | 1.2 |  | 187
ASHRAE 90.1-2001LaboratoryGeneral | ASHRAE 90.1-2001 | Laboratory | General | 1.4 |  | 188
ASHRAE 90.1-2001RestroomsGeneral | ASHRAE 90.1-2001 | Restrooms | General | 0.9 |  | 189
ASHRAE 90.1-2001Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-2001 | Dressing/Locker/Fitting Room | General | 0.6 |  | 190
ASHRAE 90.1-2001Corridor/TransitionGeneral | ASHRAE 90.1-2001 | Corridor/Transition | General | 0.5 |  | 191
ASHRAE 90.1-2001Corridor/TransitionFor Hospital | ASHRAE 90.1-2001 | Corridor/Transition | For Hospital | 1 |  | 192
ASHRAE 90.1-2001Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-2001 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 193
ASHRAE 90.1-2001Stairs—ActiveGeneral | ASHRAE 90.1-2001 | Stairs—Active | General | 0.6 |  | 194
ASHRAE 90.1-2001Active StorageGeneral | ASHRAE 90.1-2001 | Active Storage | General | 0.8 |  | 195
ASHRAE 90.1-2001Active StorageFor Hospital | ASHRAE 90.1-2001 | Active Storage | For Hospital | 0.9 |  | 196
ASHRAE 90.1-2001Inactive storageGeneral | ASHRAE 90.1-2001 | Inactive storage | General | 0.3 |  | 197
ASHRAE 90.1-2001Inactive storageFor Museum | ASHRAE 90.1-2001 | Inactive storage | For Museum | 0.8 |  | 198
ASHRAE 90.1-2001Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-2001 | Gymnasium/Exercise Center | Playing Area | 1.4 |  | 199
ASHRAE 90.1-2001Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-2001 | Gymnasium/Exercise Center | Exercise Area | 0.9 |  | 200
ASHRAE 90.1-2001Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-2001 | Courthouse/Police Station/Penitentiary | Courtroom | 1.9 |  | 201
ASHRAE 90.1-2001Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-2001 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.9 |  | 202
ASHRAE 90.1-2001Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-2001 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.3 |  | 203
ASHRAE 90.1-2001Fire StationsFire Station Engine Room | ASHRAE 90.1-2001 | Fire Stations | Fire Station Engine Room | 0.8 |  | 204
ASHRAE 90.1-2001Fire StationsSleeping Quarters | ASHRAE 90.1-2001 | Fire Stations | Sleeping Quarters | 0.3 |  | 205
ASHRAE 90.1-2001Post OfficeSorting Area | ASHRAE 90.1-2001 | Post Office | Sorting Area | 1.2 |  | 206
ASHRAE 90.1-2001Convention CenterExhibit Space | ASHRAE 90.1-2001 | Convention Center | Exhibit Space | 1.3 |  | 207
ASHRAE 90.1-2001LibraryCard File and Cataloging | ASHRAE 90.1-2001 | Library | Card File and Cataloging | 1.1 |  | 208
ASHRAE 90.1-2001LibraryStacks | ASHRAE 90.1-2001 | Library | Stacks | 1.7 |  | 209
ASHRAE 90.1-2001LibraryReading Area | ASHRAE 90.1-2001 | Library | Reading Area | 1.2 |  | 210
ASHRAE 90.1-2001HospitalEmergency | ASHRAE 90.1-2001 | Hospital | Emergency | 2.7 |  | 211
ASHRAE 90.1-2001HospitalRecovery | ASHRAE 90.1-2001 | Hospital | Recovery | 0.8 |  | 212
ASHRAE 90.1-2001HospitalNurse Station | ASHRAE 90.1-2001 | Hospital | Nurse Station | 1 |  | 213
ASHRAE 90.1-2001HospitalExam/Treatment | ASHRAE 90.1-2001 | Hospital | Exam/Treatment | 1.5 |  | 214
ASHRAE 90.1-2001HospitalPharmacy | ASHRAE 90.1-2001 | Hospital | Pharmacy | 1.2 |  | 215
ASHRAE 90.1-2001HospitalPatient Room | ASHRAE 90.1-2001 | Hospital | Patient Room | 0.7 |  | 216
ASHRAE 90.1-2001HospitalOperating Room | ASHRAE 90.1-2001 | Hospital | Operating Room | 2.2 |  | 217
ASHRAE 90.1-2001HospitalNursery | ASHRAE 90.1-2001 | Hospital | Nursery | 0.6 |  | 218
ASHRAE 90.1-2001HospitalMedical Supply | ASHRAE 90.1-2001 | Hospital | Medical Supply | 1.4 |  | 219
ASHRAE 90.1-2001HospitalPhysical Therapy | ASHRAE 90.1-2001 | Hospital | Physical Therapy | 0.9 |  | 220
ASHRAE 90.1-2001HospitalRadiology | ASHRAE 90.1-2001 | Hospital | Radiology | 0.4 |  | 221
ASHRAE 90.1-2001HospitalLaundry—Washing | ASHRAE 90.1-2001 | Hospital | Laundry—Washing | 0.6 |  | 222
ASHRAE 90.1-2001AutomotiveService/Repair | ASHRAE 90.1-2001 | Automotive | Service/Repair | 0.7 |  | 223
ASHRAE 90.1-2001ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2001 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.2 |  | 224
ASHRAE 90.1-2001ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-2001 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.7 |  | 225
ASHRAE 90.1-2001ManufacturingDetailed Manufacturing | ASHRAE 90.1-2001 | Manufacturing | Detailed Manufacturing | 2.1 |  | 226
ASHRAE 90.1-2001ManufacturingEquipment Room | ASHRAE 90.1-2001 | Manufacturing | Equipment Room | 1.2 |  | 227
ASHRAE 90.1-2001ManufacturingControl Room | ASHRAE 90.1-2001 | Manufacturing | Control Room | 0.5 |  | 228
ASHRAE 90.1-2001Hotel/MotelGuest Rooms | ASHRAE 90.1-2001 | Hotel/Motel | Guest Rooms | 1.1 |  | 229
ASHRAE 90.1-2001DormitoryLiving Quarters | ASHRAE 90.1-2001 | Dormitory | Living Quarters | 1.1 |  | 230
ASHRAE 90.1-2001MuseumGeneral Exhibition | ASHRAE 90.1-2001 | Museum | General Exhibition | 1 |  | 231
ASHRAE 90.1-2001MuseumRestoration | ASHRAE 90.1-2001 | Museum | Restoration | 1.7 |  | 232
ASHRAE 90.1-2001Electrical/MechanicalGeneral | ASHRAE 90.1-2001 | Electrical/Mechanical | General | 1.5 |  | 233
ASHRAE 90.1-2001WorkshopGeneral | ASHRAE 90.1-2001 | Workshop | General | 1.9 |  | 234
ASHRAE 90.1-2001Bank/OfficeBanking Activity Area | ASHRAE 90.1-2001 | Bank/Office | Banking Activity Area | 1.5 |  | 235
ASHRAE 90.1-2001Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2001 | Religious Buildings | Worship Pulpit, Choir | 2.4 |  | 236
ASHRAE 90.1-2001Religious BuildingsFellowship Hall | ASHRAE 90.1-2001 | Religious Buildings | Fellowship Hall | 0.9 |  | 237
ASHRAE 90.1-2001Retail (not including accent lighting)Sales Area | ASHRAE 90.1-2001 | Retail (not including accent lighting) | Sales Area | 2.1 |  | 238
ASHRAE 90.1-2001Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-2001 | Retail (not including accent lighting) | Mall Concourse | 1.7 |  | 239
ASHRAE 90.1-2001Sports ArenaRing Sports Area | ASHRAE 90.1-2001 | Sports Arena | Ring Sports Area | 2.7 |  | 240
ASHRAE 90.1-2001Sports ArenaCourt Sports Area | ASHRAE 90.1-2001 | Sports Arena | Court Sports Area | 2.3 |  | 241
ASHRAE 90.1-2001Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-2001 | Sports Arena | Indoor Playing Field Area | 1.4 |  | 242
ASHRAE 90.1-2001WarehouseFine Material Storage | ASHRAE 90.1-2001 | Warehouse | Fine Material Storage | 1.4 |  | 243
ASHRAE 90.1-2001WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2001 | Warehouse | Medium/Bulky Material Storage | 0.9 |  | 244
ASHRAE 90.1-2001Parking GarageGarage Area | ASHRAE 90.1-2001 | Parking Garage | Garage Area | 0.2 |  | 245
ASHRAE 90.1-2001TransportationAirport—Concourse | ASHRAE 90.1-2001 | Transportation | Airport—Concourse | 0.6 |  | 246
ASHRAE 90.1-2001TransportationAir/Train/Bus—Baggage Area | ASHRAE 90.1-2001 | Transportation | Air/Train/Bus—Baggage Area | 1 |  | 247
ASHRAE 90.1-2001TransportationTerminal—Ticket Counter | ASHRAE 90.1-2001 | Transportation | Terminal—Ticket Counter | 1.5 |  | 248
ASHRAE 90.1-2001Exterior SpacesGeneral | ASHRAE 90.1-2001 | Exterior Spaces | General | 0 |  | 249
ASHRAE 90.1-2001AtticsGeneral | ASHRAE 90.1-2001 | Attics | General | 0 |  | 250
ASHRAE 90.1-2004Active StorageFor Hospital | ASHRAE 90.1-2004 | Active Storage | For Hospital | 0.9 |  | 321
ASHRAE 90.1-2004Active StorageGeneral | ASHRAE 90.1-2004 | Active Storage | General | 0.8 |  | 320
ASHRAE 90.1-2004AtriumEach Floor over First Three Floors | ASHRAE 90.1-2004 | Atrium | Each Floor over First Three Floors | 0.2 |  | 303
ASHRAE 90.1-2004AtriumFirst Three Floors | ASHRAE 90.1-2004 | Atrium | First Three Floors | 0.6 |  | 302
ASHRAE 90.1-2004AtticsGeneral | ASHRAE 90.1-2004 | Attics | General | 0 |  | 375
ASHRAE 90.1-2004Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2004 | Audience/Seating Area | For Convention Center | 0.7 |  | 295
ASHRAE 90.1-2004Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-2004 | Audience/Seating Area | For Exercise Center | 0.3 |  | 294
ASHRAE 90.1-2004Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2004 | Audience/Seating Area | For Gymnasium | 0.4 |  | 293
ASHRAE 90.1-2004Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2004 | Audience/Seating Area | For Motion Picture Theater | 1.2 |  | 300
ASHRAE 90.1-2004Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2004 | Audience/Seating Area | For Penitentiary | 0.7 |  | 296
ASHRAE 90.1-2004Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-2004 | Audience/Seating Area | For Performing Arts Theater | 2.6 |  | 299
ASHRAE 90.1-2004Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2004 | Audience/Seating Area | For Religious Buildings | 1.7 |  | 297
ASHRAE 90.1-2004Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-2004 | Audience/Seating Area | For Sports Arena | 0.4 |  | 298
ASHRAE 90.1-2004Audience/Seating AreaFor Transportation | ASHRAE 90.1-2004 | Audience/Seating Area | For Transportation | 0.5 |  | 301
ASHRAE 90.1-2004Audience/Seating AreaGeneral | ASHRAE 90.1-2004 | Audience/Seating Area | General | 0.9 |  | 292
ASHRAE 90.1-2004AutomotiveService/Repair | ASHRAE 90.1-2004 | Automotive | Service/Repair | 0.7 |  | 348
ASHRAE 90.1-2004Bank/OfficeBanking Activity Area | ASHRAE 90.1-2004 | Bank/Office | Banking Activity Area | 1.5 |  | 360
ASHRAE 90.1-2004Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2004 | Classroom/Lecture/Training | For Penitentiary | 1.3 |  | 287
ASHRAE 90.1-2004Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2004 | Classroom/Lecture/Training | General | 1.4 |  | 286
ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | 1.3 |  | 285
ASHRAE 90.1-2004Convention CenterExhibit Space | ASHRAE 90.1-2004 | Convention Center | Exhibit Space | 1.3 |  | 332
ASHRAE 90.1-2004Corridor/TransitionFor Hospital | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | 1 |  | 317
ASHRAE 90.1-2004Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-2004 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 318
ASHRAE 90.1-2004Corridor/TransitionGeneral | ASHRAE 90.1-2004 | Corridor/Transition | General | 0.5 |  | 316
ASHRAE 90.1-2004Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-2004 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.9 |  | 327
ASHRAE 90.1-2004Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-2004 | Courthouse/Police Station/Penitentiary | Courtroom | 1.9 |  | 326
ASHRAE 90.1-2004Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-2004 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.3 |  | 328
ASHRAE 90.1-2004Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2004 | Dining Area | For Bar Lounge/Leisure Dining | 1.4 |  | 310
ASHRAE 90.1-2004Dining AreaFor Family Dining | ASHRAE 90.1-2004 | Dining Area | For Family Dining | 2.1 |  | 311
ASHRAE 90.1-2004Dining AreaFor Hotel | ASHRAE 90.1-2004 | Dining Area | For Hotel | 1.3 |  | 308
ASHRAE 90.1-2004Dining AreaFor Motel | ASHRAE 90.1-2004 | Dining Area | For Motel | 1.2 |  | 309
ASHRAE 90.1-2004Dining AreaFor Penitentiary | ASHRAE 90.1-2004 | Dining Area | For Penitentiary | 1.3 |  | 307
ASHRAE 90.1-2004Dining AreaGeneral | ASHRAE 90.1-2004 | Dining Area | General | 0.9 |  | 306
ASHRAE 90.1-2004DormitoryLiving Quarters | ASHRAE 90.1-2004 | Dormitory | Living Quarters | 1.1 |  | 355
ASHRAE 90.1-2004Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-2004 | Dressing/Locker/Fitting Room | General | 0.6 |  | 315
ASHRAE 90.1-2004Electrical/MechanicalGeneral | ASHRAE 90.1-2004 | Electrical/Mechanical | General | 1.5 |  | 358
ASHRAE 90.1-2004Exterior SpacesGeneral | ASHRAE 90.1-2004 | Exterior Spaces | General | 0 |  | 374
ASHRAE 90.1-2004Fire StationsFire Station Engine Room | ASHRAE 90.1-2004 | Fire Stations | Fire Station Engine Room | 0.8 |  | 329
ASHRAE 90.1-2004Fire StationsSleeping Quarters | ASHRAE 90.1-2004 | Fire Stations | Sleeping Quarters | 0.3 |  | 330
ASHRAE 90.1-2004Food PreparationGeneral | ASHRAE 90.1-2004 | Food Preparation | General | 1.2 |  | 312
ASHRAE 90.1-2004Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Exercise Area | 0.9 |  | 325
ASHRAE 90.1-2004Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Playing Area | 1.4 |  | 324
ASHRAE 90.1-2004HospitalEmergency | ASHRAE 90.1-2004 | Hospital | Emergency | 2.7 |  | 336
ASHRAE 90.1-2004HospitalExam/Treatment | ASHRAE 90.1-2004 | Hospital | Exam/Treatment | 1.5 |  | 339
ASHRAE 90.1-2004HospitalLaundry-Washing | ASHRAE 90.1-2004 | Hospital | Laundry-Washing | 0.6 |  | 347
ASHRAE 90.1-2004HospitalMedical Supply | ASHRAE 90.1-2004 | Hospital | Medical Supply | 1.4 |  | 344
ASHRAE 90.1-2004HospitalNurse Station | ASHRAE 90.1-2004 | Hospital | Nurse Station | 1 |  | 338
ASHRAE 90.1-2004HospitalNursery | ASHRAE 90.1-2004 | Hospital | Nursery | 0.6 |  | 343
ASHRAE 90.1-2004HospitalOperating Room | ASHRAE 90.1-2004 | Hospital | Operating Room | 2.2 |  | 342
ASHRAE 90.1-2004HospitalPatient Room | ASHRAE 90.1-2004 | Hospital | Patient Room | 0.7 |  | 341
ASHRAE 90.1-2004HospitalPharmacy | ASHRAE 90.1-2004 | Hospital | Pharmacy | 1.2 |  | 340
ASHRAE 90.1-2004HospitalPhysical Therapy | ASHRAE 90.1-2004 | Hospital | Physical Therapy | 0.9 |  | 345
ASHRAE 90.1-2004HospitalRadiology | ASHRAE 90.1-2004 | Hospital | Radiology | 0.4 |  | 346
ASHRAE 90.1-2004HospitalRecovery | ASHRAE 90.1-2004 | Hospital | Recovery | 0.8 |  | 337
ASHRAE 90.1-2004Hotel/MotelGuest Rooms | ASHRAE 90.1-2004 | Hotel/Motel | Guest Rooms | 1.1 |  | 354
ASHRAE 90.1-2004Inactive storageFor Museum | ASHRAE 90.1-2004 | Inactive storage | For Museum | 0.8 |  | 323
ASHRAE 90.1-2004Inactive storageGeneral | ASHRAE 90.1-2004 | Inactive storage | General | 0.3 |  | 322
ASHRAE 90.1-2004LaboratoryGeneral | ASHRAE 90.1-2004 | Laboratory | General | 1.4 |  | 313
ASHRAE 90.1-2004LibraryCard File and Cataloging | ASHRAE 90.1-2004 | Library | Card File and Cataloging | 1.1 |  | 333
ASHRAE 90.1-2004LibraryReading Area | ASHRAE 90.1-2004 | Library | Reading Area | 1.2 |  | 335
ASHRAE 90.1-2004LibraryStacks | ASHRAE 90.1-2004 | Library | Stacks | 1.7 |  | 334
ASHRAE 90.1-2004LobbyFor Hotel | ASHRAE 90.1-2004 | Lobby | For Hotel | 1.1 |  | 289
ASHRAE 90.1-2004LobbyFor Motion Picture Theater | ASHRAE 90.1-2004 | Lobby | For Motion Picture Theater | 1.1 |  | 291
ASHRAE 90.1-2004LobbyFor Performing Arts Theater | ASHRAE 90.1-2004 | Lobby | For Performing Arts Theater | 3.3 |  | 290
ASHRAE 90.1-2004LobbyGeneral | ASHRAE 90.1-2004 | Lobby | General | 1.3 |  | 288
ASHRAE 90.1-2004Lounge/RecreationFor Hospital | ASHRAE 90.1-2004 | Lounge/Recreation | For Hospital | 0.8 |  | 305
ASHRAE 90.1-2004Lounge/RecreationGeneral | ASHRAE 90.1-2004 | Lounge/Recreation | General | 1.2 |  | 304
ASHRAE 90.1-2004ManufacturingDetailed Manufacturing | ASHRAE 90.1-2004 | Manufacturing | Detailed Manufacturing | 2.1 |  | 351
ASHRAE 90.1-2004ManufacturingGeneral | ASHRAE 90.1-2004 | Manufacturing | General | 0.5 |  | 353
ASHRAE 90.1-2004ManufacturingGeneral | ASHRAE 90.1-2004 | Manufacturing | General | 1.2 |  | 352
ASHRAE 90.1-2004ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-2004 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.7 |  | 350
ASHRAE 90.1-2004ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2004 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.2 |  | 349
ASHRAE 90.1-2004MuseumGeneral Exhibition | ASHRAE 90.1-2004 | Museum | General Exhibition | 1 |  | 356
ASHRAE 90.1-2004MuseumRestoration | ASHRAE 90.1-2004 | Museum | Restoration | 1.7 |  | 357
ASHRAE 90.1-2004Office-EnclosedGeneral | ASHRAE 90.1-2004 | Office-Enclosed | General | 1.1 |  | 283
ASHRAE 90.1-2004Office-Open PlanGeneral | ASHRAE 90.1-2004 | Office-Open Plan | General | 1.1 |  | 284
ASHRAE 90.1-2004Parking GarageGarage Area | ASHRAE 90.1-2004 | Parking Garage | Garage Area | 0.2 |  | 370
ASHRAE 90.1-2004Post OfficeSorting Area | ASHRAE 90.1-2004 | Post Office | Sorting Area | 1.2 |  | 331
ASHRAE 90.1-2004Religious BuildingsFellowship Hall | ASHRAE 90.1-2004 | Religious Buildings | Fellowship Hall | 0.9 |  | 362
ASHRAE 90.1-2004Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2004 | Religious Buildings | Worship Pulpit, Choir | 2.4 |  | 361
ASHRAE 90.1-2004RestroomsGeneral | ASHRAE 90.1-2004 | Restrooms | General | 0.9 |  | 314
ASHRAE 90.1-2004Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Mall Concourse | 1.7 |  | 364
ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | 1.7 |  | 363
ASHRAE 90.1-2004Sports ArenaCourt Sports Area | ASHRAE 90.1-2004 | Sports Arena | Court Sports Area | 2.3 |  | 366
ASHRAE 90.1-2004Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-2004 | Sports Arena | Indoor Playing Field Area | 1.4 |  | 367
ASHRAE 90.1-2004Sports ArenaRing Sports Area | ASHRAE 90.1-2004 | Sports Arena | Ring Sports Area | 2.7 |  | 365
ASHRAE 90.1-2004Stairs-ActiveGeneral | ASHRAE 90.1-2004 | Stairs-Active | General | 0.6 |  | 319
ASHRAE 90.1-2004TransportationAir/Train/Bus—Baggage Area | ASHRAE 90.1-2004 | Transportation | Air/Train/Bus—Baggage Area | 1 |  | 372
ASHRAE 90.1-2004TransportationAirport—Concourse | ASHRAE 90.1-2004 | Transportation | Airport—Concourse | 0.6 |  | 371
ASHRAE 90.1-2004TransportationTerminal—Ticket Counter | ASHRAE 90.1-2004 | Transportation | Terminal—Ticket Counter | 1.5 |  | 373
ASHRAE 90.1-2004WarehouseFine Material Storage | ASHRAE 90.1-2004 | Warehouse | Fine Material Storage | 1.4 |  | 368
ASHRAE 90.1-2004WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2004 | Warehouse | Medium/Bulky Material Storage | 0.9 |  | 369
ASHRAE 90.1-2004Whole BuildingAutomotive Facility | ASHRAE 90.1-2004 | Whole Building | Automotive Facility | 0.9 |  | 251
ASHRAE 90.1-2004Whole BuildingConvention Center | ASHRAE 90.1-2004 | Whole Building | Convention Center | 1.2 |  | 252
ASHRAE 90.1-2004Whole BuildingCourt House | ASHRAE 90.1-2004 | Whole Building | Court House | 1.2 |  | 253
ASHRAE 90.1-2004Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2004 | Whole Building | Dining: Bar Lounge/Leisure | 1.3 |  | 254
ASHRAE 90.1-2004Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2004 | Whole Building | Dining: Cafeteria/Fast Food | 1.4 |  | 255
ASHRAE 90.1-2004Whole BuildingDining: Family | ASHRAE 90.1-2004 | Whole Building | Dining: Family | 1.6 |  | 256
ASHRAE 90.1-2004Whole BuildingDormitory | ASHRAE 90.1-2004 | Whole Building | Dormitory | 1 |  | 257
ASHRAE 90.1-2004Whole BuildingExercise Center | ASHRAE 90.1-2004 | Whole Building | Exercise Center | 1 |  | 258
ASHRAE 90.1-2004Whole BuildingGymnasium | ASHRAE 90.1-2004 | Whole Building | Gymnasium | 1.1 |  | 259
ASHRAE 90.1-2004Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2004 | Whole Building | Health Care-Clinic | 1 |  | 260
ASHRAE 90.1-2004Whole BuildingHospital | ASHRAE 90.1-2004 | Whole Building | Hospital | 1.2 |  | 261
ASHRAE 90.1-2004Whole BuildingHotel | ASHRAE 90.1-2004 | Whole Building | Hotel | 1 |  | 262
ASHRAE 90.1-2004Whole BuildingLibrary | ASHRAE 90.1-2004 | Whole Building | Library | 1.3 |  | 263
ASHRAE 90.1-2004Whole BuildingManufacturing Facility | ASHRAE 90.1-2004 | Whole Building | Manufacturing Facility | 1.3 |  | 264
ASHRAE 90.1-2004Whole BuildingMotel | ASHRAE 90.1-2004 | Whole Building | Motel | 1 |  | 265
ASHRAE 90.1-2004Whole BuildingMotion Picture Theater | ASHRAE 90.1-2004 | Whole Building | Motion Picture Theater | 1.2 |  | 266
ASHRAE 90.1-2004Whole BuildingMulti-Family | ASHRAE 90.1-2004 | Whole Building | Multi-Family | 0.7 |  | 267
ASHRAE 90.1-2004Whole BuildingMuseum | ASHRAE 90.1-2004 | Whole Building | Museum | 1.1 |  | 268
ASHRAE 90.1-2004Whole BuildingOffice | ASHRAE 90.1-2004 | Whole Building | Office | 1 |  | 269
ASHRAE 90.1-2004Whole BuildingParking Garage | ASHRAE 90.1-2004 | Whole Building | Parking Garage | 0.3 |  | 270
ASHRAE 90.1-2004Whole BuildingPenitentiary | ASHRAE 90.1-2004 | Whole Building | Penitentiary | 1 |  | 271
ASHRAE 90.1-2004Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2004 | Whole Building | Performing Arts Theater | 1.6 |  | 272
ASHRAE 90.1-2004Whole BuildingPolice/Fire Station | ASHRAE 90.1-2004 | Whole Building | Police/Fire Station | 1 |  | 273
ASHRAE 90.1-2004Whole BuildingPost Office | ASHRAE 90.1-2004 | Whole Building | Post Office | 1.1 |  | 274
ASHRAE 90.1-2004Whole BuildingReligious Building | ASHRAE 90.1-2004 | Whole Building | Religious Building | 1.3 |  | 275
ASHRAE 90.1-2004Whole BuildingRetail | ASHRAE 90.1-2004 | Whole Building | Retail | 1.5 |  | 276
ASHRAE 90.1-2004Whole BuildingSchool/University | ASHRAE 90.1-2004 | Whole Building | School/University | 1.2 |  | 277
ASHRAE 90.1-2004Whole BuildingSports Arena | ASHRAE 90.1-2004 | Whole Building | Sports Arena | 1.1 |  | 278
ASHRAE 90.1-2004Whole BuildingTown Hall | ASHRAE 90.1-2004 | Whole Building | Town Hall | 1.1 |  | 279
ASHRAE 90.1-2004Whole BuildingTransportation | ASHRAE 90.1-2004 | Whole Building | Transportation | 1 |  | 280
ASHRAE 90.1-2004Whole BuildingWarehouse | ASHRAE 90.1-2004 | Whole Building | Warehouse | 0.8 |  | 281
ASHRAE 90.1-2004Whole BuildingWorkshop | ASHRAE 90.1-2004 | Whole Building | Workshop | 1.4 |  | 282
ASHRAE 90.1-2004WorkshopWorkshop | ASHRAE 90.1-2004 | Workshop | Workshop | 1.9 |  | 359
ASHRAE 90.1-2007Whole BuildingAutomotive Facility | ASHRAE 90.1-2007 | Whole Building | Automotive Facility | 0.9 |  | 376
ASHRAE 90.1-2007Whole BuildingConvention Center | ASHRAE 90.1-2007 | Whole Building | Convention Center | 1.2 |  | 377
ASHRAE 90.1-2007Whole BuildingCourt House | ASHRAE 90.1-2007 | Whole Building | Court House | 1.2 |  | 378
ASHRAE 90.1-2007Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2007 | Whole Building | Dining: Bar Lounge/Leisure | 1.3 |  | 379
ASHRAE 90.1-2007Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2007 | Whole Building | Dining: Cafeteria/Fast Food | 1.4 |  | 380
ASHRAE 90.1-2007Whole BuildingDining: Family | ASHRAE 90.1-2007 | Whole Building | Dining: Family | 1.6 |  | 381
ASHRAE 90.1-2007Whole BuildingDormitory | ASHRAE 90.1-2007 | Whole Building | Dormitory | 1 |  | 382
ASHRAE 90.1-2007Whole BuildingExercise Center | ASHRAE 90.1-2007 | Whole Building | Exercise Center | 1 |  | 383
ASHRAE 90.1-2007Whole BuildingGymnasium | ASHRAE 90.1-2007 | Whole Building | Gymnasium | 1.1 |  | 384
ASHRAE 90.1-2007Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2007 | Whole Building | Health Care-Clinic | 1 |  | 385
ASHRAE 90.1-2007Whole BuildingHospital | ASHRAE 90.1-2007 | Whole Building | Hospital | 1.2 |  | 386
ASHRAE 90.1-2007Whole BuildingHotel | ASHRAE 90.1-2007 | Whole Building | Hotel | 1 |  | 387
ASHRAE 90.1-2007Whole BuildingLibrary | ASHRAE 90.1-2007 | Whole Building | Library | 1.3 |  | 388
ASHRAE 90.1-2007Whole BuildingManufacturing Facility | ASHRAE 90.1-2007 | Whole Building | Manufacturing Facility | 1.3 |  | 389
ASHRAE 90.1-2007Whole BuildingMotel | ASHRAE 90.1-2007 | Whole Building | Motel | 1 |  | 390
ASHRAE 90.1-2007Whole BuildingMotion Picture Theater | ASHRAE 90.1-2007 | Whole Building | Motion Picture Theater | 1.2 |  | 391
ASHRAE 90.1-2007Whole BuildingMulti-Family | ASHRAE 90.1-2007 | Whole Building | Multi-Family | 0.7 |  | 392
ASHRAE 90.1-2007Whole BuildingMuseum | ASHRAE 90.1-2007 | Whole Building | Museum | 1.1 |  | 393
ASHRAE 90.1-2007Whole BuildingOffice | ASHRAE 90.1-2007 | Whole Building | Office | 1 |  | 394
ASHRAE 90.1-2007Whole BuildingParking Garage | ASHRAE 90.1-2007 | Whole Building | Parking Garage | 0.3 |  | 395
ASHRAE 90.1-2007Whole BuildingPenitentiary | ASHRAE 90.1-2007 | Whole Building | Penitentiary | 1 |  | 396
ASHRAE 90.1-2007Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2007 | Whole Building | Performing Arts Theater | 1.6 |  | 397
ASHRAE 90.1-2007Whole BuildingPolice/Fire Station | ASHRAE 90.1-2007 | Whole Building | Police/Fire Station | 1 |  | 398
ASHRAE 90.1-2007Whole BuildingPost Office | ASHRAE 90.1-2007 | Whole Building | Post Office | 1.1 |  | 399
ASHRAE 90.1-2007Whole BuildingReligious Building | ASHRAE 90.1-2007 | Whole Building | Religious Building | 1.3 |  | 400
ASHRAE 90.1-2007Whole BuildingRetail | ASHRAE 90.1-2007 | Whole Building | Retail | 1.5 |  | 401
ASHRAE 90.1-2007Whole BuildingSchool/University | ASHRAE 90.1-2007 | Whole Building | School/University | 1.2 |  | 402
ASHRAE 90.1-2007Whole BuildingSports Arena | ASHRAE 90.1-2007 | Whole Building | Sports Arena | 1.1 |  | 403
ASHRAE 90.1-2007Whole BuildingTown Hall | ASHRAE 90.1-2007 | Whole Building | Town Hall | 1.1 |  | 404
ASHRAE 90.1-2007Whole BuildingTransportation | ASHRAE 90.1-2007 | Whole Building | Transportation | 1 |  | 405
ASHRAE 90.1-2007Whole BuildingWarehouse | ASHRAE 90.1-2007 | Whole Building | Warehouse | 0.8 |  | 406
ASHRAE 90.1-2007Whole BuildingWorkshop | ASHRAE 90.1-2007 | Whole Building | Workshop | 1.4 |  | 407
ASHRAE 90.1-2007Office-EnclosedGeneral | ASHRAE 90.1-2007 | Office-Enclosed | General | 1.1 |  | 408
ASHRAE 90.1-2007Office-Open PlanGeneral | ASHRAE 90.1-2007 | Office-Open Plan | General | 1.1 |  | 409
ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | 1.3 |  | 410
ASHRAE 90.1-2007Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2007 | Classroom/Lecture/Training | General | 1.4 |  | 411
ASHRAE 90.1-2007Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2007 | Classroom/Lecture/Training | For Penitentiary | 1.3 |  | 412
ASHRAE 90.1-2007LobbyGeneral | ASHRAE 90.1-2007 | Lobby | General | 1.3 |  | 413
ASHRAE 90.1-2007LobbyFor Hotel | ASHRAE 90.1-2007 | Lobby | For Hotel | 1.1 |  | 414
ASHRAE 90.1-2007LobbyFor Performing Arts Theater | ASHRAE 90.1-2007 | Lobby | For Performing Arts Theater | 3.3 |  | 415
ASHRAE 90.1-2007LobbyFor Motion Picture Theater | ASHRAE 90.1-2007 | Lobby | For Motion Picture Theater | 1.1 |  | 416
ASHRAE 90.1-2007Audience/Seating AreaGeneral | ASHRAE 90.1-2007 | Audience/Seating Area | General | 0.9 |  | 417
ASHRAE 90.1-2007Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2007 | Audience/Seating Area | For Gymnasium | 0.4 |  | 418
ASHRAE 90.1-2007Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-2007 | Audience/Seating Area | For Exercise Center | 0.3 |  | 419
ASHRAE 90.1-2007Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2007 | Audience/Seating Area | For Convention Center | 0.7 |  | 420
ASHRAE 90.1-2007Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2007 | Audience/Seating Area | For Penitentiary | 0.7 |  | 421
ASHRAE 90.1-2007Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2007 | Audience/Seating Area | For Religious Buildings | 1.7 |  | 422
ASHRAE 90.1-2007Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-2007 | Audience/Seating Area | For Sports Arena | 0.4 |  | 423
ASHRAE 90.1-2007Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-2007 | Audience/Seating Area | For Performing Arts Theater | 2.6 |  | 424
ASHRAE 90.1-2007Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2007 | Audience/Seating Area | For Motion Picture Theater | 1.2 |  | 425
ASHRAE 90.1-2007Audience/Seating AreaFor Transportation | ASHRAE 90.1-2007 | Audience/Seating Area | For Transportation | 0.5 |  | 426
ASHRAE 90.1-2007AtriumFirst Three Floors | ASHRAE 90.1-2007 | Atrium | First Three Floors | 0.6 |  | 427
ASHRAE 90.1-2007AtriumEach Floor over First Three Floors | ASHRAE 90.1-2007 | Atrium | Each Floor over First Three Floors | 0.2 |  | 428
ASHRAE 90.1-2007Lounge/RecreationGeneral | ASHRAE 90.1-2007 | Lounge/Recreation | General | 1.2 |  | 429
ASHRAE 90.1-2007Lounge/RecreationFor Hospital | ASHRAE 90.1-2007 | Lounge/Recreation | For Hospital | 0.8 |  | 430
ASHRAE 90.1-2007Dining AreaGeneral | ASHRAE 90.1-2007 | Dining Area | General | 0.9 |  | 431
ASHRAE 90.1-2007Dining AreaFor Penitentiary | ASHRAE 90.1-2007 | Dining Area | For Penitentiary | 1.3 |  | 432
ASHRAE 90.1-2007Dining AreaFor Hotel | ASHRAE 90.1-2007 | Dining Area | For Hotel | 1.3 |  | 433
ASHRAE 90.1-2007Dining AreaFor Motel | ASHRAE 90.1-2007 | Dining Area | For Motel | 1.2 |  | 434
ASHRAE 90.1-2007Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2007 | Dining Area | For Bar Lounge/Leisure Dining | 1.4 |  | 435
ASHRAE 90.1-2007Dining AreaFor Family Dining | ASHRAE 90.1-2007 | Dining Area | For Family Dining | 2.1 |  | 436
ASHRAE 90.1-2007Food PreparationGeneral | ASHRAE 90.1-2007 | Food Preparation | General | 1.2 |  | 437
ASHRAE 90.1-2007LaboratoryGeneral | ASHRAE 90.1-2007 | Laboratory | General | 1.4 |  | 438
ASHRAE 90.1-2007RestroomsGeneral | ASHRAE 90.1-2007 | Restrooms | General | 0.9 |  | 439
ASHRAE 90.1-2007Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-2007 | Dressing/Locker/Fitting Room | General | 0.6 |  | 440
ASHRAE 90.1-2007Corridor/TransitionGeneral | ASHRAE 90.1-2007 | Corridor/Transition | General | 0.5 |  | 441
ASHRAE 90.1-2007Corridor/TransitionFor Hospital | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | 1 |  | 442
ASHRAE 90.1-2007Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-2007 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 443
ASHRAE 90.1-2007Stairs-ActiveGeneral | ASHRAE 90.1-2007 | Stairs-Active | General | 0.6 |  | 444
ASHRAE 90.1-2007Active StorageGeneral | ASHRAE 90.1-2007 | Active Storage | General | 0.8 |  | 445
ASHRAE 90.1-2007Active StorageFor Hospital | ASHRAE 90.1-2007 | Active Storage | For Hospital | 0.9 |  | 446
ASHRAE 90.1-2007Inactive storageGeneral | ASHRAE 90.1-2007 | Inactive storage | General | 0.3 |  | 447
ASHRAE 90.1-2007Inactive storageFor Museum | ASHRAE 90.1-2007 | Inactive storage | For Museum | 0.8 |  | 448
ASHRAE 90.1-2007Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Playing Area | 1.4 |  | 449
ASHRAE 90.1-2007Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Exercise Area | 0.9 |  | 450
ASHRAE 90.1-2007Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-2007 | Courthouse/Police Station/Penitentiary | Courtroom | 1.9 |  | 451
ASHRAE 90.1-2007Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-2007 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.9 |  | 452
ASHRAE 90.1-2007Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-2007 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.3 |  | 453
ASHRAE 90.1-2007Fire StationsFire Station Engine Room | ASHRAE 90.1-2007 | Fire Stations | Fire Station Engine Room | 0.8 |  | 454
ASHRAE 90.1-2007Fire StationsSleeping Quarters | ASHRAE 90.1-2007 | Fire Stations | Sleeping Quarters | 0.3 |  | 455
ASHRAE 90.1-2007Post OfficeSorting Area | ASHRAE 90.1-2007 | Post Office | Sorting Area | 1.2 |  | 456
ASHRAE 90.1-2007Convention CenterExhibit Space | ASHRAE 90.1-2007 | Convention Center | Exhibit Space | 1.3 |  | 457
ASHRAE 90.1-2007LibraryCard File and Cataloging | ASHRAE 90.1-2007 | Library | Card File and Cataloging | 1.1 |  | 458
ASHRAE 90.1-2007LibraryStacks | ASHRAE 90.1-2007 | Library | Stacks | 1.7 |  | 459
ASHRAE 90.1-2007LibraryReading Area | ASHRAE 90.1-2007 | Library | Reading Area | 1.2 |  | 460
ASHRAE 90.1-2007HospitalEmergency | ASHRAE 90.1-2007 | Hospital | Emergency | 2.7 |  | 461
ASHRAE 90.1-2007HospitalRecovery | ASHRAE 90.1-2007 | Hospital | Recovery | 0.8 |  | 462
ASHRAE 90.1-2007HospitalNurse Station | ASHRAE 90.1-2007 | Hospital | Nurse Station | 1 |  | 463
ASHRAE 90.1-2007HospitalExam/Treatment | ASHRAE 90.1-2007 | Hospital | Exam/Treatment | 1.5 |  | 464
ASHRAE 90.1-2007HospitalPharmacy | ASHRAE 90.1-2007 | Hospital | Pharmacy | 1.2 |  | 465
ASHRAE 90.1-2007HospitalPatient Room | ASHRAE 90.1-2007 | Hospital | Patient Room | 0.7 |  | 466
ASHRAE 90.1-2007HospitalOperating Room | ASHRAE 90.1-2007 | Hospital | Operating Room | 2.2 |  | 467
ASHRAE 90.1-2007HospitalNursery | ASHRAE 90.1-2007 | Hospital | Nursery | 0.6 |  | 468
ASHRAE 90.1-2007HospitalMedical Supply | ASHRAE 90.1-2007 | Hospital | Medical Supply | 1.4 |  | 469
ASHRAE 90.1-2007HospitalPhysical Therapy | ASHRAE 90.1-2007 | Hospital | Physical Therapy | 0.9 |  | 470
ASHRAE 90.1-2007HospitalRadiology | ASHRAE 90.1-2007 | Hospital | Radiology | 0.4 |  | 471
ASHRAE 90.1-2007HospitalLaundry-Washing | ASHRAE 90.1-2007 | Hospital | Laundry-Washing | 0.6 |  | 472
ASHRAE 90.1-2007AutomotiveService/Repair | ASHRAE 90.1-2007 | Automotive | Service/Repair | 0.7 |  | 473
ASHRAE 90.1-2007ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2007 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.2 |  | 474
ASHRAE 90.1-2007ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-2007 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.7 |  | 475
ASHRAE 90.1-2007ManufacturingDetailed Manufacturing | ASHRAE 90.1-2007 | Manufacturing | Detailed Manufacturing | 2.1 |  | 476
ASHRAE 90.1-2007ManufacturingEquipment Room | ASHRAE 90.1-2007 | Manufacturing | Equipment Room | 1.2 |  | 477
ASHRAE 90.1-2007ManufacturingControl Room | ASHRAE 90.1-2007 | Manufacturing | Control Room | 0.5 |  | 478
ASHRAE 90.1-2007Hotel/MotelGuest Rooms | ASHRAE 90.1-2007 | Hotel/Motel | Guest Rooms | 1.1 |  | 479
ASHRAE 90.1-2007DormitoryLiving Quarters | ASHRAE 90.1-2007 | Dormitory | Living Quarters | 1.1 |  | 480
ASHRAE 90.1-2007MuseumGeneral Exhibition | ASHRAE 90.1-2007 | Museum | General Exhibition | 1 |  | 481
ASHRAE 90.1-2007MuseumRestoration | ASHRAE 90.1-2007 | Museum | Restoration | 1.7 |  | 482
ASHRAE 90.1-2007Electrical/MechanicalGeneral | ASHRAE 90.1-2007 | Electrical/Mechanical | General | 1.5 |  | 483
ASHRAE 90.1-2007WorkshopGeneral | ASHRAE 90.1-2007 | Workshop | General | 1.9 |  | 484
ASHRAE 90.1-2007Bank/OfficeBanking Activity Area | ASHRAE 90.1-2007 | Bank/Office | Banking Activity Area | 1.5 |  | 485
ASHRAE 90.1-2007Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2007 | Religious Buildings | Worship Pulpit, Choir | 2.4 |  | 486
ASHRAE 90.1-2007Religious BuildingsFellowship Hall | ASHRAE 90.1-2007 | Religious Buildings | Fellowship Hall | 0.9 |  | 487
ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | 1.7 |  | 488
ASHRAE 90.1-2007Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Mall Concourse | 1.7 |  | 489
ASHRAE 90.1-2007Sports ArenaRing Sports Area | ASHRAE 90.1-2007 | Sports Arena | Ring Sports Area | 2.7 |  | 490
ASHRAE 90.1-2007Sports ArenaCourt Sports Area | ASHRAE 90.1-2007 | Sports Arena | Court Sports Area | 2.3 |  | 491
ASHRAE 90.1-2007Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-2007 | Sports Arena | Indoor Playing Field Area | 1.4 |  | 492
ASHRAE 90.1-2007WarehouseFine Material Storage | ASHRAE 90.1-2007 | Warehouse | Fine Material Storage | 1.4 |  | 493
ASHRAE 90.1-2007WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2007 | Warehouse | Medium/Bulky Material Storage | 0.9 |  | 494
ASHRAE 90.1-2007Parking GarageGarage Area | ASHRAE 90.1-2007 | Parking Garage | Garage Area | 0.2 |  | 495
ASHRAE 90.1-2007TransportationAirport-Concourse | ASHRAE 90.1-2007 | Transportation | Airport-Concourse | 0.6 |  | 496
ASHRAE 90.1-2007TransportationAir/Train/Bus-Baggage Area | ASHRAE 90.1-2007 | Transportation | Air/Train/Bus-Baggage Area | 1 |  | 497
ASHRAE 90.1-2007TransportationTerminal-Ticket Counter | ASHRAE 90.1-2007 | Transportation | Terminal-Ticket Counter | 1.5 |  | 498
ASHRAE 90.1-2007Exterior SpacesGeneral | ASHRAE 90.1-2007 | Exterior Spaces | General | 0 |  | 499
ASHRAE 90.1-2007AtticsGeneral | ASHRAE 90.1-2007 | Attics | General | 0 |  | 500
GGHC v2.2Health CareAnesthesia Storage | GGHC v2.2 | Health Care | Anesthesia Storage | 3 |  | 501
GGHC v2.2Health CareAngiographic-All Other Types | GGHC v2.2 | Health Care | Angiographic-All Other Types | 3 |  | 502
GGHC v2.2Health CareAngiographic-Heart Only | GGHC v2.2 | Health Care | Angiographic-Heart Only | 3 |  | 503
GGHC v2.2Health CareAutopsy | GGHC v2.2 | Health Care | Autopsy | 1.2 |  | 504
GGHC v2.2Health CareBathroom/ Public | GGHC v2.2 | Health Care | Bathroom/ Public | 0.6 |  | 505
GGHC v2.2Health CareBedpan Room | GGHC v2.2 | Health Care | Bedpan Room | 0.5 |  | 506
GGHC v2.2Health CareCast Room | GGHC v2.2 | Health Care | Cast Room | 3 |  | 507
GGHC v2.2Health CareClean Linen Storage | GGHC v2.2 | Health Care | Clean Linen Storage | 0.5 |  | 508
GGHC v2.2Health CareClean Utility / Workroom | GGHC v2.2 | Health Care | Clean Utility / Workroom | 1.2 |  | 509
GGHC v2.2Health CareConference Rooms | GGHC v2.2 | Health Care | Conference Rooms | 1.2 |  | 510
GGHC v2.2Health CareCorridors | GGHC v2.2 | Health Care | Corridors | 0.6 |  | 511
GGHC v2.2Health CareCystoscopy | GGHC v2.2 | Health Care | Cystoscopy | 3 |  | 512
GGHC v2.2Health CareDarkroom | GGHC v2.2 | Health Care | Darkroom | 0.3 |  | 513
GGHC v2.2Health CareDecontamination | GGHC v2.2 | Health Care | Decontamination | 1.2 |  | 514
GGHC v2.2Health CareDelivery Room | GGHC v2.2 | Health Care | Delivery Room | 4.5 |  | 515
GGHC v2.2Health CareDietary Day Storage | GGHC v2.2 | Health Care | Dietary Day Storage | 0.5 |  | 516
GGHC v2.2Health CareDining Room | GGHC v2.2 | Health Care | Dining Room | 1.1 |  | 517
GGHC v2.2Health CareDishwashing | GGHC v2.2 | Health Care | Dishwashing | 1.7 |  | 518
GGHC v2.2Health CareEndoscopy | GGHC v2.2 | Health Care | Endoscopy | 3 |  | 519
GGHC v2.2Health CareHistology | GGHC v2.2 | Health Care | Histology | 4.5 |  | 520
GGHC v2.2Health CareIsolation | GGHC v2.2 | Health Care | Isolation | 0.5 |  | 521
GGHC v2.2Health CareJanitors Closet / Utility | GGHC v2.2 | Health Care | Janitors Closet / Utility | 0.5 |  | 522
GGHC v2.2Health CareKitchen, Food Preparation | GGHC v2.2 | Health Care | Kitchen, Food Preparation | 1.7 |  | 523
GGHC v2.2Health CareLabor/ Delivery/Recovery | GGHC v2.2 | Health Care | Labor/ Delivery/Recovery | 4.5 |  | 524
GGHC v2.2Health CareL / D / R / Post Partum | GGHC v2.2 | Health Care | L / D / R / Post Partum | 0.7 |  | 525
GGHC v2.2Health CareLaboratory | GGHC v2.2 | Health Care | Laboratory | 3 |  | 526
GGHC v2.2Health CareLinen Storage, Clean | GGHC v2.2 | Health Care | Linen Storage, Clean | 0.5 |  | 527
GGHC v2.2Health CareLobby | GGHC v2.2 | Health Care | Lobby | 1.1 |  | 528
GGHC v2.2Health CareLockers | GGHC v2.2 | Health Care | Lockers | 0.7 |  | 529
GGHC v2.2Health CareMammography | GGHC v2.2 | Health Care | Mammography | 3 |  | 530
GGHC v2.2Health CareMechanical Equipment Room | GGHC v2.2 | Health Care | Mechanical Equipment Room | 0.7 |  | 531
GGHC v2.2Health CareMedical Records | GGHC v2.2 | Health Care | Medical Records | 3 |  | 532
GGHC v2.2Health CareNuclear Medicine, Hot Lab | GGHC v2.2 | Health Care | Nuclear Medicine, Hot Lab | 1.2 |  | 533
GGHC v2.2Health CareNursery, General | GGHC v2.2 | Health Care | Nursery, General | 3 |  | 534
GGHC v2.2Health CareNursery, Exam | GGHC v2.2 | Health Care | Nursery, Exam | 0.7 |  | 535
GGHC v2.2Health CareNursing Stations- General | GGHC v2.2 | Health Care | Nursing Stations- General | 1.2 |  | 536
GGHC v2.2Health CareOperating Room | GGHC v2.2 | Health Care | Operating Room | 4.5 |  | 537
GGHC v2.2Health CarePathology | GGHC v2.2 | Health Care | Pathology | 3 |  | 538
GGHC v2.2Health CarePatient Room | GGHC v2.2 | Health Care | Patient Room | 0.5 |  | 539
GGHC v2.2Health CarePharmacy / Medicine Room | GGHC v2.2 | Health Care | Pharmacy / Medicine Room | 3 |  | 540
GGHC v2.2Health CarePhysical Therapy and Hydrotherapy | GGHC v2.2 | Health Care | Physical Therapy and Hydrotherapy | 1.2 |  | 541
GGHC v2.2Health CareRecovery | GGHC v2.2 | Health Care | Recovery | 3 |  | 542
GGHC v2.2Health CareScrub Up Area, Surgical Corridor | GGHC v2.2 | Health Care | Scrub Up Area, Surgical Corridor | 4.5 |  | 543
GGHC v2.2Health CareSoiled Linen, Sorting | GGHC v2.2 | Health Care | Soiled Linen, Sorting | 1.2 |  | 544
GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | 3 |  | 545
GGHC v2.2Health CareSpecial Procedure Room, Invasive | GGHC v2.2 | Health Care | Special Procedure Room, Invasive | 3 |  | 546
GGHC v2.2Health CareStairways | GGHC v2.2 | Health Care | Stairways | 0.6 |  | 547
GGHC v2.2Health CareSterilizer Room | GGHC v2.2 | Health Care | Sterilizer Room | 1.2 |  | 548
GGHC v2.2Health CareSub-Sterile | GGHC v2.2 | Health Care | Sub-Sterile | 0.7 |  | 549
GGHC v2.2Health CareSurgical Supply | GGHC v2.2 | Health Care | Surgical Supply | 1.2 |  | 550
GGHC v2.2Health CareTrash Chute Room | GGHC v2.2 | Health Care | Trash Chute Room | 0.5 |  | 551
GGHC v2.2Health CareTrauma | GGHC v2.2 | Health Care | Trauma | 3 |  | 552
GGHC v2.2Health CareTreatment / Examination | GGHC v2.2 | Health Care | Treatment / Examination | 1.2 |  | 553
GGHC v2.2Health CareUnsterile Supply | GGHC v2.2 | Health Care | Unsterile Supply | 0.5 |  | 554
GGHC v2.2Health CareWaiting Areas/Lounges | GGHC v2.2 | Health Care | Waiting Areas/Lounges | 1.1 |  | 555
GGHC v2.2Health CareX-ray, Diagnostic and Treatment | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | 3 |  | 556
ASHRAE 189.1-2009Whole BuildingAutomotive Facility | ASHRAE 189.1-2009 | Whole Building | Automotive Facility | 0.81
ASHRAE 189.1-2009Whole BuildingConvention Center | ASHRAE 189.1-2009 | Whole Building | Convention Center | 1.08
ASHRAE 189.1-2009Whole BuildingCourt House | ASHRAE 189.1-2009 | Whole Building | Court House | 1.08
ASHRAE 189.1-2009Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 189.1-2009 | Whole Building | Dining: Bar Lounge/Leisure | 1.17
ASHRAE 189.1-2009Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 189.1-2009 | Whole Building | Dining: Cafeteria/Fast Food | 1.26
ASHRAE 189.1-2009Whole BuildingDining: Family | ASHRAE 189.1-2009 | Whole Building | Dining: Family | 1.44
ASHRAE 189.1-2009Whole BuildingDormitory | ASHRAE 189.1-2009 | Whole Building | Dormitory | 0.9
ASHRAE 189.1-2009Whole BuildingExercise Center | ASHRAE 189.1-2009 | Whole Building | Exercise Center | 0.9
ASHRAE 189.1-2009Whole BuildingGymnasium | ASHRAE 189.1-2009 | Whole Building | Gymnasium | 0.99
ASHRAE 189.1-2009Whole BuildingHealth Care-Clinic | ASHRAE 189.1-2009 | Whole Building | Health Care-Clinic | 0.9
ASHRAE 189.1-2009Whole BuildingHospital | ASHRAE 189.1-2009 | Whole Building | Hospital | 1.08
ASHRAE 189.1-2009Whole BuildingHotel | ASHRAE 189.1-2009 | Whole Building | Hotel | 0.9
ASHRAE 189.1-2009Whole BuildingLibrary | ASHRAE 189.1-2009 | Whole Building | Library | 1.17
ASHRAE 189.1-2009Whole BuildingManufacturing Facility | ASHRAE 189.1-2009 | Whole Building | Manufacturing Facility | 1.17
ASHRAE 189.1-2009Whole BuildingMotel | ASHRAE 189.1-2009 | Whole Building | Motel | 0.9
ASHRAE 189.1-2009Whole BuildingMotion Picture Theater | ASHRAE 189.1-2009 | Whole Building | Motion Picture Theater | 1.08
ASHRAE 189.1-2009Whole BuildingMulti-Family | ASHRAE 189.1-2009 | Whole Building | Multi-Family | 0.63
ASHRAE 189.1-2009Whole BuildingMuseum | ASHRAE 189.1-2009 | Whole Building | Museum | 0.99
ASHRAE 189.1-2009Whole BuildingOffice | ASHRAE 189.1-2009 | Whole Building | Office | 0.9
ASHRAE 189.1-2009Whole BuildingParking Garage | ASHRAE 189.1-2009 | Whole Building | Parking Garage | 0.27
ASHRAE 189.1-2009Whole BuildingPenitentiary | ASHRAE 189.1-2009 | Whole Building | Penitentiary | 0.9
ASHRAE 189.1-2009Whole BuildingPerforming Arts Theater | ASHRAE 189.1-2009 | Whole Building | Performing Arts Theater | 1.44
ASHRAE 189.1-2009Whole BuildingPolice/Fire Station | ASHRAE 189.1-2009 | Whole Building | Police/Fire Station | 0.9
ASHRAE 189.1-2009Whole BuildingPost Office | ASHRAE 189.1-2009 | Whole Building | Post Office | 0.99
ASHRAE 189.1-2009Whole BuildingReligious Building | ASHRAE 189.1-2009 | Whole Building | Religious Building | 1.17
ASHRAE 189.1-2009Whole BuildingRetail | ASHRAE 189.1-2009 | Whole Building | Retail | 1.35
ASHRAE 189.1-2009Whole BuildingSchool/University | ASHRAE 189.1-2009 | Whole Building | School/University | 1.08
ASHRAE 189.1-2009Whole BuildingSports Arena | ASHRAE 189.1-2009 | Whole Building | Sports Arena | 0.99
ASHRAE 189.1-2009Whole BuildingTown Hall | ASHRAE 189.1-2009 | Whole Building | Town Hall | 0.99
ASHRAE 189.1-2009Whole BuildingTransportation | ASHRAE 189.1-2009 | Whole Building | Transportation | 0.9
ASHRAE 189.1-2009Whole BuildingWarehouse | ASHRAE 189.1-2009 | Whole Building | Warehouse | 0.72
ASHRAE 189.1-2009Whole BuildingWorkshop | ASHRAE 189.1-2009 | Whole Building | Workshop | 1.26
ASHRAE 189.1-2009Office-EnclosedGeneral | ASHRAE 189.1-2009 | Office-Enclosed | General | 0.99
ASHRAE 189.1-2009Office-Open PlanGeneral | ASHRAE 189.1-2009 | Office-Open Plan | General | 0.99
ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | 1.17
ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | 1.26
ASHRAE 189.1-2009Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 189.1-2009 | Classroom/Lecture/Training | For Penitentiary | 1.17
ASHRAE 189.1-2009LobbyGeneral | ASHRAE 189.1-2009 | Lobby | General | 1.17
ASHRAE 189.1-2009LobbyFor Hotel | ASHRAE 189.1-2009 | Lobby | For Hotel | 0.99
ASHRAE 189.1-2009LobbyFor Performing Arts Theater | ASHRAE 189.1-2009 | Lobby | For Performing Arts Theater | 2.97
ASHRAE 189.1-2009LobbyFor Motion Picture Theater | ASHRAE 189.1-2009 | Lobby | For Motion Picture Theater | 0.99
ASHRAE 189.1-2009Audience/Seating AreaGeneral | ASHRAE 189.1-2009 | Audience/Seating Area | General | 0.81
ASHRAE 189.1-2009Audience/Seating AreaFor Gymnasium | ASHRAE 189.1-2009 | Audience/Seating Area | For Gymnasium | 0.36
ASHRAE 189.1-2009Audience/Seating AreaFor Exercise Center | ASHRAE 189.1-2009 | Audience/Seating Area | For Exercise Center | 0.27
ASHRAE 189.1-2009Audience/Seating AreaFor Convention Center | ASHRAE 189.1-2009 | Audience/Seating Area | For Convention Center | 0.63
ASHRAE 189.1-2009Audience/Seating AreaFor Penitentiary | ASHRAE 189.1-2009 | Audience/Seating Area | For Penitentiary | 0.63
ASHRAE 189.1-2009Audience/Seating AreaFor Religious Buildings | ASHRAE 189.1-2009 | Audience/Seating Area | For Religious Buildings | 1.53
ASHRAE 189.1-2009Audience/Seating AreaFor Sports Arena | ASHRAE 189.1-2009 | Audience/Seating Area | For Sports Arena | 0.36
ASHRAE 189.1-2009Audience/Seating AreaFor Performing Arts Theater | ASHRAE 189.1-2009 | Audience/Seating Area | For Performing Arts Theater | 2.34
ASHRAE 189.1-2009Audience/Seating AreaFor Motion Picture Theater | ASHRAE 189.1-2009 | Audience/Seating Area | For Motion Picture Theater | 1.08
ASHRAE 189.1-2009Audience/Seating AreaFor Transportation | ASHRAE 189.1-2009 | Audience/Seating Area | For Transportation | 0.45
ASHRAE 189.1-2009AtriumFirst Three Floors | ASHRAE 189.1-2009 | Atrium | First Three Floors | 0.54
ASHRAE 189.1-2009AtriumEach Floor over First Three Floors | ASHRAE 189.1-2009 | Atrium | Each Floor over First Three Floors | 0.18
ASHRAE 189.1-2009Lounge/RecreationGeneral | ASHRAE 189.1-2009 | Lounge/Recreation | General | 1.08
ASHRAE 189.1-2009Lounge/RecreationFor Hospital | ASHRAE 189.1-2009 | Lounge/Recreation | For Hospital | 0.72
ASHRAE 189.1-2009Dining AreaGeneral | ASHRAE 189.1-2009 | Dining Area | General | 0.81
ASHRAE 189.1-2009Dining AreaFor Penitentiary | ASHRAE 189.1-2009 | Dining Area | For Penitentiary | 1.17
ASHRAE 189.1-2009Dining AreaFor Hotel | ASHRAE 189.1-2009 | Dining Area | For Hotel | 1.17
ASHRAE 189.1-2009Dining AreaFor Motel | ASHRAE 189.1-2009 | Dining Area | For Motel | 1.08
ASHRAE 189.1-2009Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 189.1-2009 | Dining Area | For Bar Lounge/Leisure Dining | 1.26
ASHRAE 189.1-2009Dining AreaFor Family Dining | ASHRAE 189.1-2009 | Dining Area | For Family Dining | 1.89
ASHRAE 189.1-2009Food PreparationGeneral | ASHRAE 189.1-2009 | Food Preparation | General | 1.08
ASHRAE 189.1-2009LaboratoryGeneral | ASHRAE 189.1-2009 | Laboratory | General | 1.26
ASHRAE 189.1-2009RestroomsGeneral | ASHRAE 189.1-2009 | Restrooms | General | 0.81
ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | 0.54
ASHRAE 189.1-2009Corridor/TransitionGeneral | ASHRAE 189.1-2009 | Corridor/Transition | General | 0.45
ASHRAE 189.1-2009Corridor/TransitionFor Hospital | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | 0.9
ASHRAE 189.1-2009Corridor/TransitionFor Manufacturing Facility | ASHRAE 189.1-2009 | Corridor/Transition | For Manufacturing Facility | 0.45
ASHRAE 189.1-2009Stairs-ActiveGeneral | ASHRAE 189.1-2009 | Stairs-Active | General | 0.54
ASHRAE 189.1-2009Active StorageGeneral | ASHRAE 189.1-2009 | Active Storage | General | 0.72
ASHRAE 189.1-2009Active StorageFor Hospital | ASHRAE 189.1-2009 | Active Storage | For Hospital | 0.81
ASHRAE 189.1-2009Inactive storageGeneral | ASHRAE 189.1-2009 | Inactive storage | General | 0.27
ASHRAE 189.1-2009Inactive storageFor Museum | ASHRAE 189.1-2009 | Inactive storage | For Museum | 0.72
ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | 1.26
ASHRAE 189.1-2009Gymnasium/Exercise CenterExercise Area | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Exercise Area | 0.81
ASHRAE 189.1-2009Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 189.1-2009 | Courthouse/Police Station/Penitentiary | Courtroom | 1.71
ASHRAE 189.1-2009Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 189.1-2009 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.81
ASHRAE 189.1-2009Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 189.1-2009 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.17
ASHRAE 189.1-2009Fire StationsFire Station Engine Room | ASHRAE 189.1-2009 | Fire Stations | Fire Station Engine Room | 0.72
ASHRAE 189.1-2009Fire StationsSleeping Quarters | ASHRAE 189.1-2009 | Fire Stations | Sleeping Quarters | 0.27
ASHRAE 189.1-2009Post OfficeSorting Area | ASHRAE 189.1-2009 | Post Office | Sorting Area | 1.08
ASHRAE 189.1-2009Convention CenterExhibit Space | ASHRAE 189.1-2009 | Convention Center | Exhibit Space | 1.17
ASHRAE 189.1-2009LibraryCard File and Cataloging | ASHRAE 189.1-2009 | Library | Card File and Cataloging | 0.99
ASHRAE 189.1-2009LibraryStacks | ASHRAE 189.1-2009 | Library | Stacks | 1.53
ASHRAE 189.1-2009LibraryReading Area | ASHRAE 189.1-2009 | Library | Reading Area | 1.08
ASHRAE 189.1-2009HospitalEmergency | ASHRAE 189.1-2009 | Hospital | Emergency | 2.43
ASHRAE 189.1-2009HospitalRecovery | ASHRAE 189.1-2009 | Hospital | Recovery | 0.72
ASHRAE 189.1-2009HospitalNurse Station | ASHRAE 189.1-2009 | Hospital | Nurse Station | 0.9
ASHRAE 189.1-2009HospitalExam/Treatment | ASHRAE 189.1-2009 | Hospital | Exam/Treatment | 1.35
ASHRAE 189.1-2009HospitalPharmacy | ASHRAE 189.1-2009 | Hospital | Pharmacy | 1.08
ASHRAE 189.1-2009HospitalPatient Room | ASHRAE 189.1-2009 | Hospital | Patient Room | 0.63
ASHRAE 189.1-2009HospitalOperating Room | ASHRAE 189.1-2009 | Hospital | Operating Room | 1.98
ASHRAE 189.1-2009HospitalNursery | ASHRAE 189.1-2009 | Hospital | Nursery | 0.54
ASHRAE 189.1-2009HospitalMedical Supply | ASHRAE 189.1-2009 | Hospital | Medical Supply | 1.26
ASHRAE 189.1-2009HospitalPhysical Therapy | ASHRAE 189.1-2009 | Hospital | Physical Therapy | 0.81
ASHRAE 189.1-2009HospitalRadiology | ASHRAE 189.1-2009 | Hospital | Radiology | 0.36
ASHRAE 189.1-2009HospitalLaundry-Washing | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | 0.54
ASHRAE 189.1-2009AutomotiveService/Repair | ASHRAE 189.1-2009 | Automotive | Service/Repair | 0.63
ASHRAE 189.1-2009ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 189.1-2009 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.08
ASHRAE 189.1-2009ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 189.1-2009 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.53
ASHRAE 189.1-2009ManufacturingDetailed Manufacturing | ASHRAE 189.1-2009 | Manufacturing | Detailed Manufacturing | 1.89
ASHRAE 189.1-2009ManufacturingEquipment Room | ASHRAE 189.1-2009 | Manufacturing | Equipment Room | 1.08
ASHRAE 189.1-2009ManufacturingControl Room | ASHRAE 189.1-2009 | Manufacturing | Control Room | 0.45
ASHRAE 189.1-2009Hotel/MotelGuest Rooms | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | 0.99
ASHRAE 189.1-2009DormitoryLiving Quarters | ASHRAE 189.1-2009 | Dormitory | Living Quarters | 0.99
ASHRAE 189.1-2009MuseumGeneral Exhibition | ASHRAE 189.1-2009 | Museum | General Exhibition | 0.9
ASHRAE 189.1-2009MuseumRestoration | ASHRAE 189.1-2009 | Museum | Restoration | 1.53
ASHRAE 189.1-2009Electrical/MechanicalGeneral | ASHRAE 189.1-2009 | Electrical/Mechanical | General | 1.35
ASHRAE 189.1-2009WorkshopGeneral | ASHRAE 189.1-2009 | Workshop | General | 1.71
ASHRAE 189.1-2009Bank/OfficeBanking Activity Area | ASHRAE 189.1-2009 | Bank/Office | Banking Activity Area | 1.35
ASHRAE 189.1-2009Religious BuildingsWorship Pulpit, Choir | ASHRAE 189.1-2009 | Religious Buildings | Worship Pulpit, Choir | 2.16
ASHRAE 189.1-2009Religious BuildingsFellowship Hall | ASHRAE 189.1-2009 | Religious Buildings | Fellowship Hall | 0.81
ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | 1.53
ASHRAE 189.1-2009Retail (not including accent lighting)Mall Concourse | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Mall Concourse | 1.53
ASHRAE 189.1-2009Sports ArenaRing Sports Area | ASHRAE 189.1-2009 | Sports Arena | Ring Sports Area | 2.43
ASHRAE 189.1-2009Sports ArenaCourt Sports Area | ASHRAE 189.1-2009 | Sports Arena | Court Sports Area | 2.07
ASHRAE 189.1-2009Sports ArenaIndoor Playing Field Area | ASHRAE 189.1-2009 | Sports Arena | Indoor Playing Field Area | 1.26
ASHRAE 189.1-2009WarehouseFine Material Storage | ASHRAE 189.1-2009 | Warehouse | Fine Material Storage | 1.26
ASHRAE 189.1-2009WarehouseMedium/Bulky Material Storage | ASHRAE 189.1-2009 | Warehouse | Medium/Bulky Material Storage | 0.81
ASHRAE 189.1-2009Parking GarageGarage Area | ASHRAE 189.1-2009 | Parking Garage | Garage Area | 0.18
ASHRAE 189.1-2009TransportationAirport-Concourse | ASHRAE 189.1-2009 | Transportation | Airport-Concourse | 0.54
ASHRAE 189.1-2009TransportationAir/Train/Bus-Baggage Area | ASHRAE 189.1-2009 | Transportation | Air/Train/Bus-Baggage Area | 0.9
ASHRAE 189.1-2009TransportationTerminal-Ticket Counter | ASHRAE 189.1-2009 | Transportation | Terminal-Ticket Counter | 1.35
ASHRAE 189.1-2009Exterior SpacesGeneral | ASHRAE 189.1-2009 | Exterior Spaces | General | 0
ASHRAE 189.1-2009AtticsGeneral | ASHRAE 189.1-2009 | Attics | General | 0
ASHRAE 90.1-2010Whole BuildingAutomotive Facility | ASHRAE 90.1-2010 | Whole Building | Automotive Facility | 0.82
ASHRAE 90.1-2010Whole BuildingConvention Center | ASHRAE 90.1-2010 | Whole Building | Convention Center | 1.08
ASHRAE 90.1-2010Whole BuildingCourt House | ASHRAE 90.1-2010 | Whole Building | Court House | 1.05
ASHRAE 90.1-2010Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2010 | Whole Building | Dining: Bar Lounge/Leisure | 0.99
ASHRAE 90.1-2010Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2010 | Whole Building | Dining: Cafeteria/Fast Food | 0.9
ASHRAE 90.1-2010Whole BuildingDining: Family | ASHRAE 90.1-2010 | Whole Building | Dining: Family | 0.89
ASHRAE 90.1-2010Whole BuildingDormitory | ASHRAE 90.1-2010 | Whole Building | Dormitory | 0.61
ASHRAE 90.1-2010Whole BuildingExercise Center | ASHRAE 90.1-2010 | Whole Building | Exercise Center | 0.88
ASHRAE 90.1-2010Whole BuildingFire Station | ASHRAE 90.1-2010 | Whole Building | Fire Station | 0.71
ASHRAE 90.1-2010Whole BuildingGymnasium | ASHRAE 90.1-2010 | Whole Building | Gymnasium | 1
ASHRAE 90.1-2010Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2010 | Whole Building | Health Care-Clinic | 0.87
ASHRAE 90.1-2010Whole BuildingHospital | ASHRAE 90.1-2010 | Whole Building | Hospital | 1.21
ASHRAE 90.1-2010Whole BuildingHotel | ASHRAE 90.1-2010 | Whole Building | Hotel | 1
ASHRAE 90.1-2010Whole BuildingLibrary | ASHRAE 90.1-2010 | Whole Building | Library | 1.18
ASHRAE 90.1-2010Whole BuildingManufacturing Facility | ASHRAE 90.1-2010 | Whole Building | Manufacturing Facility | 1.11
ASHRAE 90.1-2010Whole BuildingMotel | ASHRAE 90.1-2010 | Whole Building | Motel | 0.88
ASHRAE 90.1-2010Whole BuildingMotion Picture Theater | ASHRAE 90.1-2010 | Whole Building | Motion Picture Theater | 0.83
ASHRAE 90.1-2010Whole BuildingMulti-Family | ASHRAE 90.1-2010 | Whole Building | Multi-Family | 0.6
ASHRAE 90.1-2010Whole BuildingMuseum | ASHRAE 90.1-2010 | Whole Building | Museum | 1.06
ASHRAE 90.1-2010Whole BuildingOffice | ASHRAE 90.1-2010 | Whole Building | Office | 0.9
ASHRAE 90.1-2010Whole BuildingParking Garage | ASHRAE 90.1-2010 | Whole Building | Parking Garage | 0.25
ASHRAE 90.1-2010Whole BuildingPenitentiary | ASHRAE 90.1-2010 | Whole Building | Penitentiary | 0.97
ASHRAE 90.1-2010Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2010 | Whole Building | Performing Arts Theater | 1.39
ASHRAE 90.1-2010Whole BuildingPolice Station | ASHRAE 90.1-2010 | Whole Building | Police Station | 0.96
ASHRAE 90.1-2010Whole BuildingPost Office | ASHRAE 90.1-2010 | Whole Building | Post Office | 0.87
ASHRAE 90.1-2010Whole BuildingReligious Building | ASHRAE 90.1-2010 | Whole Building | Religious Building | 1.05
ASHRAE 90.1-2010Whole BuildingRetail | ASHRAE 90.1-2010 | Whole Building | Retail | 1.4
ASHRAE 90.1-2010Whole BuildingSchool/University | ASHRAE 90.1-2010 | Whole Building | School/University | 0.99
ASHRAE 90.1-2010Whole BuildingSports Arena | ASHRAE 90.1-2010 | Whole Building | Sports Arena | 0.78
ASHRAE 90.1-2010Whole BuildingTown Hall | ASHRAE 90.1-2010 | Whole Building | Town Hall | 0.92
ASHRAE 90.1-2010Whole BuildingTransportation | ASHRAE 90.1-2010 | Whole Building | Transportation | 0.77
ASHRAE 90.1-2010Whole BuildingWarehouse | ASHRAE 90.1-2010 | Whole Building | Warehouse | 0.66
ASHRAE 90.1-2010Whole BuildingWorkshop | ASHRAE 90.1-2010 | Whole Building | Workshop | 1.2
ASHRAE 90.1-2010Office-EnclosedGeneral | ASHRAE 90.1-2010 | Office-Enclosed | General | 1.11
ASHRAE 90.1-2010Office-Open PlanGeneral | ASHRAE 90.1-2010 | Office-Open Plan | General | 0.98
ASHRAE 90.1-2010Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2010 | Conference/Meeting/Multipurpose | General | 1.23
ASHRAE 90.1-2010Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2010 | Classroom/Lecture/Training | General | 1.24
ASHRAE 90.1-2010Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2010 | Classroom/Lecture/Training | For Penitentiary | 1.34
ASHRAE 90.1-2010LobbyGeneral | ASHRAE 90.1-2010 | Lobby | General | 0.9
ASHRAE 90.1-2010LobbyFor Elevator | ASHRAE 90.1-2010 | Lobby | For Elevator | 0.64
ASHRAE 90.1-2010LobbyFor Hotel | ASHRAE 90.1-2010 | Lobby | For Hotel | 1.06
ASHRAE 90.1-2010LobbyFor Performing Arts Theater | ASHRAE 90.1-2010 | Lobby | For Performing Arts Theater | 2
ASHRAE 90.1-2010LobbyFor Motion Picture Theater | ASHRAE 90.1-2010 | Lobby | For Motion Picture Theater | 0.52
ASHRAE 90.1-2010Audience/Seating AreaFor Auditorium | ASHRAE 90.1-2010 | Audience/Seating Area | For Auditorium | 0.79
ASHRAE 90.1-2010Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2010 | Audience/Seating Area | For Gymnasium | 0.43
ASHRAE 90.1-2010Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-2010 | Audience/Seating Area | For Exercise Center
ASHRAE 90.1-2010Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2010 | Audience/Seating Area | For Convention Center | 0.82
ASHRAE 90.1-2010Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2010 | Audience/Seating Area | For Penitentiary | 0.43
ASHRAE 90.1-2010Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2010 | Audience/Seating Area | For Religious Buildings | 1.53
ASHRAE 90.1-2010Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-2010 | Audience/Seating Area | For Sports Arena | 0.43
ASHRAE 90.1-2010Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-2010 | Audience/Seating Area | For Performing Arts Theater | 2.43
ASHRAE 90.1-2010Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2010 | Audience/Seating Area | For Motion Picture Theater | 1.14
ASHRAE 90.1-2010Audience/Seating AreaFor Transportation | ASHRAE 90.1-2010 | Audience/Seating Area | For Transportation | 0.54
ASHRAE 90.1-2010AtriumFirst Forty Feet in Height | ASHRAE 90.1-2010 | Atrium | First Forty Feet in Height | 0.03
ASHRAE 90.1-2010AtriumHeight Above Forty Feet | ASHRAE 90.1-2010 | Atrium | Height Above Forty Feet | 0.02
ASHRAE 90.1-2010Lounge/RecreationGeneral | ASHRAE 90.1-2010 | Lounge/Recreation | General | 0.73
ASHRAE 90.1-2010Lounge/RecreationFor Hospital | ASHRAE 90.1-2010 | Lounge/Recreation | For Hospital | 1.07
ASHRAE 90.1-2010Dining AreaGeneral | ASHRAE 90.1-2010 | Dining Area | General | 0.65
ASHRAE 90.1-2010Dining AreaFor Penitentiary | ASHRAE 90.1-2010 | Dining Area | For Penitentiary | 1.07
ASHRAE 90.1-2010Dining AreaFor Hotel | ASHRAE 90.1-2010 | Dining Area | For Hotel | 0.82
ASHRAE 90.1-2010Dining AreaFor Highway Lodging | ASHRAE 90.1-2010 | Dining Area | For Highway Lodging | 0.88
ASHRAE 90.1-2010Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2010 | Dining Area | For Bar Lounge/Leisure Dining | 1.31
ASHRAE 90.1-2010Dining AreaFor Family Dining | ASHRAE 90.1-2010 | Dining Area | For Family Dining | 0.89
ASHRAE 90.1-2010Food PreparationGeneral | ASHRAE 90.1-2010 | Food Preparation | General | 0.99
ASHRAE 90.1-2010LaboratoryFor Classrooms | ASHRAE 90.1-2010 | Laboratory | For Classrooms | 1.28
ASHRAE 90.1-2010LaboratoryFor Medical/Industrial/Research | ASHRAE 90.1-2010 | Laboratory | For Medical/Industrial/Research | 1.81
ASHRAE 90.1-2010RestroomsGeneral | ASHRAE 90.1-2010 | Restrooms | General | 0.98
ASHRAE 90.1-2010Dressing/Fitting RoomFor Performing Arts Theater | ASHRAE 90.1-2010 | Dressing/Fitting Room | For Performing Arts Theater | 0.4
ASHRAE 90.1-2010Dressing/Fitting RoomFor Retail | ASHRAE 90.1-2010 | Dressing/Fitting Room | For Retail | 0.87
ASHRAE 90.1-2010Locker RoomGeneral | ASHRAE 90.1-2010 | Locker Room | General | 0.75
ASHRAE 90.1-2010Corridor/TransitionGeneral | ASHRAE 90.1-2010 | Corridor/Transition | General | 0.66
ASHRAE 90.1-2010Corridor/TransitionFor Hospital | ASHRAE 90.1-2010 | Corridor/Transition | For Hospital | 0.89
ASHRAE 90.1-2010Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-2010 | Corridor/Transition | For Manufacturing Facility | 0.41
ASHRAE 90.1-2010StairwayGeneral | ASHRAE 90.1-2010 | Stairway | General | 0.69
ASHRAE 90.1-2010StorageGeneral | ASHRAE 90.1-2010 | Storage | General | 0.63
ASHRAE 90.1-2010Gymnasium/Fitness CenterPlaying Area | ASHRAE 90.1-2010 | Gymnasium/Fitness Center | Playing Area | 1.2
ASHRAE 90.1-2010Gymnasium/Fitness CenterFitness Area | ASHRAE 90.1-2010 | Gymnasium/Fitness Center | Fitness Area | 0.72
ASHRAE 90.1-2010Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-2010 | Courthouse/Police Station/Penitentiary | Courtroom | 1.72
ASHRAE 90.1-2010Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-2010 | Courthouse/Police Station/Penitentiary | Confinement Cells | 1.1
ASHRAE 90.1-2010Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-2010 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.17
ASHRAE 90.1-2010Fire StationEngine Room | ASHRAE 90.1-2010 | Fire Station | Engine Room | 0.56
ASHRAE 90.1-2010Fire StationSleeping Quarters | ASHRAE 90.1-2010 | Fire Station | Sleeping Quarters | 0.25
ASHRAE 90.1-2010Post OfficeSorting Area | ASHRAE 90.1-2010 | Post Office | Sorting Area | 0.94
ASHRAE 90.1-2010Convention CenterExhibit Space | ASHRAE 90.1-2010 | Convention Center | Exhibit Space | 1.45
ASHRAE 90.1-2010LibraryCard File and Cataloging | ASHRAE 90.1-2010 | Library | Card File and Cataloging | 0.72
ASHRAE 90.1-2010LibraryStacks | ASHRAE 90.1-2010 | Library | Stacks | 1.71
ASHRAE 90.1-2010LibraryReading Area | ASHRAE 90.1-2010 | Library | Reading Area | 0.93
ASHRAE 90.1-2010HospitalEmergency | ASHRAE 90.1-2010 | Hospital | Emergency | 2.26
ASHRAE 90.1-2010HospitalRecovery | ASHRAE 90.1-2010 | Hospital | Recovery | 1.15
ASHRAE 90.1-2010HospitalNurse Station | ASHRAE 90.1-2010 | Hospital | Nurse Station | 0.87
ASHRAE 90.1-2010HospitalExam/Treatment | ASHRAE 90.1-2010 | Hospital | Exam/Treatment | 1.66
ASHRAE 90.1-2010HospitalPharmacy | ASHRAE 90.1-2010 | Hospital | Pharmacy | 1.14
ASHRAE 90.1-2010HospitalPatient Room | ASHRAE 90.1-2010 | Hospital | Patient Room | 0.62
ASHRAE 90.1-2010HospitalOperating Room | ASHRAE 90.1-2010 | Hospital | Operating Room | 1.89
ASHRAE 90.1-2010HospitalNursery | ASHRAE 90.1-2010 | Hospital | Nursery | 0.88
ASHRAE 90.1-2010HospitalMedical Supply | ASHRAE 90.1-2010 | Hospital | Medical Supply | 1.27
ASHRAE 90.1-2010HospitalPhysical Therapy | ASHRAE 90.1-2010 | Hospital | Physical Therapy | 0.91
ASHRAE 90.1-2010HospitalRadiology/Imaging | ASHRAE 90.1-2010 | Hospital | Radiology/Imaging | 1.32
ASHRAE 90.1-2010HospitalLaundry-Washing | ASHRAE 90.1-2010 | Hospital | Laundry-Washing | 0.6
ASHRAE 90.1-2010AutomotiveService/Repair | ASHRAE 90.1-2010 | Automotive | Service/Repair | 0.67
ASHRAE 90.1-2010ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2010 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.19
ASHRAE 90.1-2010ManufacturingHigh Bay (25-50 ft Floor to Ceiling Height) | ASHRAE 90.1-2010 | Manufacturing | High Bay (25-50 ft Floor to Ceiling Height) | 1.23
ASHRAE 90.1-2010ManufacturingExtra High Bay (>50 ft Floor to Ceiling Height) | ASHRAE 90.1-2010 | Manufacturing | Extra High Bay (>50 ft Floor to Ceiling Height) | 1.05
ASHRAE 90.1-2010ManufacturingDetailed Manufacturing | ASHRAE 90.1-2010 | Manufacturing | Detailed Manufacturing | 1.29
ASHRAE 90.1-2010ManufacturingEquipment Room | ASHRAE 90.1-2010 | Manufacturing | Equipment Room | 0.95
ASHRAE 90.1-2010Guest RoomFor Highway Lodging | ASHRAE 90.1-2010 | Guest Room | For Highway Lodging | 0.75
ASHRAE 90.1-2010Guest RoomFor Hotel | ASHRAE 90.1-2010 | Guest Room | For Hotel | 1.11
ASHRAE 90.1-2010DormitoryLiving Quarters | ASHRAE 90.1-2010 | Dormitory | Living Quarters | 0.38
ASHRAE 90.1-2010MuseumGeneral Exhibition | ASHRAE 90.1-2010 | Museum | General Exhibition | 1.05
ASHRAE 90.1-2010MuseumRestoration | ASHRAE 90.1-2010 | Museum | Restoration | 1.02
ASHRAE 90.1-2010Electrical/MechanicalGeneral | ASHRAE 90.1-2010 | Electrical/Mechanical | General | 0.95
ASHRAE 90.1-2010WorkshopGeneral | ASHRAE 90.1-2010 | Workshop | General | 1.59
ASHRAE 90.1-2010Bank/OfficeBanking Activity Area | ASHRAE 90.1-2010 | Bank/Office | Banking Activity Area | 1.38
ASHRAE 90.1-2010Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2010 | Religious Buildings | Worship Pulpit, Choir | 1.53
ASHRAE 90.1-2010Religious BuildingsFellowship Hall | ASHRAE 90.1-2010 | Religious Buildings | Fellowship Hall | 0.64
ASHRAE 90.1-2010Sales AreaFor Retail | ASHRAE 90.1-2010 | Sales Area | For Retail | 1.68
ASHRAE 90.1-2010Sales AreaGeneral | ASHRAE 90.1-2010 | Sales Area | General | 1.68
ASHRAE 90.1-2010RetailMall Concourse | ASHRAE 90.1-2010 | Retail | Mall Concourse | 1.1
ASHRAE 90.1-2010Sports ArenaRing Sports Arena | ASHRAE 90.1-2010 | Sports Arena | Ring Sports Arena | 2.68
ASHRAE 90.1-2010Sports ArenaCourt Sports Arena - Class 4 | ASHRAE 90.1-2010 | Sports Arena | Court Sports Arena - Class 4 | 0.72
ASHRAE 90.1-2010Sports ArenaCourt Sports Arena - Class 3 | ASHRAE 90.1-2010 | Sports Arena | Court Sports Arena - Class 3 | 1.2
ASHRAE 90.1-2010Sports ArenaCourt Sports Arena - Class 2 | ASHRAE 90.1-2010 | Sports Arena | Court Sports Arena - Class 2 | 1.92
ASHRAE 90.1-2010Sports ArenaCourt Sports Arena - Class 1 | ASHRAE 90.1-2010 | Sports Arena | Court Sports Arena - Class 1 | 3.01
ASHRAE 90.1-2010WarehouseFine Material Storage | ASHRAE 90.1-2010 | Warehouse | Fine Material Storage | 0.95
ASHRAE 90.1-2010WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2010 | Warehouse | Medium/Bulky Material Storage | 0.58
ASHRAE 90.1-2010Parking GarageGarage Area | ASHRAE 90.1-2010 | Parking Garage | Garage Area | 0.19
ASHRAE 90.1-2010TransportationAirport-Concourse | ASHRAE 90.1-2010 | Transportation | Airport-Concourse | 0.36
ASHRAE 90.1-2010TransportationAir/Train/Bus-Baggage Area | ASHRAE 90.1-2010 | Transportation | Air/Train/Bus-Baggage Area | 0.76
ASHRAE 90.1-2010TransportationTerminal-Ticket Counter | ASHRAE 90.1-2010 | Transportation | Terminal-Ticket Counter | 1.08

## Construction Sets
A Construction Set lists the typical constructions for each surface type in a building for a given building type and climate zone.
|  |  |  | Exterior Surfaces |  |  | Interior Surfaces |  |  | Ground Contact Surfaces |  |  | Exterior Sub Surfaces | [7 empty] | Interior Sub Surfaces |  |  | Misc Surfaces
Template | Building Type | Space Type | Climate Zone Set | Exterior Walls | Exterior Floors | Exterior Roofs | Interior Walls | Interior Floors | Interior Ceilings | Ground Contact Walls | Ground Contact Floors | Ground Contact Ceilings | Exterior Fixed Windows | Exterior Operable Windows | Exterior Doors | Exterior Glass Doors | Exterior Overhead Doors | Exterior Skylights | Tubular Daylight Domes | Tubular Daylight Diffusers | Interior Fixed Windows | Interior Operable Windows | Interior Doors | Space Shading | Building Shading | Site Shading | Interior Partitions
189.1-2009 | FullServiceRestaurant |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | FullServiceRestaurant |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | FullServiceRestaurant |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | FullServiceRestaurant |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | FullServiceRestaurant |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | FullServiceRestaurant |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Hospital |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Hospital |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Hospital |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Hospital |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Hospital |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Hospital |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Hospital |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 7 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | LargeHotel |  | ClimateZone 8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | MidriseApartment |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | MidriseApartment |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | MidriseApartment |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | MidriseApartment |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | MidriseApartment |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | MidriseApartment |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Office |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Office |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Office |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Office |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Office |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Office |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Office |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Outpatient |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Outpatient |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Outpatient |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Outpatient |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Outpatient |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Outpatient |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | PrimarySchool |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | PrimarySchool |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | PrimarySchool |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | PrimarySchool |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | PrimarySchool |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | PrimarySchool |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | QuickServiceRestaurant |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | QuickServiceRestaurant |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | QuickServiceRestaurant |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | QuickServiceRestaurant |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | QuickServiceRestaurant |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | QuickServiceRestaurant |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 6-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | QuickServiceRestaurant |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 6-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Retail |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Retail |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Retail |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Retail |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Retail |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Retail |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Retail |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SecondarySchool |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SecondarySchool |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SecondarySchool |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SecondarySchool |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SecondarySchool |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SecondarySchool |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SmallHotel |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SmallHotel |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SmallHotel |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SmallHotel |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SmallHotel |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SmallHotel |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | StripMall |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | StripMall |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | StripMall |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | StripMall |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | StripMall |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | StripMall |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SuperMarket |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SuperMarket |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SuperMarket |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SuperMarket |  | ClimateZone 4 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SuperMarket |  | ClimateZone 5 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SuperMarket |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | SuperMarket |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Warehouse |  | ClimateZone 1 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 1-3 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Warehouse |  | ClimateZone 2 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 1-3 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Warehouse |  | ClimateZone 3 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 1-3 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Warehouse |  | ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 4-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 2-5 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Warehouse |  | ClimateZone 6 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 4-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 | Warehouse |  | ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWall Metal ClimateZone 4-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 7-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
189.1-2009 |  | Attic | ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | ASHRAE 189.1-2009 AtticFloor ClimateZone 1-8 | AtticRoof ClimateZone 1-8 | ASHRAE 189.1-2009 AtticFloor ClimateZone 1-8 | ASHRAE 189.1-2009 AtticFloor ClimateZone 1-8 | ASHRAE 189.1-2009 AtticFloor ClimateZone 1-8
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Hospital |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Office |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Outpatient |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 1 | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 2a | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 2b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 3a | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 3b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 3b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 3c | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 4a | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 4b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 4c | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 5a | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 5b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 6a | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 6b | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 7 | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ClimateZone 8 | CBECS 1980-2004 ExtWall WoodFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Retail |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 1 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 2a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 2b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 3a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 3b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 3c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 4a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 4b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 4c | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 5a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 6a | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 6b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 7 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | StripMall |  | ClimateZone 8 | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Metal ClimateZone 1 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Metal ClimateZone 2a | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Metal ClimateZone 2b | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Metal ClimateZone 3a | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Metal ClimateZone 3b LAS | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 3b LAS | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | CBECS 1980-2004 ExtWindow ClimateZone 3b LAS | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Metal ClimateZone 3b LAX | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Metal ClimateZone 3c | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3c | CBECS 1980-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Metal ClimateZone 4a | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Metal ClimateZone 4b | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Metal ClimateZone 4c | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Metal ClimateZone 5 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 5b | CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Metal ClimateZone 6a | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Metal ClimateZone 6b | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Metal ClimateZone 7 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | Warehouse |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Metal ClimateZone 8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof Metal ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | CBECS 1980-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 |  | Attic | ClimateZone 1 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 1 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 1 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 1 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 1
DOE Ref 1980-2004 |  | Attic | ClimateZone 2a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2a
DOE Ref 1980-2004 |  | Attic | ClimateZone 2b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2b
DOE Ref 1980-2004 |  | Attic | ClimateZone 3a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3a
DOE Ref 1980-2004 |  | Attic | ClimateZone 3b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAS | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAS | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAS | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAS
DOE Ref 1980-2004 |  | Attic | ClimateZone 3b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAX | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAX | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAX | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAX
DOE Ref 1980-2004 |  | Attic | ClimateZone 4a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4a
DOE Ref 1980-2004 |  | Attic | ClimateZone 4b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4b
DOE Ref 1980-2004 |  | Attic | ClimateZone 4c | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4c | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4c | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4c | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4c
DOE Ref 1980-2004 |  | Attic | ClimateZone 5a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a
DOE Ref 1980-2004 |  | Attic | ClimateZone 5b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5b
DOE Ref 1980-2004 |  | Attic | ClimateZone 6a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6a | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6a | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6a
DOE Ref 1980-2004 |  | Attic | ClimateZone 6b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6b | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6b | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6b
DOE Ref 1980-2004 |  | Attic | ClimateZone 7 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 7 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 7 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 7 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 7
DOE Ref 1980-2004 |  | Attic | ClimateZone 8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 8 | AtticRoof ClimateZone 1-8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 8 | CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 8
90.1-2004 | FullServiceRestaurant |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | FullServiceRestaurant |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | FullServiceRestaurant |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | FullServiceRestaurant |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | FullServiceRestaurant |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | FullServiceRestaurant |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | FullServiceRestaurant |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Hospital |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Hospital |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Hospital |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Hospital |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Hospital |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Hospital |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Hospital |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Hospital |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resH 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resH 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 5-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 5-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | LargeHotel |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | MidriseApartment |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | MidriseApartment |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resA 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resA 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | MidriseApartment |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | MidriseApartment |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 4-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | MidriseApartment |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 4-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | MidriseApartment |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | MidriseApartment |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Office |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Office |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Office |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Office |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Office |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Office |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Office |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Office |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Outpatient |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Outpatient |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Outpatient |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Outpatient |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Outpatient |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Outpatient |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Outpatient |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | PrimarySchool |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | PrimarySchool |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | PrimarySchool |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | PrimarySchool |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | PrimarySchool |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | PrimarySchool |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | PrimarySchool |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | QuickServiceRestaurant |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | QuickServiceRestaurant |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | QuickServiceRestaurant |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | QuickServiceRestaurant |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | QuickServiceRestaurant |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | QuickServiceRestaurant |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | QuickServiceRestaurant |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Retail |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Retail |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Retail |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Retail |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Retail |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Retail |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Retail |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Retail |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SecondarySchool |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SecondarySchool |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SecondarySchool |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SecondarySchool |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SecondarySchool |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SecondarySchool |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SecondarySchool |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SmallHotel |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SmallHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SmallHotel |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SmallHotel |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 4-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SmallHotel |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 4-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SmallHotel |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SmallHotel |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | StripMall |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | StripMall |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | StripMall |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | StripMall |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | StripMall |  | ClimateZone 5-6 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | StripMall |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | StripMall |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SuperMarket |  | ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SuperMarket |  | ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SuperMarket |  | ClimateZone 3c | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SuperMarket |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SuperMarket |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SuperMarket |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SuperMarket |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | SuperMarket |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Warehouse |  | ClimateZone 1 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 1 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Warehouse |  | ClimateZone 2 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 2-3 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 2 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Warehouse |  | ClimateZone 3 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 2-3 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 3-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Warehouse |  | ClimateZone 4 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 4 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 3-4 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Warehouse |  | ClimateZone 5 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 5 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Warehouse |  | ClimateZone 6 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 6-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 5-6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Warehouse |  | ClimateZone 7 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 6-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 | Warehouse |  | ClimateZone 8 | ASHRAE 90.1-2004 ExtWall Metal ClimateZone 6-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2004 |  | Attic | ClimateZone 1-5 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 1-5 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 1-5 | ASHRAE 90.1-2004 AtticFloor ClimateZone 1-5 | ASHRAE 90.1-2004 AtticFloor ClimateZone 1-5
90.1-2004 |  | Attic | ClimateZone 6-8 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 6-8 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 6-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 6-8 | ASHRAE 90.1-2004 AtticFloor ClimateZone 6-8
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Hospital |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Office |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Outpatient |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Retail |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 1-3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | StripMall |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Mass ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 3a | CBECS Before-1980 ExtWall Mass ClimateZone 3a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 3b | CBECS Before-1980 ExtWall Mass ClimateZone 3b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 3c | CBECS Before-1980 ExtWall Mass ClimateZone 3c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 4a | CBECS Before-1980 ExtWall Mass ClimateZone 4a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 4b | CBECS Before-1980 ExtWall Mass ClimateZone 4b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 4c | CBECS Before-1980 ExtWall Mass ClimateZone 4c | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 5a | CBECS Before-1980 ExtWall Mass ClimateZone 5a | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 5b | CBECS Before-1980 ExtWall Mass ClimateZone 5b | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 6 | CBECS Before-1980 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 7 | CBECS Before-1980 ExtWall Mass ClimateZone 7 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | ClimateZone 8 | CBECS Before-1980 ExtWall Mass ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall Metal ClimateZone 1-2 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 3a | CBECS Before-1980 ExtWall Metal ClimateZone 3a | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 3b | CBECS Before-1980 ExtWall Metal ClimateZone 3b | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 3c | CBECS Before-1980 ExtWall Metal ClimateZone 3c | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 4a | CBECS Before-1980 ExtWall Metal ClimateZone 4a | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 4b | CBECS Before-1980 ExtWall Metal ClimateZone 4b | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 4c | CBECS Before-1980 ExtWall Metal ClimateZone 4c | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 5a | CBECS Before-1980 ExtWall Metal ClimateZone 5a | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 5b | CBECS Before-1980 ExtWall Metal ClimateZone 5b | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 6 | CBECS Before-1980 ExtWall Metal ClimateZone 6 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 7 | CBECS Before-1980 ExtWall Metal ClimateZone 7 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | Warehouse |  | ClimateZone 8 | CBECS Before-1980 ExtWall Metal ClimateZone 8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 |  | Attic | ClimateZone 1-3 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 1-3 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 1-3 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 1-3 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 1-3
DOE Ref Pre-1980 |  | Attic | ClimateZone 4a | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4a | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4a | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4a | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4a
DOE Ref Pre-1980 |  | Attic | ClimateZone 4b | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4b | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4b | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4b | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4b
DOE Ref Pre-1980 |  | Attic | ClimateZone 4c | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4c | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4c | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4c | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4c
DOE Ref Pre-1980 |  | Attic | ClimateZone 5a | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a
DOE Ref Pre-1980 |  | Attic | ClimateZone 5b | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5b | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5b | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5b | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5b
DOE Ref Pre-1980 |  | Attic | ClimateZone 6 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 6 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 6 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 6 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 6
DOE Ref Pre-1980 |  | Attic | ClimateZone 7 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 7 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 7 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 7 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 7
DOE Ref Pre-1980 |  | Attic | ClimateZone 8 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 8 | AtticRoof ClimateZone 1-8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 8 | CBECS Before-1980 ExtRoof AtticFloor ClimateZone 8
90.1-2007 | FullServiceRestaurant |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | FullServiceRestaurant |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | FullServiceRestaurant |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | FullServiceRestaurant |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | FullServiceRestaurant |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | FullServiceRestaurant |  | ClimateZone 5-6 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | FullServiceRestaurant |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | FullServiceRestaurant |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Hospital |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 6-7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 6-7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | LargeHotel |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 5-6 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | MidriseApartment |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Office |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 5-6 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Outpatient |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 5-6 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | PrimarySchool |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 6-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 6-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | QuickServiceRestaurant |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Retail |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 5-6 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SecondarySchool |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 5-6 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SmallHotel |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 5-6 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | StripMall |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 3a-3b | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 3c | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | SuperMarket |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 1 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 1 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 1 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 2 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 2-3 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 2 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 3 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 2-3 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 3-7 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 4 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 4 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 3-7 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 5 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 5 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 3-7 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 6 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 6-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 3-7 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 6-8 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 7 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 6-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 3-7 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 6-8 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 | Warehouse |  | ClimateZone 8 | ASHRAE 90.1-2007 ExtWall Metal ClimateZone 6-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 8 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 6-8 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2007 |  | Attic | ClimateZone 1 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 1 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 1 | ASHRAE 90.1-2007 AtticFloor ClimateZone 1 | ASHRAE 90.1-2007 AtticFloor ClimateZone 1
90.1-2007 |  | Attic | ClimateZone 2-7 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 2-7 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 2-7 | ASHRAE 90.1-2007 AtticFloor ClimateZone 2-7 | ASHRAE 90.1-2007 AtticFloor ClimateZone 2-7
90.1-2007 |  | Attic | ClimateZone 8 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 8 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 8 | ASHRAE 90.1-2007 AtticFloor ClimateZone 8
90.1-2010 | FullServiceRestaurant |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | FullServiceRestaurant |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | FullServiceRestaurant |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | FullServiceRestaurant |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | FullServiceRestaurant |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | FullServiceRestaurant |  | ClimateZone 5-6 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | FullServiceRestaurant |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | FullServiceRestaurant |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Hospital |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 6-7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 6-7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | LargeHotel |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 5-6 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | MidriseApartment |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Office |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 5-6 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Outpatient |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ExtSlabCarpet 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 5-6 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | PrimarySchool |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 6-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 6-7 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | QuickServiceRestaurant |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Retail |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 5-6 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SecondarySchool |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 1 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 5-6 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallHotel |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 5-6 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | StripMall |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 1 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 2 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 4 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 5 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 6 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SuperMarket |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ExtSlab 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 1 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 2-4 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 3 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 2-4 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 2-4 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 5 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 6-7 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 6-8 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 6-7 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 6-8 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | Warehouse |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 8 Semiheated | Interior Wall | Interior Floor | Interior Ceiling | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ExtSlab 8in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 6-8 Semiheated | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 |  | Attic | ClimateZone 1 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 1 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 1 | ASHRAE 90.1-2010 AtticFloor ClimateZone 1 | ASHRAE 90.1-2010 AtticFloor ClimateZone 1
90.1-2010 |  | Attic | ClimateZone 2-7 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 2-7 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 2-7 | ASHRAE 90.1-2010 AtticFloor ClimateZone 2-7 | ASHRAE 90.1-2010 AtticFloor ClimateZone 2-7
90.1-2010 |  | Attic | ClimateZone 8 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 8 | AtticRoof ClimateZone 1-8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 8 | ASHRAE 90.1-2010 AtticFloor ClimateZone 8
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 1 | CBECS 1980-2004 ExtWall Mass ClimateZone 1 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 2a | CBECS 1980-2004 ExtWall Mass ClimateZone 2a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 2b | CBECS 1980-2004 ExtWall Mass ClimateZone 2b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | CBECS 1980-2004 ExtWindow ClimateZone 1-2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 3a | CBECS 1980-2004 ExtWall Mass ClimateZone 3a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3a | CBECS 1980-2004 ExtWindow ClimateZone 3a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 3b | CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | CBECS 1980-2004 ExtWindow ClimateZone 3b LAX | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 3c | CBECS 1980-2004 ExtWall Mass ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 4a | CBECS 1980-2004 ExtWall Mass ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4a | CBECS 1980-2004 ExtWindow ClimateZone 4a | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 4b | CBECS 1980-2004 ExtWall Mass ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4b | CBECS 1980-2004 ExtWindow ClimateZone 4b | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 4c | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 4c | CBECS 1980-2004 ExtWindow ClimateZone 4c | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 5a | CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 5b | CBECS 1980-2004 ExtWall Mass ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 5 | CBECS 1980-2004 ExtWindow ClimateZone 5 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 6a | CBECS 1980-2004 ExtWall Mass ClimateZone 6a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 6 | CBECS 1980-2004 ExtWindow ClimateZone 6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 6b | CBECS 1980-2004 ExtWall Mass ClimateZone 6b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 7 | CBECS 1980-2004 ExtWall Mass ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone 7 | CBECS 1980-2004 ExtWindow ClimateZone 7 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | ClimateZone 8 | CBECS 1980-2004 ExtWall Mass ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 1-2 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 3a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 3b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 3c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 4a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 4b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 4c | CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 4c | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | CBECS Before-1980 ExtWindow ClimateZone 1-4 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 5a | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5a | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 5b | CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 5b | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 6 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 6 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 7 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 7 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | ClimateZone 8 | CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtRoof IEAD ClimateZone 8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | CBECS Before-1980 ExtWindow ClimateZone 5-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 1 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 2 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 3a-3b | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 3c | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 4 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 5 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 5 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 6 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 6-7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 7 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 6-7 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition
90.1-2010 | SmallOffice |  | ClimateZone 8 | ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | Interior Wall | Interior Floor | Interior Ceiling | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ExtSlabCarpet 4in ClimateZone 1-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | Exterior Door |  |  |  | Interior Window | Interior Window | Interior Window | Interior Window | Interior Door |  |  |  | Interior Partition

## Constructions
A Construction is a particular combination of materials that represents a typical building envelope cross section. Constructions are referenced on the Construction Sets tab.
[5 empty] | Outside |  |  |  |  | Inside
Name | Construction Standard | Climate Zone Set | Intended Surface Type | Standards Construction Type | Material 1 | Material 2 | Material 3 | Material 4 | Material 5 | Material 6
Interior Window |  | ClimateZone 1-8 | InteriorWindow |  | Clear 3mm
Interior Wall |  | ClimateZone 1-8 | InteriorWall |  | G01a 19mm gypsum board | F04 Wall air space resistance | G01a 19mm gypsum board
Interior Partition |  | ClimateZone 1-8 | InteriorPartition |  | G05 25mm wood
Interior Floor |  | ClimateZone 1-8 | InteriorFloor |  | F16 Acoustic tile | F05 Ceiling air space resistance | M11 100mm lightweight concrete
Interior Door |  | ClimateZone 1-8 | InteriorDoor |  | G05 25mm wood
Interior Ceiling |  | ClimateZone 1-8 | InteriorCeiling |  | M11 100mm lightweight concrete | F05 Ceiling air space resistance | F16 Acoustic tile
ExtSlabCarpet 8in ClimateZone 1-8 |  | ClimateZone 1-8 | ExteriorFloor |  | MAT-CC05 8 HW CONCRETE | CP02 CARPET PAD
ExtSlabCarpet 4in ClimateZone 1-8 |  | ClimateZone 1-8 | ExteriorFloor |  | MAT-CC05 4 HW CONCRETE | CP02 CARPET PAD
ExtSlab 8in ClimateZone 1-8 |  | ClimateZone 1-8 | ExteriorFloor |  | MAT-CC05 8 HW CONCRETE
ExtSlab 4in ClimateZone 1-8 |  | ClimateZone 1-8 | ExteriorFloor |  | MAT-CC05 4 HW CONCRETE
Exterior Door |  | ClimateZone 1-8 | ExteriorDoor |  | F08 Metal surface | I01 25mm insulation board
CBECS Before-1980 ExtWindow ClimateZone alt-lrgoff hosp 1-8 |  | ClimateZone 1-8 | ExteriorWindow |  | Fixed Window 5.84/0.54/0.38
CBECS Before-1980 ExtWindow ClimateZone 5-8 |  | ClimateZone 5-8 | ExteriorWindow |  | Fixed Window 3.53/0.41/0.32
CBECS Before-1980 ExtWindow ClimateZone 1-4 |  | ClimateZone 1-4 | ExteriorWindow |  | Fixed Window 5.84/0.54/0.38
CBECS Before-1980 ExtWall SteelFrame ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.41 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.30 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 6 |  | ClimateZone 6 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.22 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 5b |  | ClimateZone 5b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.09 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 5a |  | ClimateZone 5a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.13 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.01 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.96 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.99 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.79 | 1/2IN Gypsum
CBECS Before-1980 ExtWall SteelFrame ClimateZone 1-3b |  | ClimateZone 1-3b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.77 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.22 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.10 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 6 |  | ClimateZone 6 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.02 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 5b |  | ClimateZone 5b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.90 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 5a |  | ClimateZone 5a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.94 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.81 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.77 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.80 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.59 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 3b |  | ClimateZone 3b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.57 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.59 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Metal ClimateZone 1-2 |  | ClimateZone 1-2 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.57 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.41 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.30 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 6 |  | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.22 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 5b |  | ClimateZone 5b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.09 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 5a |  | ClimateZone 5a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.13 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.01 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.96 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.99 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.79 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 3b |  | ClimateZone 3b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.77 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.78 | 1/2IN Gypsum
CBECS Before-1980 ExtWall Mass ClimateZone 1-2 |  | ClimateZone 1-2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.77 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof IEAD ClimateZone 8 |  | ClimateZone 8 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.99 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 7 1 |  | ClimateZone 7 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.93 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 7 |  | ClimateZone 7 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.93 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 6 |  | ClimateZone 6 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.99 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 5b |  | ClimateZone 5b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.37 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 5a |  | ClimateZone 5a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.50 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 4c |  | ClimateZone 4c | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.07 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 4b |  | ClimateZone 4b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-1.98 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 4a |  | ClimateZone 4a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.04 | Metal Decking
CBECS Before-1980 ExtRoof IEAD ClimateZone 1-3 |  | ClimateZone 1-3 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-1.76 | Metal Decking
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 8 |  | ClimateZone 8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.99 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 7 |  | ClimateZone 7 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Res Insulation-2.93 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 6 |  | ClimateZone 6 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.99 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5b |  | ClimateZone 5b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Res Insulation-2.37 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 5a |  | ClimateZone 5a | AtticFloor | WoodFramed | 1/2IN Gypsum | IEAD NonRes Roof Insulation-2.50 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4c |  | ClimateZone 4c | AtticFloor | WoodFramed | 1/2IN Gypsum | IEAD NonRes Roof Insulation-2.07 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4b |  | ClimateZone 4b | AtticFloor | WoodFramed | 1/2IN Gypsum | IEAD NonRes Roof Insulation-1.98 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 4a |  | ClimateZone 4a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Res Insulation-2.05 | 1/2IN Gypsum
CBECS Before-1980 ExtRoof AtticFloor ClimateZone 1-3 |  | ClimateZone 1-3 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-1.76 | 1/2IN Gypsum
CBECS 1980-2004 ExtWindow ClimateZone alt-lrgoff hosp 1-8 |  | ClimateZone 1-8 | ExteriorWindow |  | Fixed Window 5.84/0.25/0.11
CBECS 1980-2004 ExtWindow ClimateZone 8 |  | ClimateZone 8 | ExteriorWindow |  | Fixed Window 2.96/0.62/0.54
CBECS 1980-2004 ExtWindow ClimateZone 7 |  | ClimateZone 7 | ExteriorWindow |  | Fixed Window 2.96/0.49/0.41
CBECS 1980-2004 ExtWindow ClimateZone 6 |  | ClimateZone 6 | ExteriorWindow |  | Fixed Window 2.96/0.39/0.31
CBECS 1980-2004 ExtWindow ClimateZone 5 |  | ClimateZone 5 | ExteriorWindow |  | Fixed Window 3.35/0.39/0.31
CBECS 1980-2004 ExtWindow ClimateZone 4c |  | ClimateZone 4c | ExteriorWindow |  | Fixed Window 4.09/0.39/0.25
CBECS 1980-2004 ExtWindow ClimateZone 4b |  | ClimateZone 4b | ExteriorWindow |  | Fixed Window 4.09/0.36/0.23
CBECS 1980-2004 ExtWindow ClimateZone 4a |  | ClimateZone 4a | ExteriorWindow |  | Fixed Window 3.35/0.36/0.27
CBECS 1980-2004 ExtWindow ClimateZone 3c |  | ClimateZone 3c | ExteriorWindow |  | Fixed Window 4.09/0.39/0.25
CBECS 1980-2004 ExtWindow ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorWindow |  | Fixed Window 5.84/0.44/0.27
CBECS 1980-2004 ExtWindow ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorWindow |  | Fixed Window 5.84/0.25/0.11
CBECS 1980-2004 ExtWindow ClimateZone 3a |  | ClimateZone 3a | ExteriorWindow |  | Fixed Window 4.09/0.26/0.13
CBECS 1980-2004 ExtWindow ClimateZone 1-2 |  | ClimateZone 1-2 | ExteriorWindow |  | Fixed Window 5.84/0.25/0.11
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-3.91 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-3.04 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 6b |  | ClimateZone 6b | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-2.44 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 6a |  | ClimateZone 6a | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-2.71 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 5 |  | ClimateZone 5 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-2.15 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.92 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.76 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.98 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.36 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-0.80 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.10 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.36 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 2b |  | ClimateZone 2b | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-0.73 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 2a |  | ClimateZone 2a | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.17 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall WoodFrame ClimateZone 1 |  | ClimateZone 1 | ExteriorWall | WoodFramed | Wood Siding | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-3.91 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-3.04 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6b |  | ClimateZone 6b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.44 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 6a |  | ClimateZone 6a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.71 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 5 |  | ClimateZone 5 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.15 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.92 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.76 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.98 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.36 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.80 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.10 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.36 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b 1 |  | ClimateZone 2b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.73 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2b |  | ClimateZone 2b | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-0.73 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 2a |  | ClimateZone 2a | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.17 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall SteelFrame ClimateZone 1 |  | ClimateZone 1 | ExteriorWall | SteelFramed | Wood Siding | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-3.72 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-2.85 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 6b |  | ClimateZone 6b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-2.25 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 6a |  | ClimateZone 6a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-2.52 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 5 |  | ClimateZone 5 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.96 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 4c |  | ClimateZone 4c | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.72 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.57 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.79 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.16 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.61 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.91 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.16 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 2b |  | ClimateZone 2b | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.54 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 2a |  | ClimateZone 2a | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.98 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Metal ClimateZone 1 |  | ClimateZone 1 | ExteriorWall | Metal | Metal Siding | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 8 |  | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-3.75 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 7 |  | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.89 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 6b |  | ClimateZone 6b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.23 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 6a |  | ClimateZone 6a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.48 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 5b |  | ClimateZone 5b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.26 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 4c-5a |  | ClimateZone 4c-5a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.76 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 4b |  | ClimateZone 4b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.93 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 4a |  | ClimateZone 4a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.47 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 3c |  | ClimateZone 3c | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.61 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 3a |  | ClimateZone 3a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.61 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 2b |  | ClimateZone 2b | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.43 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 2a |  | ClimateZone 2a | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-0.52 | 1/2IN Gypsum
CBECS 1980-2004 ExtWall Mass ClimateZone 1 |  | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof Metal ClimateZone 8 |  | ClimateZone 8 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-5.75 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 7 |  | ClimateZone 7 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-4.41 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 6b |  | ClimateZone 6b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.65 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 6a |  | ClimateZone 6a | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.97 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 5b |  | ClimateZone 5b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.38 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 5a |  | ClimateZone 5a | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.38 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 4c |  | ClimateZone 4c | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.75 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 4b |  | ClimateZone 4b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.99 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 4a |  | ClimateZone 4a | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.03 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 3c |  | ClimateZone 3c | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.00 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-1.76 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.66 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 3a |  | ClimateZone 3a | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.44 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 2b |  | ClimateZone 2b | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-3.83 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 2a |  | ClimateZone 2a | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.67 | Metal Decking
CBECS 1980-2004 ExtRoof Metal ClimateZone 1 |  | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.38 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 8 |  | ClimateZone 8 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-5.75 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 7 |  | ClimateZone 7 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-4.41 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 6b |  | ClimateZone 6b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.65 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 6a |  | ClimateZone 6a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.97 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b 1 |  | ClimateZone 5b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.51 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 5b |  | ClimateZone 5b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.51 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 5a |  | ClimateZone 5a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.38 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 4c |  | ClimateZone 4c | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.75 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 4b |  | ClimateZone 4b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.99 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 4a |  | ClimateZone 4a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.03 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 3c |  | ClimateZone 3c | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.00 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAX |  | ClimateZone 3b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-1.76 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 3b LAS |  | ClimateZone 3b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.66 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 3a |  | ClimateZone 3a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.44 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 2b |  | ClimateZone 2b | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.83 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 2a |  | ClimateZone 2a | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.67 | Metal Decking
CBECS 1980-2004 ExtRoof IEAD ClimateZone 1 |  | ClimateZone 1 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.38 | Metal Decking
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 8 |  | ClimateZone 8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-5.68 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 7 |  | ClimateZone 7 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-4.40 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6b |  | ClimateZone 6b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.59 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 6a |  | ClimateZone 6a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.91 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5b |  | ClimateZone 5b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.45 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 5a |  | ClimateZone 5a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.32 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4c |  | ClimateZone 4c | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.75 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4b |  | ClimateZone 4b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.99 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 4a |  | ClimateZone 4a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.04 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAX |  | ClimateZone 3b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-1.76 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3b LAS |  | ClimateZone 3b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.67 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 3a |  | ClimateZone 3a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.45 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2b |  | ClimateZone 2b | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-3.83 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 2a |  | ClimateZone 2a | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.67 | 1/2IN Gypsum
CBECS 1980-2004 ExtRoof AtticFloor ClimateZone 1 |  | ClimateZone 1 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-2.38 | 1/2IN Gypsum
AtticRoof ClimateZone 1-8 |  | ClimateZone 1-8 | AtticRoof | WoodFramed | Roof Membrane | Metal Decking
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 7-8 | ASHRAE 90.1-2010 | ClimateZone 7-8 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 2.00/0.45/0.35
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 6-8 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 3.69/0.70/0.60
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 5-6 | ASHRAE 90.1-2010 | ClimateZone 5-6 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 2.00/0.40/0.31
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 4 | ASHRAE 90.1-2010 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 2.30/0.40/0.31
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 3 | ASHRAE 90.1-2010 | ClimateZone 3 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 3.69/0.25/0.16
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 2 | ASHRAE 90.1-2010 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 4.26/0.25/0.16
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1-5 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 5.84/0.70/0.60
ASHRAE 90.1-2010 ExtWindow NonMetal ClimateZone 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 5.84/0.25/0.11
ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2010 | ClimateZone 7-8 | ExteriorWindow | Metal framing (all other) | Fixed Window 2.56/0.45/0.35
ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 6-8 | ExteriorWindow | Metal framing (all other) | Fixed Window 3.69/0.70/0.60
ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2010 | ClimateZone 4-6 | ExteriorWindow | Metal framing (all other) | Fixed Window 3.12/0.40/0.31
ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2010 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | Fixed Window 3.69/0.25/0.16
ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2010 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Fixed Window 4.26/0.25/0.16
ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1-5 | ExteriorWindow | Metal framing (all other) | Fixed Window 5.84/0.70/0.60
ASHRAE 90.1-2010 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Fixed Window 5.84/0.25/0.11
ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 8 | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-25.96 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 6-7 | ASHRAE 90.1-2010 | ClimateZone 6-7 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-17.79 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 5 | ASHRAE 90.1-2010 | ClimateZone 5 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-13.81 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 2-8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 2-8 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-9.42 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1-4 | ASHRAE 90.1-2010 | ClimateZone 1-4 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-9.42 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall WoodFrame ClimateZone 1 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWall | WoodFramed | Wood Siding | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 8 | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-25.21 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 7 | ASHRAE 90.1-2010 | ClimateZone 7 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-21.99 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 2-6 | ASHRAE 90.1-2010 | ClimateZone 2-6 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-13.81 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone alt-res 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-6.25 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-10.09 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 4-8 | ASHRAE 90.1-2010 | ClimateZone 4-8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-13.81 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 3 | ASHRAE 90.1-2010 | ClimateZone 3 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-10.09 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 2-7 Semiheated | ASHRAE 90.1-2010 | ClimateZone 2-7 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-6.25 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1-2 | ASHRAE 90.1-2010 | ClimateZone 1-2 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-6.25 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall SteelFrame ClimateZone 1 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWall | SteelFramed | Wood Siding | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Metal ClimateZone 7-8 | ASHRAE 90.1-2010 | ClimateZone 7-8 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-16.24 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Metal ClimateZone 5-6 | ASHRAE 90.1-2010 | ClimateZone 5-6 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-13.19 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Metal ClimateZone 3-4 | ASHRAE 90.1-2010 | ClimateZone 3-4 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-10.60 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1-8 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-7.55 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Metal ClimateZone 1-2 | ASHRAE 90.1-2010 | ClimateZone 1-2 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-9.45 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 8 | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-16.84 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 6-7 | ASHRAE 90.1-2010 | ClimateZone 6-7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-11.70 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 5 | ASHRAE 90.1-2010 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-10.11 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 4 | ASHRAE 90.1-2010 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-8.72 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 3 | ASHRAE 90.1-2010 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-7.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 2 | ASHRAE 90.1-2010 | ClimateZone 2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-5.74 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone alt-res 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-4.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-7.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7-8 | ASHRAE 90.1-2010 | ClimateZone 7-8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-16.84 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 7 Semiheated | ASHRAE 90.1-2010 | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-5.74 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 6 | ASHRAE 90.1-2010 | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-10.11 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 5-6 Semiheated | ASHRAE 90.1-2010 | ClimateZone 5-6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-4.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 5 | ASHRAE 90.1-2010 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-8.72 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 4 | ASHRAE 90.1-2010 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-7.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 3 | ASHRAE 90.1-2010 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-5.74 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 2 | ASHRAE 90.1-2010 | ClimateZone 2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-4.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 1-4 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1-4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtWall Mass ClimateZone 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-14.60 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 8 | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-27.79 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 6-7 Semiheated | ASHRAE 90.1-2010 | ClimateZone 6-7 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-13.11 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 6-7 | ASHRAE 90.1-2010 | ClimateZone 6-7 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-19.63 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 5 Semiheated | ASHRAE 90.1-2010 | ClimateZone 5 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-11.27 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 2-5 | ASHRAE 90.1-2010 | ClimateZone 2-5 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-17.40 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 2-4 Semiheated | ASHRAE 90.1-2010 | ClimateZone 2-4 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-9.53 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 1 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-5.21 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof Metal ClimateZone 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-14.60 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-14.76 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 6-7 Semiheated | ASHRAE 90.1-2010 | ClimateZone 6-7 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-9.64 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 5 Semiheated | ASHRAE 90.1-2010 | ClimateZone 5 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-7.29 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 3-4 Semiheated | ASHRAE 90.1-2010 | ClimateZone 3-4 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-4.66 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 2-8 | ASHRAE 90.1-2010 | ClimateZone 2-8 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-19.72 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1-2 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1-2 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-3.47 IP | Metal Decking
ASHRAE 90.1-2010 ExtRoof IEAD ClimateZone 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-14.76 IP | Metal Decking
ASHRAE 90.1-2010 AtticFloor ClimateZone 8 | ASHRAE 90.1-2010 | ClimateZone 8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-45.65 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 AtticFloor ClimateZone 6-8 Semiheated | ASHRAE 90.1-2010 | ClimateZone 6-8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-27.44 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 AtticFloor ClimateZone 3-5 Semiheated | ASHRAE 90.1-2010 | ClimateZone 3-5 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-16.90 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 AtticFloor ClimateZone 2-7 | ASHRAE 90.1-2010 | ClimateZone 2-7 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-35.07 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 AtticFloor ClimateZone 1-2 Semiheated | ASHRAE 90.1-2010 | ClimateZone 1-2 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-10.37 IP | 1/2IN Gypsum
ASHRAE 90.1-2010 AtticFloor ClimateZone 1 | ASHRAE 90.1-2010 | ClimateZone 1 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-27.44 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 7-8 | ASHRAE 90.1-2007 | ClimateZone 7-8 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 2.00/0.45/0.35
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 6-8 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 3.69/0.70/0.60
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 5-6 | ASHRAE 90.1-2007 | ClimateZone 5-6 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 2.00/0.40/0.31
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 4 | ASHRAE 90.1-2007 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 2.30/0.40/0.31
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 3 | ASHRAE 90.1-2007 | ClimateZone 3 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 3.69/0.25/0.16
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 2 | ASHRAE 90.1-2007 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 4.26/0.25/0.16
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1-5 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 5.84/0.70/0.60
ASHRAE 90.1-2007 ExtWindow NonMetal ClimateZone 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Fixed Window 5.84/0.25/0.11
ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 7-8 | ASHRAE 90.1-2007 | ClimateZone 7-8 | ExteriorWindow | Metal framing (all other) | Fixed Window 2.56/0.45/0.35
ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 6-8 | ExteriorWindow | Metal framing (all other) | Fixed Window 3.69/0.70/0.60
ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 4-6 | ASHRAE 90.1-2007 | ClimateZone 4-6 | ExteriorWindow | Metal framing (all other) | Fixed Window 3.12/0.40/0.31
ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 3 | ASHRAE 90.1-2007 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | Fixed Window 3.69/0.25/0.16
ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 2 | ASHRAE 90.1-2007 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Fixed Window 4.26/0.25/0.16
ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1-5 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1-5 | ExteriorWindow | Metal framing (all other) | Fixed Window 5.84/0.70/0.60
ASHRAE 90.1-2007 ExtWindow Metal ClimateZone 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Fixed Window 5.84/0.25/0.11
ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 8 | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-25.96 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 6-7 | ASHRAE 90.1-2007 | ClimateZone 6-7 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-17.79 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 5 | ASHRAE 90.1-2007 | ClimateZone 5 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-13.81 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 2-8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 2-8 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-9.42 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 1-4 | ASHRAE 90.1-2007 | ClimateZone 1-4 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame Wall Insulation R-9.42 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall WoodFrame ClimateZone 1 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWall | WoodFramed | Wood Siding | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 8 | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-25.21 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 7 | ASHRAE 90.1-2007 | ClimateZone 7 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-21.99 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 2-6 | ASHRAE 90.1-2007 | ClimateZone 2-6 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-13.81 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone alt-res 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-6.25 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-10.09 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 4-8 | ASHRAE 90.1-2007 | ClimateZone 4-8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-13.81 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 3 | ASHRAE 90.1-2007 | ClimateZone 3 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-10.09 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 2-7 Semiheated | ASHRAE 90.1-2007 | ClimateZone 2-7 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-6.25 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1-2 | ASHRAE 90.1-2007 | ClimateZone 1-2 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame Wall Insulation R-6.25 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall SteelFrame ClimateZone 1 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWall | SteelFramed | Wood Siding | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Metal ClimateZone 7-8 | ASHRAE 90.1-2007 | ClimateZone 7-8 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-16.24 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Metal ClimateZone 6-8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 6-8 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-7.55 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Metal ClimateZone 5 Semiheated | ASHRAE 90.1-2007 | ClimateZone 5 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-6.83 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Metal ClimateZone 4 Semiheated | ASHRAE 90.1-2007 | ClimateZone 4 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-6.16 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Metal ClimateZone 2-3 Semiheated | ASHRAE 90.1-2007 | ClimateZone 2-3 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-4.14 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Metal ClimateZone 1-6 | ASHRAE 90.1-2007 | ClimateZone 1-6 | ExteriorWall | Metal | Metal Siding | Metal Building Wall Insulation R-7.55 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Metal ClimateZone 1 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWall | Metal | Metal Siding | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 8 | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-16.84 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 6-7 | ASHRAE 90.1-2007 | ClimateZone 6-7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-11.70 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 5 | ASHRAE 90.1-2007 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-10.11 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 4 | ASHRAE 90.1-2007 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-8.72 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 3 | ASHRAE 90.1-2007 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-7.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 2 | ASHRAE 90.1-2007 | ClimateZone 2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-5.74 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone alt-res 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-4.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-7.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7-8 | ASHRAE 90.1-2007 | ClimateZone 7-8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-11.70 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 7 Semiheated | ASHRAE 90.1-2007 | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-5.74 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 6 | ASHRAE 90.1-2007 | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-10.11 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 5-6 Semiheated | ASHRAE 90.1-2007 | ClimateZone 5-6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-4.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 5 | ASHRAE 90.1-2007 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-8.72 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 4 | ASHRAE 90.1-2007 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-7.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 3 | ASHRAE 90.1-2007 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-5.74 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 2 | ASHRAE 90.1-2007 | ClimateZone 2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass Wall Insulation R-4.23 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 1-4 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1-4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtWall Mass ClimateZone 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-13.11 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 8 | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-19.63 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 3-7 Semiheated | ASHRAE 90.1-2007 | ClimateZone 3-4 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-9.53 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 2 Semiheated | ASHRAE 90.1-2007 | ClimateZone 2 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-5.21 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 1-7 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing | Metal Roof Insulation R-14.60 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof Metal ClimateZone 1 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing
ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-14.76 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 6-7 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-9.64 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 5 Semiheated | ASHRAE 90.1-2007 | ClimateZone 5 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-7.29 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 3-4 Semiheated | ASHRAE 90.1-2007 | ClimateZone 3-4 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-4.66 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 2-8 | ASHRAE 90.1-2007 | ClimateZone 5-6 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-19.72 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1-2 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1-2 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-3.47 IP | Metal Decking
ASHRAE 90.1-2007 ExtRoof IEAD ClimateZone 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorRoof | IEAD | Roof Membrane | IEAD Roof Insulation R-14.76 IP | Metal Decking
ASHRAE 90.1-2007 AtticFloor ClimateZone 8 | ASHRAE 90.1-2007 | ClimateZone 8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-45.65 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 AtticFloor ClimateZone 6-8 Semiheated | ASHRAE 90.1-2007 | ClimateZone 6-8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-27.44 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 AtticFloor ClimateZone 3-5 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1-5 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-16.90 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 AtticFloor ClimateZone 2-7 | ASHRAE 90.1-2007 | ClimateZone 2-5 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-35.07 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 AtticFloor ClimateZone 1-2 Semiheated | ASHRAE 90.1-2007 | ClimateZone 1-2 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-10.37 IP | 1/2IN Gypsum
ASHRAE 90.1-2007 AtticFloor ClimateZone 1 | ASHRAE 90.1-2007 | ClimateZone 1 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation R-27.44 IP | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-ware 1-8 | ASHRAE 90.1-2004 | ClimateZone 1-8 | ExteriorWindow |  | Fixed Window 5.84/0.70/0.60
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resH 3a-3b | ASHRAE 90.1-2004 | ClimateZone 3a-3b | ExteriorWindow |  | Fixed Window 3.24/0.39/0.31
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-resA 3a-3b | ASHRAE 90.1-2004 | ClimateZone 3a-3b | ExteriorWindow |  | Fixed Window 3.81/0.39/0.27
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWindow |  | Fixed Window 2.67/0.30/0.21
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorWindow |  | Fixed Window 3.81/0.49/0.38
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 4-6 | ASHRAE 90.1-2004 | ClimateZone 4-6 | ExteriorWindow |  | Fixed Window 3.81/0.39/0.27
ASHRAE 90.1-2004 ExtWindow ClimateZone alt-res 3c | ASHRAE 90.1-2004 | ClimateZone 3c | ExteriorWindow |  | Fixed Window 5.84/0.61/0.47
ASHRAE 90.1-2004 ExtWindow ClimateZone 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWindow |  | Fixed Window 2.62/0.30/0.21
ASHRAE 90.1-2004 ExtWindow ClimateZone 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorWindow |  | Fixed Window 3.24/0.49/0.41
ASHRAE 90.1-2004 ExtWindow ClimateZone 4-6 | ASHRAE 90.1-2004 | ClimateZone 4-6 | ExteriorWindow |  | Fixed Window 3.24/0.39/0.31
ASHRAE 90.1-2004 ExtWindow ClimateZone 3c | ASHRAE 90.1-2004 | ClimateZone 3c | ExteriorWindow |  | Fixed Window 5.84/0.39/0.22
ASHRAE 90.1-2004 ExtWindow ClimateZone 3a-3b | ASHRAE 90.1-2004 | ClimateZone 3a-3b | ExteriorWindow |  | Fixed Window 3.24/0.25/0.16
ASHRAE 90.1-2004 ExtWindow ClimateZone 1-2 | ASHRAE 90.1-2004 | ClimateZone 1-2 | ExteriorWindow |  | Fixed Window 5.84/0.25/0.11
ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-3.45 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall WoodFrame ClimateZone 1-7 | ASHRAE 90.1-2004 | ClimateZone 1-7 | ExteriorWall | WoodFramed | Wood Siding | Wood Frame NonRes Wall Insulation-1.98 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-3.21 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 4-6 | ASHRAE 90.1-2004 | ClimateZone 4-6 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.75 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone alt-res 3 | ASHRAE 90.1-2004 | ClimateZone 3 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.10 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 7-8 | ASHRAE 90.1-2004 | ClimateZone 7-8 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.75 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 5-6 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-2.10 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall SteelFrame ClimateZone 1-4 | ASHRAE 90.1-2004 | ClimateZone 1-4 | ExteriorWall | SteelFramed | Wood Siding | Steel Frame NonRes Wall Insulation-1.42 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Metal ClimateZone 6-8 | ASHRAE 90.1-2004 | ClimateZone 6-8 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.37 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Metal ClimateZone 5 | ASHRAE 90.1-2004 | ClimateZone 5 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.24 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Metal ClimateZone 4 | ASHRAE 90.1-2004 | ClimateZone 4 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-1.12 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Metal ClimateZone 2-3 | ASHRAE 90.1-2004 | ClimateZone 2-3 | ExteriorWall | Metal | Metal Siding | Metal Building Semi-Cond Wall Insulation-0.77 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Metal ClimateZone 1 | ASHRAE 90.1-2004 | ClimateZone 1 | ExteriorWall | Metal | Metal Siding | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.48 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.20 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 5-6 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.96 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 4 | ASHRAE 90.1-2004 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.69 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 3 | ASHRAE 90.1-2004 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.43 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone alt-res 1-2 | ASHRAE 90.1-2004 | ClimateZone 1-2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.17 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-2.20 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.96 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 6 | ASHRAE 90.1-2004 | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.69 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 5 | ASHRAE 90.1-2004 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.43 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 3-4 | ASHRAE 90.1-2004 | ClimateZone 3-4 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | Mass NonRes Wall Insulation-1.17 | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtWall Mass ClimateZone 1-2 | ASHRAE 90.1-2004 | ClimateZone 1-2 | ExteriorWall | Mass | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-2.50 | Metal Decking
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-1.81 | Metal Decking
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 5-6 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-1.87 | Metal Decking
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 3-4 | ASHRAE 90.1-2004 | ClimateZone 3-4 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-1.81 | Metal Decking
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 2 | ASHRAE 90.1-2004 | ClimateZone 2 | ExteriorRoof | Metal | Metal Roofing | Metal Semi-Cond Roof Insulation-1.05 | Metal Decking
ASHRAE 90.1-2004 ExtRoof Metal ClimateZone 1 | ASHRAE 90.1-2004 | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing
ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-3.72 | Metal Decking
ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.79 | Metal Decking
ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 1 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.85 | Metal Decking
ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 5-6 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.85 | Metal Decking
ASHRAE 90.1-2004 ExtRoof IEAD ClimateZone 1-4 | ASHRAE 90.1-2004 | ClimateZone 1-4 | ExteriorRoof | IEAD | Roof Membrane | IEAD NonRes Roof Insulation-2.79 | Metal Decking
ASHRAE 90.1-2004 AtticFloor ClimateZone 6-8 | ASHRAE 90.1-2004 | ClimateZone 6-8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-6.52 | 1/2IN Gypsum
ASHRAE 90.1-2004 AtticFloor ClimateZone 1-5 | ASHRAE 90.1-2004 | ClimateZone 1-5 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor NonRes Insulation-5.18 | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | ASHRAE 189.1-2009 | ClimateZone 4-5 | ExteriorWindow |  | Theoretical Glass [216]
ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ASHRAE 189.1-2009 | ClimateZone 7-8 | ExteriorWindow |  | Theoretical Glass [221]
ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ASHRAE 189.1-2009 | ClimateZone 6 | ExteriorWindow |  | Theoretical Glass [216]
ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ASHRAE 189.1-2009 | ClimateZone 4-5 | ExteriorWindow |  | Theoretical Glass [207]
ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ASHRAE 189.1-2009 | ClimateZone 3 | ExteriorWindow |  | Theoretical Glass [202]
ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ASHRAE 189.1-2009 | ClimateZone 2 | ExteriorWindow |  | Theoretical Glass [197]
ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ASHRAE 189.1-2009 | ClimateZone 1 | ExteriorWindow |  | Theoretical Glass [167]
ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 6-8 | ASHRAE 189.1-2009 | ClimateZone 6-8 | ExteriorWall | WoodFramed | Wood Siding | Wall Insulation [43] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 5 | ASHRAE 189.1-2009 | ClimateZone 5 | ExteriorWall | WoodFramed | Wood Siding | Wall Insulation [41] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall WoodFrame ClimateZone 1-4 | ASHRAE 189.1-2009 | ClimateZone 1-4 | ExteriorWall | WoodFramed | Wood Siding | Wall Insulation [34] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 4-8 | ASHRAE 189.1-2009 | ClimateZone 4-8 | ExteriorWall | SteelFramed | MAT-SHEATH | Wall Insulation [39] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall SteelFrame ClimateZone 1-3 | ASHRAE 189.1-2009 | ClimateZone 1-3 | ExteriorWall | SteelFramed | MAT-SHEATH | Wall Insulation [33] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Metal ClimateZone 4-8 | ASHRAE 189.1-2009 | ClimateZone 4-8 | ExteriorWall | Metal | Metal Siding | Wall Insulation [38] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Metal ClimateZone 1-3 | ASHRAE 189.1-2009 | ClimateZone 1-3 | ExteriorWall | Metal | Metal Siding | Wall Insulation [32] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 8 | ASHRAE 189.1-2009 | ClimateZone 8 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [46] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 7 | ASHRAE 189.1-2009 | ClimateZone 7 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [44] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 6 | ASHRAE 189.1-2009 | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [44] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 5 | ASHRAE 189.1-2009 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [42] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 4 | ASHRAE 189.1-2009 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [40] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 3 | ASHRAE 189.1-2009 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [37] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 2 | ASHRAE 189.1-2009 | ClimateZone 2 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [36] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone alt-res 1 | ASHRAE 189.1-2009 | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [35] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 7-8 | ASHRAE 189.1-2009 | ClimateZone 7-8 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [44] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 6 | ASHRAE 189.1-2009 | ClimateZone 6 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [42] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 5 | ASHRAE 189.1-2009 | ClimateZone 5 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [40] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 4 | ASHRAE 189.1-2009 | ClimateZone 4 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [37] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 3 | ASHRAE 189.1-2009 | ClimateZone 3 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [36] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 2 | ASHRAE 189.1-2009 | ClimateZone 2 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [35] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtWall Mass ClimateZone 1 | ASHRAE 189.1-2009 | ClimateZone 1 | ExteriorWall | Mass | 1IN Stucco | 8IN Concrete HW | Wall Insulation [31] | 1/2IN Gypsum
ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 7-8 | ASHRAE 189.1-2009 | ClimateZone 7-8 | ExteriorRoof | Metal | Metal Roofing | Roof Insulation [27] | Metal Decking
ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 6 | ASHRAE 189.1-2009 | ClimateZone 6 | ExteriorRoof | Metal | Metal Roofing | Roof Insulation [25] | Metal Decking
ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 2-5 | ASHRAE 189.1-2009 | ClimateZone 2-5 | ExteriorRoof | Metal | Metal Roofing | Roof Insulation [22] | Metal Decking
ASHRAE 189.1-2009 ExtRoof Metal ClimateZone 1 | ASHRAE 189.1-2009 | ClimateZone 1 | ExteriorRoof | Metal | Metal Roofing | Roof Insulation [19] | Metal Decking
ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 7-8 | ASHRAE 189.1-2009 | ClimateZone 7-8 | ExteriorRoof | IEAD | Roof Membrane | Roof Insulation [26] | Metal Decking
ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 6 | ASHRAE 189.1-2009 | ClimateZone 6 | ExteriorRoof | IEAD | Roof Membrane | Roof Insulation [24] | Metal Decking
ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 2-5 | ASHRAE 189.1-2009 | ClimateZone 2-5 | ExteriorRoof | IEAD | Roof Membrane | Roof Insulation [21] | Metal Decking
ASHRAE 189.1-2009 ExtRoof IEAD ClimateZone 1 | ASHRAE 189.1-2009 | ClimateZone 1 | ExteriorRoof | IEAD | Roof Membrane | Roof Insulation [18] | Metal Decking
ASHRAE 189.1-2009 AtticFloor ClimateZone 1-8 | ASHRAE 189.1-2009 | ClimateZone 1-8 | AtticFloor | WoodFramed | 1/2IN Gypsum | AtticFloor Insulation | 1/2IN Gypsum
MetalFrameWallInterior | CEC Title24-2013 |  | InteriorWall |  | Gypsum Board - 1/2 in. | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in.
MetalFrameWallU062 | CEC Title24-2013 |  | ExteriorWall |  | Stucco - 7/8 in. | Compliance Insulation R13.99 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in.
MetalFrameWallU082 | CEC Title24-2013 |  | ExteriorWall |  | Stucco - 7/8 in. | Compliance Insulation R10.06 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in.
MetalFrameWallU098 | CEC Title24-2013 |  | ExteriorWall |  | Stucco - 7/8 in. | Compliance Insulation R8.07 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in.
MetalFrameWallU105 | CEC Title24-2013 |  | ExteriorWall |  | Stucco - 7/8 in. | Compliance Insulation R7.39 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in.
MetalFrameWallUnconditioned | CEC Title24-2013 |  | ExteriorWall |  | Stucco - 7/8 in.
MassLightWallU440 | CEC Title24-2013 |  | ExteriorWall |  | Concrete - 140 lb/ft3 - 4 in. | Compliance Insulation R0.02 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in.
MassLightWallU278 | CEC Title24-2013 |  | ExteriorWall |  | Concrete - 140 lb/ft3 - 4 in. | Compliance Insulation R1.35 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in.
MassLightWallU227 | CEC Title24-2013 |  | ExteriorWall |  | Concrete - 140 lb/ft3 - 4 in. | Compliance Insulation R2.15 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in.
MassLightWallU196 | CEC Title24-2013 |  | ExteriorWall |  | Concrete - 140 lb/ft3 - 4 in. | Compliance Insulation R2.85 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in.
MassLightWallU170 | CEC Title24-2013 |  | ExteriorWall |  | Concrete - 140 lb/ft3 - 4 in. | Compliance Insulation R3.63 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in.
MassLightWallU107 | CEC Title24-2013 |  | ExteriorWall |  | Concrete - 140 lb/ft3 - 4 in. | Compliance Insulation R7.10 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in.
MassHeavyWallU690 | CEC Title24-2013 |  | ExteriorWall |  | Concrete - 140 lb/ft3 - 8 in. | Compliance Insulation R0.01
MassHeavyWallU650 | CEC Title24-2013 |  | ExteriorWall |  | Concrete - 140 lb/ft3 - 8 in. | Compliance Insulation R0.10
MassHeavyWallU253 | CEC Title24-2013 |  | ExteriorWall |  | Concrete - 140 lb/ft3 - 8 in. | Compliance Insulation R1.41 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in.
MassHeavyWallU211 | CEC Title24-2013 |  | ExteriorWall |  | Concrete - 140 lb/ft3 - 8 in. | Compliance Insulation R2.19 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in.
MassHeavyWallU184 | CEC Title24-2013 |  | ExteriorWall |  | Concrete - 140 lb/ft3 - 8 in. | Compliance Insulation R2.89 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in.
MassHeavyWallU160 | CEC Title24-2013 |  | ExteriorWall |  | Concrete - 140 lb/ft3 - 8 in. | Compliance Insulation R3.70 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in.
MetalBldgWallU113 | CEC Title24-2013 |  | ExteriorWall |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R8.00
MetalBldgWallU061 | CEC Title24-2013 |  | ExteriorWall |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R15.54
MetalBldgWallU057 | CEC Title24-2013 |  | ExteriorWall |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R16.69
WoodWallU110 | CEC Title24-2013 |  | ExteriorWall |  | Plywood - 5/8 in. | Compliance Insulation R6.46 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 3/8 in.
WoodWallU102 | CEC Title24-2013 |  | ExteriorWall |  | Plywood - 5/8 in. | Compliance Insulation R7.18 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 3/8 in.
WoodWallU059 | CEC Title24-2013 |  | ExteriorWall |  | Plywood - 5/8 in. | Compliance Insulation R14.32 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 3/8 in.
WoodWallU042 | CEC Title24-2013 |  | ExteriorWall |  | Plywood - 5/8 in. | Compliance Insulation R21.18 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 3/8 in.
FlatNonresMetalBuildingRoofU065 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R14.60
FlatNonresMetalBuildingRoofU048 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R20.05
FlatNonresWoodFramingAndOtherRoofU028 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R34.93
FlatNonresWoodFramingAndOtherRoofU034 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R28.63
FlatNonresWoodFramingAndOtherRoofU039 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R24.86
FlatNonresWoodFramingAndOtherRoofU049 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R19.63
FlatNonresWoodFramingAndOtherRoofU067 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R14.14
FlatNonresWoodFramingAndOtherRoofU075 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R12.55
FlatNonresWoodFramingAndOtherRoofUnconditioned | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in.
SteepNonresMetalBuildingRoofU065 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R14.60
SteepNonresMetalBuildingRoofU048 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R20.05
SteepNonresWoodFramingAndOtherRoofU028 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R34.93
SteepNonresWoodFramingAndOtherRoofU034 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R28.63
SteepNonresWoodFramingAndOtherRoofU039 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R24.86
SteepNonresWoodFramingAndOtherRoofU049 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R19.63
SteepNonresWoodFramingAndOtherRoofU067 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R14.14
SteepNonresWoodFramingAndOtherRoofU075 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R12.55
SteepNonresWoodFramingAndOtherRoofUnconditioned | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in.
FlatResMetalBuildingRoofU065 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R14.60
FlatResMetalBuildingRoofU048 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R20.05
FlatResWoodFramingAndOtherRoofU028 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R34.93
FlatResWoodFramingAndOtherRoofU034 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R28.63
FlatResWoodFramingAndOtherRoofU039 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R24.86
FlatResWoodFramingAndOtherRoofU049 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R19.63
FlatResWoodFramingAndOtherRoofU067 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R14.14
FlatResWoodFramingAndOtherRoofU075 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R12.55
FlatResWoodFramingAndOtherRoofUnconditioned | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in.
SteepResMetalBuildingRoofU065 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R14.60
SteepResMetalBuildingRoofU048 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R20.05
SteepResWoodFramingAndOtherRoofU028 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R34.93
SteepResWoodFramingAndOtherRoofU034 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R28.63
SteepResWoodFramingAndOtherRoofU039 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R24.86
SteepResWoodFramingAndOtherRoofU049 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R19.63
SteepResWoodFramingAndOtherRoofU067 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R14.14
SteepResWoodFramingAndOtherRoofU075 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R12.55
SteepResWoodFramingAndOtherRoofUnconditioned | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in.
MetalBuildingRoofU065 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R14.60
MetalBuildingRoofU048 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R20.05
WoodFramingAndOtherRoofU028 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R34.93
WoodFramingAndOtherRoofU034 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R28.63
WoodFramingAndOtherRoofU039 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R24.86
WoodFramingAndOtherRoofU049 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R19.63
WoodFramingAndOtherRoofU067 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R14.14
WoodFramingAndOtherRoofU075 | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in. | Compliance Insulation R12.55
WoodFramingAndOtherRoofUnconditioned | CEC Title24-2013 |  | ExteriorRoof |  | Metal Standing Seam - 1/16 in.
OtherFloorU034 | CEC Title24-2013 |  | ExteriorFloor |  | Compliance Insulation R25.16 | Plywood - 5/8 in. | Carpet - 3/4 in.
OtherFloorU039 | CEC Title24-2013 |  | ExteriorFloor |  | Compliance Insulation R21.39 | Plywood - 5/8 in. | Carpet - 3/4 in.
OtherFloorU048 | CEC Title24-2013 |  | ExteriorFloor |  | Compliance Insulation R16.58 | Plywood - 5/8 in. | Carpet - 3/4 in.
OtherFloorU071 | CEC Title24-2013 |  | ExteriorFloor |  | Compliance Insulation R9.83 | Plywood - 5/8 in. | Carpet - 3/4 in.
OtherFloorUnconditioned | CEC Title24-2013 |  | ExteriorFloor |  | Plywood - 5/8 in.
MassFloorU037 | CEC Title24-2013 |  | ExteriorFloor |  | Concrete - 140 lb/ft3 - 4 in. | Compliance Insulation R22.48 | Plywood - 5/8 in. | Carpet - 3/4 in.
MassFloorU045 | CEC Title24-2013 |  | ExteriorFloor |  | Concrete - 140 lb/ft3 - 4 in. | Compliance Insulation R17.67 | Plywood - 5/8 in. | Carpet - 3/4 in.
MassFloorU058 | CEC Title24-2013 |  | ExteriorFloor |  | Concrete - 140 lb/ft3 - 4 in. | Compliance Insulation R12.69 | Plywood - 5/8 in. | Carpet - 3/4 in.
MassFloorU069 | CEC Title24-2013 |  | ExteriorFloor |  | Concrete - 140 lb/ft3 - 4 in. | Compliance Insulation R9.94 | Plywood - 5/8 in. | Carpet - 3/4 in.
MassFloorU092 | CEC Title24-2013 |  | ExteriorFloor |  | Concrete - 140 lb/ft3 - 4 in. | Compliance Insulation R6.32 | Plywood - 5/8 in. | Carpet - 3/4 in.
MassFloorU269 | CEC Title24-2013 |  | ExteriorFloor |  | Concrete - 140 lb/ft3 - 4 in. | Compliance Insulation R1.54 | Plywood - 5/8 in.
DOE Prototype Air Wall |  | ClimateZone 1-8 | InteriorWall |  | DOE Prototype Air Wall Material R-1.18
DOE Prototype AtticRoofDeck |  | ClimateZone 1-8 | AtticRoof |  | DOE Prototype Asphalt Shingles | DOE Prototype 5/8 in. Plywood
DOE Prototype Basement Floor |  | ClimateZone 1-8 | GroundContactFloor | Mass | DOE Prototype 8 in. Concrete Block Basement Wall | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype Basement Wall |  | ClimateZone 1-8 | GroundContactWall | Mass | DOE Prototype 8 in. Concrete Block Basement Wall
DOE Prototype DropCeiling |  | ClimateZone 1-8 | InteriorCeiling |  | DOE Prototype Acoustic Ceiling
DOE Prototype Ext Slab 6in |  | ClimateZone 1-8 | GroundContactFloor | Mass | DOE Prototype 6 in. Normalweight Concrete Floor
DOE Prototype Ext Slab 6in with Carpet |  | ClimateZone 1-8 | GroundContactFloor | Mass | DOE Prototype 6 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype Ext Slab 8in with Carpet |  | ClimateZone 1-8 | GroundContactFloor | Mass | DOE Prototype 8 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype Ext Soffit Floor |  | ClimateZone 1-8 | AtticWall |  | DOE Prototype 5/8 in. Plywood
DOE Prototype ExtDoor |  | ClimateZone 1-8 | ExteriorDoor |  | DOE Prototype Std Opaque Door Panel R-0.7
DOE Prototype InsulatedCeiling |  | ClimateZone 1-8 | ExteriorRoof |  | DOE Prototype Interior Wall Addi Insul | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Int Slab Ceiling |  | ClimateZone 1-8 | InteriorCeiling | Mass | DOE Prototype Cp02 Carpet Pad R-1.23 | DOE Prototype 4 in. Normalweight Concrete Floor
DOE Prototype Int Slab Floor |  | ClimateZone 1-8 | InteriorFloor | Mass | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype Int Wall |  | ClimateZone 1-8 | InteriorWall | WoodFramed | DOE Prototype 1/2 in. Gypsum Board | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype Interior Wall |  | ClimateZone 1-8 | InteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Interior Wall Addi Insul | DOE Prototype Steel Frame/Cavity | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2004 1-4 | ASHRAE 90.1-2004 | ClimateZone 1-4 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-5.89 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2004 5-6 | ASHRAE 90.1-2004 | ClimateZone 5-6 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-9.73 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2004 7-8 | ASHRAE 90.1-2004 | ClimateZone 7-8 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-13.45 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2007 1-2 | ASHRAE 90.1-2007 | ClimateZone 1-2 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-5.89 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2007 3 | ASHRAE 90.1-2007 | ClimateZone 3 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-9.73 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2007 4-8 | ASHRAE 90.1-2007 | ClimateZone 4-8 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-13.45 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2010 1-2 | ASHRAE 90.1-2010 | ClimateZone 1-2 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-5.89 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2010 3 | ASHRAE 90.1-2010 | ClimateZone 3 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-9.73 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2010 4-8 | ASHRAE 90.1-2010 | ClimateZone 4-8 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-13.45 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2013 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-5.89 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2013 2 | ASHRAE 90.1-2013 | ClimateZone 2 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-9.73 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2013 3 | ASHRAE 90.1-2013 | ClimateZone 3 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-10.81 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2013 4 | ASHRAE 90.1-2013 | ClimateZone 4 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-13.45 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2013 5 | ASHRAE 90.1-2013 | ClimateZone 5 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-16.0 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2013 6-7 | ASHRAE 90.1-2013 | ClimateZone 6-7 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-18.23 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Framed 2013 8 | ASHRAE 90.1-2013 | ClimateZone 8 | ExteriorWall | SteelFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Exterior Wall Insulation R-24.85 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2004 1-2 | ASHRAE 90.1-2004 | ClimateZone 1-2 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-0.17 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2004 3-4 | ASHRAE 90.1-2004 | ClimateZone 3-4 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-4.82 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2004 5 | ASHRAE 90.1-2004 | ClimateZone 5 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-6.33 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2004 6 | ASHRAE 90.1-2004 | ClimateZone 6 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-7.82 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2004 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-9.31 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2004 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-10.7 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2007 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-0.17 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2007 2 | ASHRAE 90.1-2007 | ClimateZone 2 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-4.82 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2007 3 | ASHRAE 90.1-2007 | ClimateZone 3 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-6.33 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2007 4 | ASHRAE 90.1-2007 | ClimateZone 4 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-7.82 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2007 5 | ASHRAE 90.1-2007 | ClimateZone 5 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-9.31 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2007 6 | ASHRAE 90.1-2007 | ClimateZone 6 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-10.7 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2007 7-8 | ASHRAE 90.1-2007 | ClimateZone 7-8 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-12.28 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2010 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-0.17 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2010 2 | ASHRAE 90.1-2010 | ClimateZone 2 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-4.82 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2010 3 | ASHRAE 90.1-2010 | ClimateZone 3 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-6.33 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2010 4 | ASHRAE 90.1-2010 | ClimateZone 4 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-7.82 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2010 5 | ASHRAE 90.1-2010 | ClimateZone 5 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-9.31 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2010 6 | ASHRAE 90.1-2010 | ClimateZone 6 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-10.7 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2010 7-8 | ASHRAE 90.1-2010 | ClimateZone 7-8 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-12.28 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2013 1 | ASHRAE 90.1-2013 | ClimateZone 1 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-0.17 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2013 2 | ASHRAE 90.1-2013 | ClimateZone 2 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-4.82 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2013 3 | ASHRAE 90.1-2013 | ClimateZone 3 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-6.33 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2013 4 | ASHRAE 90.1-2013 | ClimateZone 4 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-7.82 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2013 5 | ASHRAE 90.1-2013 | ClimateZone 5 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-9.31 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2013 6 | ASHRAE 90.1-2013 | ClimateZone 6 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-10.7 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2013 7 | ASHRAE 90.1-2013 | ClimateZone 7 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-12.28 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall Mass 2013 8 | ASHRAE 90.1-2013 | ClimateZone 8 | ExteriorWall | Mass | DOE Prototype 8 in. Normalweight Concrete Wall | DOE Prototype Nonres Exterior Wall Insulation R-19.03 | DOE Prototype 1/2 in. Gypsum Board
DOE Prototype NonRes Ext Wall MetalBuilding 2004 1-6 | ASHRAE 90.1-2004 | ClimateZone 1-6 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Nonres Exterior Wall Insulation R-7.55 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall MetalBuilding 2004 7-8 | ASHRAE 90.1-2004 | ClimateZone 7-8 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Nonres Exterior Wall Insulation R-16.24 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall MetalBuilding 2007 1-6 | ASHRAE 90.1-2007 | ClimateZone 1-6 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Nonres Exterior Wall Insulation R-7.55 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall MetalBuilding 2007 7-8 | ASHRAE 90.1-2007 | ClimateZone 7-8 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Nonres Exterior Wall Insulation R-16.24 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall MetalBuilding 2010 1-2 | ASHRAE 90.1-2010 | ClimateZone 1-2 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Nonres Exterior Wall Insulation R-9.45 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall MetalBuilding 2010 3-4 | ASHRAE 90.1-2010 | ClimateZone 3-4 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Nonres Exterior Wall Insulation R-10.6 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall MetalBuilding 2010 5-6 | ASHRAE 90.1-2010 | ClimateZone 5-6 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Nonres Exterior Wall Insulation R-13.19 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall MetalBuilding 2010 7-8 | ASHRAE 90.1-2010 | ClimateZone 7-8 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Nonres Exterior Wall Insulation R-16.24 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall MetalBuilding 2013 1-3 | ASHRAE 90.1-2013 | ClimateZone 1-3 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Nonres Exterior Wall Insulation R-9.45 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall MetalBuilding 2013 4 | ASHRAE 90.1-2013 | ClimateZone 4 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Nonres Exterior Wall Insulation R-15.37 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall MetalBuilding 2013 5-6 | ASHRAE 90.1-2013 | ClimateZone 5-6 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Nonres Exterior Wall Insulation R-18.7 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall MetalBuilding 2013 7 | ASHRAE 90.1-2013 | ClimateZone 7 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Nonres Exterior Wall Insulation R-21.43 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Ext Wall MetalBuilding 2013 8 | ASHRAE 90.1-2013 | ClimateZone 8 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Nonres Exterior Wall Insulation R-24.34 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Floor 2004 1 | ASHRAE 90.1-2004 | ClimateZone 1 | ExteriorFloor | Mass | DOE Prototype Nonres Floor Insulation R-0.17 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype NonRes Floor 2004 2-5 | ASHRAE 90.1-2004 | ClimateZone 2-5 | ExteriorFloor | Mass | DOE Prototype Nonres Floor Insulation R-16.37 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype NonRes Floor 2004 6-8 | ASHRAE 90.1-2004 | ClimateZone 6-8 | ExteriorFloor | Mass | DOE Prototype Nonres Floor Insulation R-23.45 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype NonRes Floor 2007 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorFloor | Mass | DOE Prototype Nonres Floor Insulation R-0.17 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype NonRes Floor 2007 2-3 | ASHRAE 90.1-2007 | ClimateZone 2-3 | ExteriorFloor | Mass | DOE Prototype Nonres Floor Insulation R-16.37 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype NonRes Floor 2007 4-7 | ASHRAE 90.1-2007 | ClimateZone 4-7 | ExteriorFloor | Mass | DOE Prototype Nonres Floor Insulation R-23.45 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype NonRes Floor 2007 8 | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorFloor | Mass | DOE Prototype Nonres Floor Insulation R-28.39 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype NonRes Floor 2010 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorFloor | Mass | DOE Prototype Nonres Floor Insulation R-0.17 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype NonRes Floor 2010 2-3 | ASHRAE 90.1-2010 | ClimateZone 2-3 | ExteriorFloor | Mass | DOE Prototype Nonres Floor Insulation R-16.37 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype NonRes Floor 2010 4-7 | ASHRAE 90.1-2010 | ClimateZone 4-7 | ExteriorFloor | Mass | DOE Prototype Nonres Floor Insulation R-23.45 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype NonRes Floor 2010 8 | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorFloor | Mass | DOE Prototype Nonres Floor Insulation R-28.39 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype NonRes Floor 2013 1 | ASHRAE 90.1-2013 | ClimateZone 1 | ExteriorFloor | Mass | DOE Prototype Nonres Floor Insulation R-0.17 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype NonRes Floor 2013 2-5 | ASHRAE 90.1-2013 | ClimateZone 2-5 | ExteriorFloor | Mass | DOE Prototype Nonres Floor Insulation R-23.45 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype NonRes Floor 2013 6-8 | ASHRAE 90.1-2013 | ClimateZone 6-8 | ExteriorFloor | Mass | DOE Prototype Nonres Floor Insulation R-28.39 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Cp02 Carpet Pad R-1.23
DOE Prototype NonRes Floor Ceiling 2004 1 | ASHRAE 90.1-2004 | ClimateZone 1 | ExteriorFloor | Mass | DOE Prototype Cp02 Carpet Pad R-1.23 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Nonres Floor Insulation R-0.17
DOE Prototype NonRes Floor Ceiling 2004 2-5 | ASHRAE 90.1-2004 | ClimateZone 2-5 | ExteriorFloor | Mass | DOE Prototype Cp02 Carpet Pad R-1.23 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Nonres Floor Insulation R-16.37
DOE Prototype NonRes Floor Ceiling 2004 6-8 | ASHRAE 90.1-2004 | ClimateZone 6-8 | ExteriorFloor | Mass | DOE Prototype Cp02 Carpet Pad R-1.23 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Nonres Floor Insulation R-23.45
DOE Prototype NonRes Floor Ceiling 2007 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorFloor | Mass | DOE Prototype Cp02 Carpet Pad R-1.23 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Nonres Floor Insulation R-0.17
DOE Prototype NonRes Floor Ceiling 2007 2-3 | ASHRAE 90.1-2007 | ClimateZone 2-3 | ExteriorFloor | Mass | DOE Prototype Cp02 Carpet Pad R-1.23 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Nonres Floor Insulation R-16.37
DOE Prototype NonRes Floor Ceiling 2007 4-7 | ASHRAE 90.1-2007 | ClimateZone 4-7 | ExteriorFloor | Mass | DOE Prototype Cp02 Carpet Pad R-1.23 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Nonres Floor Insulation R-23.45
DOE Prototype NonRes Floor Ceiling 2007 8 | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorFloor | Mass | DOE Prototype Cp02 Carpet Pad R-1.23 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Nonres Floor Insulation R-28.39
DOE Prototype NonRes Floor Ceiling 2010 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorFloor | Mass | DOE Prototype Cp02 Carpet Pad R-1.23 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Nonres Floor Insulation R-0.17
DOE Prototype NonRes Floor Ceiling 2010 2-3 | ASHRAE 90.1-2010 | ClimateZone 2-3 | ExteriorFloor | Mass | DOE Prototype Cp02 Carpet Pad R-1.23 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Nonres Floor Insulation R-16.37
DOE Prototype NonRes Floor Ceiling 2010 4-7 | ASHRAE 90.1-2010 | ClimateZone 4-7 | ExteriorFloor | Mass | DOE Prototype Cp02 Carpet Pad R-1.23 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Nonres Floor Insulation R-23.45
DOE Prototype NonRes Floor Ceiling 2010 8 | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorFloor | Mass | DOE Prototype Cp02 Carpet Pad R-1.23 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Nonres Floor Insulation R-28.39
DOE Prototype NonRes Floor Ceiling 2013 1 | ASHRAE 90.1-2013 | ClimateZone 1 | ExteriorFloor | Mass | DOE Prototype Cp02 Carpet Pad R-1.23 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Nonres Floor Insulation R-0.17
DOE Prototype NonRes Floor Ceiling 2013 2-5 | ASHRAE 90.1-2013 | ClimateZone 2-5 | ExteriorFloor | Mass | DOE Prototype Cp02 Carpet Pad R-1.23 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Nonres Floor Insulation R-23.45
DOE Prototype NonRes Floor Ceiling 2013 6-8 | ASHRAE 90.1-2013 | ClimateZone 6-8 | ExteriorFloor | Mass | DOE Prototype Cp02 Carpet Pad R-1.23 | DOE Prototype 4 in. Normalweight Concrete Floor | DOE Prototype Nonres Floor Insulation R-28.39
DOE Prototype NonRes Roof Floor WoodJoistAttic 2004 1-5 | ASHRAE 90.1-2004 | ClimateZone 1-5 | AtticFloor | WoodFramed | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Roof Insulation R-27.78
DOE Prototype NonRes Roof Floor WoodJoistAttic 2004 6-8 | ASHRAE 90.1-2004 | ClimateZone 6-8 | AtticFloor | WoodFramed | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Roof Insulation R-35.4
DOE Prototype NonRes Roof Floor WoodJoistAttic 2007 1 | ASHRAE 90.1-2007 | ClimateZone 1 | AtticFloor | WoodFramed | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Roof Insulation R-27.78
DOE Prototype NonRes Roof Floor WoodJoistAttic 2007 2-7 | ASHRAE 90.1-2007 | ClimateZone 2-7 | AtticFloor | WoodFramed | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Roof Insulation R-35.4
DOE Prototype NonRes Roof Floor WoodJoistAttic 2007 8 | ASHRAE 90.1-2007 | ClimateZone 8 | AtticFloor | WoodFramed | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Roof Insulation R-45.98
DOE Prototype NonRes Roof Floor WoodJoistAttic 2010 1 | ASHRAE 90.1-2010 | ClimateZone 1 | AtticFloor | WoodFramed | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Roof Insulation R-27.78
DOE Prototype NonRes Roof Floor WoodJoistAttic 2010 2-7 | ASHRAE 90.1-2010 | ClimateZone 2-7 | AtticFloor | WoodFramed | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Roof Insulation R-35.4
DOE Prototype NonRes Roof Floor WoodJoistAttic 2010 8 | ASHRAE 90.1-2010 | ClimateZone 8 | AtticFloor | WoodFramed | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Roof Insulation R-45.98
DOE Prototype NonRes Roof Floor WoodJoistAttic 2013 1-3 | ASHRAE 90.1-2013 | ClimateZone 1-3 | AtticFloor | WoodFramed | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Roof Insulation R-35.4
DOE Prototype NonRes Roof Floor WoodJoistAttic 2013 4-6 | ASHRAE 90.1-2013 | ClimateZone 4-6 | AtticFloor | WoodFramed | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Roof Insulation R-45.98
DOE Prototype NonRes Roof Floor WoodJoistAttic 2013 7-8 | ASHRAE 90.1-2013 | ClimateZone 7-8 | AtticFloor | WoodFramed | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Nonres Roof Insulation R-57.19
DOE Prototype NonRes Roof LightweightOrMetalDeck 2004 1-7 | ASHRAE 90.1-2004 | ClimateZone 1-7 | ExteriorRoof | Metal | DOE Prototype Built-up Roofing | DOE Prototype Nonres Roof Insulation R-14.76 | DOE Prototype Metal Surface
DOE Prototype NonRes Roof LightweightOrMetalDeck 2004 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorRoof | Metal | DOE Prototype Built-up Roofing | DOE Prototype Nonres Roof Insulation R-19.72 | DOE Prototype Metal Surface
DOE Prototype NonRes Roof LightweightOrMetalDeck 2007 1-8 | ASHRAE 90.1-2007 | ClimateZone 1-8 | ExteriorRoof | Metal | DOE Prototype Built-up Roofing | DOE Prototype Nonres Roof Insulation R-19.72 | DOE Prototype Metal Surface
DOE Prototype NonRes Roof LightweightOrMetalDeck 2010 1-8 | ASHRAE 90.1-2007 | ClimateZone 1-8 | ExteriorRoof | Metal | DOE Prototype Built-up Roofing | DOE Prototype Nonres Roof Insulation R-19.72 | DOE Prototype Metal Surface
DOE Prototype NonRes Roof LightweightOrMetalDeck 2013 1 | ASHRAE 90.1-2013 | ClimateZone 1 | ExteriorRoof | Metal | DOE Prototype Built-up Roofing | DOE Prototype Nonres Roof Insulation R-19.72 | DOE Prototype Metal Surface
DOE Prototype NonRes Roof LightweightOrMetalDeck 2013 2-3 | ASHRAE 90.1-2013 | ClimateZone 2-3 | ExteriorRoof | Metal | DOE Prototype Built-up Roofing | DOE Prototype Nonres Roof Insulation R-24.52 | DOE Prototype Metal Surface
DOE Prototype NonRes Roof LightweightOrMetalDeck 2013 4-6 | ASHRAE 90.1-2013 | ClimateZone 4-6 | ExteriorRoof | Metal | DOE Prototype Built-up Roofing | DOE Prototype Nonres Roof Insulation R-30.13 | DOE Prototype Metal Surface
DOE Prototype NonRes Roof LightweightOrMetalDeck 2013 7-8 | ASHRAE 90.1-2013 | ClimateZone 7-8 | ExteriorRoof | Metal | DOE Prototype Built-up Roofing | DOE Prototype Nonres Roof Insulation R-34.6 | DOE Prototype Metal Surface
DOE Prototype NonRes Roof MetalBuilding 2004 1-7 | ASHRAE 90.1-2004 | ClimateZone 1-7 | ExteriorRoof | Metal | DOE Prototype Metal Roof Surface | DOE Prototype Nonres Roof Insulation R-14.6
DOE Prototype NonRes Roof MetalBuilding 2004 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorRoof | Metal | DOE Prototype Metal Roof Surface | DOE Prototype Nonres Roof Insulation R-19.63
DOE Prototype NonRes Roof MetalBuilding 2007 1-7 | ASHRAE 90.1-2007 | ClimateZone 1-7 | ExteriorRoof | Metal | DOE Prototype Metal Roof Surface | DOE Prototype Nonres Roof Insulation R-14.6
DOE Prototype NonRes Roof MetalBuilding 2007 8 | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorRoof | Metal | DOE Prototype Metal Roof Surface | DOE Prototype Nonres Roof Insulation R-19.63
DOE Prototype NonRes Roof MetalBuilding 2010 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorRoof | Metal | DOE Prototype Metal Roof Surface | DOE Prototype Nonres Roof Insulation R-14.6
DOE Prototype NonRes Roof MetalBuilding 2010 2-5 | ASHRAE 90.1-2010 | ClimateZone 2-5 | ExteriorRoof | Metal | DOE Prototype Metal Roof Surface | DOE Prototype Nonres Roof Insulation R-17.4
DOE Prototype NonRes Roof MetalBuilding 2010 6-7 | ASHRAE 90.1-2010 | ClimateZone 6-7 | ExteriorRoof | Metal | DOE Prototype Metal Roof Surface | DOE Prototype Nonres Roof Insulation R-19.63
DOE Prototype NonRes Roof MetalBuilding 2010 8 | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorRoof | Metal | DOE Prototype Metal Roof Surface | DOE Prototype Nonres Roof Insulation R-27.79
DOE Prototype NonRes Roof MetalBuilding 2013 1 | ASHRAE 90.1-2013 | ClimateZone 1 | ExteriorRoof | Metal | DOE Prototype Metal Roof Surface | DOE Prototype Nonres Roof Insulation R-23.61
DOE Prototype NonRes Roof MetalBuilding 2013 2-3 | ASHRAE 90.1-2013 | ClimateZone 2-3 | ExteriorRoof | Metal | DOE Prototype Metal Roof Surface | DOE Prototype Nonres Roof Insulation R-24.86
DOE Prototype NonRes Roof MetalBuilding 2013 4-5 | ASHRAE 90.1-2013 | ClimateZone 4-5 | ExteriorRoof | Metal | DOE Prototype Metal Roof Surface | DOE Prototype Nonres Roof Insulation R-26.25
DOE Prototype NonRes Roof MetalBuilding 2013 6 | ASHRAE 90.1-2013 | ClimateZone 6 | ExteriorRoof | Metal | DOE Prototype Metal Roof Surface | DOE Prototype Nonres Roof Insulation R-31.48
DOE Prototype NonRes Roof MetalBuilding 2013 7 | ASHRAE 90.1-2013 | ClimateZone 7 | ExteriorRoof | Metal | DOE Prototype Metal Roof Surface | DOE Prototype Nonres Roof Insulation R-33.7
DOE Prototype NonRes Roof MetalBuilding 2013 8 | ASHRAE 90.1-2013 | ClimateZone 8 | ExteriorRoof | Metal | DOE Prototype Metal Roof Surface | DOE Prototype Nonres Roof Insulation R-37.68
DOE Prototype NonRes Roof WoodJoistAttic 2004 1-5 | ASHRAE 90.1-2004 | ClimateZone 1-5 | AtticFloor | WoodFramed | DOE Prototype Nonres Roof Insulation R-27.78 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Roof WoodJoistAttic 2004 6-8 | ASHRAE 90.1-2004 | ClimateZone 6-8 | AtticFloor | WoodFramed | DOE Prototype Nonres Roof Insulation R-35.4 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Roof WoodJoistAttic 2007 1 | ASHRAE 90.1-2007 | ClimateZone 1 | AtticFloor | WoodFramed | DOE Prototype Nonres Roof Insulation R-27.78 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Roof WoodJoistAttic 2007 2-7 | ASHRAE 90.1-2007 | ClimateZone 2-7 | AtticFloor | WoodFramed | DOE Prototype Nonres Roof Insulation R-35.4 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Roof WoodJoistAttic 2007 8 | ASHRAE 90.1-2007 | ClimateZone 8 | AtticFloor | WoodFramed | DOE Prototype Nonres Roof Insulation R-45.98 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Roof WoodJoistAttic 2010 1 | ASHRAE 90.1-2010 | ClimateZone 1 | AtticFloor | WoodFramed | DOE Prototype Nonres Roof Insulation R-27.78 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Roof WoodJoistAttic 2010 2-7 | ASHRAE 90.1-2010 | ClimateZone 2-7 | AtticFloor | WoodFramed | DOE Prototype Nonres Roof Insulation R-35.4 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Roof WoodJoistAttic 2010 8 | ASHRAE 90.1-2010 | ClimateZone 8 | AtticFloor | WoodFramed | DOE Prototype Nonres Roof Insulation R-45.98 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Roof WoodJoistAttic 2013 1-3 | ASHRAE 90.1-2013 | ClimateZone 1-3 | AtticFloor | WoodFramed | DOE Prototype Nonres Roof Insulation R-35.4 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Roof WoodJoistAttic 2013 4-6 | ASHRAE 90.1-2013 | ClimateZone 4-6 | AtticFloor | WoodFramed | DOE Prototype Nonres Roof Insulation R-45.98 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype NonRes Roof WoodJoistAttic 2013 7-8 | ASHRAE 90.1-2013 | ClimateZone 7-8 | AtticFloor | WoodFramed | DOE Prototype Nonres Roof Insulation R-57.19 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Overhead Door 2004 1-8 | ASHRAE 90.1-2004 | ClimateZone 1-8 | ExteriorDoor | RollUp | DOE Prototype Overhead Door Panel R-0.69
DOE Prototype Overhead Door 2007 1-7 | ASHRAE 90.1-2004 | ClimateZone 1-7 | ExteriorDoor | RollUp | DOE Prototype Overhead Door Panel R-0.69
DOE Prototype Overhead Door 2007 8 | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorDoor | RollUp | DOE Prototype Overhead Door Panel R-2.0
DOE Prototype Overhead Door 2010 1-7 | ASHRAE 90.1-2010 | ClimateZone 1-7 | ExteriorDoor | RollUp | DOE Prototype Overhead Door Panel R-0.69
DOE Prototype Overhead Door 2010 8 | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorDoor | RollUp | DOE Prototype Overhead Door Panel R-2.0
DOE Prototype Overhead Door 2013 1-7 | ASHRAE 90.1-2013 | ClimateZone 1-7 | ExteriorDoor | RollUp | DOE Prototype Overhead Door Panel R-0.69
DOE Prototype Overhead Door 2013 8 | ASHRAE 90.1-2013 | ClimateZone 8 | ExteriorDoor | RollUp | DOE Prototype Overhead Door Panel R-2.0
DOE Prototype Res Ext Wall 2004 1-2 | ASHRAE 90.1-2004 | ClimateZone 1-2 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-5.89 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2004 3 | ASHRAE 90.1-2004 | ClimateZone 3 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-9.73 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2004 4-7 | ASHRAE 90.1-2004 | ClimateZone 4-7 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-13.45 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2004 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-16.0 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2007 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-5.89 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2007 2-6 | ASHRAE 90.1-2007 | ClimateZone 2-6 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-13.45 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2007 7 | ASHRAE 90.1-2007 | ClimateZone 7 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-21.63 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2007 8 | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-24.85 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2010 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-5.89 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2010 2-6 | ASHRAE 90.1-2010 | ClimateZone 2-6 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-13.45 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2010 7 | ASHRAE 90.1-2010 | ClimateZone 7 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-21.63 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2010 8 | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-24.85 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2013 1 | ASHRAE 90.1-2013 | ClimateZone 1 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-5.89 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2013 2-4 | ASHRAE 90.1-2013 | ClimateZone 2-4 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-13.45 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2013 5 | ASHRAE 90.1-2013 | ClimateZone 5 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-16.0 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2013 6 | ASHRAE 90.1-2013 | ClimateZone 6 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-18.23 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2013 7 | ASHRAE 90.1-2013 | ClimateZone 7 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-21.63 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Ext Wall 2013 8 | ASHRAE 90.1-2013 | ClimateZone 8 | ExteriorWall | WoodFramed | DOE Prototype 25mm Stucco | DOE Prototype 5/8 in. Gypsum Board | DOE Prototype Res Exterior Wall Insulation R-24.85 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Res Roof 2004 1-7 | ASHRAE 90.1-2004 | ClimateZone 1-7 | ExteriorRoof | IEAD | DOE Prototype Built-up Roofing | DOE Prototype Res Roof Insulation R-14.76 | DOE Prototype Metal Surface
DOE Prototype Res Roof 2004 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorRoof | IEAD | DOE Prototype Built-up Roofing | DOE Prototype Res Roof Insulation R-19.72 | DOE Prototype Metal Surface
DOE Prototype Res Roof 2007 1-8 | ASHRAE 90.1-2007 | ClimateZone 1-8 | ExteriorRoof | IEAD | DOE Prototype Built-up Roofing | DOE Prototype Res Roof Insulation R-19.72 | DOE Prototype Metal Surface
DOE Prototype Res Roof 2010 1-8 | ASHRAE 90.1-2010 | ClimateZone 1-8 | ExteriorRoof | IEAD | DOE Prototype Built-up Roofing | DOE Prototype Res Roof Insulation R-19.72 | DOE Prototype Metal Surface
DOE Prototype Res Roof 2013 1-3 | ASHRAE 90.1-2010 | ClimateZone 1-3 | ExteriorRoof | IEAD | DOE Prototype Built-up Roofing | DOE Prototype Res Roof Insulation R-24.52 | DOE Prototype Metal Surface
DOE Prototype Res Roof 2013 4-6 | ASHRAE 90.1-2013 | ClimateZone 4-6 | ExteriorRoof | IEAD | DOE Prototype Built-up Roofing | DOE Prototype Res Roof Insulation R-30.13 | DOE Prototype Metal Surface
DOE Prototype Res Roof 2013 7-8 | ASHRAE 90.1-2013 | ClimateZone 7-8 | ExteriorRoof | IEAD | DOE Prototype Built-up Roofing | DOE Prototype Res Roof Insulation R-34.6 | DOE Prototype Metal Surface
DOE Prototype Semiheated Ext Wall 2004 1 | ASHRAE 90.1-2004 | ClimateZone 1 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Semiheated Exterior Wall Insulation R-0.17 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Semiheated Ext Wall 2004 2-3 | ASHRAE 90.1-2004 | ClimateZone 2-3 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Semiheated Exterior Wall Insulation R-4.13 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Semiheated Ext Wall 2004 4 | ASHRAE 90.1-2004 | ClimateZone 4 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Semiheated Exterior Wall Insulation R-6.16 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Semiheated Ext Wall 2004 5 | ASHRAE 90.1-2004 | ClimateZone 5 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Semiheated Exterior Wall Insulation R-6.83 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Semiheated Ext Wall 2004 6-8 | ASHRAE 90.1-2004 | ClimateZone 6-8 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Semiheated Exterior Wall Insulation R-7.55 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Semiheated Ext Wall 2007 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Semiheated Exterior Wall Insulation R-0.17 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Semiheated Ext Wall 2007 2-3 | ASHRAE 90.1-2007 | ClimateZone 2-3 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Semiheated Exterior Wall Insulation R-4.13 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Semiheated Ext Wall 2007 4 | ASHRAE 90.1-2007 | ClimateZone 4 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Semiheated Exterior Wall Insulation R-6.16 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Semiheated Ext Wall 2007 5 | ASHRAE 90.1-2007 | ClimateZone 5 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Semiheated Exterior Wall Insulation R-6.83 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Semiheated Ext Wall 2007 6-8 | ASHRAE 90.1-2007 | ClimateZone 6-8 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Semiheated Exterior Wall Insulation R-7.55 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Semiheated Ext Wall 2010 1-8 | ASHRAE 90.1-2010 | ClimateZone 1-8 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Semiheated Exterior Wall Insulation R-7.55 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Semiheated Ext Wall 2013 1-8 | ASHRAE 90.1-2010 | ClimateZone 1-8 | ExteriorWall | Metal | DOE Prototype Metal Surface | DOE Prototype Semiheated Exterior Wall Insulation R-7.55 | DOE Prototype 5/8 in. Gypsum Board
DOE Prototype Semiheated Roof 2004 1 | ASHRAE 90.1-2004 | ClimateZone 1 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-0.01
DOE Prototype Semiheated Roof 2004 2 | ASHRAE 90.1-2004 | ClimateZone 2 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-5.21
DOE Prototype Semiheated Roof 2004 3-4-7 | ASHRAE 90.1-2004 | ClimateZone 3-7 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-9.53
DOE Prototype Semiheated Roof 2004 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-13.11
DOE Prototype Semiheated Roof 2007 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-0.01
DOE Prototype Semiheated Roof 2007 2 | ASHRAE 90.1-2007 | ClimateZone 2 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-5.21
DOE Prototype Semiheated Roof 2007 3-7 | ASHRAE 90.1-2007 | ClimateZone 3-7 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-9.53
DOE Prototype Semiheated Roof 2007 8 | ASHRAE 90.1-2007 | ClimateZone 8 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-13.11
DOE Prototype Semiheated Roof 2010 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-5.21
DOE Prototype Semiheated Roof 2010 2-4 | ASHRAE 90.1-2010 | ClimateZone 2-4 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-9.53
DOE Prototype Semiheated Roof 2010 5 | ASHRAE 90.1-2010 | ClimateZone 5 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-11.27
DOE Prototype Semiheated Roof 2010 6-7 | ASHRAE 90.1-2010 | ClimateZone 6-7 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-13.11
DOE Prototype Semiheated Roof 2010 8 | ASHRAE 90.1-2010 | ClimateZone 8 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-14.6
DOE Prototype Semiheated Roof 2013 1 | ASHRAE 90.1-2013 | ClimateZone 1 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-5.21
DOE Prototype Semiheated Roof 2013 2-4 | ASHRAE 90.1-2013 | ClimateZone 2-4 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-9.53
DOE Prototype Semiheated Roof 2013 5 | ASHRAE 90.1-2013 | ClimateZone 5 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-11.27
DOE Prototype Semiheated Roof 2013 6-7 | ASHRAE 90.1-2013 | ClimateZone 6-7 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-13.11
DOE Prototype Semiheated Roof 2013 8 | ASHRAE 90.1-2013 | ClimateZone 8 | ExteriorRoof | IEAD | DOE Prototype Metal Roof Surface | DOE Prototype Semiheated Roof Insulation R-14.6
DOE Prototype Swinging Door 2004 1-7 | ASHRAE 90.1-2004 | ClimateZone 1-7 | ExteriorDoor | Swinging | DOE Prototype Opaque Door Panel Con R-1.43
DOE Prototype Swinging Door 2004 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorDoor | Swinging | DOE Prototype Opaque Door Panel Con R-2.0
DOE Prototype Swinging Door 2007 1-6 | ASHRAE 90.1-2007 | ClimateZone 1-6 | ExteriorDoor | Swinging | DOE Prototype Opaque Door Panel Con R-1.43
DOE Prototype Swinging Door 2007 7-8 | ASHRAE 90.1-2007 | ClimateZone 7-8 | ExteriorDoor | Swinging | DOE Prototype Opaque Door Panel Con R-2.0
DOE Prototype Swinging Door 2010 1-6 | ASHRAE 90.1-2010 | ClimateZone 1-6 | ExteriorDoor | Swinging | DOE Prototype Opaque Door Panel Con R-1.43
DOE Prototype Swinging Door 2010 7-8 | ASHRAE 90.1-2010 | ClimateZone 7-8 | ExteriorDoor | Swinging | DOE Prototype Opaque Door Panel Con R-2.0
DOE Prototype Swinging Door 2013 1-6 | ASHRAE 90.1-2013 | ClimateZone 1-6 | ExteriorDoor | Swinging | DOE Prototype Opaque Door Panel Con R-1.43
DOE Prototype Swinging Door 2013 7-8 | ASHRAE 90.1-2013 | ClimateZone 7-8 | ExteriorDoor | Swinging | DOE Prototype Opaque Door Panel Con R-2.0
DOE Prototype Swinging Door Semiheated |  | All Climates | ExteriorDoor | Swinging | DOE Prototype Opaque Door Panel Semi R-1.43
DOE Prototype Window U 0.40 SHGC 0.45 2013 7-8 | ASHRAE 90.1-2013 | ClimateZone 7-8 | ExteriorWindow | Metal framing (all other) | ECABS-2 BLEACHED 6MM | AIR 6MM | LoE SPEC SEL CLEAR 6MM Rev
DOE Prototype Window U 0.42 SHGC 0.40 2013 4-7 | ASHRAE 90.1-2013 | ClimateZone 4-7 | ExteriorWindow | Metal framing (all other) | LoE TINT 6MM | AIR 6MM | CLEAR 6MM
DOE Prototype Window U 0.42 SHGC 0.45 2007 7-8 | ASHRAE 90.1-2007 | ClimateZone 7-8 | ExteriorWindow | Metal framing (all other) | REF D CLEAR 6MM | ARGON 13MM | CLEAR 6MM
DOE Prototype Window U 0.42 SHGC 0.45 2010 7-8 | ASHRAE 90.1-2010 | ClimateZone 7-8 | ExteriorWindow | Metal framing (all other) | REF D CLEAR 6MM | ARGON 13MM | CLEAR 6MM
DOE Prototype Window U 0.45 SHGC 0.31 2013 4-6 | ASHRAE 90.1-2013 | ClimateZone 4-6 | ExteriorWindow | Metal framing (all other) | REF B CLEAR HI 6MM | AIR 13MM | CLEAR 6MM
DOE Prototype Window U 0.46 SHGC 0.45 2004 8 | ASHRAE 90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | GREY 6MM | AIR 13MM | CLEAR 6MM
DOE Prototype Window U 0.46 SHGC 0.45 2007 7-8 | ASHRAE 90.1-2007 | ClimateZone 7-8 | ExteriorWindow | Metal framing (all other) | GREY 6MM | AIR 13MM | CLEAR 6MM
DOE Prototype Window U 0.46 SHGC 0.45 2010 7-8 | ASHRAE 90.1-2010 | ClimateZone 7-8 | ExteriorWindow | Metal framing (all other) | GREY 6MM | AIR 13MM | CLEAR 6MM
DOE Prototype Window U 0.47 SHGC 0.40 2013 4-6 | ASHRAE 90.1-2013 | ClimateZone 4-6 | ExteriorWindow | Metal framing (all other) | Glass_2052_LayerAvg | Gap_1_W_0_0043 | Glass_2010F_LayerAvg
DOE Prototype Window U 0.48 SHGC 0.40 2007 4-6 | ASHRAE 90.1-2007 | ClimateZone 4-6 | ExteriorWindow | Metal framing (all other) | REF D CLEAR 6MM | AIR 13MM | CLEAR 6MM
DOE Prototype Window U 0.48 SHGC 0.40 2010 4-6 | ASHRAE 90.1-2010 | ClimateZone 4-6 | ExteriorWindow | Metal framing (all other) | REF D CLEAR 6MM | AIR 13MM | CLEAR 6MM
DOE Prototype Window U 0.48 SHGC 0.40 2013 4-6 | ASHRAE 90.1-2013 | ClimateZone 4-6 | ExteriorWindow | Metal framing (all other) | REF D CLEAR 6MM | AIR 13MM | CLEAR 6MM
DOE Prototype Window U 0.50 SHGC 0.40 2013 3-8 | ASHRAE 90.1-2013 | ClimateZone 3-8 | ExteriorWindow | Metal framing (all other) | Glass_2052_LayerAvg | Gap_1_W_0_0038 | Glass_2027F_LayerAvg
DOE Prototype Window U 0.55 SHGC 0.25 2013 3 | ASHRAE 90.1-2013 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | Glass_2175_LayerAvg | Gap_1_W_0_0032 | Glass_2022F_LayerAvg
DOE Prototype Window U 0.57 SHGC 0.25 2004 3 | ASHRAE 90.1-2004 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | REF C CLEAR HI 6MM | AIR 6MM | CLEAR 6MM
DOE Prototype Window U 0.57 SHGC 0.25 2007 3 | ASHRAE 90.1-2007 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | REF C CLEAR HI 6MM | AIR 6MM | CLEAR 6MM
DOE Prototype Window U 0.57 SHGC 0.25 2010 3 | ASHRAE 90.1-2010 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | REF C CLEAR HI 6MM | AIR 6MM | CLEAR 6MM
DOE Prototype Window U 0.57 SHGC 0.39 2004 3-6 | ASHRAE 90.1-2004 | ClimateZone 3-6 | ExteriorWindow | Metal framing (all other) | REF D CLEAR 6MM | AIR 6MM | CLEAR 6MM
DOE Prototype Window U 0.57 SHGC 0.39 2007 4-6 | ASHRAE 90.1-2007 | ClimateZone 4-6 | ExteriorWindow | Metal framing (all other) | REF D CLEAR 6MM | AIR 6MM | CLEAR 6MM
DOE Prototype Window U 0.57 SHGC 0.39 2010 4-6 | ASHRAE 90.1-2010 | ClimateZone 4-6 | ExteriorWindow | Metal framing (all other) | REF D CLEAR 6MM | AIR 6MM | CLEAR 6MM
DOE Prototype Window U 0.57 SHGC 0.49 2004 5-7 | ASHRAE 90.1-2004 | ClimateZone 5-7 | ExteriorWindow | Metal framing (all other) | BLUE 6MM | AIR 6MM | CLEAR 6MM
DOE Prototype Window U 0.60 SHGC 0.25 2013 1-2 | ASHRAE 90.1-2013 | ClimateZone 1-2 | ExteriorWindow | Metal framing (all other) | Glass_2175_LayerAvg | Gap_1_W_0_0025 | Glass_2022F_LayerAvg
DOE Prototype Window U 0.65 SHGC 0.35 2013 2 | ASHRAE 90.1-2013 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Glass_2052_LayerAvg | Gap_1_W_0_0024 | Glass_2027F_LayerAvg
DOE Prototype Window U 0.72 SHGC 0.25 2007 2 | ASHRAE 90.1-2007 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | REF B TINT MID 6MM
DOE Prototype Window U 0.72 SHGC 0.25 2010 2 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | REF B TINT MID 6MM
DOE Prototype Window U 0.75 SHGC 0.35 2013 1 | ASHRAE 90.1-2013 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Glass_2052_LayerAvg | Gap_1_W_0_0018 | Glass_2027F_LayerAvg
DOE Prototype Window U 0.9 SHGC 0.6 2004 1-3 + 8 | ASHRAE 90.1-2004 | ClimateZone 1-3 + 8 | ExteriorWindow | Metal framing (all other) | REF B CLEAR HI 6MM
DOE Prototype Window U 0.9 SHGC 0.6 2007 1-3 + 8 | ASHRAE 90.1-2004 | ClimateZone 1-3 + 8 | ExteriorWindow | Metal framing (all other) | REF B CLEAR HI 6MM
DOE Prototype Window U 0.9 SHGC 0.6 2010 1-3 + 8 | ASHRAE 90.1-2004 | ClimateZone 1-3 + 8 | ExteriorWindow | Metal framing (all other) | REF B CLEAR HI 6MM
DOE Prototype Window U 1.1 SHGC 0.68 2004 7 | ASHRAE 90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | GREEN 3MM
DOE Prototype Window U 1.1 SHGC 0.68 2007 7 | ASHRAE 90.1-2007 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | GREEN 3MM
DOE Prototype Window U 1.1 SHGC 0.68 2010 7 | ASHRAE 90.1-2010 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | GREEN 3MM
DOE Prototype Window U 1.17 SHGC 0.49 2004 4-6 | ASHRAE 90.1-2004 | ClimateZone 4-6 | ExteriorWindow | Metal framing (all other) | REF D CLEAR 6MM
DOE Prototype Window U 1.17 SHGC 0.49 2007 4-6 | ASHRAE 90.1-2007 | ClimateZone 4-6 | ExteriorWindow | Metal framing (all other) | REF D CLEAR 6MM
DOE Prototype Window U 1.17 SHGC 0.49 2010 4-6 | ASHRAE 90.1-2010 | ClimateZone 4-6 | ExteriorWindow | Metal framing (all other) | REF D CLEAR 6MM
DOE Prototype Window U 1.22 SHGC 0.25 2004 1-2 | ASHRAE 90.1-2004 | ClimateZone 1-2 | ExteriorWindow | Metal framing (all other) | ECREF-1 COLORED 6MM
DOE Prototype Window U 1.22 SHGC 0.25 2007 1 | ASHRAE 90.1-2007 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | ECREF-1 COLORED 6MM
DOE Prototype Window U 1.22 SHGC 0.25 2010 1 | ASHRAE 90.1-2010 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | ECREF-1 COLORED 6MM
DOE Prototype Window U 1.22 SHGC 0.4 C 2004 3 | ASHRAE 90.1-2004 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | REF C CLEAR HI 6MM
DOE Prototype Window U 1.22 SHGC 0.61 C 2004 3 | ASHRAE 90.1-2004 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | GREEN 6MM

## Materials
Each Material represents a layer of typical building material. Materials are referenced on the Constructions tab.
|  | Opaque Material Properties | [9 empty] | Simple Glazing Material Properties |  |  | Detailed Glazing Material Properties | [11 empty] | Standards Information
Name | Material Type | Roughness | Thickness (in) | Conductivity (Btu*in/hr*ft^2*F) | Resistance (hr*ft^2*F/Btu) | Density (lb/ft^3) | Specific Heat (Btu/lbm*F) | Thermal Absorptance | Solar Absorptance | Visible Absorptance | Gas Type | U-Factor (Btu/hr*ft^2*F) | Solar Heat Gain Coefficient | Visible Transmittance | Optical Data Type | Solar Transmittance At Normal Incidence | Front Side Solar Reflectance At Normal Incidence | Back Side Solar Relectance At Normal Incidence | Visible Transmittance At Normal Incidence | Front Side Visible Reflectance At Normal Incidence | Back Side Visible Relectance At Normal Incidence | Infrared Transmittance At Normal Incidence | Front Side Infrared Hemispherical Emissivity | Back Side Infrared Hemispherical Emissivity | Dirt Correction Factor For Solar And Visible Transmittance | Solar Diffusing | Material Standard | Material Standard Source | Code Category | Code Identifier | Framing Material | Framing Configuration | Framing Depth | Framing Size | Cavity Insulation (hr*ft^2*F/Btu)
1/2IN Gypsum | StandardOpaqueMaterial | Smooth | 0.5 | 1.1094 | 0.45071 | 48.9997 | 0.19824 | 0.9 | 0.4 | 0.4
1IN Stucco | StandardOpaqueMaterial | Smooth | 0.99606 | 4.7966 | 0.20766 | 115.9912 | 0.19991 | 0.9 | 0.92 | 0.92
8IN Concrete HW | StandardOpaqueMaterial | MediumRough | 8.0039 | 11.9921 | 0.66743 | 140.0259 | 0.19991 | 0.9 | 0.65 | 0.65
8IN CONCRETE HW RefBldg | StandardOpaqueMaterial | Rough | 8 | 9.0898 | 0.88011 | 139.8386 | 0.19987 | 0.9 | 0.7 | 0.7
Air 13mm | Gas |  | 0.5 | [7 empty] | Air
AtticFloor Insulation | StandardOpaqueMaterial | MediumRough | 9.3661 | 0.33974 | 27.5685 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-1.76 | StandardOpaqueMaterial | MediumRough | 2.6224 | 0.33974 | 7.719 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-2.38 | StandardOpaqueMaterial | MediumRough | 3.8162 | 0.33974 | 11.2327 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-2.45 | StandardOpaqueMaterial | MediumRough | 3.9437 | 0.33974 | 11.608 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-2.67 | StandardOpaqueMaterial | MediumRough | 4.3727 | 0.33974 | 12.8707 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-2.75 | StandardOpaqueMaterial | MediumRough | 4.5336 | 0.33974 | 13.3442 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-2.99 | StandardOpaqueMaterial | MediumRough | 4.9835 | 0.33974 | 14.6685 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.04 | StandardOpaqueMaterial | MediumRough | 5.0827 | 0.33974 | 14.9607 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.32 | StandardOpaqueMaterial | MediumRough | 5.7407 | 0.33974 | 16.8973 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.45 | StandardOpaqueMaterial | MediumRough | 5.9921 | 0.33974 | 17.6373 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.59 | StandardOpaqueMaterial | MediumRough | 6.264 | 0.33974 | 18.4376 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.67 | StandardOpaqueMaterial | MediumRough | 6.3031 | 0.33974 | 18.5528 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.83 | StandardOpaqueMaterial | MediumRough | 6.6109 | 0.33974 | 19.4587 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-3.91 | StandardOpaqueMaterial | MediumRough | 6.8803 | 0.33974 | 20.2518 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-4.40 | StandardOpaqueMaterial | MediumRough | 7.7188 | 0.33974 | 22.7197 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-5.18 | StandardOpaqueMaterial | MediumRough | 11.9138 | 0.33974 | 35.0673 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-5.68 | StandardOpaqueMaterial | MediumRough | 10.2901 | 0.33974 | 30.2881 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor NonRes Insulation-6.52 | StandardOpaqueMaterial | MediumRough | 11.9138 | 0.33974 | 35.0673 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Res Insulation-2.05 | StandardOpaqueMaterial | MediumRough | 3.1755 | 0.33974 | 9.347 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Res Insulation-2.37 | StandardOpaqueMaterial | MediumRough | 3.8007 | 0.33974 | 11.187 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Res Insulation-2.93 | StandardOpaqueMaterial | MediumRough | 4.8875 | 0.33974 | 14.386 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Insulation R-10.37 IP | StandardOpaqueMaterial | MediumRough | 3.5246 | 0.33974 | 10.3743 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Insulation R-16.90 IP | StandardOpaqueMaterial | MediumRough | 5.7404 | 0.33974 | 16.8965 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Insulation R-27.44 IP | StandardOpaqueMaterial | MediumRough | 9.3226 | 0.33974 | 27.4403 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Insulation R-35.07 IP | StandardOpaqueMaterial | MediumRough | 11.9132 | 0.33974 | 35.0656 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
AtticFloor Insulation R-45.65 IP | StandardOpaqueMaterial | MediumRough | 15.5083 | 0.33974 | 45.6476 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Clear 3mm | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.837 | 0.075 | 0.075 | 0.898 | 0.081 | 0.081 | 0 | 0.84 | 0.84 | 1 | FALSE
CP02 CARPET PAD | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00019108 | 0.9 | 0.8 | 0.8
F04 Wall air space resistance | AirGap |  |  | 46.2231 | 0.021634
F05 Ceiling air space resistance | AirGap |  |  | 38.5193 | 0.025961
F08 Metal surface | StandardOpaqueMaterial | Smooth | 0.031496 | 313.9476 | 0.00010032 | 488.4364 | 0.11942 | 0.9 | 0.7 | 0.7
F16 Acoustic tile | StandardOpaqueMaterial | MediumSmooth | 0.75197 | 0.41601 | 1.8076 | 22.9735 | 0.14092 | 0.9 | 0.3 | 0.3
Fixed Window 2.00/0.40/0.31 | SimpleGlazing | [10 empty] | 0.35 | 0.4 | 0.31
Fixed Window 2.00/0.45/0.35 | SimpleGlazing | [10 empty] | 0.35 | 0.45 | 0.35
Fixed Window 2.30/0.40/0.31 | SimpleGlazing | [10 empty] | 0.4 | 0.4 | 0.31
Fixed Window 2.56/0.45/0.35 | SimpleGlazing | [10 empty] | 0.45 | 0.45 | 0.35
Fixed Window 2.62/0.30/0.21 | SimpleGlazing | [10 empty] | 0.45998 | 0.3 | 0.21
Fixed Window 2.67/0.30/0.21 | SimpleGlazing | [10 empty] | 0.46998 | 0.49 | 0.38
Fixed Window 2.96/0.39/0.31 | SimpleGlazing | [10 empty] | 0.51998 | 0.39 | 0.31
Fixed Window 2.96/0.49/0.41 | SimpleGlazing | [10 empty] | 0.51998 | 0.49 | 0.41
Fixed Window 2.96/0.62/0.54 | SimpleGlazing | [10 empty] | 0.51998 | 0.62 | 0.54
Fixed Window 3.12/0.40/0.31 | SimpleGlazing | [10 empty] | 0.55 | 0.4 | 0.31
Fixed Window 3.24/0.25/0.16 | SimpleGlazing | [10 empty] | 0.56997 | 0.25 | 0.16
Fixed Window 3.24/0.39/0.31 | SimpleGlazing | [10 empty] | 0.56997 | 0.39 | 0.31
Fixed Window 3.24/0.49/0.41 | SimpleGlazing | [10 empty] | 0.56997 | 0.49 | 0.41
Fixed Window 3.35/0.36/0.27 | SimpleGlazing | [10 empty] | 0.58997 | 0.36 | 0.27
Fixed Window 3.35/0.39/0.31 | SimpleGlazing | [10 empty] | 0.58997 | 0.39 | 0.31
Fixed Window 3.53/0.41/0.32 | SimpleGlazing | [10 empty] | 0.61997 | 0.41 | 0.32
Fixed Window 3.69/0.25/0.16 | SimpleGlazing | [10 empty] | 0.65 | 0.25 | 0.16
Fixed Window 3.69/0.70/0.60 | SimpleGlazing | [10 empty] | 0.65 | 0.7 | 0.6
Fixed Window 3.81/0.39/0.27 | SimpleGlazing | [10 empty] | 0.51998 | 0.39 | 0.27
Fixed Window 3.81/0.49/0.38 | SimpleGlazing | [10 empty] | 0.51998 | 0.49 | 0.38
Fixed Window 4.09/0.26/0.13 | SimpleGlazing | [10 empty] | 0.71997 | 0.25 | 0.13
Fixed Window 4.09/0.36/0.23 | SimpleGlazing | [10 empty] | 0.71997 | 0.36 | 0.23
Fixed Window 4.09/0.39/0.25 | SimpleGlazing | [10 empty] | 0.71997 | 0.39 | 0.25
Fixed Window 4.26/0.25/0.16 | SimpleGlazing | [10 empty] | 0.75 | 0.25 | 0.16
Fixed Window 5.84/0.25/0.11 | SimpleGlazing | [10 empty] | 1.0285 | 0.25 | 0.11
Fixed Window 5.84/0.39/0.22 | SimpleGlazing | [10 empty] | 1.0285 | 0.39 | 0.22
Fixed Window 5.84/0.44/0.27 | SimpleGlazing | [10 empty] | 1.0285 | 0.44 | 0.27
Fixed Window 5.84/0.54/0.38 | SimpleGlazing | [10 empty] | 1.0285 | 0.54 | 0.38
Fixed Window 5.84/0.61/0.47 | SimpleGlazing | [10 empty] | 1.0285 | 0.61 | 0.47
Fixed Window 5.84/0.70/0.60 | SimpleGlazing | [10 empty] | 1.0285 | 0.7 | 0.6
G01a 19mm gypsum board | StandardOpaqueMaterial | MediumSmooth | 0.74803 | 1.1094 | 0.67429 | 49.9424 | 0.26034 | 0.9 | 0.4 | 0.4
G05 25mm wood | StandardOpaqueMaterial | MediumSmooth | 1 | 1.04 | 0.96152 | 37.9562 | 0.38932 | 0.9 | 0.5 | 0.5
I01 25mm insulation board | StandardOpaqueMaterial | MediumRough | 1 | 0.208 | 4.8076 | 2.6844 | 0.289 | 0.9 | 0.6 | 0.6
I02 50mm insulation board | StandardOpaqueMaterial | MediumRough | 2 | 0.208 | 9.6152 | 2.6844 | 0.289 | 0.9 | 0.6 | 0.6
IEAD NonRes Roof Insulation-1.76 | StandardOpaqueMaterial | MediumRough | 2.9126 | 0.33974 | 8.5731 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-1.98 | StandardOpaqueMaterial | MediumRough | 3.3325 | 0.33974 | 9.8091 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.00 | StandardOpaqueMaterial | MediumRough | 3.3759 | 0.33974 | 9.9368 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.04 | StandardOpaqueMaterial | MediumRough | 3.4657 | 0.33974 | 10.2011 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.07 | StandardOpaqueMaterial | MediumRough | 3.5122 | 0.33974 | 10.3379 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.37 | StandardOpaqueMaterial | MediumRough | 4.0909 | 0.33974 | 12.0411 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.38 | StandardOpaqueMaterial | MediumRough | 4.1064 | 0.33974 | 12.0868 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.44 | StandardOpaqueMaterial | MediumRough | 4.2339 | 0.33974 | 12.4621 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.50 | StandardOpaqueMaterial | MediumRough | 4.3392 | 0.33974 | 12.7722 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.67 | StandardOpaqueMaterial | MediumRough | 4.6629 | 0.33974 | 13.7248 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.75 | StandardOpaqueMaterial | MediumRough | 4.8237 | 0.33974 | 14.1983 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.79 | StandardOpaqueMaterial | MediumRough | 4.908 | 0.33974 | 14.4464 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.85 | StandardOpaqueMaterial | MediumRough | 5.0133 | 0.33974 | 14.7564 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.93 | StandardOpaqueMaterial | MediumRough | 5.1777 | 0.33974 | 15.2401 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-2.99 | StandardOpaqueMaterial | MediumRough | 5.2736 | 0.33974 | 15.5226 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.03 | StandardOpaqueMaterial | MediumRough | 5.3729 | 0.33974 | 15.8148 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.38 | StandardOpaqueMaterial | MediumRough | 6.0309 | 0.33974 | 17.7514 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.51 | StandardOpaqueMaterial | MediumRough | 6.2823 | 0.33974 | 18.4914 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.65 | StandardOpaqueMaterial | MediumRough | 6.5542 | 0.33974 | 19.2917 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.66 | StandardOpaqueMaterial | MediumRough | 6.5933 | 0.33974 | 19.4069 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.72 | StandardOpaqueMaterial | MediumRough | 6.6986 | 0.33974 | 19.7169 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.83 | StandardOpaqueMaterial | MediumRough | 6.9011 | 0.33974 | 20.3128 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-3.97 | StandardOpaqueMaterial | MediumRough | 7.1705 | 0.33974 | 21.1059 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-4.41 | StandardOpaqueMaterial | MediumRough | 8.009 | 0.33974 | 23.5738 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD NonRes Roof Insulation-5.75 | StandardOpaqueMaterial | MediumRough | 10.5803 | 0.33974 | 31.1422 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD Roof Insulation R-3.47 IP | StandardOpaqueMaterial | MediumRough | 1.1788 | 0.33974 | 3.4698 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD Roof Insulation R-4.66 IP | StandardOpaqueMaterial | MediumRough | 1.5842 | 0.33974 | 4.663 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD Roof Insulation R-7.29 IP | StandardOpaqueMaterial | MediumRough | 2.4754 | 0.33974 | 7.286 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD Roof Insulation R-9.64 IP | StandardOpaqueMaterial | MediumRough | 3.2735 | 0.33974 | 9.6354 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD Roof Insulation R-14.76 IP | StandardOpaqueMaterial | MediumRough | 5.0131 | 0.33974 | 14.7557 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD Roof Insulation R-19.72 IP | StandardOpaqueMaterial | MediumRough | 6.6983 | 0.33974 | 19.716 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
M01 100mm brick | StandardOpaqueMaterial | MediumRough | 4 | 6.1708 | 0.64822 | 119.8617 | 0.18869 | 0.9 | 0.7 | 0.7
M11 100mm lightweight concrete | StandardOpaqueMaterial | MediumRough | 4 | 3.6747 | 1.0885 | 79.9078 | 0.20063 | 0.9 | 0.5 | 0.5
M15 200mm heavyweight concrete | StandardOpaqueMaterial | MediumRough | 8 | 13.5203 | 0.5917 | 139.8386 | 0.21496 | 0.9 | 0.5 | 0.5
Mass NonRes Wall Insulation-0.43 | StandardOpaqueMaterial | MediumRough | 0.017196 | 0.33974 | 0.050616 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.52 | StandardOpaqueMaterial | MediumRough | 0.18781 | 0.33974 | 0.55279 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.61 | StandardOpaqueMaterial | MediumRough | 0.3601 | 0.33974 | 1.0599 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.77 | StandardOpaqueMaterial | MediumRough | 0.66572 | 0.33974 | 1.9595 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.78 | StandardOpaqueMaterial | MediumRough | 0.69855 | 0.33974 | 2.0561 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.79 | StandardOpaqueMaterial | MediumRough | 0.70529 | 0.33974 | 2.076 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.93 | StandardOpaqueMaterial | MediumRough | 0.97671 | 0.33974 | 2.8749 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.96 | StandardOpaqueMaterial | MediumRough | 1.035 | 0.33974 | 3.0465 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-0.99 | StandardOpaqueMaterial | MediumRough | 1.0973 | 0.33974 | 3.2297 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.01 | StandardOpaqueMaterial | MediumRough | 1.13 | 0.33974 | 3.326 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.09 | StandardOpaqueMaterial | MediumRough | 1.2988 | 0.33974 | 3.8229 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.13 | StandardOpaqueMaterial | MediumRough | 1.3664 | 0.33974 | 4.022 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.17 | StandardOpaqueMaterial | MediumRough | 1.4386 | 0.33974 | 4.2343 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.22 | StandardOpaqueMaterial | MediumRough | 1.5317 | 0.33974 | 4.5083 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.26 | StandardOpaqueMaterial | MediumRough | 1.6154 | 0.33974 | 4.7547 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.30 | StandardOpaqueMaterial | MediumRough | 1.6867 | 0.33974 | 4.9648 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.41 | StandardOpaqueMaterial | MediumRough | 1.9066 | 0.33974 | 5.6118 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.43 | StandardOpaqueMaterial | MediumRough | 1.9508 | 0.33974 | 5.7419 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.47 | StandardOpaqueMaterial | MediumRough | 2.0198 | 0.33974 | 5.9452 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.69 | StandardOpaqueMaterial | MediumRough | 2.4554 | 0.33974 | 7.2273 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.76 | StandardOpaqueMaterial | MediumRough | 2.5861 | 0.33974 | 7.6119 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-1.96 | StandardOpaqueMaterial | MediumRough | 2.9636 | 0.33974 | 8.7231 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-2.20 | StandardOpaqueMaterial | MediumRough | 3.4355 | 0.33974 | 10.1121 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-2.23 | StandardOpaqueMaterial | MediumRough | 3.4892 | 0.33974 | 10.2703 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-2.48 | StandardOpaqueMaterial | MediumRough | 3.9738 | 0.33974 | 11.6966 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-2.89 | StandardOpaqueMaterial | MediumRough | 4.7583 | 0.33974 | 14.0057 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass NonRes Wall Insulation-3.75 | StandardOpaqueMaterial | MediumRough | 6.4174 | 0.33974 | 18.8891 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass Wall Insulation R-4.23 IP | StandardOpaqueMaterial | MediumRough | 1.4385 | 0.33974 | 4.234 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass Wall Insulation R-5.74 IP | StandardOpaqueMaterial | MediumRough | 1.9507 | 0.33974 | 5.7416 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass Wall Insulation R-7.23 IP | StandardOpaqueMaterial | MediumRough | 2.4553 | 0.33974 | 7.2269 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass Wall Insulation R-8.72 IP | StandardOpaqueMaterial | MediumRough | 2.9634 | 0.33974 | 8.7226 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass Wall Insulation R-10.11 IP | StandardOpaqueMaterial | MediumRough | 3.4353 | 0.33974 | 10.1115 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass Wall Insulation R-11.70 IP | StandardOpaqueMaterial | MediumRough | 3.9736 | 0.33974 | 11.696 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass Wall Insulation R-16.84 IP | StandardOpaqueMaterial | MediumRough | 5.722 | 0.33974 | 16.8423 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
MAT-CC05 4 HW CONCRETE | StandardOpaqueMaterial | Rough | 4 | 9.0898 | 0.44005 | 139.8386 | 0.19987 | 0.9 | 0.85 | 0.85
MAT-CC05 8 HW CONCRETE | StandardOpaqueMaterial | Rough | 8 | 9.0898 | 0.88011 | 139.8386 | 0.19987 | 0.9 | 0.85 | 0.85
MAT-SHEATH | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.54 | StandardOpaqueMaterial | MediumRough | 0.60417 | 0.33974 | 1.7783 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.57 | StandardOpaqueMaterial | MediumRough | 0.66572 | 0.33974 | 1.9595 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.59 | StandardOpaqueMaterial | MediumRough | 0.69855 | 0.33974 | 2.0561 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.61 | StandardOpaqueMaterial | MediumRough | 0.73287 | 0.33974 | 2.1571 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.77 | StandardOpaqueMaterial | MediumRough | 1.035 | 0.33974 | 3.0465 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.80 | StandardOpaqueMaterial | MediumRough | 1.0973 | 0.33974 | 3.2297 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.81 | StandardOpaqueMaterial | MediumRough | 1.13 | 0.33974 | 3.326 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.90 | StandardOpaqueMaterial | MediumRough | 1.2988 | 0.33974 | 3.8229 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.91 | StandardOpaqueMaterial | MediumRough | 1.312 | 0.33974 | 3.8618 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.94 | StandardOpaqueMaterial | MediumRough | 1.3664 | 0.33974 | 4.022 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.98 | StandardOpaqueMaterial | MediumRough | 1.4536 | 0.33974 | 4.2785 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.02 | StandardOpaqueMaterial | MediumRough | 1.5317 | 0.33974 | 4.5083 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.10 | StandardOpaqueMaterial | MediumRough | 1.6867 | 0.33974 | 4.9648 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.12 | StandardOpaqueMaterial | MediumRough | 1.724 | 0.33974 | 5.0745 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.16 | StandardOpaqueMaterial | MediumRough | 1.802 | 0.33974 | 5.3041 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.22 | StandardOpaqueMaterial | MediumRough | 1.9066 | 0.33974 | 5.6118 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.24 | StandardOpaqueMaterial | MediumRough | 1.9508 | 0.33974 | 5.7419 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.37 | StandardOpaqueMaterial | MediumRough | 2.1952 | 0.33974 | 6.4614 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.57 | StandardOpaqueMaterial | MediumRough | 2.5861 | 0.33974 | 7.6119 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.72 | StandardOpaqueMaterial | MediumRough | 2.8815 | 0.33974 | 8.4815 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.79 | StandardOpaqueMaterial | MediumRough | 3.006 | 0.33974 | 8.848 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-1.96 | StandardOpaqueMaterial | MediumRough | 3.3319 | 0.33974 | 9.8072 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-2.25 | StandardOpaqueMaterial | MediumRough | 3.9074 | 0.33974 | 11.501 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-2.52 | StandardOpaqueMaterial | MediumRough | 4.4155 | 0.33974 | 12.9968 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-2.85 | StandardOpaqueMaterial | MediumRough | 5.0464 | 0.33974 | 14.8537 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-3.72 | StandardOpaqueMaterial | MediumRough | 6.7387 | 0.33974 | 19.8347 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-4.14 IP | StandardOpaqueMaterial | MediumRough | 1.4044 | 0.33974 | 4.1339 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-6.16 IP | StandardOpaqueMaterial | MediumRough | 2.0934 | 0.33974 | 6.1618 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-6.83 IP | StandardOpaqueMaterial | MediumRough | 2.3201 | 0.33974 | 6.8292 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-7.55 IP | StandardOpaqueMaterial | MediumRough | 2.5646 | 0.33974 | 7.5487 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-9.45 IP | StandardOpaqueMaterial | MediumRough | 3.2112 | 0.33974 | 9.4518 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-10.60 IP | StandardOpaqueMaterial | MediumRough | 3.6026 | 0.33974 | 10.6039 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-13.19 IP | StandardOpaqueMaterial | MediumRough | 4.4818 | 0.33974 | 13.1919 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-16.24 IP | StandardOpaqueMaterial | MediumRough | 5.5184 | 0.33974 | 16.243 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Decking | StandardOpaqueMaterial | MediumSmooth | 0.059055 | 312.0478 | 0.00018925 | 479.4467 | 0.099933 | 0.9 | 0.6 | 0.6
Metal Roofing | StandardOpaqueMaterial | MediumSmooth | 0.059055 | 312.0478 | 0.00018925 | 479.4467 | 0.099933 | 0.9 | 0.6 | 0.6
Metal Semi-Cond Roof Insulation-1.05 | StandardOpaqueMaterial | MediumRough | 1.6641 | 0.33974 | 4.8981 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-1.76 | StandardOpaqueMaterial | MediumRough | 3.0272 | 0.33974 | 8.9102 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-1.81 | StandardOpaqueMaterial | MediumRough | 3.1322 | 0.33974 | 9.2195 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-1.87 | StandardOpaqueMaterial | MediumRough | 3.2376 | 0.33974 | 9.5295 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.00 | StandardOpaqueMaterial | MediumRough | 3.4905 | 0.33974 | 10.2739 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.38 | StandardOpaqueMaterial | MediumRough | 4.2209 | 0.33974 | 12.4239 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.44 | StandardOpaqueMaterial | MediumRough | 4.3484 | 0.33974 | 12.7993 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.50 | StandardOpaqueMaterial | MediumRough | 4.4538 | 0.33974 | 13.1093 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.67 | StandardOpaqueMaterial | MediumRough | 4.7774 | 0.33974 | 14.062 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.75 | StandardOpaqueMaterial | MediumRough | 4.9383 | 0.33974 | 14.5355 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-2.99 | StandardOpaqueMaterial | MediumRough | 5.3882 | 0.33974 | 15.8597 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.03 | StandardOpaqueMaterial | MediumRough | 5.4875 | 0.33974 | 16.1519 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.38 | StandardOpaqueMaterial | MediumRough | 6.1454 | 0.33974 | 18.0886 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.65 | StandardOpaqueMaterial | MediumRough | 6.6687 | 0.33974 | 19.6289 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.66 | StandardOpaqueMaterial | MediumRough | 6.7078 | 0.33974 | 19.7441 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.83 | StandardOpaqueMaterial | MediumRough | 7.0156 | 0.33974 | 20.6499 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-3.97 | StandardOpaqueMaterial | MediumRough | 7.2851 | 0.33974 | 21.443 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-4.41 | StandardOpaqueMaterial | MediumRough | 8.1235 | 0.33974 | 23.9109 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Semi-Cond Roof Insulation-5.75 | StandardOpaqueMaterial | MediumRough | 10.6948 | 0.33974 | 31.4793 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-5.21 IP | StandardOpaqueMaterial | MediumRough | 1.7692 | 0.33974 | 5.2076 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-9.53 IP | StandardOpaqueMaterial | MediumRough | 3.2373 | 0.33974 | 9.5289 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-11.27 IP | StandardOpaqueMaterial | MediumRough | 3.8281 | 0.33974 | 11.2678 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-13.11 IP | StandardOpaqueMaterial | MediumRough | 4.4535 | 0.33974 | 13.1085 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-14.60 IP | StandardOpaqueMaterial | MediumRough | 4.9616 | 0.33974 | 14.6042 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-17.40 IP | StandardOpaqueMaterial | MediumRough | 5.912 | 0.33974 | 17.4014 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-19.63 IP | StandardOpaqueMaterial | MediumRough | 6.6683 | 0.33974 | 19.6278 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Insulation R-27.79 IP | StandardOpaqueMaterial | MediumRough | 9.4417 | 0.33974 | 27.7911 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Siding | StandardOpaqueMaterial | Smooth | 0.059055 | 311.7289 | 0.00018944 | 479.9998 | 0.097927 | 0.9 | 0.6 | 0.6
Roof Insulation [18] | StandardOpaqueMaterial | MediumRough | 6.6654 | 0.33974 | 19.619 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [19] | StandardOpaqueMaterial | MediumRough | 7.3543 | 0.33974 | 21.6469 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [21] | StandardOpaqueMaterial | MediumRough | 8.2874 | 0.33974 | 24.3934 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [22] | StandardOpaqueMaterial | MediumRough | 9.2835 | 0.33974 | 27.3252 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [24] | StandardOpaqueMaterial | MediumRough | 10.2402 | 0.33974 | 30.1411 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [25] | StandardOpaqueMaterial | MediumRough | 10.3543 | 0.33974 | 30.4772 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [26] | StandardOpaqueMaterial | MediumRough | 11.5787 | 0.33974 | 34.0812 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Insulation [27] | StandardOpaqueMaterial | MediumRough | 11.6929 | 0.33974 | 34.4172 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Membrane | StandardOpaqueMaterial | VeryRough | 0.37402 | 1.1094 | 0.33715 | 69.9998 | 0.34872 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.73 | StandardOpaqueMaterial | MediumRough | 0.79836 | 0.33974 | 2.3499 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.77 | StandardOpaqueMaterial | MediumRough | 0.85991 | 0.33974 | 2.5311 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.79 | StandardOpaqueMaterial | MediumRough | 0.89947 | 0.33974 | 2.6475 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.80 | StandardOpaqueMaterial | MediumRough | 0.92705 | 0.33974 | 2.7287 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.96 | StandardOpaqueMaterial | MediumRough | 1.2292 | 0.33974 | 3.6181 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.99 | StandardOpaqueMaterial | MediumRough | 1.2914 | 0.33974 | 3.8013 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.01 | StandardOpaqueMaterial | MediumRough | 1.3242 | 0.33974 | 3.8976 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.09 | StandardOpaqueMaterial | MediumRough | 1.493 | 0.33974 | 4.3945 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.10 | StandardOpaqueMaterial | MediumRough | 1.5062 | 0.33974 | 4.4333 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.13 | StandardOpaqueMaterial | MediumRough | 1.5606 | 0.33974 | 4.5936 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.17 | StandardOpaqueMaterial | MediumRough | 1.6477 | 0.33974 | 4.85 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.22 | StandardOpaqueMaterial | MediumRough | 1.7259 | 0.33974 | 5.0799 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.30 | StandardOpaqueMaterial | MediumRough | 1.8809 | 0.33974 | 5.5363 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.36 | StandardOpaqueMaterial | MediumRough | 1.9962 | 0.33974 | 5.8757 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.41 | StandardOpaqueMaterial | MediumRough | 2.1008 | 0.33974 | 6.1834 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.42 | StandardOpaqueMaterial | MediumRough | 2.1227 | 0.33974 | 6.2479 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.76 | StandardOpaqueMaterial | MediumRough | 2.7803 | 0.33974 | 8.1835 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.92 | StandardOpaqueMaterial | MediumRough | 3.0757 | 0.33974 | 9.0531 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-1.98 | StandardOpaqueMaterial | MediumRough | 3.2002 | 0.33974 | 9.4195 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-2.10 | StandardOpaqueMaterial | MediumRough | 3.4274 | 0.33974 | 10.0884 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-2.15 | StandardOpaqueMaterial | MediumRough | 3.5261 | 0.33974 | 10.3787 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-2.44 | StandardOpaqueMaterial | MediumRough | 4.1015 | 0.33974 | 12.0726 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-2.71 | StandardOpaqueMaterial | MediumRough | 4.6097 | 0.33974 | 13.5684 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-2.75 | StandardOpaqueMaterial | MediumRough | 4.6914 | 0.33974 | 13.8088 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-3.04 | StandardOpaqueMaterial | MediumRough | 5.2406 | 0.33974 | 15.4252 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-3.21 | StandardOpaqueMaterial | MediumRough | 5.5601 | 0.33974 | 16.3657 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-3.91 | StandardOpaqueMaterial | MediumRough | 6.9328 | 0.33974 | 20.4063 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame Wall Insulation R-1.02 IP | StandardOpaqueMaterial | MediumRough | 0.34789 | 0.33974 | 1.024 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame Wall Insulation R-6.25 IP | StandardOpaqueMaterial | MediumRough | 2.1226 | 0.33974 | 6.2476 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame Wall Insulation R-10.09 IP | StandardOpaqueMaterial | MediumRough | 3.4272 | 0.33974 | 10.0878 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame Wall Insulation R-13.81 IP | StandardOpaqueMaterial | MediumRough | 4.6912 | 0.33974 | 13.8081 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame Wall Insulation R-21.99 IP | StandardOpaqueMaterial | MediumRough | 7.4718 | 0.33974 | 21.9926 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame Wall Insulation R-25.21 IP | StandardOpaqueMaterial | MediumRough | 8.5649 | 0.33974 | 25.2101 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Theoretical Glass [167] | StandardGlazing |  | 0.11811 | 14.6109 | 0.068442 | [9 empty] | SpectralAverage | 0.2374 | 0.7126 | 0.7126 | 0.2512 | 0.6988 | 0.6988 | 0 | 0.985 | 0.985 | 1 | FALSE
Theoretical Glass [197] | StandardGlazing |  | 0.11811 | 0.28774 | 3.4754 | [9 empty] | SpectralAverage | 0.2349 | 0.7151 | 0.7151 | 0.2512 | 0.6988 | 0.6988 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [202] | StandardGlazing |  | 0.11811 | 0.13312 | 7.5119 | [9 empty] | SpectralAverage | 0.2325 | 0.7175 | 0.7175 | 0.3192 | 0.6308 | 0.6308 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [207] | StandardGlazing |  | 0.11811 | 0.092215 | 10.8442 | [9 empty] | SpectralAverage | 0.3311 | 0.6189 | 0.6189 | 0.44 | 0.51 | 0.51 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [216] | StandardGlazing |  | 0.11811 | 0.092215 | 10.8442 | [9 empty] | SpectralAverage | 0.3801 | 0.5699 | 0.5699 | 0.5079 | 0.4421 | 0.4421 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [221] | StandardGlazing |  | 0.11811 | 0.061708 | 16.2054 | [9 empty] | SpectralAverage | 0.4296 | 0.5204 | 0.5204 | 0.4503 | 0.4997 | 0.4997 | 0 | 0.9 | 0.9 | 1 | FALSE
Wall Insulation [31] | StandardOpaqueMaterial | MediumRough | 1.3268 | 0.29953 | 4.4296 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [32] | StandardOpaqueMaterial | MediumRough | 3.5315 | 0.31201 | 11.3187 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [33] | StandardOpaqueMaterial | MediumRough | 3.0748 | 0.31201 | 9.8549 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [34] | StandardOpaqueMaterial | MediumRough | 4.3465 | 0.31201 | 13.9307 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [35] | StandardOpaqueMaterial | MediumRough | 1.7795 | 0.29953 | 5.9411 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [36] | StandardOpaqueMaterial | MediumRough | 2.2283 | 0.29953 | 7.4396 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [37] | StandardOpaqueMaterial | MediumRough | 2.6811 | 0.29953 | 8.9512 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [38] | StandardOpaqueMaterial | MediumRough | 5.4961 | 0.31201 | 17.6152 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [39] | StandardOpaqueMaterial | MediumRough | 4.6614 | 0.31201 | 14.9401 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [40] | StandardOpaqueMaterial | MediumRough | 3.126 | 0.29953 | 10.4364 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [41] | StandardOpaqueMaterial | MediumRough | 5.5315 | 0.31201 | 17.7288 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [42] | StandardOpaqueMaterial | MediumRough | 3.5984 | 0.29953 | 12.0137 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [43] | StandardOpaqueMaterial | MediumRough | 6.2323 | 0.31201 | 19.9749 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wall Insulation [44] | StandardOpaqueMaterial | MediumRough | 4.3465 | 0.29953 | 14.5111 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wall Insulation [46] | StandardOpaqueMaterial | MediumRough | 6.4331 | 0.29953 | 21.4775 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wood Frame NonRes Wall Insulation-0.73 | StandardOpaqueMaterial | MediumRough | 0.79836 | 0.33974 | 2.3499 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-0.80 | StandardOpaqueMaterial | MediumRough | 0.92705 | 0.33974 | 2.7287 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.10 | StandardOpaqueMaterial | MediumRough | 1.5062 | 0.33974 | 4.4333 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.17 | StandardOpaqueMaterial | MediumRough | 1.6477 | 0.33974 | 4.85 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.36 | StandardOpaqueMaterial | MediumRough | 1.9962 | 0.33974 | 5.8757 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.76 | StandardOpaqueMaterial | MediumRough | 2.7803 | 0.33974 | 8.1835 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.92 | StandardOpaqueMaterial | MediumRough | 3.0757 | 0.33974 | 9.0531 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-1.98 | StandardOpaqueMaterial | MediumRough | 3.2002 | 0.33974 | 9.4195 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-2.15 | StandardOpaqueMaterial | MediumRough | 3.5261 | 0.33974 | 10.3787 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-2.44 | StandardOpaqueMaterial | MediumRough | 4.1015 | 0.33974 | 12.0726 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-2.71 | StandardOpaqueMaterial | MediumRough | 4.6097 | 0.33974 | 13.5684 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-3.04 | StandardOpaqueMaterial | MediumRough | 5.2406 | 0.33974 | 15.4252 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-3.45 | StandardOpaqueMaterial | MediumRough | 6.0446 | 0.33974 | 17.7918 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame NonRes Wall Insulation-3.91 | StandardOpaqueMaterial | MediumRough | 6.9328 | 0.33974 | 20.4063 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame Wall Insulation R-1.61 IP | StandardOpaqueMaterial | MediumRough | 0.54621 | 0.33974 | 1.6077 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame Wall Insulation R-9.42 IP | StandardOpaqueMaterial | MediumRough | 3.2 | 0.33974 | 9.419 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame Wall Insulation R-13.81 IP | StandardOpaqueMaterial | MediumRough | 4.6912 | 0.33974 | 13.8081 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame Wall Insulation R-17.79 IP | StandardOpaqueMaterial | MediumRough | 6.0443 | 0.33974 | 17.7909 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame Wall Insulation R-25.96 IP | StandardOpaqueMaterial | MediumRough | 8.8199 | 0.33974 | 25.9609 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Siding | StandardOpaqueMaterial | MediumSmooth | 0.3937 | 0.76268 | 0.51621 | 33.9995 | 0.289 | 0.9 | 0.78 | 0.78
Air - Cavity - Wall Roof Ceiling - 4 in. or more | StandardOpaqueMaterial |  | 6 | 6.5196 | 0.92 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | JA4 | Air | Air - Cavity - Wall Roof Ceiling - 4 in. or more
Air - Metal Wall Framing - 16 or 24 in. OC | StandardOpaqueMaterial |  | 5.5 | 8.46 | 0.65 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | JA4 | Air | Air - Metal Wall Framing - 16 or 24 in. OC
Air - Wall - 1/2 in. | StandardOpaqueMaterial |  | 0.5 | 0.6504 | 0.77 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Wall - 1/2 in.
Air - Wall - 3/4 in. | StandardOpaqueMaterial |  | 0.75 | 0.8904 | 0.84 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Wall - 3/4 in.
Air - Wall - 1 1/2 in. | StandardOpaqueMaterial |  | 1.5 | 1.7196 | 0.87 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Wall - 1 1/2 in.
Air - Wall - 3 1/2 in. | StandardOpaqueMaterial |  | 3.5 | 4.1196 | 0.85 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Wall - 3 1/2 in.
Air - Ceiling - 1/2 in. | StandardOpaqueMaterial |  | 0.5 | 0.6804 | 0.73 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Ceiling - 1/2 in.
Air - Ceiling - 3/4 in. | StandardOpaqueMaterial |  | 0.75 | 0.9996 | 0.75 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Ceiling - 3/4 in.
Air - Ceiling - 1 1/2 in. | StandardOpaqueMaterial |  | 1.5 | 1.95 | 0.77 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Ceiling - 1 1/2 in.
Air - Ceiling - 3 1/2 in. | StandardOpaqueMaterial |  | 3.5 | 4.38 | 0.8 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Ceiling - 3 1/2 in.
Air - Roof - 1/2 in. | StandardOpaqueMaterial |  | 0.5 | 0.66 | 0.76 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Roof - 1/2 in.
Air - Roof - 3/4 in. | StandardOpaqueMaterial |  | 0.75 | 0.93 | 0.81 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Roof - 3/4 in.
Air - Roof - 1 1/2 in. | StandardOpaqueMaterial |  | 1.5 | 1.8804 | 0.8 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Roof - 1 1/2 in.
Air - Roof - 3 1/2 in. | StandardOpaqueMaterial |  | 3.5 | 4.2696 | 0.82 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Roof - 3 1/2 in.
Air - Floor - 1/2 in. | StandardOpaqueMaterial |  | 0.5 | 0.6504 | 0.77 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Floor - 1/2 in.
Air - Floor - 3/4 in. | StandardOpaqueMaterial |  | 0.75 | 0.8796 | 0.85 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Floor - 3/4 in.
Air - Floor - 1 1/2 in. | StandardOpaqueMaterial |  | 1.5 | 1.5996 | 0.94 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Floor - 1 1/2 in.
Air - Floor - 3 1/2 in. | StandardOpaqueMaterial |  | 3.5 | 3.5004 | 1 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Floor - 3 1/2 in.
Fiber cement board - 63 lb/ft3 - 1/3 in. | StandardOpaqueMaterial | Smooth | 0.31 | 1.2996 | 0.24 | 63 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Fiber cement board - 63 lb/ft3 - 1/3 in.
Fiber cement board - 88 lb/ft3 - 1/3 in. | StandardOpaqueMaterial | Smooth | 0.31 | 1.7004 | 0.18 | 88 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Fiber cement board - 88 lb/ft3 - 1/3 in.
Fiber cement board - 88 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.47 | 1.7004 | 0.28 | 88 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Fiber cement board - 88 lb/ft3 - 1/2 in.
Fiberboard sheathing - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.4896 | 1.03 | 24.96 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Fiberboard sheathing - 1/2 in.
Gypsum Board - 3/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.38 | 1.1 | 0.32 | 40 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Gypsum Board - 3/8 in.
Gypsum Board - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 1.1 | 0.45 | 40 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Gypsum Board - 1/2 in.
Gypsum Board - 5/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.63 | 1.1 | 0.56 | 40 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Gypsum Board - 5/8 in.
Gypsum Board - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 1.1 | 0.68 | 40 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Gypsum Board - 3/4 in.
Hard Board - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 0.72 | 1.04 | 50 | 0.31 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Hard Board - 3/4 in.
Hardboard - HDF - 50 lb/ft3 - 3/8 in. | StandardOpaqueMaterial | Smooth | 0.38 | 0.7296 | 0.51 | 50 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Hardboard - HDF - 50 lb/ft3 - 3/8 in.
Hardboard - HDF - 50 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.7296 | 0.68 | 50 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Hardboard - HDF - 50 lb/ft3 - 1/2 in.
Hardboard - HDF - 50 lb/ft3 - 5/8 in. | StandardOpaqueMaterial | Smooth | 0.63 | 0.7296 | 0.86 | 50 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Hardboard - HDF - 50 lb/ft3 - 5/8 in.
Hardboard - HDF - 50 lb/ft3 - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 0.7296 | 1.03 | 50 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Hardboard - HDF - 50 lb/ft3 - 3/4 in.
HB Part. Brd - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 1.18 | 0.64 | 50 | 0.31 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | HB Part. Brd - 3/4 in.
Metal Deck - 1/16 in. | StandardOpaqueMaterial | Smooth | 0.0625 | 314.4 | 0 | 488.22 | 0.12 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Metal Deck - 1/16 in.
Metal Siding - 1/16 in. | StandardOpaqueMaterial | Smooth | 0.0625 | 314.4 | 0 | 488.22 | 0.12 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Metal Siding - 1/16 in.
OSB - Oriented Strand Board - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.6204 | 0.8 | 41 | 0.45 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | OSB - Oriented Strand Board - 1/2 in.
OSB - Oriented Strand Board - 5/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.63 | 0.7596 | 0.82 | 41 | 0.45 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | OSB - Oriented Strand Board - 5/8 in.
OSB - Oriented Strand Board - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.9096 | 0.83 | 41 | 0.45 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | OSB - Oriented Strand Board - 3/4 in.
Plywood - 1/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.25 | 0.8004 | 0.31 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 1/4 in.
Plywood - 3/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.38 | 0.8004 | 0.47 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 3/8 in.
Plywood - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.8004 | 0.63 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 1/2 in.
Plywood - 5/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.63 | 0.8004 | 0.78 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 5/8 in.
Plywood - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.8004 | 0.94 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 3/4 in.
Plywood - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 0.8004 | 1.25 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 1 in.
Plywood - 1 1/4 in. | StandardOpaqueMaterial | MediumSmooth | 1.25 | 0.8004 | 1.56 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC RJ | Bldg Board and Siding | Plywood - 1 1/4 in.
Plywood - 1 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 1.5 | 0.8004 | 1.88 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC RJ | Bldg Board and Siding | Plywood - 1 1/2 in.
Shingles - Asbestos cement - lapped - 1/4 in. | StandardOpaqueMaterial | VeryRough | 0.25 | 1.1904 | 0.21 | 120 | 0.24 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Shingles - Asbestos cement - lapped - 1/4 in.
Shingles - Asphalt roll siding - 1/4 in. | StandardOpaqueMaterial | VeryRough | 0.25 | 1.6704 | 0.15 | 70 | 0.36 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Shingles - Asphalt roll siding - 1/4 in.
Shingles - Wood - 16 in. - 7 1/2 in. exposure - 1/2 in. | StandardOpaqueMaterial | MediumRough | 0.5 | 0.57 | 0.87 | 22 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Shingles - Wood - 16 in. - 7 1/2 in. exposure - 1/2 in.
Shingles - Wood - plus insulated backer board Siding - 5/16 in. | StandardOpaqueMaterial | MediumRough | 0.31 | 0.2196 | 1.4 | 22 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Shingles - Wood - plus insulated backer board Siding - 5/16 in.
Wood shingles - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 0.8304 | 0.9 | 36.94 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Wood shingles - 3/4 in.
Wood shingles - plain and plastic film faced - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 0.8004 | 0.94 | 22 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Wood shingles - plain and plastic film faced - 3/4 in.
Siding - Asphalt insulating siding - 1/2 in. bed - 1/2 in. | StandardOpaqueMaterial | VeryRough | 0.5 | 0.3396 | 1.46 | 70 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Siding - Asphalt insulating siding - 1/2 in. bed - 1/2 in.
Siding - Wood - bevel - 10 in. - lapped - 3/4 in. | StandardOpaqueMaterial | Rough | 0.75 | 0.7104 | 1.05 | 22 | 0.28 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Siding - Wood - bevel - 10 in. - lapped - 3/4 in.
Synthetic Stucco - EIFS finish - 1 in. | StandardOpaqueMaterial | Smooth | 1 | 0.2496 | 4 | 1.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Synthetic Stucco - EIFS finish - 1 in.
Building Paper - 1/16 in. | StandardOpaqueMaterial | MediumSmooth | 0.06 | 2.0004 | 0.03 | 70 | 0.3 | [19 empty] | CEC Title24-2013 | CEC Doug | Building Membrane | Building Paper - 1/16 in.
Roofing felt - 1/8 in. | StandardOpaqueMaterial | VeryRough | 0.13 | 8.3004 | 0.02 | 141 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Building Membrane | Roofing felt - 1/8 in.
Vapor permeable felt - 1/8 in. | StandardOpaqueMaterial | Rough | 0.13 | 2.0796 | 0.06 | 22 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Building Membrane | Vapor permeable felt - 1/8 in.
Vapor seal - 2 layers of mopped 15 lb felt - 1/4 in. | StandardOpaqueMaterial | Rough | 0.25 | 2.0796 | 0.12 | 22 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Building Membrane | Vapor seal - 2 layers of mopped 15 lb felt - 1/4 in.
Vapor seal - plastic film - 1/16 in. | StandardOpaqueMaterial | Rough | 0.63 | 62.4996 | 0.01 | 30 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Building Membrane | Vapor seal - plastic film - 1/16 in.
Concrete - 80 lb/ft3 - 2 in. | StandardOpaqueMaterial | MediumRough | 2 | 3.6804 | 0.54 | 79.87 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 2 in.
Concrete - 80 lb/ft3 - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 3.6804 | 1.09 | 79.87 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 4 in.
Concrete - 80 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.6804 | 1.63 | 79.87 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 6 in.
Concrete - 80 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.6804 | 2.17 | 79.87 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 8 in.
Concrete - 80 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 3.6804 | 2.72 | 79.87 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 10 in.
Concrete - 80 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 3.6804 | 3.26 | 79.87 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 12 in.
Concrete - 100 lb/ft3 - 2 in. | StandardOpaqueMaterial | MediumRough | 2 | 6.2496 | 0.32 | 100 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 2 in.
Concrete - 100 lb/ft3 - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 6.2496 | 0.64 | 100 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 4 in.
Concrete - 100 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 6.2496 | 0.97 | 100 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 6 in.
Concrete - 100 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 6.2496 | 1.29 | 100 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 8 in.
Concrete - 100 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 6.2496 | 1.61 | 100 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 10 in.
Concrete - 100 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 6.2496 | 1.93 | 100 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 12 in.
Concrete - 140 lb/ft3 - 2 in. | StandardOpaqueMaterial | MediumRough | 2 | 13.53 | 0.15 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 2 in.
Concrete - 140 lb/ft3 - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 13.53 | 0.3 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 4 in.
Concrete - 140 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 13.53 | 0.44 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 6 in.
Concrete - 140 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 13.53 | 0.59 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 8 in.
Concrete - 140 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 13.53 | 0.74 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 10 in.
Concrete - 140 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 13.53 | 0.89 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 12 in.
Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 15.8604 | 0.851 | 133.44 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in.
Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 14.7504 | 0.949 | 128.71 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 2 in.
Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 11.9904 | 1.251 | 120.2 | 0.12 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 3 in.
Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 10.3404 | 1.548 | 112.75 | 0.12 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 4 in.
Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 8.3604 | 2.153 | 100.33 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 6 in.
Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 15.8604 | 0.851 | 133.44 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in.
Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 25.1796 | 0.556 | 128.71 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 2 in.
Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 31.5096 | 0.476 | 120.2 | 0.12 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 3 in.
Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 38.37 | 0.417 | 112.75 | 0.12 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 4 in.
Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 54.0504 | 0.333 | 100.33 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 6 in.
Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 10.7904 | 1.251 | 133.44 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in.
Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 9.66 | 1.449 | 128.71 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 2 in.
Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 7.32 | 2.049 | 120.2 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 3 in.
Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 6.0396 | 2.647 | 112.75 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 4 in.
Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 4.7904 | 3.758 | 100.33 | 0.12 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 6 in.
Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 11.7396 | 1.15 | 133.44 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in.
Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 9.66 | 1.449 | 128.71 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 2 in.
Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 7.6896 | 1.951 | 120.2 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 3 in.
Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 6.5304 | 2.45 | 112.75 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 4 in.
Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 5.0604 | 3.555 | 100.33 | 0.12 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 6 in.
Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 1.8396 | 7.347 | 133.44 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in.
Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 1.4496 | 9.68 | 128.71 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 2 in.
Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 1.05 | 14.302 | 120.2 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 3 in.
Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 0.8496 | 18.83 | 112.75 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 4 in.
Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 0.63 | 28.562 | 100.33 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 6 in.
Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 2.5704 | 5.248 | 133.44 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in.
Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 2.01 | 6.963 | 128.71 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 2 in.
Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 1.4796 | 10.139 | 120.2 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 3 in.
Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 1.1904 | 13.436 | 112.75 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 4 in.
Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 0.9 | 19.983 | 100.33 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 6 in.
Acoustic Tile - 3/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.38 | 0.39 | 0.95 | 18 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Finish Materials | Acoustic Tile - 3/8 in.
Acoustic Tile - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.3996 | 1.26 | 18 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Finish Materials | Acoustic Tile - 1/2 in.
Acoustic Tile - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.3996 | 1.89 | 18 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Finish Materials | Acoustic Tile - 3/4 in.
Carpet - 3/4 in. | StandardOpaqueMaterial | Rough | 0.75 | 0.3156 | 2.38 | 18 | 0.33 | [19 empty] | CEC Title24-2013 | CEC Doug | Finish Materials | Carpet - 3/4 in.
Linoleum/cork tile - 1/4 in. | StandardOpaqueMaterial | MediumRough | 0.25 | 0.51 | 0.49 | 29 | 0.45 | [19 empty] | CEC Title24-2013 | AEC | Finish Materials | Linoleum/cork tile - 1/4 in.
Rubber tile - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 0.3396 | 2.94 | 119 | 0.48 | [19 empty] | CEC Title24-2013 | AEC | Finish Materials | Rubber tile - 1 in.
Slate or tile - 1/2 in. | StandardOpaqueMaterial | VeryRough | 0.5 | 11.0304 | 0.05 | 119.81 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Finish Materials | Slate or tile - 1/2 in.
Terrazzo - 1 in. | StandardOpaqueMaterial | Rough | 1 | 12.5004 | 0.08 | 160 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Finish Materials | Terrazzo - 1 in.
Insulating Concrete Forms - 1 1/2 in. Polyurethane Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 9 | 0.4704 | 19.13 | 100.33 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 1 1/2 in. Polyurethane Ins. each side - concrete 6 in.
Insulating Concrete Forms - 1 1/2 in. Polyurethane Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 11 | 0.57 | 19.318 | 109.36 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 1 1/2 in. Polyurethane Ins. each side - concrete 8 in.
Insulating Concrete Forms - 2 in. Polyurethane Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 10 | 0.4404 | 22.72 | 90.4 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. Polyurethane Ins. each side - concrete 6 in.
Insulating Concrete Forms - 2 in. Polyurethane Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 12 | 0.5196 | 23.09 | 100.33 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. Polyurethane Ins. each side - concrete 8 in.
Insulating Concrete Forms - 4 1/2 in. Polyurethane Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 15 | 0.3504 | 42.81 | 60.6 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 1/2 in. Polyurethane Ins. each side - concrete 6 in.
Insulating Concrete Forms - 4 1/2 in. Polyurethane Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 17 | 0.3996 | 42.54 | 71.12 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 1/2 in. Polyurethane Ins. each side - concrete 8 in.
Insulating Concrete Forms - 2 in. EPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 10 | 0.6096 | 16.4 | 90.4 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. EPS Ins. each side - concrete 6 in.
Insulating Concrete Forms - 2 in. EPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 12 | 0.72 | 16.67 | 100.33 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. EPS Ins. each side - concrete 8 in.
Insulating Concrete Forms - 2 1/2 in. EPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 11 | 0.51648 | 21.3 | 76.81 | 0.23 | [19 empty] | CEC Title24-2013 | CEC RJ | ICF Wall | Insulating Concrete Forms - 2 1/2 in. EPS Ins. each side - concrete 6 in.
Insulating Concrete Forms - 2 1/2 in. EPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 13 | 0.60612 | 21.45 | 86.54 | 0.22 | [19 empty] | CEC Title24-2013 | CEC RJ | ICF Wall | Insulating Concrete Forms - 2 1/2 in. EPS Ins. each side - concrete 8 in.
Insulating Concrete Forms - 3 in. EPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 12 | 0.5004 | 23.98 | 75.5 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 3 in. EPS Ins. each side - concrete 6 in.
Insulating Concrete Forms - 3 in. EPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 14 | 0.57 | 24.551 | 86.14 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 3 in. EPS Ins. each side - concrete 8 in.
Insulating Concrete Forms - 4 in. EPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 14 | 0.4296 | 32.59 | 64.86 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 in. EPS Ins. each side - concrete 6 in.
Insulating Concrete Forms - 4 in. EPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 16 | 0.5004 | 31.97 | 75.5 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 in. EPS Ins. each side - concrete 8 in.
Insulating Concrete Forms - 2 in. XPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 10 | 0.4704 | 21.26 | 90.4 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. XPS Ins. each side - concrete 6 in.
Insulating Concrete Forms - 2 in. XPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 12 | 0.57 | 21.05 | 100.33 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. XPS Ins. each side - concrete 8 in.
Insulating Concrete Forms - 3 in. XPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 12 | 0.39 | 30.77 | 75.5 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 3 in. XPS Ins. each side - concrete 6 in.
Insulating Concrete Forms - 3 in. XPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 14 | 0.45 | 31.11 | 86.14 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 3 in. XPS Ins. each side - concrete 8 in.
Insulating Concrete Forms - 4 in. XPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 14 | 0.3504 | 39.95 | 64.86 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 in. XPS Ins. each side - concrete 6 in.
Insulating Concrete Forms - 4 in. XPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 16 | 0.39 | 41.03 | 75.5 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 in. XPS Ins. each side - concrete 8 in.
Glass fiber batt - 3 1/2 in. R11 (CEC Default) | StandardOpaqueMaterial | MediumRough | 3.5 | 0.318 | 11 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 3 1/2 in. R11 (CEC Default)
Glass fiber batt - 3 1/2 in. R13 (CEC Default) | StandardOpaqueMaterial | MediumRough | 3.5 | 0.2688 | 13 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 3 1/2 in. R13 (CEC Default)
Glass fiber batt - 3 1/2 in. R15 (CEC Default) | StandardOpaqueMaterial | MediumRough | 3.5 | 0.2328 | 15 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 3 1/2 in. R15 (CEC Default)
Glass fiber batt - 5 1/2 in. R19 (CEC Default) | StandardOpaqueMaterial | MediumRough | 5.5 | 0.306 | 18 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 5 1/2 in. R19 (CEC Default)
Glass fiber batt - 5 1/2 in. R21 (CEC Default) | StandardOpaqueMaterial | MediumRough | 5.5 | 0.2616 | 21 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 5 1/2 in. R21 (CEC Default)
Glass fiber batt - 7 1/4 in. R25 (CEC Default) | StandardOpaqueMaterial | MediumRough | 7.25 | 0.3024 | 24 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 7 1/4 in. R25 (CEC Default)
Glass fiber batt - 7 1/4 in. R30 (CEC Default) | StandardOpaqueMaterial | MediumRough | 7.25 | 0.2904 | 25 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 7 1/4 in. R30 (CEC Default)
Glass fiber batt - 8 1/4 in. R30C (CEC Default) | StandardOpaqueMaterial | MediumRough | 8.25 | 0.2748 | 30 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 8 1/4 in. R30C (CEC Default)
Glass fiber batt - 10 in. R30 (CEC Default) | StandardOpaqueMaterial | MediumRough | 10 | 0.3336 | 30 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 10 in. R30 (CEC Default)
Glass fiber batt - 12 in. R38 (CEC Default) | StandardOpaqueMaterial | MediumRough | 12 | 0.3156 | 38 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 12 in. R38 (CEC Default)
Glass fiber batt - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 0.3 | 13.33 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Batt | Glass fiber batt - 4 in.
Glass fiber batt - 4 1/2 in. | StandardOpaqueMaterial | MediumRough | 4.5 | 0.3 | 15 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Batt | Glass fiber batt - 4 1/2 in.
Glass fiber batt - 5 in. | StandardOpaqueMaterial | MediumRough | 5 | 0.3 | 16.67 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Batt | Glass fiber batt - 5 in.
Glass fiber batt - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 0.3 | 20 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Batt | Glass fiber batt - 6 in.
Glass fiber batt - 6 1/2 in. | StandardOpaqueMaterial | MediumRough | 6.5 | 0.3 | 21.67 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Batt | Glass fiber batt - 6 1/2 in.
Cellular polyisocyanurate (unfaced) - 1/8 in. R0.7 | StandardOpaqueMaterial | Rough | 0.13 | 0.1704 | 0.73 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 1/8 in. R0.7
Cellular polyisocyanurate (unfaced) - 1/4 in. R1.5 | StandardOpaqueMaterial | Rough | 0.25 | 0.1704 | 1.47 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 1/4 in. R1.5
Cellular polyisocyanurate (unfaced) - 1/2 in. R2.9 | StandardOpaqueMaterial | Rough | 0.5 | 0.1704 | 2.93 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 1/2 in. R2.9
Cellular polyisocyanurate (unfaced) - 1 in. R5.9 | StandardOpaqueMaterial | Rough | 1 | 0.1704 | 5.87 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 1 in. R5.9
Cellular polyisocyanurate (unfaced) - 1 1/2 in. R8.8 | StandardOpaqueMaterial | Rough | 1.5 | 0.1704 | 8.8 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 1 1/2 in. R8.8
Cellular polyisocyanurate (unfaced) - 2 in. R12 | StandardOpaqueMaterial | Rough | 2 | 0.1704 | 11.74 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 2 in. R12
Cellular polyisocyanurate (unfaced) - 2 1/2 in. R15 | StandardOpaqueMaterial | Rough | 2.5 | 0.1704 | 14.67 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 2 1/2 in. R15
Cellular polyisocyanurate (unfaced) - 3 in. R18 | StandardOpaqueMaterial | Rough | 3 | 0.1704 | 17.6 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 3 in. R18
Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 | StandardOpaqueMaterial | Rough | 3.5 | 0.1704 | 20.54 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21
Cellular polyisocyanurate (unfaced) - 4 in. R23 | StandardOpaqueMaterial | Rough | 4 | 0.1704 | 23.47 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 4 in. R23
Cellular polyisocyanurate (unfaced) - 4 1/2 in. R26 | StandardOpaqueMaterial | Rough | 4.5 | 0.1704 | 26.41 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 4 1/2 in. R26
Cellular polyisocyanurate (unfaced) - 5 in. R29 | StandardOpaqueMaterial | Rough | 5 | 0.1704 | 29.34 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 5 in. R29
Cellular polyisocyanurate (unfaced) - 5 1/2 in. R32 | StandardOpaqueMaterial | Rough | 5.5 | 0.1704 | 32.28 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 5 1/2 in. R32
Cellular polyisocyanurate (unfaced) - 6 in. R35 | StandardOpaqueMaterial | Rough | 6 | 0.1704 | 35.21 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 6 in. R35
Cellular polyisocyanurate (unfaced) - 6 1/2 in. R38 | StandardOpaqueMaterial | Rough | 6.5 | 0.1704 | 38.15 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 6 1/2 in. R38
Expanded perlite - organic bonded - 3/4 in. R2.1 | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.36 | 2.08 | 1 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 3/4 in. R2.1
Expanded perlite - organic bonded - 1 in. R2.8 | StandardOpaqueMaterial | MediumSmooth | 1 | 0.36 | 2.78 | 1 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 1 in. R2.8
Expanded perlite - organic bonded - 1 1/2 in. R4.2 | StandardOpaqueMaterial | MediumSmooth | 1.5 | 0.36 | 4.17 | 1 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 1 1/2 in. R4.2
Expanded perlite - organic bonded - 2 in. R5.6 | StandardOpaqueMaterial | MediumSmooth | 2 | 0.36 | 5.56 | 1 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 2 in. R5.6
Expanded perlite - organic bonded - 3 in. R8.3 | StandardOpaqueMaterial | MediumSmooth | 3 | 0.36 | 8.33 | 1 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 3 in. R8.3
Expanded perlite - organic bonded - 4 in. R11 | StandardOpaqueMaterial | MediumSmooth | 4 | 0.36 | 11.11 | 1 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 4 in. R11
Expanded perlite - organic bonded - 6 in. R17 | StandardOpaqueMaterial | MediumSmooth | 6 | 0.36 | 16.67 | 1 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 6 in. R17
Expanded Polystyrene - EPS - 1/4 in. R1.0 | StandardOpaqueMaterial | MediumSmooth | 0.25 | 0.24 | 1.04 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 1/4 in. R1.0
Expanded Polystyrene - EPS - 1/2 in. R2.1 | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.24 | 2.08 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polystyrene - EPS - 1/2 in. R2.1
Expanded Polystyrene - EPS - 3/4 in. R3.1 | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.24 | 3.13 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 3/4 in. R3.1
Expanded Polystyrene - EPS - 1 in. R4.2 | StandardOpaqueMaterial | MediumSmooth | 1 | 0.24 | 4.17 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polystyrene - EPS - 1 in. R4.2
Expanded Polystyrene - EPS - 1 1/4 in. R5.2 | StandardOpaqueMaterial | MediumSmooth | 1.25 | 0.24 | 5.21 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polystyrene - EPS - 1 1/4 in. R5.2
Expanded Polystyrene - EPS - 1 1/2 in. R6.3 | StandardOpaqueMaterial | MediumSmooth | 1.5 | 0.24 | 6.25 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 1 1/2 in. R6.3
Expanded Polystyrene - EPS - 1 3/4 in. R7.3 | StandardOpaqueMaterial | MediumSmooth | 1.75 | 0.24 | 7.29 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 1 3/4 in. R7.3
Expanded Polystyrene - EPS - 1 7/8 in. R8.0 | StandardOpaqueMaterial | MediumSmooth | 1.92 | 0.24 | 8 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 1 7/8 in. R8.0
Expanded Polystyrene - EPS - 1 15/16 in. R8.1 | StandardOpaqueMaterial | MediumSmooth | 1.94 | 0.24 | 8.07 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 1 15/16 in. R8.1
Expanded Polystyrene - EPS - 2 in. R8.3 | StandardOpaqueMaterial | MediumSmooth | 2 | 0.24 | 8.33 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polystyrene - EPS - 2 in. R8.3
Expanded Polystyrene - EPS - 2 2/5 in. R10 | StandardOpaqueMaterial | MediumSmooth | 2.4 | 0.24 | 10 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 2 2/5 in. R10
Expanded Polystyrene - EPS - 2 7/16 in. R10 | StandardOpaqueMaterial | MediumSmooth | 2.43 | 0.24 | 10.13 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 2 7/16 in. R10
Expanded Polystyrene - EPS - 3 in. R13 | StandardOpaqueMaterial | MediumSmooth | 3.01 | 0.24 | 12.54 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 3 in. R13
Expanded Polystyrene - EPS - 3 1/3 in. R14 | StandardOpaqueMaterial | MediumSmooth | 3.35 | 0.24 | 13.96 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 3 1/3 in. R14
Expanded Polystyrene - EPS - 3 2/5 in. R14 | StandardOpaqueMaterial | MediumSmooth | 3.39 | 0.24 | 14.13 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 3 2/5 in. R14
Expanded Polystyrene - EPS - 3 1/2 in. R15 | StandardOpaqueMaterial | MediumSmooth | 3.5 | 0.24 | 14.58 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 3 1/2 in. R15
Expanded Polystyrene - EPS - 4 1/16 in. R17 | StandardOpaqueMaterial | MediumSmooth | 4.05 | 0.24 | 16.88 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 4 1/16 in. R17
Expanded Polystyrene - EPS - 4 7/10 in. R20 | StandardOpaqueMaterial | MediumSmooth | 4.71 | 0.24 | 19.63 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 4 7/10 in. R20
Expanded Polystyrene - EPS - 5 2/5 in. R22 | StandardOpaqueMaterial | MediumSmooth | 5.2 | 0.24 | 21.67 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 5 2/5 in. R22
Expanded Polystyrene - EPS - 5 19/20 in. R25 | StandardOpaqueMaterial | MediumSmooth | 5.96 | 0.24 | 24.83 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 5 19/20 in. R25
Expanded Polystyrene - EPS - 6 1/10 in. R25 | StandardOpaqueMaterial | MediumSmooth | 6.11 | 0.24 | 25.46 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 6 1/10 in. R25
Expanded Polystyrene - EPS - 6 7/8 in. R29 | StandardOpaqueMaterial | MediumSmooth | 6.87 | 0.24 | 28.63 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 6 7/8 in. R29
Expanded Polystyrene - EPS - 8 3/5 in. R35 | StandardOpaqueMaterial | MediumSmooth | 8.38 | 0.24 | 34.92 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 8 3/5 in. R35
Extruded Polystyrene - XPS - 1/4 in. R1.25 | StandardOpaqueMaterial | MediumSmooth | 0.25 | 0.2 | 1.25 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1/4 in. R1.25
Extruded Polystyrene - XPS - 1/2 in. R2.50 | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.2 | 2.5 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1/2 in. R2.50
Extruded Polystyrene - XPS - 3/4 in. R3.75 | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.2 | 3.75 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 3/4 in. R3.75
Extruded Polystyrene - XPS - 1 in. R5.00 | StandardOpaqueMaterial | MediumSmooth | 1 | 0.2 | 5 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1 in. R5.00
Extruded Polystyrene - XPS - 1 1/4 in. R6.25 | StandardOpaqueMaterial | MediumSmooth | 1.25 | 0.2 | 6.25 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1 1/4 in. R6.25
Extruded Polystyrene - XPS - 1 1/2 in. R7.50 | StandardOpaqueMaterial | MediumSmooth | 1.5 | 0.2 | 7.5 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1 1/2 in. R7.50
Extruded Polystyrene - XPS - 1 3/4 in. R8.75 | StandardOpaqueMaterial | MediumSmooth | 1.75 | 0.2 | 8.75 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1 3/4 in. R8.75
Extruded Polystyrene - XPS - 1 7/8 in. R9.37 | StandardOpaqueMaterial | MediumSmooth | 1.88 | 0.2 | 9.37 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1 7/8 in. R9.37
Extruded Polystyrene - XPS - 2 in. R10.00 | StandardOpaqueMaterial | MediumSmooth | 2 | 0.2 | 10 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 2 in. R10.00
Extruded Polystyrene - XPS - 2 1/2 in. R12.50 | StandardOpaqueMaterial | MediumSmooth | 2.5 | 0.2 | 12.5 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 2 1/2 in. R12.50
Extruded Polystyrene - XPS - 3 in. R15.00 | StandardOpaqueMaterial | MediumSmooth | 3 | 0.2 | 15 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 3 in. R15.00
Extruded Polystyrene - XPS - 3 1/2 in. R17.50 | StandardOpaqueMaterial | MediumSmooth | 3.5 | 0.2 | 17.5 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 3 1/2 in. R17.50
Extruded Polystyrene - XPS - 4 in. R20.00 | StandardOpaqueMaterial | MediumSmooth | 4 | 0.2 | 20 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 4 in. R20.00
Extruded Polystyrene - XPS - 4 1/2 in. R22.50 | StandardOpaqueMaterial | MediumSmooth | 4.5 | 0.2 | 22.5 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 4 1/2 in. R22.50
Extruded Polystyrene - XPS - 5 in. R25.00 | StandardOpaqueMaterial | MediumSmooth | 5 | 0.2 | 25 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 5 in. R25.00
Extruded Polystyrene - XPS - 5 1/2 in. R27.50 | StandardOpaqueMaterial | MediumSmooth | 5.5 | 0.2 | 27.5 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 5 1/2 in. R27.50
Extruded Polystyrene - XPS - 6 in. R30.00 | StandardOpaqueMaterial | MediumSmooth | 6 | 0.2 | 30 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 6 in. R30.00
Extruded Polystyrene - XPS - 6 1/2 in. R32.50 | StandardOpaqueMaterial | MediumSmooth | 6.5 | 0.2 | 32.5 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 6 1/2 in. R32.50
Extruded Polystyrene - XPS - 8 in. R40.00 | StandardOpaqueMaterial | MediumSmooth | 8 | 0.2 | 40 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 8 in. R40.00
Extruded Polystyrene - XPS - 8 1/2 in. R42.50 | StandardOpaqueMaterial | MediumSmooth | 8.5 | 0.2 | 42.5 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 8 1/2 in. R42.50
Expanded Polyurethane - 1/2 in. R3.1 | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.1596 | 3.13 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polyurethane - 1/2 in. R3.1
Expanded Polyurethane - 3/4 in. R4.7 | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.1596 | 4.7 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polyurethane - 3/4 in. R4.7
Expanded Polyurethane - 1 in. R6.3 | StandardOpaqueMaterial | MediumSmooth | 1 | 0.1596 | 6.27 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polyurethane - 1 in. R6.3
Expanded Polyurethane - 1 1/4 in. R7.8 | StandardOpaqueMaterial | MediumSmooth | 1.25 | 0.1596 | 7.83 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polyurethane - 1 1/4 in. R7.8
Expanded Polyurethane - 2 in. R12.6 | StandardOpaqueMaterial | MediumSmooth | 2 | 0.1596 | 12.53 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polyurethane - 2 in. R12.6
Perlite board - 3/4 in. R1.9 | StandardOpaqueMaterial | Rough | 0.75 | 0.3996 | 1.88 | 10 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Perlite board - 3/4 in. R1.9
Perlite board - 1 in. R2.5 | StandardOpaqueMaterial | Rough | 1 | 0.3996 | 2.5 | 10 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Perlite board - 1 in. R2.5
Perlite board - 1 1/2 in. R3.8 | StandardOpaqueMaterial | Rough | 1.5 | 0.3996 | 3.75 | 10 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Perlite board - 1 1/2 in. R3.8
Perlite board - 2 in. R5.0 | StandardOpaqueMaterial | Rough | 2 | 0.3996 | 5 | 10 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Perlite board - 2 in. R5.0
R-24 Batt Wall - 8 in. R24 | StandardOpaqueMaterial | VeryRough | 8 | 0.3336 | 24 | 1.19 | 0.23 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | R-24 Batt Wall - 8 in. R24
Compliance Insulation R0.01 | StandardOpaqueMaterial | MediumSmooth | 0.0016 | 0.1596 | 0.01 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R0.01
Compliance Insulation R0.02 | StandardOpaqueMaterial | MediumSmooth | 0.0032 | 0.1596 | 0.02 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R0.02
Compliance Insulation R0.10 | StandardOpaqueMaterial | MediumSmooth | 0.016 | 0.1596 | 0.1 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R0.10
Compliance Insulation R1.35 | StandardOpaqueMaterial | MediumSmooth | 0.216 | 0.1596 | 1.35 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R1.35
Compliance Insulation R1.41 | StandardOpaqueMaterial | MediumSmooth | 0.2256 | 0.1596 | 1.41 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R1.41
Compliance Insulation R1.54 | StandardOpaqueMaterial | MediumSmooth | 0.2464 | 0.1596 | 1.54 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R1.54
Compliance Insulation R2.15 | StandardOpaqueMaterial | MediumSmooth | 0.344 | 0.1596 | 2.15 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R2.15
Compliance Insulation R2.19 | StandardOpaqueMaterial | MediumSmooth | 0.3504 | 0.1596 | 2.19 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R2.19
Compliance Insulation R2.85 | StandardOpaqueMaterial | MediumSmooth | 0.456 | 0.1596 | 2.85 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R2.85
Compliance Insulation R2.89 | StandardOpaqueMaterial | MediumSmooth | 0.4624 | 0.1596 | 2.89 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R2.89
Compliance Insulation R3.63 | StandardOpaqueMaterial | MediumSmooth | 0.5808 | 0.1596 | 3.63 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R3.63
Compliance Insulation R3.70 | StandardOpaqueMaterial | MediumSmooth | 0.592 | 0.1596 | 3.7 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R3.70
Compliance Insulation R6.32 | StandardOpaqueMaterial | MediumSmooth | 1.0112 | 0.1596 | 6.32 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R6.32
Compliance Insulation R6.46 | StandardOpaqueMaterial | MediumSmooth | 1.0336 | 0.1596 | 6.46 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R6.46
Compliance Insulation R7.10 | StandardOpaqueMaterial | MediumSmooth | 1.136 | 0.1596 | 7.1 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R7.10
Compliance Insulation R7.18 | StandardOpaqueMaterial | MediumSmooth | 1.1488 | 0.1596 | 7.18 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R7.18
Compliance Insulation R7.39 | StandardOpaqueMaterial | MediumSmooth | 1.1824 | 0.1596 | 7.39 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R7.39
Compliance Insulation R8.00 | StandardOpaqueMaterial | MediumSmooth | 1.28 | 0.1596 | 8 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R8.00
Compliance Insulation R8.07 | StandardOpaqueMaterial | MediumSmooth | 1.2912 | 0.1596 | 8.07 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R8.07
Compliance Insulation R9.83 | StandardOpaqueMaterial | MediumSmooth | 1.5697 | 0.1596 | 9.83 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R9.83
Compliance Insulation R9.94 | StandardOpaqueMaterial | MediumSmooth | 1.5904 | 0.1596 | 9.94 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R9.94
Compliance Insulation R10.06 | StandardOpaqueMaterial | MediumSmooth | 1.6096 | 0.1596 | 10.06 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R10.06
Compliance Insulation R12.55 | StandardOpaqueMaterial | MediumSmooth | 2.008 | 0.1596 | 12.55 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R12.55
Compliance Insulation R12.69 | StandardOpaqueMaterial | MediumSmooth | 2.0304 | 0.1596 | 12.69 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R12.69
Compliance Insulation R13.99 | StandardOpaqueMaterial | MediumSmooth | 2.2384 | 0.1596 | 13.99 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R13.99
Compliance Insulation R14.14 | StandardOpaqueMaterial | MediumSmooth | 2.2624 | 0.1596 | 14.14 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R14.14
Compliance Insulation R14.32 | StandardOpaqueMaterial | MediumSmooth | 2.2912 | 0.1596 | 14.32 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R14.32
Compliance Insulation R14.60 | StandardOpaqueMaterial | MediumSmooth | 2.336 | 0.1596 | 14.6 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R14.60
Compliance Insulation R15.54 | StandardOpaqueMaterial | MediumSmooth | 2.4864 | 0.1596 | 15.54 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R15.54
Compliance Insulation R16.58 | StandardOpaqueMaterial | MediumSmooth | 2.6528 | 0.1596 | 16.58 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R16.58
Compliance Insulation R16.69 | StandardOpaqueMaterial | MediumSmooth | 2.6704 | 0.1596 | 16.69 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R16.69
Compliance Insulation R17.67 | StandardOpaqueMaterial | MediumSmooth | 2.8272 | 0.1596 | 17.67 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R17.67
Compliance Insulation R19.63 | StandardOpaqueMaterial | MediumSmooth | 3.1408 | 0.1596 | 19.63 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R19.63
Compliance Insulation R20.05 | StandardOpaqueMaterial | MediumSmooth | 3.208 | 0.1596 | 20.05 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R20.05
Compliance Insulation R21.18 | StandardOpaqueMaterial | MediumSmooth | 3.3888 | 0.1596 | 21.18 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R21.18
Compliance Insulation R21.39 | StandardOpaqueMaterial | MediumSmooth | 3.4224 | 0.1596 | 21.39 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R21.39
Compliance Insulation R22.48 | StandardOpaqueMaterial | MediumSmooth | 3.5968 | 0.1596 | 22.48 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R22.48
Compliance Insulation R24.86 | StandardOpaqueMaterial | MediumSmooth | 3.9776 | 0.1596 | 24.86 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R24.86
Compliance Insulation R25.16 | StandardOpaqueMaterial | MediumSmooth | 4.0256 | 0.1596 | 25.16 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R25.16
Compliance Insulation R28.63 | StandardOpaqueMaterial | MediumSmooth | 4.5808 | 0.1596 | 28.63 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R28.63
Compliance Insulation R34.93 | StandardOpaqueMaterial | MediumSmooth | 5.5888 | 0.1596 | 34.93 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R34.93
Loose fill - Mineral fiber - closed sidewalls - 3 1/2 in. | StandardOpaqueMaterial | Rough | 3.5 | 0.336 | 10.42 | 2 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - closed sidewalls - 3 1/2 in.
Loose fill - Mineral fiber - 2 lb/ft3 - 4 in. | StandardOpaqueMaterial | Rough | 4 | 0.336 | 11.9 | 2 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - 2 lb/ft3 - 4 in.
Loose fill - Mineral fiber - 2 lb/ft3 - 6 1/2 in. | StandardOpaqueMaterial | Rough | 6.5 | 0.336 | 19.35 | 2 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - 2 lb/ft3 - 6 1/2 in.
Loose fill - Mineral fiber - 2 lb/ft3 - 7 1/2 in. | StandardOpaqueMaterial | Rough | 7.5 | 0.336 | 22.32 | 2 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - 2 lb/ft3 - 7 1/2 in.
Loose fill - Mineral fiber - 2 lb/ft3 - 8 1/4 in. | StandardOpaqueMaterial | Rough | 8.25 | 0.336 | 24.55 | 2 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - 2 lb/ft3 - 8 1/4 in.
Loose fill - Mineral fiber - 2 lb/ft3 - 13 3/4 in. | StandardOpaqueMaterial | Rough | 13.75 | 0.336 | 40.92 | 2 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - 2 lb/ft3 - 13 3/4 in.
Rammed Earth | StandardOpaqueMaterial | Rough | 18 | 1.4796 | 12.19 | 115 | 0.2 | [19 empty] | CEC Title24-2013 | CEC | Insulation Other | Rammed Earth
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 3 1/2 in. | StandardOpaqueMaterial | Rough | 3.5 | 0.3204 | 10.92 | 4.6 | 0.34 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 3 1/2 in.
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 4 in. | StandardOpaqueMaterial | Rough | 4 | 0.3204 | 12.48 | 4.6 | 0.34 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 4 in.
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 4 1/2 in. | StandardOpaqueMaterial | Rough | 4.5 | 0.3204 | 14.04 | 4.6 | 0.34 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 4 1/2 in.
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 5 in. | StandardOpaqueMaterial | Rough | 5 | 0.3204 | 15.61 | 4.6 | 0.34 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 5 in.
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 5 1/2 in. | StandardOpaqueMaterial | Rough | 5.5 | 0.3204 | 17.17 | 4.6 | 0.34 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 5 1/2 in.
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 6 in. | StandardOpaqueMaterial | Rough | 6 | 0.3204 | 18.73 | 4.6 | 0.34 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 6 in.
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 6 1/2 in. | StandardOpaqueMaterial | Rough | 6.5 | 0.3204 | 20.29 | 4.6 | 0.34 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 6 1/2 in.
Spray applied - Glass fiber - 3.9 lb/ft3 - 3 1/2 in. | StandardOpaqueMaterial | MediumRough | 3.5 | 0.27 | 12.96 | 3.9 | 0.23 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 3 1/2 in.
Spray applied - Glass fiber - 3.9 lb/ft3 - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 0.27 | 14.81 | 3.9 | 0.23 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 4 in.
Spray applied - Glass fiber - 3.9 lb/ft3 - 4 1/2 in. | StandardOpaqueMaterial | MediumRough | 4.5 | 0.27 | 16.67 | 3.9 | 0.23 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 4 1/2 in.
Spray applied - Glass fiber - 3.9 lb/ft3 - 5 in. | StandardOpaqueMaterial | MediumRough | 5 | 0.27 | 18.52 | 3.9 | 0.23 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 5 in.
Spray applied - Glass fiber - 3.9 lb/ft3 - 5 1/2 in. | StandardOpaqueMaterial | MediumRough | 5.5 | 0.27 | 20.37 | 3.9 | 0.23 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 5 1/2 in.
Spray applied - Glass fiber - 3.9 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 0.27 | 22.22 | 3.9 | 0.23 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 6 in.
Spray applied - Glass fiber - 3.9 lb/ft3 - 6 1/2 in. | StandardOpaqueMaterial | MediumRough | 6.5 | 0.27 | 24.07 | 3.9 | 0.23 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 6 1/2 in.
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 3 1/2 in. | StandardOpaqueMaterial | Rough | 3.5 | 0.3 | 11.67 | 0.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 3 1/2 in.
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 4 in. | StandardOpaqueMaterial | Rough | 4 | 0.3 | 13.33 | 0.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 4 in.
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 4 1/2 in. | StandardOpaqueMaterial | Rough | 4.5 | 0.3 | 15 | 0.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 4 1/2 in.
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 5 in. | StandardOpaqueMaterial | Rough | 5 | 0.3 | 16.67 | 0.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 5 in.
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 5 1/2 in. | StandardOpaqueMaterial | Rough | 5.5 | 0.3 | 18.33 | 0.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 5 1/2 in.
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 6 in. | StandardOpaqueMaterial | Rough | 6 | 0.3 | 20 | 0.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 6 in.
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 6 1/2 in. | StandardOpaqueMaterial | Rough | 6.5 | 0.3 | 21.67 | 0.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 6 1/2 in.
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 3 1/2 in. | StandardOpaqueMaterial | Rough | 3.5 | 0.20004 | 17.5 | 3 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 3 1/2 in.
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 4 in. | StandardOpaqueMaterial | Rough | 4 | 0.20004 | 20 | 3 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 4 in.
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 4 1/2 in. | StandardOpaqueMaterial | Rough | 4.5 | 0.20004 | 22.5 | 3 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 4 1/2 in.
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 5 in. | StandardOpaqueMaterial | Rough | 5 | 0.20004 | 25 | 3 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 5 in.
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 5 1/2 in. | StandardOpaqueMaterial | Rough | 5.5 | 0.20004 | 27.5 | 3 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 5 1/2 in.
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 6 in. | StandardOpaqueMaterial | Rough | 6 | 0.20004 | 30 | 3 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 6 in.
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 6 1/2 in. | StandardOpaqueMaterial | Rough | 6.5 | 0.20004 | 32.5 | 3 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 6 1/2 in.
Brick - 48 lb/ft3 - 3 5/8 in. | StandardOpaqueMaterial | Rough | 3.63 | 1.5 | 2.42 | 48 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Brick - 48 lb/ft3 - 3 5/8 in.
Brick - fired clay - 140 lb/ft3 - 3 5/8 in. | StandardOpaqueMaterial | MediumRough | 3.63 | 8.22 | 0.44 | 139.78 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Brick - fired clay - 140 lb/ft3 - 3 5/8 in.
Clay tile - hollow - 1 cell deep - 3 in. | StandardOpaqueMaterial | MediumRough | 3 | 3.75 | 0.8 | 85 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 1 cell deep - 3 in.
Clay tile - hollow - 1 cell deep - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 3.6 | 1.11 | 85 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 1 cell deep - 4 in.
Clay tile - hollow - 2 cells deep - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.9504 | 1.52 | 85 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 2 cells deep - 6 in.
Clay tile - hollow - 2 cells deep - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 4.32 | 1.85 | 85 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 2 cells deep - 8 in.
Clay tile - hollow - 2 cells deep - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 4.5 | 2.22 | 85 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 2 cells deep - 10 in.
Clay tile - hollow - 3 cells deep - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 4.8 | 2.5 | 85 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 3 cells deep - 12 in.
Clay Tile - Paver | StandardOpaqueMaterial | MediumRough | 0.38 | 12.504 | 0.03 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | CEC Doug | Masonry Materials | Clay Tile - Paver
Concrete Paver | StandardOpaqueMaterial | MediumRough | 0.38 | 4.5024 | 0.08 | 144 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Bruce | Masonry Materials | Concrete Paver
Gypsum partition block - solid - 3 in. x 12 in. x 30 in. - 3 in. | StandardOpaqueMaterial | MediumRough | 3 | 2.3796 | 1.26 | 62.4 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Gypsum partition block - solid - 3 in. x 12 in. x 30 in. - 3 in.
Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. | StandardOpaqueMaterial | MediumRough | 3 | 2.22 | 1.35 | 53.1 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in.
Gypsum partition block - 3 cells - 4 in. x 12 in. x 30 in. - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 2.4 | 1.67 | 53.1 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Gypsum partition block - 3 cells - 4 in. x 12 in. x 30 in. - 4 in.
Stone - 1 in. | StandardOpaqueMaterial | MediumRough | 1 | 12.504 | 0.08 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | CEC Doug | Masonry Materials | Stone - 1 in.
1 Coat Stucco | StandardOpaqueMaterial | MediumRough | 0.38 | 5.0004 | 0.08 | 115.81 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Masonry Materials | 1 Coat Stucco
3 Coat Stucco | StandardOpaqueMaterial | MediumRough | 0.88 | 4.3752 | 0.2 | 116 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Bruce | Masonry Materials | 3 Coat Stucco
Synthetic Stucco - EIFS finish - 1 in. | StandardOpaqueMaterial | Smooth | 1 | 0.2496 | 4 | 1.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Synthetic Stucco - EIFS finish - 1 in.
Terrazzo - 1 in. | StandardOpaqueMaterial | MediumRough | 1 | 12.504 | 0.08 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | CEC Doug | Masonry Materials | Terrazzo - 1 in.
Clay - Part Grouted and Empty - 130 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.12 | 1.923 | 130 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Clay - Part Grouted and Empty - 130 lb/ft3 - 6 in.
Clay - Part Grouted and Empty - 130 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.7596 | 2.128 | 130 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Clay - Part Grouted and Empty - 130 lb/ft3 - 8 in.
Concrete - Part Grouted and Empty - 105 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.24 | 1.852 | 105 | 0.15 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 105 lb/ft3 - 6 in.
Concrete - Part Grouted and Empty - 105 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.9996 | 2 | 105 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 105 lb/ft3 - 8 in.
Concrete - Part Grouted and Empty - 105 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 4.5996 | 2.174 | 105 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 105 lb/ft3 - 10 in.
Concrete - Part Grouted and Empty - 105 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 5.16 | 2.326 | 105 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 105 lb/ft3 - 12 in.
Concrete - Part Grouted and Empty - 115 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.48 | 1.724 | 115 | 0.15 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 115 lb/ft3 - 6 in.
Concrete - Part Grouted and Empty - 115 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 4.2396 | 1.887 | 115 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 115 lb/ft3 - 8 in.
Concrete - Part Grouted and Empty - 115 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 4.8996 | 2.041 | 115 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 115 lb/ft3 - 10 in.
Concrete - Part Grouted and Empty - 115 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 5.52 | 2.174 | 115 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 115 lb/ft3 - 12 in.
Concrete - Part Grouted and Empty - 125 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.66 | 1.639 | 125 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 125 lb/ft3 - 6 in.
Concrete - Part Grouted and Empty - 125 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 4.4796 | 1.786 | 125 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 125 lb/ft3 - 8 in.
Concrete - Part Grouted and Empty - 125 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 5.1996 | 1.923 | 125 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 125 lb/ft3 - 10 in.
Concrete - Part Grouted and Empty - 125 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 5.88 | 2.041 | 125 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 125 lb/ft3 - 12 in.
Clay - Solid Grout - 130 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.9 | 1.538 | 130 | 0.17 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Clay - Solid Grout - 130 lb/ft3 - 6 in.
Clay - Solid Grout - 130 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 4.56 | 1.754 | 130 | 0.17 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Clay - Solid Grout - 130 lb/ft3 - 8 in.
Concrete - Solid Grout - 105 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 8.3328 | 0.72 | 105 | 0.21 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 105 lb/ft3 - 6 in.
Concrete - Solid Grout - 105 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 8.3328 | 0.96 | 105 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 105 lb/ft3 - 8 in.
Concrete - Solid Grout - 105 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 8.4744 | 1.18 | 105 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 105 lb/ft3 - 10 in.
Concrete - Solid Grout - 105 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 8.5704 | 1.4 | 105 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 105 lb/ft3 - 12 in.
Concrete - Solid Grout - 115 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 10.17 | 0.59 | 115 | 0.2 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 115 lb/ft3 - 6 in.
Concrete - Solid Grout - 115 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 9.1224 | 0.877 | 115 | 0.2 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 115 lb/ft3 - 8 in.
Concrete - Solid Grout - 115 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 9.174 | 1.09 | 115 | 0.21 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 115 lb/ft3 - 10 in.
Concrete - Solid Grout - 115 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 9.2304 | 1.3 | 115 | 0.21 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 115 lb/ft3 - 12 in.
Concrete - Solid Grout - 125 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 10.17 | 0.59 | 125 | 0.19 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 125 lb/ft3 - 6 in.
Concrete - Solid Grout - 125 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 10.1268 | 0.79 | 125 | 0.2 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 125 lb/ft3 - 8 in.
Concrete - Solid Grout - 125 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 10.1016 | 0.99 | 125 | 0.2 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 125 lb/ft3 - 10 in.
Concrete - Solid Grout - 125 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 10.0836 | 1.19 | 125 | 0.2 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 125 lb/ft3 - 12 in.
Clay - Part Grouted and Insulated - 130 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 2.7 | 2.222 | 130 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Clay - Part Grouted and Insulated - 130 lb/ft3 - 6 in.
Clay - Part Grouted and Insulated - 130 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.12 | 2.564 | 130 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Clay - Part Grouted and Insulated - 130 lb/ft3 - 8 in.
Concrete - Part Grouted and Insulated - 105 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 2.64 | 2.273 | 105 | 0.15 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 6 in.
Concrete - Part Grouted and Insulated - 105 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 2.9604 | 2.703 | 105 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 8 in.
Concrete - Part Grouted and Insulated - 105 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 3.3996 | 2.941 | 105 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 10 in.
Concrete - Part Grouted and Insulated - 105 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 3.6 | 3.333 | 105 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 12 in.
Concrete - Part Grouted and Insulated - 115 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 2.88 | 2.083 | 115 | 0.15 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 6 in.
Concrete - Part Grouted and Insulated - 115 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.2796 | 2.439 | 115 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 8 in.
Concrete - Part Grouted and Insulated - 115 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 3.6996 | 2.703 | 115 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 10 in.
Concrete - Part Grouted and Insulated - 115 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 3.96 | 3.03 | 115 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 12 in.
Concrete - Part Grouted and Insulated - 125 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.12 | 1.923 | 125 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 6 in.
Concrete - Part Grouted and Insulated - 125 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.5196 | 2.273 | 125 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 8 in.
Concrete - Part Grouted and Insulated - 125 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 4.1004 | 2.439 | 125 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 10 in.
Concrete - Part Grouted and Insulated - 125 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 4.32 | 2.778 | 125 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 12 in.
Metal Insulated Panels - 2 in. | StandardOpaqueMaterial | Smooth | 2 | 0.16704 | 11.971 | 34.87 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 2 in.
Metal Insulated Panels - 2 1/2 in. | StandardOpaqueMaterial | Smooth | 2.5 | 0.16644 | 15.023 | 28.47 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 2 1/2 in.
Metal Insulated Panels - 3 in. | StandardOpaqueMaterial | Smooth | 3 | 0.16656 | 18.018 | 24.11 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 3 in.
Metal Insulated Panels - 4 in. | StandardOpaqueMaterial | Smooth | 4 | 0.16992 | 23.54 | 18.54 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 4 in.
Metal Insulated Panels - 5 in. | StandardOpaqueMaterial | Smooth | 5 | 0.1698 | 29.453 | 15.14 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 5 in.
Metal Insulated Panels - 6 in. | StandardOpaqueMaterial | Smooth | 6 | 0.16584 | 36.187 | 12.84 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 6 in.
Aggregate - 45 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 1.56 | 0.32 | 45 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - 45 lb/ft3 - 1/2 in.
Aggregate - 45 lb/ft3 - 5/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.63 | 1.5996 | 0.39 | 45 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - 45 lb/ft3 - 5/8 in.
Aggregate - 45 lb/ft3 - on metal lath - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 1.5996 | 0.47 | 45 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - 45 lb/ft3 - on metal lath - 3/4 in.
Aggregate - Perlite - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 1.2996 | 0.38 | 45 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - Perlite - 1/2 in.
Aggregate - Perlite - 5/8 in. | StandardOpaqueMaterial | Smooth | 0.63 | 1.5 | 0.42 | 45 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - Perlite - 5/8 in.
Aggregate - Perlite - on metal lath - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 1.7004 | 0.44 | 45 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - Perlite - on metal lath - 3/4 in.
Concrete/Sand Aggregate - 6 in. | StandardOpaqueMaterial | Smooth | 6.01 | 4.29 | 1.4 | 116 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Concrete/Sand Aggregate - 6 in.
Gypsum plaster - 80 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 3.2004 | 0.16 | 80 | 0.26 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Gypsum plaster - 80 lb/ft3 - 1/2 in.
Gypsum plaster - 80 lb/ft3 - 5/8 in. | StandardOpaqueMaterial | Smooth | 0.63 | 3.2004 | 0.2 | 80 | 0.26 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Gypsum plaster - 80 lb/ft3 - 5/8 in.
Gypsum plaster - on metal lath 70 lb/ft3 - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 2.6004 | 0.29 | 70 | 0.26 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Gypsum plaster - on metal lath 70 lb/ft3 - 3/4 in.
Gypsum plaster - on metal lath 80 lb/ft3 - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 3.2004 | 0.23 | 80 | 0.26 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Gypsum plaster - on metal lath 80 lb/ft3 - 3/4 in.
Mortar - Cement - 1 in. | StandardOpaqueMaterial | Smooth | 1.01 | 5.0304 | 0.2 | 116 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Mortar - Cement - 1 in.
Mortar - Cement - 1 3/4 in. | StandardOpaqueMaterial | Smooth | 1.76 | 5.01 | 0.35 | 116 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Mortar - Cement - 1 3/4 in.
Perlite plaster - 25 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.6 | 0.83 | 25 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Perlite plaster - 25 lb/ft3 - 1/2 in.
Perlite plaster - 38 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 1.2996 | 0.38 | 38 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Perlite plaster - 38 lb/ft3 - 1/2 in.
Plaster/Sand Aggregate - 1 in. | StandardOpaqueMaterial | Smooth | 1.01 | 5.0304 | 0.2 | 116 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Plaster/Sand Aggregate - 1 in.
Pulpboard or paper plaster - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.5004 | 1 | 38 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Pulpboard or paper plaster - 1/2 in.
Sand aggregate - 3/8 in. | StandardOpaqueMaterial | Smooth | 0.38 | 5.1504 | 0.07 | 116 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Sand aggregate - 3/8 in.
Sand aggregate - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 5.4504 | 0.09 | 105 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Sand aggregate - 1/2 in.
Sand aggregate - 5/8 in. | StandardOpaqueMaterial | Smooth | 0.63 | 5.6004 | 0.11 | 105 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Sand aggregate - 5/8 in.
Sand aggregate - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 5.0796 | 0.14 | 116 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Sand aggregate - 3/4 in.
Sand aggregate on metal lath - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 5.7696 | 0.13 | 105 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Sand aggregate on metal lath - 3/4 in.
Vermiculite aggregate - 45 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 1.7004 | 0.29 | 45 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Vermiculite aggregate - 45 lb/ft3 - 1/2 in.
Stucco - 3/8 in. | StandardOpaqueMaterial | Smooth | 0.38 | 5.0004 | 0.08 | 115.81 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Stucco - 3/8 in.
Stucco - 7/8 in. | StandardOpaqueMaterial | Smooth | 0.88 | 4.86 | 0.18 | 115.81 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Stucco - 7/8 in.
Synthetic Stucco - EIFS finish - 1 in. | StandardOpaqueMaterial | Smooth | 1 | 0.2496 | 4 | 1.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Synthetic Stucco - EIFS finish - 1 in.
5 PSF Roof - 1/2 in. | StandardOpaqueMaterial | VeryRough | 0.5 | 6.0024 | 0.08 | 120 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Bruce | Roofing | 5 PSF Roof - 1/2 in.
10 PSF Roof - 1 in. | StandardOpaqueMaterial | VeryRough | 1 | 12.0048 | 0.08 | 120 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Bruce | Roofing | 10 PSF Roof - 1 in.
15 PSF Roof - 1 1/2 in. | StandardOpaqueMaterial | VeryRough | 1.5 | 18.0072 | 0.08 | 120 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Bruce | Roofing | 15 PSF Roof - 1 1/2 in.
25 PSF Roof - 2 1/2 in. | StandardOpaqueMaterial | VeryRough | 2.5 | 30.012 | 0.08 | 120 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Bruce | Roofing | 25 PSF Roof - 2 1/2 in.
Asbestos or cement shingles - 3/8 in. | StandardOpaqueMaterial | VeryRough | 0.38 | 1.7904 | 0.21 | 120 | 0.24 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Asbestos or cement shingles - 3/8 in.
Asphalt - bitumen with inert fill - 100 lb/ft3 - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 3 | 0.25 | 100 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Asphalt - bitumen with inert fill - 100 lb/ft3 - 3/4 in.
Asphalt - bitumen with inert fill - 144 lb/ft3 - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 8.0004 | 0.09 | 144 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Asphalt - bitumen with inert fill - 144 lb/ft3 - 3/4 in.
Asphalt roll roofing - 1/4 in. | StandardOpaqueMaterial | VeryRough | 0.25 | 1.6704 | 0.15 | 70 | 0.36 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Asphalt roll roofing - 1/4 in.
Asphalt shingles - 1/4 in. | StandardOpaqueMaterial | VeryRough | 0.25 | 0.5604 | 0.45 | 69.89 | 0.3 | [19 empty] | CEC Title24-2013 | CEC Doug | Roofing | Asphalt shingles - 1/4 in.
Built-up roofing - 3/8 in. | StandardOpaqueMaterial | VeryRough | 0.38 | 1.14 | 0.33 | 70 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Built-up roofing - 3/8 in.
Clay tile - 1/2 in. | StandardOpaqueMaterial | MediumRough | 0.5 | 0.1896 | 2.63 | 85 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Clay tile - 1/2 in.
Light Roof - 2/5 in. | StandardOpaqueMaterial | VeryRough | 0.2 | 2.4012 | 0.08 | 120 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Bruce | Roofing | Light Roof - 2/5 in.
Mastic asphalt (heavy - 20% grit) - 1 in. | StandardOpaqueMaterial | VeryRough | 1 | 1.2996 | 0.77 | 59 | 0.22 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Mastic asphalt (heavy - 20% grit) - 1 in.
Metal Standing Seam - 1/16 in. | StandardOpaqueMaterial | Smooth | 0.0625 | 3.9996 | 0 | 488.22 | 0.12 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Metal Standing Seam - 1/16 in.
Roof Gravel - 1 in. | StandardOpaqueMaterial | VeryRough | 1 | 9.9996 | 0.1 | 159.74 | 0.19 | [19 empty] | CEC Title24-2013 | CEC Doug | Roofing | Roof Gravel - 1 in.
Roof Gravel - 1/2 in. | StandardOpaqueMaterial | VeryRough | 0.5 | 9.9996 | 0.05 | 159.74 | 0.19 | [19 empty] | CEC Title24-2013 | CEC Doug | Roofing | Roof Gravel - 1/2 in.
Slate - 1/2 in. | StandardOpaqueMaterial | VeryRough | 0.5 | 11.0304 | 0.05 | 119.81 | 0.3 | [19 empty] | CEC Title24-2013 | CEC Doug | Roofing | Slate - 1/2 in.
Tile Gap - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 0.6612 | 1.13 | 70 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Bruce | Roofing | Tile Gap - 3/4 in.
Wood shingles - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 0.8304 | 0.9 | 36.94 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Wood shingles - 3/4 in.
Wood shingles - plain and plastic film faced - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 0.8004 | 0.94 | 22 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Wood shingles - plain and plastic film faced - 3/4 in.
SIPS - Crawl Space - R22 - I Joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.23148 | 28.08 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R22 - I Joist Spline - 6 1/2 in.
SIPS - Crawl Space - R33 - I Joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.16884 | 38.497 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R33 - I Joist Spline - 6 1/2 in.
SIPS - Crawl Space - R28 - I Joist Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.2436 | 33.867 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R28 - I Joist Spline - 8 1/4 in.
SIPS - Crawl Space - R36 - I Joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.2424 | 42.285 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R36 - I Joist Spline - 10 1/4 in.
SIPS - Crawl Space - R22 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.23952 | 27.133 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R22 - Single 2x Spline - 6 1/2 in.
SIPS - Crawl Space - R33 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.16884 | 38.497 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R33 - Single 2x Spline - 6 1/2 in.
SIPS - Crawl Space - R28 - Single 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.2436 | 33.867 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R28 - Single 2x Spline - 8 1/4 in.
SIPS - Crawl Space - R36 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.25428 | 40.308 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R36 - Single 2x Spline - 10 1/4 in.
SIPS - Crawl Space - R22 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.24768 | 26.242 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R22 - Double 2x Spline - 6 1/2 in.
SIPS - Crawl Space - R33 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.1842 | 35.292 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R33 - Double 2x Spline - 6 1/2 in.
SIPS - Crawl Space - R28 - Double 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.25356 | 32.544 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R28 - Double 2x Spline - 8 1/4 in.
SIPS - Crawl Space - R36 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.26628 | 38.497 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R36 - Double 2x Spline - 10 1/4 in.
SIPS - No Crawl Space - R22 - I Joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.29772 | 21.83 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R22 - I Joist Spline - 6 1/2 in.
SIPS - No Crawl Space - R33 - I Joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.19968 | 32.544 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R33 - I Joist Spline - 6 1/2 in.
SIPS - No Crawl Space - R28 - I Joist Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.29376 | 28.08 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R28 - I Joist Spline - 8 1/4 in.
SIPS - No Crawl Space - R36 - I Joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.2904 | 35.292 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R36 - I Joist Spline - 10 1/4 in.
SIPS - No Crawl Space - R22 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.30636 | 21.22 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R22 - Single 2x Spline - 6 1/2 in.
SIPS - No Crawl Space - R33 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.2076 | 31.313 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R33 - Single 2x Spline - 6 1/2 in.
SIPS - No Crawl Space - R28 - Single 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.30408 | 27.133 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R28 - Single 2x Spline - 8 1/4 in.
SIPS - No Crawl Space - R36 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.2904 | 35.292 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R36 - Single 2x Spline - 10 1/4 in.
SIPS - No Crawl Space - R22 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.32364 | 20.086 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R22 - Double 2x Spline - 6 1/2 in.
SIPS - No Crawl Space - R33 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.23148 | 28.08 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R33 - Double 2x Spline - 6 1/2 in.
SIPS - No Crawl Space - R28 - Double 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.3144 | 26.242 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R28 - Double 2x Spline - 8 1/4 in.
SIPS - No Crawl Space - R36 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.315 | 32.544 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R36 - Double 2x Spline - 10 1/4 in.
SIPS - R22 - I joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.30216 | 21.516 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R22 - I joist Spline - 6 1/2 in.
SIPS - R33 - I joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.213 | 30.518 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R33 - I joist Spline - 6 1/2 in.
SIPS - R28 - I joist Spline - 8 1/2 in. | StandardOpaqueMaterial | Smooth | 8.5 | 0.2976 | 28.563 | 5.71 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R28 - I joist Spline - 8 1/2 in.
SIPS - R36 - I joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.2904 | 35.297 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R36 - I joist Spline - 10 1/4 in.
SIPS - R55 - I joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.19044 | 53.816 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R55 - I joist Spline - 10 1/4 in.
SIPS - R44 - I joist Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.2802 | 43.715 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R44 - I joist Spline - 12 1/4 in.
SIPS - R22 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.3096 | 20.987 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R22 - Single 2x Spline - 6 1/2 in.
SIPS - R33 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.213 | 30.518 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R33 - Single 2x Spline - 6 1/2 in.
SIPS - R28 - Single 2x Spline - 8 1/2 in. | StandardOpaqueMaterial | Smooth | 8.5 | 0.3072 | 27.672 | 5.71 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R28 - Single 2x Spline - 8 1/2 in.
SIPS - R36 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.30168 | 33.974 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R36 - Single 2x Spline - 10 1/4 in.
SIPS - R55 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.20136 | 50.892 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R55 - Single 2x Spline - 10 1/4 in.
SIPS - R44 - Single 2x Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.29352 | 41.738 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R44 - Single 2x Spline - 12 1/4 in.
SIPS - R22 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.32496 | 19.999 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R22 - Double 2x Spline - 6 1/2 in.
SIPS - R33 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.23484 | 27.672 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R33 - Double 2x Spline - 6 1/2 in.
SIPS - R28 - Double 2x Spline - 8 1/2 in. | StandardOpaqueMaterial | Smooth | 8.5 | 0.33612 | 25.287 | 5.71 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R28 - Double 2x Spline - 8 1/2 in.
SIPS - R36 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.31308 | 32.743 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R36 - Double 2x Spline - 10 1/4 in.
SIPS - R55 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.22344 | 45.879 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R55 - Double 2x Spline - 10 1/4 in.
SIPS - R44 - Double 2x Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.32016 | 38.26 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R44 - Double 2x Spline - 12 1/4 in.
SIPS - R22 - OSB Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.28692 | 22.65 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R22 - OSB Spline - 6 1/2 in.
SIPS - R33 - OSB Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.2058 | 31.593 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R33 - OSB Spline - 6 1/2 in.
SIPS - R28 - OSB Spline - 8 1/2 in. | StandardOpaqueMaterial | Smooth | 8.5 | 0.2976 | 28.563 | 5.71 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R28 - OSB Spline - 8 1/2 in.
SIPS - R36 - OSB Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.27912 | 36.722 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R36 - OSB Spline - 10 1/4 in.
SIPS - R55 - OSB Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.17952 | 57.084 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R55 - OSB Spline - 10 1/4 in.
SIPS - R44 - OSB Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.267 | 45.879 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R44 - OSB Spline - 12 1/4 in.
SIPS - R14 - Metal Spline - 48 in. | StandardOpaqueMaterial | Smooth | 48 | 4.14 | 11.593 | 1.83 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R14 - Metal Spline - 48 in.
SIPS - R22 - Metal Spline - 48 in. | StandardOpaqueMaterial | Smooth | 48 | 3.0396 | 15.804 | 1.83 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R22 - Metal Spline - 48 in.
SIPS - R28 - Metal Spline - 48 in. | StandardOpaqueMaterial | Smooth | 48 | 2.4569 | 19.537 | 1.83 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R28 - Metal Spline - 48 in.
SIPS - R36 - Metal Spline - 48 in. | StandardOpaqueMaterial | Smooth | 48 | 2.2296 | 21.516 | 1.83 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R36 - Metal Spline - 48 in.
SIPS - R14 - I joist Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.35304 | 12.746 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R14 - I joist Spline - 4 1/2 in.
SIPS - R18 - I joist Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.29208 | 15.409 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R18 - I joist Spline - 4 1/2 in.
SIPS - R22 - I joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.33696 | 19.293 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R22 - I joist Spline - 6 1/2 in.
SIPS - R33 - I joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.24768 | 26.238 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R33 - I joist Spline - 6 1/2 in.
SIPS - R28 - I joist Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.32364 | 25.487 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R28 - I joist Spline - 8 1/4 in.
SIPS - R36 - I joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.32244 | 31.793 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R36 - I joist Spline - 10 1/4 in.
SIPS - R55 - I joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.2334 | 43.915 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R55 - I joist Spline - 10 1/4 in.
SIPS - R44 - I joist Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.31848 | 38.46 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R44 - I joist Spline - 12 1/4 in.
SIPS - R14 - Single 2x Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.35868 | 12.545 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R14 - Single 2x Spline - 4 1/2 in.
SIPS - R18 - Single 2x Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.303 | 14.853 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R18 - Single 2x Spline - 4 1/2 in.
SIPS - R22 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.35208 | 18.46 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R22 - Single 2x Spline - 6 1/2 in.
SIPS - R33 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.26232 | 24.776 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R33 - Single 2x Spline - 6 1/2 in.
SIPS - R28 - Single 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.34236 | 24.101 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R28 - Single 2x Spline - 8 1/4 in.
SIPS - R36 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.345 | 29.71 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R36 - Single 2x Spline - 10 1/4 in.
SIPS - R55 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.25548 | 40.127 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R55 - Single 2x Spline - 10 1/4 in.
SIPS - R44 - Single 2x Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.34512 | 35.497 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R44 - Single 2x Spline - 12 1/4 in.
SIPS - R14 - Double 2x Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.39312 | 11.447 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R14 - Double 2x Spline - 4 1/2 in.
SIPS - R18 - Double 2x Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.3306 | 13.612 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R18 - Double 2x Spline - 4 1/2 in.
SIPS - R22 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.3828 | 16.979 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R22 - Double 2x Spline - 6 1/2 in.
SIPS - R33 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.29928 | 21.716 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R33 - Double 2x Spline - 6 1/2 in.
SIPS - R28 - Double 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.37992 | 21.716 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R28 - Double 2x Spline - 8 1/4 in.
SIPS - R36 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.3792 | 27.031 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R36 - Double 2x Spline - 10 1/4 in.
SIPS - R55 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.3 | 34.174 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R55 - Double 2x Spline - 10 1/4 in.
SIPS - R44 - Double 2x Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.35844 | 34.174 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R44 - Double 2x Spline - 12 1/4 in.
SIPS - R14 - OSB Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.303 | 14.853 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R14 - OSB Spline - 4 1/2 in.
SIPS - R18 - OSB Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.25968 | 17.328 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R18 - OSB Spline - 4 1/2 in.
SIPS - R22 - OSB Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.28452 | 22.85 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R22 - OSB Spline - 6 1/2 in.
SIPS - R33 - OSB Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.21876 | 29.71 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R33 - OSB Spline - 6 1/2 in.
SIPS - R28 - OSB Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.27768 | 29.71 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R28 - OSB Spline - 8 1/4 in.
SIPS - R36 - OSB Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.27756 | 36.922 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R36 - OSB Spline - 10 1/4 in.
SIPS - R55 - OSB Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.21156 | 48.46 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R55 - OSB Spline - 10 1/4 in.
SIPS - R44 - OSB Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.279 | 43.915 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R44 - OSB Spline - 12 1/4 in.
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 1.1304 | 2.007 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - No Ins.
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.4704 | 3.889 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R4 Ins.
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.5604 | 4.526 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R7 Ins.
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.66 | 4.93 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R10 Ins.
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.84 | 5.323 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R15 Ins.
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 1.0104 | 5.602 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R20 Ins.
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.1904 | 5.773 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R25 Ins.
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.38 | 5.861 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R30 Ins.
Aluminum w/out Thrml Break - Double glass with no low e coatings - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.8304 | 2.721 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - No Ins.
Aluminum w/out Thrml Break - Double glass with no low e coatings - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.4404 | 4.15 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R4 Ins.
Aluminum w/out Thrml Break - Double glass with no low e coatings - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.54 | 4.706 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R7 Ins.
Aluminum w/out Thrml Break - Double glass with no low e coatings - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.6504 | 5.032 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R10 Ins.
Aluminum w/out Thrml Break - Double glass with no low e coatings - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.8304 | 5.4 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R15 Ins.
Aluminum w/out Thrml Break - Double glass with no low e coatings - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 1.0046 | 5.644 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R20 Ins.
Aluminum w/out Thrml Break - Double glass with no low e coatings - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.1904 | 5.773 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R25 Ins.
Aluminum w/out Thrml Break - Double glass with no low e coatings - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.3704 | 5.907 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R30 Ins.
Aluminum w/out Thrml Break - Triple or low e glass - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.69 | 3.299 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - No Ins.
Aluminum w/out Thrml Break - Triple or low e glass - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.41724 | 4.386 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R4 Ins.
Aluminum w/out Thrml Break - Triple or low e glass - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.5304 | 4.832 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R7 Ins.
Aluminum w/out Thrml Break - Triple or low e glass - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.63648 | 5.138 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R10 Ins.
Aluminum w/out Thrml Break - Triple or low e glass - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.8196 | 5.439 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R15 Ins.
Aluminum w/out Thrml Break - Triple or low e glass - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.9996 | 5.686 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R20 Ins.
Aluminum w/out Thrml Break - Triple or low e glass - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.1796 | 5.817 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R25 Ins.
Aluminum w/out Thrml Break - Triple or low e glass - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.3704 | 5.907 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R30 Ins.
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 1.1796 | 1.928 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - No Ins.
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.5604 | 3.282 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R4 Ins.
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.6996 | 3.655 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R7 Ins.
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.8496 | 3.867 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R10 Ins.
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 1.1004 | 4.076 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R15 Ins.
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 1.35 | 4.201 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R20 Ins.
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.6104 | 4.278 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R25 Ins.
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.86 | 4.331 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R30 Ins.
Aluminum w/ Thrml Break - Double glass with no low e - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.9 | 2.517 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - No Ins.
Aluminum w/ Thrml Break - Double glass with no low e - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.5304 | 3.442 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R4 Ins.
Aluminum w/ Thrml Break - Double glass with no low e - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.6696 | 3.823 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R7 Ins.
Aluminum w/ Thrml Break - Double glass with no low e - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.8196 | 3.981 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R10 Ins.
Aluminum w/ Thrml Break - Double glass with no low e - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 1.08 | 4.15 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R15 Ins.
Aluminum w/ Thrml Break - Double glass with no low e - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 1.3296 | 4.252 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R20 Ins.
Aluminum w/ Thrml Break - Double glass with no low e - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.5996 | 4.305 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R25 Ins.
Aluminum w/ Thrml Break - Double glass with no low e - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.8504 | 4.358 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R30 Ins.
Aluminum w/ Thrml Break - Triple or low e glass - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.78 | 2.895 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - No Ins.
Aluminum w/ Thrml Break - Triple or low e glass - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.51 | 3.575 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R4 Ins.
Aluminum w/ Thrml Break - Triple or low e glass - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.6696 | 3.823 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R7 Ins.
Aluminum w/ Thrml Break - Triple or low e glass - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.8196 | 3.981 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R10 Ins.
Aluminum w/ Thrml Break - Triple or low e glass - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 1.08 | 4.15 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R15 Ins.
Aluminum w/ Thrml Break - Triple or low e glass - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 1.3296 | 4.252 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R20 Ins.
Aluminum w/ Thrml Break - Triple or low e glass - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.5996 | 4.305 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R25 Ins.
Aluminum w/ Thrml Break - Triple or low e glass - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.8504 | 4.358 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R30 Ins.
Continuous Ins. - Single glass pane. stone. or metal pane - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 1.1796 | 1.928 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - No Ins.
Continuous Ins. - Single glass pane. stone. or metal pane - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.3096 | 5.907 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R4 Ins.
Continuous Ins. - Single glass pane. stone. or metal pane - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.28476 | 8.954 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R7 Ins.
Continuous Ins. - Single glass pane. stone. or metal pane - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.27312 | 11.971 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R10 Ins.
Continuous Ins. - Single glass pane. stone. or metal pane - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.2628 | 17.007 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R15 Ins.
Continuous Ins. - Single glass pane. stone. or metal pane - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.2592 | 21.877 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R20 Ins.
Continuous Ins. - Single glass pane. stone. or metal pane - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 0.25512 | 26.928 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R25 Ins.
Continuous Ins. - Single glass pane. stone. or metal pane - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 0.25692 | 31.408 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R30 Ins.
Continuous Ins. - Double glass with no low e coatings - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.9 | 2.517 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - No Ins.
Continuous Ins. - Double glass with no low e coatings - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.2814 | 6.503 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R4 Ins.
Continuous Ins. - Double glass with no low e coatings - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.27 | 9.459 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R7 Ins.
Continuous Ins. - Double glass with no low e coatings - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.26196 | 12.483 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R10 Ins.
Continuous Ins. - Double glass with no low e coatings - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.25296 | 17.669 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R15 Ins.
Continuous Ins. - Double glass with no low e coatings - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.25308 | 22.406 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R20 Ins.
Continuous Ins. - Double glass with no low e coatings - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 0.2478 | 27.721 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R25 Ins.
Continuous Ins. - Double glass with no low e coatings - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 0.2484 | 32.483 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R30 Ins.
Continuous Ins. - Triple or low e glass - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.78 | 2.895 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - No Ins.
Continuous Ins. - Triple or low e glass - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.2652 | 6.902 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R4 Ins.
Continuous Ins. - Triple or low e glass - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.25752 | 9.903 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R7 Ins.
Continuous Ins. - Triple or low e glass - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.25452 | 12.849 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R10 Ins.
Continuous Ins. - Triple or low e glass - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.24804 | 18.018 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R15 Ins.
Continuous Ins. - Triple or low e glass - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.24696 | 22.96 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R20 Ins.
Continuous Ins. - Triple or low e glass - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 0.2478 | 27.721 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R25 Ins.
Continuous Ins. - Triple or low e glass - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 0.2484 | 32.483 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R30 Ins.
Structural Glazing - Single glass pane. stone. or metal pane - No Ins. | StandardOpaqueMaterial | Smooth | 2.52 | 1.2804 | 1.975 | 41.9 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - No Ins.
Structural Glazing - Single glass pane. stone. or metal pane - R4 Ins. | StandardOpaqueMaterial | Smooth | 2.08 | 0.48624 | 4.278 | 50.36 | 0.25 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R4 Ins.
Structural Glazing - Single glass pane. stone. or metal pane - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.8 | 0.5304 | 5.285 | 37.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R7 Ins.
Structural Glazing - Single glass pane. stone. or metal pane - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.52 | 0.5904 | 5.953 | 30.2 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R10 Ins.
Structural Glazing - Single glass pane. stone. or metal pane - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.72 | 0.6996 | 6.726 | 22.79 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R15 Ins.
Structural Glazing - Single glass pane. stone. or metal pane - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.92 | 0.81324 | 7.28 | 18.37 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R20 Ins.
Structural Glazing - Single glass pane. stone. or metal pane - R25 Ins. | StandardOpaqueMaterial | Smooth | 7.12 | 0.93372 | 7.625 | 15.45 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R25 Ins.
Structural Glazing - Single glass pane. stone. or metal pane - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.32 | 1.05 | 7.922 | 13.37 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R30 Ins.
Structural Glazing - Double glass with no low e coatings - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.81 | 2.8 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - No Ins.
Structural Glazing - Double glass with no low e coatings - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.39 | 4.706 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R4 Ins.
Structural Glazing - Double glass with no low e coatings - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.4596 | 5.56 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R7 Ins.
Structural Glazing - Double glass with no low e coatings - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.5304 | 6.192 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R10 Ins.
Structural Glazing - Double glass with no low e coatings - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.64764 | 6.902 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R15 Ins.
Structural Glazing - Double glass with no low e coatings - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.7704 | 7.347 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R20 Ins.
Structural Glazing - Double glass with no low e coatings - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 0.8904 | 7.697 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R25 Ins.
Structural Glazing - Double glass with no low e coatings - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.02 | 7.922 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R30 Ins.
Structural Glazing - Triple or low e glass - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.6504 | 3.479 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - No Ins.
Structural Glazing - Triple or low e glass - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.36 | 5.067 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R4 Ins.
Structural Glazing - Triple or low e glass - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.43836 | 5.817 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R7 Ins.
Structural Glazing - Triple or low e glass - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.51 | 6.396 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R10 Ins.
Structural Glazing - Triple or low e glass - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.63636 | 7.024 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R15 Ins.
Structural Glazing - Triple or low e glass - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.76476 | 7.414 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R20 Ins.
Structural Glazing - Triple or low e glass - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 0.88404 | 7.771 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R25 Ins.
Structural Glazing - Triple or low e glass - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.0104 | 8 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R30 Ins.
Straw Bale - Int and Ext Stucco - 18 in. | StandardOpaqueMaterial | Smooth | 19.5 | 0.6504 | 30 | 12.95 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Straw Bale Wall | Straw Bale - Int and Ext Stucco - 18 in.
Ash - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.1004 | 0.91 | 40.06 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Ash - 1 in.
Birch - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.1904 | 0.84 | 43.93 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Birch - 1 in.
California Redwood - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 0.78 | 1.28 | 26.21 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | California Redwood - 1 in.
Douglas Fir-Larch - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 0.9804 | 1.02 | 34.88 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Douglas Fir-Larch - 1 in.
Hardwood - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.1604 | 0.86 | 42.43 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Hardwood - 1 in.
Hardwood - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 1.1604 | 0.43 | 42.43 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Hardwood - 1/2 in.
Hardwood - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 1.1604 | 0.65 | 42.43 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Hardwood - 3/4 in.
Maple - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.14 | 0.88 | 41.87 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Maple - 1 in.
Oak - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.1796 | 0.85 | 43.93 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Oak - 1 in.
Pine (oven-dried) - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 0.6396 | 1.56 | 23 | 0.45 | [19 empty] | CEC Title24-2013 | AEC | Woods | Pine (oven-dried) - 1 in.
Wood - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.0404 | 0.96 | 37.94 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Wood - 1 in.
Wood - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 1.0404 | 0.48 | 37.94 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Wood - 1/2 in.
Wood - 2 in. | StandardOpaqueMaterial | MediumSmooth | 2 | 1.0404 | 1.92 | 37.94 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Wood - 2 in.
Wood - 4 in. | StandardOpaqueMaterial | MediumSmooth | 4 | 1.0404 | 3.84 | 37.94 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Wood - 4 in.
Wood siding - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.6204 | 0.8 | 36.94 | 0.28 | [19 empty] | CEC Title24-2013 | AEC | Woods | Wood siding - 1/2 in.
Metal Framed Wall - 16inOC - 2x4 - R0 ins. | MasslessOpaqueMaterial |  |  |  | 0.643 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 3_5in | 2x4 | 0
Metal Framed Wall - 16inOC - 2x4 - R5 ins. | MasslessOpaqueMaterial |  |  |  | 1.309 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 3_5in | 2x4 | 5
Metal Framed Wall - 16inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 2.924 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 3_5in | 2x4 | 11
Metal Framed Wall - 16inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 3.068 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 3_5in | 2x4 | 13
Metal Framed Wall - 16inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 3.199 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 3_5in | 2x4 | 15
Metal Framed Wall - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 3.924 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 5_5in | 2x6 | 19
Metal Framed Wall - 16inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 4.078 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 5_5in | 2x6 | 21
Metal Framed Wall - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 4.558 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 7_25in | 2x8 | 19
Metal Framed Wall - 16inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 4.71 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 7_25in | 2x8 | 22
Metal Framed Wall - 16inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 4.789 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 7_25in | 2x8 | 25
Metal Framed Wall - 16inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 4.829 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 7_25in | 2x8 | 30
Metal Framed Wall - 24inOC - 2x4 - R0 ins. | MasslessOpaqueMaterial |  |  |  | 0.658 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 3_5in | 2x4 | 0
Metal Framed Wall - 24inOC - 2x4 - R5 ins. | MasslessOpaqueMaterial |  |  |  | 1.463 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 3_5in | 2x4 | 5
Metal Framed Wall - 24inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 3.222 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 3_5in | 2x4 | 11
Metal Framed Wall - 24inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 3.386 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 3_5in | 2x4 | 13
Metal Framed Wall - 24inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 3.536 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 3_5in | 2x4 | 15
Metal Framed Wall - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 4.558 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 5_5in | 2x6 | 19
Metal Framed Wall - 24inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 4.671 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 5_5in | 2x6 | 21
Metal Framed Wall - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 4.996 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 7_25in | 2x8 | 19
Metal Framed Wall - 24inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 5.171 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 7_25in | 2x8 | 22
Metal Framed Wall - 24inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 5.263 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 7_25in | 2x8 | 25
Metal Framed Wall - 24inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 5.309 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 7_25in | 2x8 | 30
Metal Framed Floor - 16inOC - 2x6 - R0 ins. | MasslessOpaqueMaterial |  |  |  | 0.003 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 5_5in | 2x6 | 0
Metal Framed Floor - 16inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 5.309 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 5_5in | 2x6 | 11
Metal Framed Floor - 16inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 5.854 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 5_5in | 2x6 | 13
Metal Framed Floor - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 6.92 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 5_5in | 2x6 | 19
Metal Framed Floor - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 7.414 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 7_25in | 2x8 | 19
Metal Framed Floor - 16inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 7.815 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 7_25in | 2x8 | 22
Metal Framed Floor - 16inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 9.383 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 9_25in | 2x10 | 30
Metal Framed Floor - 16inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 10.756 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 11_25in | 2x12 | 38
Metal Framed Floor - 24inOC - 2x6 - R0 ins. | MasslessOpaqueMaterial |  |  |  | 0.003 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 5_5in | 2x6 | 0
Metal Framed Floor - 24inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 6.576 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 5_5in | 2x6 | 11
Metal Framed Floor - 24inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 7.544 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 5_5in | 2x6 | 13
Metal Framed Floor - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 9.037 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 5_5in | 2x6 | 19
Metal Framed Floor - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 9.564 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 7_25in | 2x8 | 19
Metal Framed Floor - 24inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 10.336 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 7_25in | 2x8 | 22
Metal Framed Floor - 24inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 12.443 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 9_25in | 2x10 | 30
Metal Framed Floor - 24inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 14.569 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 11_25in | 2x12 | 38
Metal Screw Down Roof - No Thrml Blk - R10 ins. | MasslessOpaqueMaterial |  |  |  | 5.756 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalScrewDown | NA | NA | 10
Metal Screw Down Roof - No Thrml Blk - R11 ins. | MasslessOpaqueMaterial |  |  |  | 6.414 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalScrewDown | NA | NA | 11
Metal Screw Down Roof - No Thrml Blk - R13ins. | MasslessOpaqueMaterial |  |  |  | 6.912 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalScrewDown | NA | NA | 13
Metal Screw Down Roof - No Thrml Blk - R16 ins. | MasslessOpaqueMaterial |  |  |  | 8.654 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalScrewDown | NA | NA | 16
Metal Screw Down Roof - No Thrml Blk - R19 ins. | MasslessOpaqueMaterial |  |  |  | 9.424 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalScrewDown | NA | NA | 19
Metal Standing Seam Roof - Thrml Blk - R6 ins. | MasslessOpaqueMaterial |  |  |  | 5.208 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 6
Metal Standing Seam Roof - Thrml Blk - R10 ins. | MasslessOpaqueMaterial |  |  |  | 9.529 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 10
Metal Standing Seam Roof - Thrml Blk - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.09 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 11
Metal Standing Seam Roof - Thrml Blk - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.268 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 13
Metal Standing Seam Roof - Thrml Blk - R16 ins. | MasslessOpaqueMaterial |  |  |  | 13.109 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 16
Metal Standing Seam Roof - Thrml Blk - R19 ins. | MasslessOpaqueMaterial |  |  |  | 14.605 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 19
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R10 + R10 Ins. | MasslessOpaqueMaterial |  |  |  | 15.093 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 20
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R10 + R11 Ins. | MasslessOpaqueMaterial |  |  |  | 15.613 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 21
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R11 + R11 Ins. | MasslessOpaqueMaterial |  |  |  | 15.887 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 22
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R10 + R13 Ins. | MasslessOpaqueMaterial |  |  |  | 16.461 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 23
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R11 + R13 Ins. | MasslessOpaqueMaterial |  |  |  | 16.764 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 24
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R13 + R13 Ins. | MasslessOpaqueMaterial |  |  |  | 17.402 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 26
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R10 + R19 Ins. | MasslessOpaqueMaterial |  |  |  | 18.451 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 29
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R11 + R19 Ins. | MasslessOpaqueMaterial |  |  |  | 18.828 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 30
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R13 + R19 Ins. | MasslessOpaqueMaterial |  |  |  | 19.628 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 32
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R16 + R19 Ins. | MasslessOpaqueMaterial |  |  |  | 20.497 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 35
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R19 + R19 Ins. | MasslessOpaqueMaterial |  |  |  | 20.959 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 36
Metal Standing Seam Roof - Thrml Blk - Ins. and Filled Cavity - R19 + R10 Ins. | MasslessOpaqueMaterial |  |  |  | 23.61 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeamFilledCavity | NA | NA | 29
Metal Framed Roof - 16inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 6.01 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 3_5In | 2x4 | 11
Metal Framed Roof - 16inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 6.52 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 3_5In | 2x4 | 13
Metal Framed Roof - 16inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 6.96 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 3_5In | 2x4 | 15
Metal Framed Roof - 16inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 6.52 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 3_5In | 2x4 | 19
Metal Framed Roof - 16inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 6.39 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 5_5In | 2x6 | 11
Metal Framed Roof - 16inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 6.96 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 5_5In | 2x6 | 13
Metal Framed Roof - 16inOC - 2x6 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 8.16 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 5_5In | 2x6 | 15
Metal Framed Roof - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 8.26 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 5_5In | 2x6 | 19
Metal Framed Roof - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 8.68 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 7_25In | 2x8 | 19
Metal Framed Roof - 16inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 9.01 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 7_25In | 2x8 | 21
Metal Framed Roof - 16inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 10.16 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 9_25In | 2x10 | 25
Metal Framed Roof - 16inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 10.92 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 9_25In | 2x10 | 30
Metal Framed Roof - 16inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 11.42 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 11_25In | 2x12 | 30
Metal Framed Roof - 16inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 12.34 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 11_25In | 2x12 | 38
Metal Framed Roof - 16inOC - 2x14 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 12.97 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 13_25In | 2x14 | 38
Metal Framed Roof - 24inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 7.27 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 3_5In | 2x4 | 11
Metal Framed Roof - 24inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 8.06 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 3_5In | 2x4 | 13
Metal Framed Roof - 24inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 8.68 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 3_5In | 2x4 | 15
Metal Framed Roof - 24inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 8.06 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 3_5In | 2x4 | 19
Metal Framed Roof - 24inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 7.61 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 5_5In | 2x6 | 11
Metal Framed Roof - 24inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 8.36 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 5_5In | 2x6 | 13
Metal Framed Roof - 24inOC - 2x6 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 9.89 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 5_5In | 2x6 | 15
Metal Framed Roof - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 10.31 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 5_5In | 2x6 | 19
Metal Framed Roof - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 10.76 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 7_25In | 2x8 | 19
Metal Framed Roof - 24inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 11.42 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 7_25In | 2x8 | 21
Metal Framed Roof - 24inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 12.97 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 9_25In | 2x10 | 25
Metal Framed Roof - 24inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 14.13 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 9_25In | 2x10 | 30
Metal Framed Roof - 24inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 14.65 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 11_25In | 2x12 | 30
Metal Framed Roof - 24inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 16.44 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 11_25In | 2x12 | 38
Metal Framed Roof - 24inOC - 2x14 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 17.13 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 13_25In | 2x14 | 38
Wood Framed Wall - 16inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 7.126 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 3_5In | 2x4 | 11
Wood Framed Wall - 16inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 7.7016 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 3_5In | 2x4 | 13
Wood Framed Wall - 16inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 8.1867 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 3_5In | 2x4 | 15
Wood Framed Wall - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 11.7113 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 5_5In | 2x6 | 19
Wood Framed Wall - 16inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 12.2507 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 5_5In | 2x6 | 21
Wood Framed Wall - 16inOC - 2x6 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 12.4993 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 5_5In | 2x6 | 22
Wood Framed Wall - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 13.4581 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 7_25In | 2x8 | 19
Wood Framed Wall - 16inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 14.5092 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 7_25In | 2x8 | 22
Wood Framed Wall - 16inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 15.4247 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 7_25In | 2x8 | 25
Wood Framed Wall - 16inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 16.7137 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 7_25In | 2x8 | 30
Wood Framed Wall - 24inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 7.4404 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 3_5In | 2x4 | 11
Wood Framed Wall - 24inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 8.0977 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 3_5In | 2x4 | 13
Wood Framed Wall - 24inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 8.6586 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 3_5In | 2x4 | 15
Wood Framed Wall - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 12.2765 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 5_5In | 2x6 | 19
Wood Framed Wall - 24inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 12.8954 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 5_5In | 2x6 | 21
Wood Framed Wall - 24inOC - 2x6 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 13.1824 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 5_5In | 2x6 | 22
Wood Framed Wall - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 13.9462 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 7_25In | 2x8 | 19
Wood Framed Wall - 24inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 15.1272 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 7_25In | 2x8 | 22
Wood Framed Wall - 24inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 16.1678 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 7_25In | 2x8 | 25
Wood Framed Wall - 24inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 17.6518 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 7_25In | 2x8 | 30
Wood Framed Wall - 24inOC - 2x4 - R11 ins. AWS | MasslessOpaqueMaterial |  |  |  | 8.0311 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 3_5In | 2x4 | 11
Wood Framed Wall - 24inOC - 2x4 - R13 ins. AWS | MasslessOpaqueMaterial |  |  |  | 8.8567 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 3_5In | 2x4 | 13
Wood Framed Wall - 24inOC - 2x4 - R15 ins. AWS | MasslessOpaqueMaterial |  |  |  | 9.579 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 3_5In | 2x4 | 15
Wood Framed Wall - 24inOC - 2x6 - R19 ins. AWS | MasslessOpaqueMaterial |  |  |  | 13.3502 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 5_5In | 2x6 | 19
Wood Framed Wall - 24inOC - 2x6 - R21 ins. AWS | MasslessOpaqueMaterial |  |  |  | 14.1353 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 5_5In | 2x6 | 21
Wood Framed Wall - 24inOC - 2x6 - R22 ins. AWS | MasslessOpaqueMaterial |  |  |  | 14.5036 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 5_5In | 2x6 | 22
Wood Framed Wall - 24inOC - 2x8 - R19 ins. AWS | MasslessOpaqueMaterial |  |  |  | 14.8435 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 7_25In | 2x8 | 19
Wood Framed Wall - 24inOC - 2x8 - R22 ins. AWS | MasslessOpaqueMaterial |  |  |  | 16.2834 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 7_25In | 2x8 | 22
Wood Framed Wall - 24inOC - 2x8 - R25 ins. AWS | MasslessOpaqueMaterial |  |  |  | 17.5793 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 7_25In | 2x8 | 25
Wood Framed Wall - 24inOC - 2x8 - R30 ins. AWS | MasslessOpaqueMaterial |  |  |  | 19.4735 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 7_25In | 2x8 | 30
Wood Framed Wall - 48inOC - 2x4 - R11 ins. AWS | MasslessOpaqueMaterial |  |  |  | 10.1197 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 3_5In | 2x4 | 11
Wood Framed Wall - 48inOC - 2x4 - R13 ins. AWS | MasslessOpaqueMaterial |  |  |  | 11.711 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 3_5In | 2x4 | 13
Wood Framed Wall - 48inOC - 2x4 - R15 ins. AWS | MasslessOpaqueMaterial |  |  |  | 13.2373 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 3_5In | 2x4 | 15
Wood Framed Wall - 48inOC - 2x6 - R19 ins. AWS | MasslessOpaqueMaterial |  |  |  | 17.2794 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 5_5In | 2x6 | 19
Wood Framed Wall - 48inOC - 2x6 - R21 ins. AWS | MasslessOpaqueMaterial |  |  |  | 18.8464 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 5_5In | 2x6 | 21
Wood Framed Wall - 48inOC - 2x6 - R22 ins. AWS | MasslessOpaqueMaterial |  |  |  | 19.6146 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 5_5In | 2x6 | 22
Wood Framed Wall - 48inOC - 2x8 - R19 ins. AWS | MasslessOpaqueMaterial |  |  |  | 17.8255 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 7_25In | 2x8 | 19
Wood Framed Wall - 48inOC - 2x8 - R22 ins. AWS | MasslessOpaqueMaterial |  |  |  | 20.3213 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 7_25In | 2x8 | 22
Wood Framed Wall - 48inOC - 2x8 - R25 ins. AWS | MasslessOpaqueMaterial |  |  |  | 22.7412 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 7_25In | 2x8 | 25
Wood Framed Wall - 48inOC - 2x8 - R30 ins. AWS | MasslessOpaqueMaterial |  |  |  | 26.6149 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 7_25In | 2x8 | 30
Wood Framed Floor - 16inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.9817 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 5_5In | 2x6 | 11
Wood Framed Floor - 16inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.416 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 5_5In | 2x6 | 13
Wood Framed Floor - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 15.2129 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 5_5In | 2x6 | 19
Wood Framed Floor - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.313 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 7_25In | 2x8 | 19
Wood Framed Floor - 16inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 18.2344 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 7_25In | 2x8 | 22
Wood Framed Floor - 16inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 21.3129 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 9_25In | 2x10 | 25
Wood Framed Floor - 16inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 24.4379 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 9_25In | 2x10 | 30
Wood Framed Floor - 16inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 30.6158 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 11_25In | 2x12 | 38
Wood Framed Floor - 24inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.2668 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 5_5In | 2x6 | 11
Wood Framed Floor - 24inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.8491 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 5_5In | 2x6 | 13
Wood Framed Floor - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.1804 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 5_5In | 2x6 | 19
Wood Framed Floor - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.0358 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 7_25In | 2x8 | 19
Wood Framed Floor - 24inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 19.2214 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 7_25In | 2x8 | 22
Wood Framed Floor - 24inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 22.2995 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 9_25In | 2x10 | 25
Wood Framed Floor - 24inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 25.8772 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 9_25In | 2x10 | 30
Wood Framed Floor - 24inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 32.5111 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 11_25In | 2x12 | 38
Wood Framed Attic Floor - 16inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.0352 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 11
Wood Framed Attic Floor - 16inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 10.1946 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 13
Wood Framed Attic Floor - 16inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 13.1185 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 19
Wood Framed Attic Floor - 16inOC - 2x4 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 13.9437 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 21
Wood Framed Attic Floor - 16inOC - 2x4 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 14.333 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 22
Wood Framed Attic Floor - 16inOC - 2x4 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 15.4178 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 25
Wood Framed Attic Floor - 16inOC - 2x4 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 16.9895 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 30
Wood Framed Attic Floor - 16inOC - 2x4 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 19.0316 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 38
Wood Framed Attic Floor - 16inOC - 2x4 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 20.278 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 44
Wood Framed Attic Floor - 16inOC - 2x4 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 21.1742 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 49
Wood Framed Attic Floor - 16inOC - 2x4 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 22.7998 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 60
Wood Framed Attic Floor - 24inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.5468 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 11
Wood Framed Attic Floor - 24inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 10.9003 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 13
Wood Framed Attic Floor - 24inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 14.4614 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 19
Wood Framed Attic Floor - 24inOC - 2x4 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 15.5068 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 21
Wood Framed Attic Floor - 24inOC - 2x4 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 16.0065 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 22
Wood Framed Attic Floor - 24inOC - 2x4 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 17.421 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 25
Wood Framed Attic Floor - 24inOC - 2x4 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 19.5305 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 30
Wood Framed Attic Floor - 24inOC - 2x4 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 22.3835 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 38
Wood Framed Attic Floor - 24inOC - 2x4 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 24.1906 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 44
Wood Framed Attic Floor - 24inOC - 2x4 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 25.5222 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 49
Wood Framed Attic Floor - 24inOC - 2x4 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 28.0096 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 60
Wood Framed Attic Floor - 16inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.9817 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 11
Wood Framed Attic Floor - 16inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.416 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 13
Wood Framed Attic Floor - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 15.2129 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 19
Wood Framed Attic Floor - 16inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 16.3338 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 21
Wood Framed Attic Floor - 16inOC - 2x6 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 16.8706 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 22
Wood Framed Attic Floor - 16inOC - 2x6 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 18.394 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 25
Wood Framed Attic Floor - 16inOC - 2x6 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 20.6759 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 30
Wood Framed Attic Floor - 16inOC - 2x6 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 23.7814 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 38
Wood Framed Attic Floor - 16inOC - 2x6 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 25.7599 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 44
Wood Framed Attic Floor - 16inOC - 2x6 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 27.2236 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 49
Wood Framed Attic Floor - 16inOC - 2x6 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 29.9711 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 60
Wood Framed Attic Floor - 24inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.2668 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 11
Wood Framed Attic Floor - 24inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.8491 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 13
Wood Framed Attic Floor - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.1804 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 19
Wood Framed Attic Floor - 24inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 17.5004 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 21
Wood Framed Attic Floor - 24inOC - 2x6 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 18.1394 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 22
Wood Framed Attic Floor - 24inOC - 2x6 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 19.9777 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 25
Wood Framed Attic Floor - 24inOC - 2x6 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 22.802 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 30
Wood Framed Attic Floor - 24inOC - 2x6 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 26.7885 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 38
Wood Framed Attic Floor - 24inOC - 2x6 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 29.4185 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 44
Wood Framed Attic Floor - 24inOC - 2x6 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 31.4116 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 49
Wood Framed Attic Floor - 24inOC - 2x6 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 35.2661 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 60
Wood Framed Attic Floor - 16inOC - 2x8 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.4438 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 11
Wood Framed Attic Floor - 16inOC - 2x8 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.0246 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 13
Wood Framed Attic Floor - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.313 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 19
Wood Framed Attic Floor - 16inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 17.6089 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 21
Wood Framed Attic Floor - 16inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 18.2344 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 22
Wood Framed Attic Floor - 16inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 20.0271 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 25
Wood Framed Attic Floor - 16inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 22.7622 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 30
Wood Framed Attic Floor - 16inOC - 2x8 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 26.584 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 38
Wood Framed Attic Floor - 16inOC - 2x8 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 29.0808 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 44
Wood Framed Attic Floor - 16inOC - 2x8 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 30.96 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 49
Wood Framed Attic Floor - 16inOC - 2x8 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 34.5633 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 60
Wood Framed Attic Floor - 24inOC - 2x8 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.6047 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 11
Wood Framed Attic Floor - 24inOC - 2x8 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.3015 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 13
Wood Framed Attic Floor - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.0358 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 19
Wood Framed Attic Floor - 24inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 18.5054 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 21
Wood Framed Attic Floor - 24inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 19.2214 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 22
Wood Framed Attic Floor - 24inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 21.298 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 25
Wood Framed Attic Floor - 24inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 24.5383 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 30
Wood Framed Attic Floor - 24inOC - 2x8 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 29.2172 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 38
Wood Framed Attic Floor - 24inOC - 2x8 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 32.3739 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 44
Wood Framed Attic Floor - 24inOC - 2x8 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 34.804 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 49
Wood Framed Attic Floor - 24inOC - 2x8 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 39.5997 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 60
Wood Framed Attic Floor - 16inOC - 2x10 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.783 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 11
Wood Framed Attic Floor - 16inOC - 2x10 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.4765 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 13
Wood Framed Attic Floor - 16inOC - 2x10 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.1561 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 19
Wood Framed Attic Floor - 16inOC - 2x10 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 18.5953 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 21
Wood Framed Attic Floor - 16inOC - 2x10 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 19.2942 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 22
Wood Framed Attic Floor - 16inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 21.3129 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 25
Wood Framed Attic Floor - 16inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 24.4379 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 30
Wood Framed Attic Floor - 16inOC - 2x10 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 28.8982 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 38
Wood Framed Attic Floor - 16inOC - 2x10 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 31.873 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 44
Wood Framed Attic Floor - 16inOC - 2x10 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 34.1444 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 49
Wood Framed Attic Floor - 16inOC - 2x10 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 38.5802 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 60
Wood Framed Attic Floor - 24inOC - 2x10 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.8472 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 11
Wood Framed Attic Floor - 24inOC - 2x10 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.6291 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 13
Wood Framed Attic Floor - 24inOC - 2x10 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.6705 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 19
Wood Framed Attic Floor - 24inOC - 2x10 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 19.2568 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 21
Wood Framed Attic Floor - 24inOC - 2x10 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 20.0334 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 22
Wood Framed Attic Floor - 24inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 22.2995 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 25
Wood Framed Attic Floor - 24inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 25.8772 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 30
Wood Framed Attic Floor - 24inOC - 2x10 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 31.1355 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 38
Wood Framed Attic Floor - 24inOC - 2x10 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 34.7459 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 44
Wood Framed Attic Floor - 24inOC - 2x10 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 37.5607 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 49
Wood Framed Attic Floor - 24inOC - 2x10 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 43.2077 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 60
Wood Framed Attic Floor - 16inOC - 2x12 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 11.0136 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 11
Wood Framed Attic Floor - 16inOC - 2x12 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.7862 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 13
Wood Framed Attic Floor - 16inOC - 2x12 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.7471 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 19
Wood Framed Attic Floor - 16inOC - 2x12 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 19.2917 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 21
Wood Framed Attic Floor - 16inOC - 2x12 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 20.045 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 22
Wood Framed Attic Floor - 16inOC - 2x12 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 22.2328 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 25
Wood Framed Attic Floor - 16inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 25.6551 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 30
Wood Framed Attic Floor - 16inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 30.6158 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 38
Wood Framed Attic Floor - 16inOC - 2x12 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 33.9752 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 44
Wood Framed Attic Floor - 16inOC - 2x12 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 36.5684 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 49
Wood Framed Attic Floor - 16inOC - 2x12 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 41.7037 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 60
Wood Framed Attic Floor - 24inOC - 2x12 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 11.0095 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 11
Wood Framed Attic Floor - 24inOC - 2x12 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.8496 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 13
Wood Framed Attic Floor - 24inOC - 2x12 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 18.1053 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 19
Wood Framed Attic Floor - 24inOC - 2x12 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 19.7743 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 21
Wood Framed Attic Floor - 24inOC - 2x12 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 20.594 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 22
Wood Framed Attic Floor - 24inOC - 2x12 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 22.9964 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 25
Wood Framed Attic Floor - 24inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 26.8204 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 30
Wood Framed Attic Floor - 24inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 32.5111 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 38
Wood Framed Attic Floor - 24inOC - 2x12 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 36.4678 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 44
Wood Framed Attic Floor - 24inOC - 2x12 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 39.581 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 49
Wood Framed Attic Floor - 24inOC - 2x12 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 45.903 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 60
Wood Framed Rafter Roof - 16inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.0352 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 3_5In | 2x4 | 11
Wood Framed Rafter Roof - 16inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 10.1946 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 3_5In | 2x4 | 13
Wood Framed Rafter Roof - 16inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 11.2537 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 3_5In | 2x4 | 15
Wood Framed Rafter Roof - 16inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 13.1185 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 3_5In | 2x4 | 19
Wood Framed Rafter Roof - 16inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.9817 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 5_5In | 2x6 | 11
Wood Framed Rafter Roof - 16inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.416 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 5_5In | 2x6 | 13
Wood Framed Rafter Roof - 16inOC - 2x6 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 12.7607 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 5_5In | 2x6 | 15
Wood Framed Rafter Roof - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 15.2129 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 5_5In | 2x6 | 19
Wood Framed Rafter Roof - 16inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 16.3338 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 5_5In | 2x6 | 21
Wood Framed Rafter Roof - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.313 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 7_25In | 2x8 | 19
Wood Framed Rafter Roof - 16inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 17.6089 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 7_25In | 2x8 | 21
Wood Framed Rafter Roof - 16inOC - 2x10 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 19.2942 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 9_25In | 2x10 | 22
Wood Framed Rafter Roof - 16inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 21.3129 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 9_25In | 2x10 | 25
Wood Framed Rafter Roof - 16inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 24.4379 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 9_25In | 2x10 | 30
Wood Framed Rafter Roof - 16inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 25.6551 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 11_25In | 2x12 | 30
Wood Framed Rafter Roof - 16inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 30.6158 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 11_25In | 2x12 | 38
Wood Framed Rafter Roof - 16inOC - 2x14 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 30.6158 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 11_25In | 2x14 | 38
Wood Framed Rafter Roof - 24inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.5468 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 3_5In | 2x4 | 11
Wood Framed Rafter Roof - 24inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 10.9003 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 3_5In | 2x4 | 13
Wood Framed Rafter Roof - 24inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 12.1652 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 3_5In | 2x4 | 15
Wood Framed Rafter Roof - 24inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 14.4614 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 3_5In | 2x4 | 19
Wood Framed Rafter Roof - 24inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.2668 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 5_5In | 2x6 | 11
Wood Framed Rafter Roof - 24inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.8491 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 5_5In | 2x6 | 13
Wood Framed Rafter Roof - 24inOC - 2x6 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 13.359 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 5_5In | 2x6 | 15
Wood Framed Rafter Roof - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.1804 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 5_5In | 2x6 | 19
Wood Framed Rafter Roof - 24inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 17.5004 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 5_5In | 2x6 | 21
Wood Framed Rafter Roof - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.0358 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 7_25In | 2x8 | 19
Wood Framed Rafter Roof - 24inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 18.5054 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 7_25In | 2x8 | 21
Wood Framed Rafter Roof - 24inOC - 2x10 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 20.0334 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 9_25In | 2x10 | 22
Wood Framed Rafter Roof - 24inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 22.2995 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 9_25In | 2x10 | 25
Wood Framed Rafter Roof - 24inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 25.8772 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 9_25In | 2x10 | 30
Wood Framed Rafter Roof - 24inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 26.8204 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 11_25In | 2x12 | 30
Wood Framed Rafter Roof - 24inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 32.5111 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 11_25In | 2x12 | 38
Wood Framed Rafter Roof - 24inOC - 2x14 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 32.5111 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 11_25In | 2x14 | 38
DOE Prototype 1/2 in. Gypsum Board | StandardOpaqueMaterial | Smooth | 0.5 | 1.1094 | 0.90142 | 49.9424 | 0.26034 | 0.9 | 0.7 | 0.5
DOE Prototype 25mm Stucco | StandardOpaqueMaterial | Smooth | 1 | 4.9921 | 0.20032 | 115.8663 | 0.20063 | 0.9 | 0.7 | 0.7
DOE Prototype 4 in. Normalweight Concrete Floor | StandardOpaqueMaterial | MediumRough | 4 | 16.0163 | 0.062436 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7
DOE Prototype 4 in. Normalweight Concrete Wall | StandardOpaqueMaterial | MediumRough | 4 | 16.0163 | 0.062436 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7
DOE Prototype 5/8 in. Gypsum Board | StandardOpaqueMaterial | MediumSmooth | 0.62598 | 1.1094 | 0.90142 | 49.9424 | 0.26034 | 0.9 | 0.7 | 0.7
DOE Prototype 5/8 in. Plywood | StandardOpaqueMaterial | Smooth | 0.62598 | 0.83202 | 1.2019 | 33.9608 | 0.289 | 0.9 | 0.7 | 0.7
DOE Prototype 6 in. Heavyweight Concrete Roof | StandardOpaqueMaterial | MediumRough | 6 | 16.0163 | 0.062436 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7
DOE Prototype 6 in. Normalweight Concrete Floor | StandardOpaqueMaterial | MediumRough | 6 | 16.0163 | 0.062436 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7
DOE Prototype 8 in. Concrete Block Basement Wall | StandardOpaqueMaterial | MediumRough | 8 | 9.1938 | 0.10877 | 114.9923 | 0.21783 | 0.9 | 0.7 | 0.7
DOE Prototype 8 in. Concrete Block Wall | StandardOpaqueMaterial | MediumRough | 8 | 4.9921 | 0.20032 | 49.9424 | 0.19872 | 0.9 | 0.7 | 0.7
DOE Prototype 8 in. Normalweight Concrete Floor | StandardOpaqueMaterial | MediumRough | 8 | 16.0163 | 0.062436 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7
DOE Prototype 8 in. Normalweight Concrete Wall | StandardOpaqueMaterial | MediumRough | 8 | 16.0163 | 0.062436 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7
DOE Prototype Acoustic Ceiling | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.39521 | 2.5303 | 17.9793 | 0.31981 | 0.9 | 0.7 | 0.2
DOE Prototype Asphalt Shingles | StandardOpaqueMaterial | VeryRough | 0.12598 | 0.27734 | 3.6057 | 69.9193 | 0.30095 | 0.9 | 0.7 | 0.7
DOE Prototype Built-up Roofing | StandardOpaqueMaterial | Rough | 0.37402 | 1.1094 | 0.90142 | 69.9193 | 0.34872 | 0.9 | 0.7 | 0.7
DOE Prototype Bulk Storage Products Material | StandardOpaqueMaterial | Rough | 96.0002 | 9.9981 | 0.10002 | 12.5 | 0.19987 | 0.9 | 0.7 | 0.7
DOE Prototype Gypsum Or Plaster Board - 3/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.37402 | 4.0214 | 0.24867 | 49.9424 | 0.26034 | 0.9 | 0.7 | 0.7
DOE Prototype Interior Wall Addi Insul | StandardOpaqueMaterial | MediumRough | 1e-06 | 0.29994 | 3.334 | 1.4 | 0.19987 | 0.9 | 0.7 | 0.7
DOE Prototype Metal Roof Surface | StandardOpaqueMaterial | Smooth | 0.031496 | 313.9476 | 0.0031852 | 488.4364 | 0.11942 | 0.9 | 0.7 | 0.7
DOE Prototype Metal Surface | StandardOpaqueMaterial | Smooth | 0.031496 | 313.9476 | 0.0031852 | 488.4364 | 0.11942 | 0.9 | 0.7 | 0.7
DOE Prototype Std Wood 6 in. | StandardOpaqueMaterial | MediumSmooth | 5.9055 | 0.83202 | 1.2019 | 33.7111 | 0.289 | 0.9 | 0.7 | 0.7
DOE Prototype Steel Frame/Cavity | StandardOpaqueMaterial | MediumRough | 3.5 | 0.58322 | 1.7146 | 40.04 | 0.11992 | 0.9 | 0.7 | 0.7
DOE Prototype Air Wall Material R-1.18 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Cp02 Carpet Pad R-1.23 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00019108 | 0.9 | 0.7 | 0.8
DOE Prototype Nonres Exterior Wall Insulation R-0.17 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-10.6 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-10.7 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-10.81 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-12.28 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-13.19 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-13.45 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-15.37 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-16.0 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-16.24 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-17.43 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-18.23 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-18.7 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-19.03 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-21.43 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-24.34 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-24.85 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-25.6 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-29.07 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-4.82 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-5.89 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-6.33 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-7.55 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-7.82 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-9.06 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-9.31 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-9.45 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Exterior Wall Insulation R-9.73 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Floor Insulation R-0.17 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Floor Insulation R-16.37 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Floor Insulation R-23.45 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Floor Insulation R-28.39 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-0.17 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-14.6 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-14.76 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-17.4 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-19.63 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-19.72 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-23.61 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-24.52 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-24.86 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-26.25 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-27.78 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-27.79 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-30.13 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-31.48 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-33.7 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-34.6 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-35.4 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-37.68 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-45.98 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-45.99 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Nonres Roof Insulation R-57.19 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Opaque Door Panel Con R-1.43 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Opaque Door Panel Con R-2.0 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Opaque Door Panel Semi R-1.43 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Overhead Door Panel R-0.69 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Overhead Door Panel R-2.0 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype R13 Insulation R-12.99 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-0.17 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-10.7 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-12.28 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-13.45 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-16.0 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-17.43 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-18.23 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-19.03 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-21.63 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-24.85 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-4.82 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-5.89 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-6.33 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-7.82 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-9.31 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Exterior Wall Insulation R-9.73 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Floor Insulation R-0.17 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Roof Insulation R-0.17 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Roof Insulation R-14.76 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Roof Insulation R-19.72 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Roof Insulation R-24.52 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Roof Insulation R-30.13 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Res Roof Insulation R-34.6 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Semiheated Exterior Wall Insulation R-0.17 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Semiheated Exterior Wall Insulation R-4.13 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Semiheated Exterior Wall Insulation R-6.16 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Semiheated Exterior Wall Insulation R-6.83 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Semiheated Exterior Wall Insulation R-7.55 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Semiheated Floor Insulation R-0.17 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Semiheated Roof Insulation R-0.01 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Semiheated Roof Insulation R-0.17 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Semiheated Roof Insulation R-11.27 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Semiheated Roof Insulation R-13.11 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Semiheated Roof Insulation R-14.6 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Semiheated Roof Insulation R-5.21 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Semiheated Roof Insulation R-9.53 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
DOE Prototype Std Opaque Door Panel R-0.7 | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
BLUE 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.48 | 0.05 | 0.05 | 0.57 | 0.06 | 0.06 | 0 | 0.84 | 0.84 | 1 | FALSE
BRONZE 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.482 | 0.054 | 0.054 | 0.534 | 0.057 | 0.057 | 0 | 0.84 | 0.84 | 1 | FALSE
CLEAR 2.5MM | StandardGlazing |  | 0.098425 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.8 | 0.075 | 0.075 | 0.901 | 0.081 | 0.081 | 0 | 0.84 | 0.84 | 1 | FALSE
CLEAR 3MM | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.837 | 0.075 | 0.075 | 0.898 | 0.081 | 0.081 | 0 | 0.84 | 0.84 | 1 | FALSE
CLEAR 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.775 | 0.071 | 0.071 | 0.881 | 0.08 | 0.08 | 0 | 0.84 | 0.84 | 1 | FALSE
COATED POLY-55 | StandardGlazing |  | 0.020079 | 0.97069 | 1.0302 | [9 empty] | SpectralAverage | 0.32 | 0.582 | 0.593 | 0.551 | 0.336 | 0.375 | 0 | 0.046 | 0.72 | 1 | FALSE
COATED POLY-77 | StandardGlazing |  | 0.020079 | 0.97069 | 1.0302 | [9 empty] | SpectralAverage | 0.504 | 0.402 | 0.398 | 0.766 | 0.147 | 0.167 | 0 | 0.075 | 0.72 | 1 | FALSE
ECABS-2 BLEACHED 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.814 | 0.086 | 0.086 | 0.847 | 0.099 | 0.099 | 0 | 0.84 | 0.1 | 1 | FALSE
ECABS-2 COLORED 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.111 | 0.179 | 0.179 | 0.128 | 0.081 | 0.081 | 0 | 0.84 | 0.1 | 1 | FALSE
ECREF-1 COLORED 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.099 | 0.219 | 0.219 | 0.155 | 0.073 | 0.073 | 0 | 0.84 | 0.84 | 1 | FALSE
ECREF-2 BLEACHED 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.694 | 0.168 | 0.168 | 0.818 | 0.11 | 0.11 | 0 | 0.84 | 0.1 | 1 | FALSE
ECREF-2 COLORED 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.099 | 0.219 | 0.219 | 0.155 | 0.073 | 0.073 | 0 | 0.84 | 0.1 | 1 | FALSE
Glass_2010F_LayerAvg | StandardGlazing |  | 0.087008 | 6.9335 | 0.14423 | [9 empty] | SpectralAverage | 0.43429 | 0.41837 | 0.34107 | 0.79758 | 0.043577 | 0.056031 | 0 | 0.042274 | 0.84 | 1 | FALSE
Glass_2022F_LayerAvg | StandardGlazing |  | 0.15354 | 6.9335 | 0.14423 | [9 empty] | SpectralAverage | 0.3559 | 0.39409 | 0.26565 | 0.67769 | 0.042734 | 0.05547 | 0 | 0.046 | 0.84 | 1 | FALSE
Glass_2027F_LayerAvg | StandardGlazing |  | 0.15748 | 6.9335 | 0.14423 | [9 empty] | SpectralAverage | 0.36974 | 0.47007 | 0.34093 | 0.76522 | 0.0546 | 0.073741 | 0 | 0.03675 | 0.84 | 1 | FALSE
Glass_2052_LayerAvg | StandardGlazing |  | 0.32953 | 6.9335 | 0.14423 | [9 empty] | SpectralAverage | 0.50777 | 0.054228 | 0.054493 | 0.58683 | 0.05805 | 0.058397 | 0 | 0.84 | 0.84 | 1 | FALSE
Glass_2175_LayerAvg | StandardGlazing |  | 0.33858 | 6.9335 | 0.14423 | [9 empty] | SpectralAverage | 0.16776 | 0.21761 | 0.43798 | 0.41604 | 0.078729 | 0.10654 | 0 | 0.84 | 0.84 | 1 | FALSE
GREEN 3MM | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.635 | 0.063 | 0.063 | 0.822 | 0.075 | 0.075 | 0 | 0.84 | 0.84 | 1 | FALSE
GREEN 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.487 | 0.056 | 0.056 | 0.749 | 0.07 | 0.07 | 0 | 0.84 | 0.84 | 1 | FALSE
GREY 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.455 | 0.053 | 0.053 | 0.431 | 0.052 | 0.052 | 0 | 0.84 | 0.84 | 1 | FALSE
LoE CLEAR 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.6 | 0.17 | 0.22 | 0.84 | 0.055 | 0.078 | 0 | 0.84 | 0.1 | 1 | FALSE
LoE SPEC SEL CLEAR 3MM | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.45 | 0.34 | 0.37 | 0.78 | 0.07 | 0.06 | 0 | 0.84 | 0.03 | 1 | FALSE
LoE SPEC SEL CLEAR 6MM Rev | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.43 | 0.42 | 0.3 | 0.77 | 0.06 | 0.07 | 0 | 0.03 | 0.84 | 1 | FALSE
LoE SPEC SEL TINT 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.26 | 0.14 | 0.41 | 0.46 | 0.06 | 0.04 | 0 | 0.84 | 0.03 | 1 | FALSE
LoE TINT 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.36 | 0.093 | 0.2 | 0.5 | 0.035 | 0.054 | 0 | 0.84 | 0.1 | 1 | FALSE
PYR B CLEAR 3MM | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.74 | 0.09 | 0.1 | 0.82 | 0.11 | 0.12 | 0 | 0.84 | 0.2 | 1 | FALSE
PYR B CLEAR 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.68 | 0.09 | 0.1 | 0.81 | 0.11 | 0.12 | 0 | 0.84 | 0.2 | 1 | FALSE
REF A CLEAR LO 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.066 | 0.341 | 0.493 | 0.08 | 0.41 | 0.37 | 0 | 0.84 | 0.4 | 1 | FALSE
REF A CLEAR MID 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.11 | 0.27 | 0.43 | 0.14 | 0.31 | 0.35 | 0 | 0.84 | 0.47 | 1 | FALSE
REF A TINT MID 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.06 | 0.13 | 0.42 | 0.09 | 0.14 | 0.35 | 0 | 0.84 | 0.47 | 1 | FALSE
REF B CLEAR HI 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.24 | 0.16 | 0.32 | 0.3 | 0.16 | 0.29 | 0 | 0.84 | 0.6 | 1 | FALSE
REF B CLEAR LO 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.15 | 0.22 | 0.38 | 0.2 | 0.23 | 0.33 | 0 | 0.84 | 0.58 | 1 | FALSE
REF B TINT HI 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.15 | 0.09 | 0.33 | 0.18 | 0.08 | 0.28 | 0 | 0.84 | 0.6 | 1 | FALSE
REF B TINT MID 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.1 | 0.11 | 0.41 | 0.13 | 0.1 | 0.32 | 0 | 0.84 | 0.45 | 1 | FALSE
REF C CLEAR HI 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.2 | 0.16 | 0.39 | 0.22 | 0.17 | 0.35 | 0 | 0.84 | 0.55 | 1 | FALSE
REF C CLEAR MID 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.17 | 0.2 | 0.42 | 0.19 | 0.21 | 0.38 | 0 | 0.84 | 0.51 | 1 | FALSE
REF D CLEAR 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.429 | 0.308 | 0.379 | 0.334 | 0.453 | 0.505 | 0 | 0.84 | 0.82 | 1 | FALSE
REF D TINT 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.3 | 0.14 | 0.36 | 0.25 | 0.18 | 0.45 | 0 | 0.84 | 0.82 | 1 | FALSE
Theoretical Glass 297 | StandardGlazing |  | 0.11811 | 0.071804 | 13.9269 | [9 empty] | SpectralAverage | 0.37504 | 0.57496 | 0.57496 | 0.5297 | 0.4203 | 0.4203 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass 347 | StandardGlazing |  | 0.11811 | 0.071817 | 13.9243 | [9 empty] | SpectralAverage | 0.31586 | 0.63414 | 0.63414 | 0.47991 | 0.47009 | 0.47009 | 0 | 0.9 | 0.9 | 1 | FALSE
AIR 13MM | Gas |  | 0.5 | [7 empty] | Air
AIR 3MM | Gas |  | 0.12598 | [7 empty] | Air
AIR 6MM | Gas |  | 0.24803 | [7 empty] | Air
ARGON 13MM | Gas |  | 0.5 | [7 empty] | Argon
Gap_1_W_0_0018 | Gas |  | 0.070866 | [7 empty] | Air
Gap_1_W_0_0024 | Gas |  | 0.094488 | [7 empty] | Air
Gap_1_W_0_0025 | Gas |  | 0.098425 | [7 empty] | Air
Gap_1_W_0_0032 | Gas |  | 0.12598 | [7 empty] | Air
Gap_1_W_0_0038 | Gas |  | 0.14961 | [7 empty] | Air
Gap_1_W_0_0042 | Gas |  | 0.16535 | [7 empty] | Air
Gap_1_W_0_0043 | Gas |  | 0.16929 | [7 empty] | Air

## Schedules
Each row represents the efficiency standards for a specificy type of chiller
Day Type choices: Default, Wkdy, Wknd, Mon, Tue, Wed, Thu, Fri, Sat, Sun, WntrDsn, SmrDsn, Hol
Name | Category | Units | Day Types | Start Date | End Date | Type | Hr 1 | Hr 2 | Hr 3 | Hr 4 | Hr 5 | Hr 6 | Hr 7 | Hr 8 | Hr 9 | Hr 10 | Hr 11 | Hr 12 | Hr 13 | Hr 14 | Hr 15 | Hr 16 | Hr 17 | Hr 18 | Hr 19 | Hr 20 | Hr 21 | Hr 22 | Hr 23 | Hr 24 | Notes
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Always On | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Bldg Equip | Equipment |  | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
FullServiceRestaurant Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | From DOE Reference Buildings
FullServiceRestaurant Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | From DOE Reference Buildings
FullServiceRestaurant Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2 | From DOE Reference Buildings
FullServiceRestaurant Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35 | From DOE Reference Buildings
FullServiceRestaurant Bldg Swh | Service Water Heating |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | From DOE Reference Buildings
FullServiceRestaurant Bldg Swh | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | From DOE Reference Buildings
FullServiceRestaurant Bldg Swh | Service Water Heating |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | From DOE Reference Buildings
FullServiceRestaurant ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Reference Buildings
FullServiceRestaurant ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Reference Buildings
FullServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Gas Equip | Equipment |  | Default¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | From DOE Reference Buildings
FullServiceRestaurant Gas Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Gas Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | From DOE Reference Buildings
FullServiceRestaurant HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | From DOE Reference Buildings
FullServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 19 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Infil Half On | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
FullServiceRestaurant Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Hospital Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
Hospital Bldg ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Reference Buildings
Hospital Bldg ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Reference Buildings
Hospital Bldg ClgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | 25 | [23 empty] | From DOE Reference Buildings
Hospital BLDG ELEVATORS | Elevator |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | From DOE Reference Buildings
Hospital BLDG ELEVATORS | Elevator |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Reference Buildings
Hospital BLDG ELEVATORS | Elevator |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Reference Buildings
Hospital Bldg Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Hospital Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Reference Buildings
Hospital Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Hospital Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Hospital Bldg HtgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Reference Buildings
Hospital Bldg HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Reference Buildings
Hospital Bldg HtgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | 18.3 | [23 empty] | From DOE Reference Buildings
Hospital Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Reference Buildings
Hospital Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Hospital Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Hospital Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Hospital Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Hospital Bldg Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
Hospital Bldg Occ | Occupancy |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Hospital Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Hospital Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Hospital Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Hospital Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Hospital Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Hospital Critical ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22.2 | [23 empty] | From DOE Reference Buildings
Hospital Critical Equip | Equipment |  | Default¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
Hospital Critical Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Reference Buildings
Hospital Critical HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.1 | [23 empty] | From DOE Reference Buildings
Hospital Critical Light | Lighting |  | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | From DOE Reference Buildings
Hospital Critical Occ | Occupancy |  | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | From DOE Reference Buildings
Hospital Infil Quarter On | Infiltration |  | Default¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
Hospital Infil Quarter On | Infiltration |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Hospital Kitchen ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
Hospital Kitchen ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
Hospital Kitchen ClgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
Hospital Kitchen Exhaust | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Hospital Kitchen Exhaust | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Hospital Kitchen Exhaust | Equipment |  | Wknd | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Hospital Kitchen Gas | Equipment |  | Default¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | From DOE Reference Buildings
Hospital Kitchen Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Hospital Kitchen Gas | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
Hospital Kitchen HtgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Hospital Kitchen HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Hospital Kitchen HtgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
Hospital OR ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | From DOE Reference Buildings
Hospital OR HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.3 | [23 empty] | From DOE Reference Buildings
Hospital Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Large Office Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
Large Office BLDG ELEVATORS | Elevator |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Reference Buildings
Large Office Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | From DOE Reference Buildings
Large Office Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Large Office Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Large Office Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Reference Buildings
Large Office Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Large Office Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | From DOE Reference Buildings
Large Office Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Large Office Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Large Office Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Reference Buildings
Large Office Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Large Office Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
Large Office Bldg Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Large Office Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Reference Buildings
Large Office Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Large Office ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Reference Buildings
Large Office ClgSetp | Thermostat Setpoint | C | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Reference Buildings
Large Office ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Reference Buildings
Large Office Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Large Office Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Large Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Large Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Large Office HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
Large Office HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
Large Office HtgSetp | Thermostat Setpoint | C | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
Large Office HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Large Office Infil Quarter On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Reference Buildings
Large Office Infil Quarter On | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
Large Office Infil Quarter On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Large Office Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
LargeHotel BLDG ELEVATORS | Elevator |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Reference Buildings
LargeHotel Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | From DOE Reference Buildings
LargeHotel Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | From DOE Reference Buildings
LargeHotel Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | From DOE Reference Buildings
LargeHotel Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Reference Buildings
LargeHotel Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Reference Buildings
LargeHotel Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Reference Buildings
LargeHotel Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | From DOE Reference Buildings
LargeHotel Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | From DOE Reference Buildings
LargeHotel Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | From DOE Reference Buildings
LargeHotel ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Reference Buildings
LargeHotel Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
LargeHotel Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
LargeHotel Corridor ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
LargeHotel Corridor HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Reference Buildings
LargeHotel GuestRoom Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom Equip | Equipment |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Reference Buildings
LargeHotel GuestRoom HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | From DOE Reference Buildings
LargeHotel GuestRoom Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
LargeHotel HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | From DOE Reference Buildings
LargeHotel Infil Quarter On | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
LargeHotel Kitchen ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Reference Buildings
LargeHotel Kitchen Equip | Equipment |  | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
LargeHotel Kitchen Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel Kitchen Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
LargeHotel Kitchen Exhaust | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
LargeHotel Kitchen Gas | Equipment |  | Default¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | From DOE Reference Buildings
LargeHotel Kitchen Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel Kitchen Gas | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
LargeHotel Kitchen HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | From DOE Reference Buildings
LargeHotel LaundryRoom Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
LargeHotel LaundryRoom Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel LaundryRoom Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel LaundryRoom Gas | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
LargeHotel LaundryRoom Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel LaundryRoom Gas | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel Lobby Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Reference Buildings
LargeHotel Lobby Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel Lobby Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel Lobby Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Reference Buildings
LargeHotel Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Medium Office Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
Medium Office BLDG ELEVATORS | Elevator |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | From DOE Reference Buildings
Medium Office BLDG ELEVATORS | Elevator |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Medium Office BLDG ELEVATORS | Elevator |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | From DOE Reference Buildings
Medium Office Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Medium Office Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Medium Office Bldg Swh | Service Water Heating |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Swh | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Swh | Service Water Heating |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | From DOE Reference Buildings
Medium Office ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Reference Buildings
Medium Office ClgSetp | Thermostat Setpoint | C | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Reference Buildings
Medium Office ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Reference Buildings
Medium Office Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Medium Office Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Medium Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Medium Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Medium Office HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
Medium Office HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
Medium Office HtgSetp | Thermostat Setpoint | C | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
Medium Office HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Medium Office Infil Quarter On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Reference Buildings
Medium Office Infil Quarter On | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
Medium Office Infil Quarter On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Medium Office Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
MidriseApartment Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
MidriseApartment Apartment ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.9 | [23 empty] | From DOE Reference Buildings
MidriseApartment Apartment DHW | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29 | From DOE Reference Buildings
MidriseApartment Apartment Equip | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58 | From DOE Reference Buildings
MidriseApartment Apartment HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.1 | [23 empty] | From DOE Reference Buildings
MidriseApartment Apartment Light | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.067 | 0.067 | 0.067 | 0.067 | 0.187 | 0.394 | 0.44 | 0.393 | 0.172 | 0.119 | 0.119 | 0.119 | 0.119 | 0.119 | 0.119 | 0.206 | 0.439 | 0.616 | 0.829 | 0.986 | 1 | 0.692 | 0.384 | 0.16 | From DOE Reference Buildings
MidriseApartment Apartment Occ | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1 | From DOE Reference Buildings
MidriseApartment Apartment Operation | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
MidriseApartment BLDG ELEVATORS | Elevator |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Reference Buildings
MidriseApartment Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
MidriseApartment Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
MidriseApartment Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
MidriseApartment Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
MidriseApartment Corridor ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 40 | [23 empty] | From DOE Reference Buildings
MidriseApartment Corridor HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
MidriseApartment Corridor Light | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
MidriseApartment Infil | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
MidriseApartment Office ClgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Reference Buildings
MidriseApartment Office ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.4 | [23 empty] | From DOE Reference Buildings
MidriseApartment Office ClgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Reference Buildings
MidriseApartment Office Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | From DOE Reference Buildings
MidriseApartment Office Equip | Equipment |  | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Reference Buildings
MidriseApartment Office HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
MidriseApartment Office HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
MidriseApartment Office HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
MidriseApartment OFFICE Infil | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
MidriseApartment OFFICE Infil | Infiltration |  | WntrDsn¦SmrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
MidriseApartment Office Light | Lighting |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | From DOE Reference Buildings
MidriseApartment Office Light | Lighting |  | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 0.18 | [23 empty] | From DOE Reference Buildings
MidriseApartment Office Occ | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
MidriseApartment Office Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
MidriseApartment Office Operation | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
MidriseApartment Office Operation | Operation |  | Wknd | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
MidriseApartment UnitHeater ClgSP Sch | Thermostat Setpoint |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
MidriseApartment UnitHeater HtgSP Sch | Thermostat Setpoint |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
MidriseApartment Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Office Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 132 | [23 empty] | From DOE Reference Buildings
Office Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | From DOE Reference Buildings
Office Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Office Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Office Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Reference Buildings
Office Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Office Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | From DOE Reference Buildings
Office Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Office Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Office Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Reference Buildings
Office Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Office Infil Quarter On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Reference Buildings
Office Infil Quarter On | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
Office Infil Quarter On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Office Misc Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
Office Misc Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Office Misc Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Reference Buildings
Office Misc Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Office Work Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.85 | 0.85 | 0.85 | 0.85 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
Office Work Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Office Work Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Reference Buildings
Office Work Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Outpatient Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
Outpatient BLDG ELEVATORS | Elevator |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient BLDG ELEVATORS | Elevator |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient BLDG ELEVATORS | Elevator |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient Bldg Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Outpatient Bldg Equip | Equipment |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Outpatient Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Outpatient Bldg Light | Lighting |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Reference Buildings
Outpatient Bldg Light | Lighting |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Outpatient Bldg Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient Bldg Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Outpatient Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Reference Buildings
Outpatient ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Reference Buildings
Outpatient ClgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | 25 | [23 empty] | From DOE Reference Buildings
Outpatient Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Outpatient Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Outpatient Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Outpatient Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Outpatient HtgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Reference Buildings
Outpatient HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Reference Buildings
Outpatient HtgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | 18.3 | [23 empty] | From DOE Reference Buildings
Outpatient Infil | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Outpatient Infil | Infiltration |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Outpatient OR ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | From DOE Reference Buildings
Outpatient OR HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.3 | [23 empty] | From DOE Reference Buildings
Outpatient Radiology Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | From DOE Reference Buildings
Outpatient Radiology Equip | Equipment |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0.01 | [23 empty] | From DOE Reference Buildings
Outpatient Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
PrimarySchool BathCorrMechKitchen ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 27 | [23 empty] | From DOE Reference Buildings
PrimarySchool BathCorrMechKitchen ClgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
PrimarySchool BathCorrMechKitchen HtgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Reference Buildings
PrimarySchool BathCorrMechKitchen HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool ClgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
PrimarySchool ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 27 | [23 empty] | From DOE Reference Buildings
PrimarySchool ClgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Reference Buildings
PrimarySchool ClgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
PrimarySchool ClgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27 | From DOE Reference Buildings
PrimarySchool Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Reference Buildings
PrimarySchool Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.6 | [23 empty] | From DOE Reference Buildings
PrimarySchool Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Reference Buildings
PrimarySchool Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.6 | [23 empty] | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
PrimarySchool HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
PrimarySchool HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Reference Buildings
PrimarySchool HtgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
PrimarySchool HtgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | From DOE Reference Buildings
PrimarySchool Infil | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13 | 0.13 | 0.2 | 0.2 | 0.2 | 0.13 | 0.13 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Exhaust | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Kitchen Exhaust | Equipment |  | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Bldg Equip | Equipment |  | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.35 | 0.35 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.3 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.2 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Bldg Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.2 | 0.45 | 0.6 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.2 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Swh | Service Water Heating |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Swh | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Swh | Service Water Heating |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | From DOE Reference Buildings
QuickServiceRestaurant ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Reference Buildings
QuickServiceRestaurant ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Reference Buildings
QuickServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Gas Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.09 | 0.14 | 0.1 | 0.1 | 0.22 | 0.27 | 0.24 | 0.21 | 0.14 | 0.13 | 0.15 | 0.17 | 0.17 | 0.17 | 0.15 | 0.14 | 0.12 | 0.02 | From DOE Reference Buildings
QuickServiceRestaurant Gas Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Gas Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 19 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Infil Half On | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
QuickServiceRestaurant Kitchen Exhaust | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
QuickServiceRestaurant Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Retail Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
Retail Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | From DOE Reference Buildings
Retail Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Retail Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Retail Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | From DOE Reference Buildings
Retail Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | From DOE Reference Buildings
Retail Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
Retail Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Retail Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Retail Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Retail Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
Retail Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | From DOE Reference Buildings
Retail Bldg Occ | Occupancy |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Retail Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Retail Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | From DOE Reference Buildings
Retail ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | From DOE Reference Buildings
Retail ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
Retail ClgSetp | Thermostat Setpoint | C | Sun | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
Retail ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | From DOE Reference Buildings
Retail Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Retail Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Retail Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Retail Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Retail FRONT ENTRY COOLING | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 90 | [23 empty] | From DOE Reference Buildings
Retail HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Retail HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
Retail HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
Retail HtgSetp | Thermostat Setpoint | C | Sun | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Retail HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
Retail INFIL FRONT | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
Retail INFIL FRONT | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Retail INFIL FRONT | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
Retail INFIL FRONT | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | From DOE Reference Buildings
Retail Infil Half On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Reference Buildings
Retail Infil Half On | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Retail Infil Half On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
Retail Infil Half On | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | From DOE Reference Buildings
Retail Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Schedule:Compact 1 | Unknown |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Reference Buildings
Schedule:Compact 1 | Unknown |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Schedule:Compact 1 | Unknown |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
SecondarySchool Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool BLDG ELEVATORS | Elevator |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool BLDG ELEVATORS | Elevator |  | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool ClgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
SecondarySchool ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 27 | [23 empty] | From DOE Reference Buildings
SecondarySchool ClgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Reference Buildings
SecondarySchool ClgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
SecondarySchool ClgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27 | From DOE Reference Buildings
SecondarySchool ClgSetp BathCorrMechKitchen | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 27 | [23 empty] | From DOE Reference Buildings
SecondarySchool ClgSetp BathCorrMechKitchen | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
SecondarySchool Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Reference Buildings
SecondarySchool Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.6 | [23 empty] | From DOE Reference Buildings
SecondarySchool Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Reference Buildings
SecondarySchool Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.6 | [23 empty] | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
SecondarySchool HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
SecondarySchool HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Reference Buildings
SecondarySchool HtgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
SecondarySchool HtgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | From DOE Reference Buildings
SecondarySchool HtgSetp BathCorrMechKitchen | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Reference Buildings
SecondarySchool HtgSetp BathCorrMechKitchen | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
SecondarySchool Infil | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13 | 0.13 | 0.2 | 0.2 | 0.2 | 0.13 | 0.13 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Exhaust | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Kitchen Exhaust | Equipment |  | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Small Office Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Reference Buildings
Small Office Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Small Office Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | From DOE Reference Buildings
Small Office Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Small Office Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Small Office Bldg Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Reference Buildings
Small Office Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Small Office ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Reference Buildings
Small Office ClgSetp | Thermostat Setpoint | C | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Reference Buildings
Small Office ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Reference Buildings
Small Office Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Small Office Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Small Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Small Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Small Office HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
Small Office HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
Small Office HtgSetp | Thermostat Setpoint | C | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
Small Office HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Small Office Infil Quarter On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Reference Buildings
Small Office Infil Quarter On | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
Small Office Infil Quarter On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Small Office Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
SmallHotel BLDG ELEVATORS | Elevator |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Reference Buildings
SmallHotel Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | From DOE Reference Buildings
SmallHotel Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | From DOE Reference Buildings
SmallHotel Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | From DOE Reference Buildings
SmallHotel Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Reference Buildings
SmallHotel Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Reference Buildings
SmallHotel Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Reference Buildings
SmallHotel Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | From DOE Reference Buildings
SmallHotel Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | From DOE Reference Buildings
SmallHotel Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | From DOE Reference Buildings
SmallHotel ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Reference Buildings
SmallHotel Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
SmallHotel Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
SmallHotel Corridor Light | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Exercise Equip | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | From DOE Reference Buildings
SmallHotel Exercise Light | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | From DOE Reference Buildings
SmallHotel Exercise Occ | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | From DOE Reference Buildings
SmallHotel GuestRoom Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Reference Buildings
SmallHotel GuestRoom Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel GuestRoom Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel GuestRoom Equip | Equipment |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Reference Buildings
SmallHotel GuestRoom Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | From DOE Reference Buildings
SmallHotel GuestRoom Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel GuestRoom Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel GuestRoom Light | Lighting |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | From DOE Reference Buildings
SmallHotel GuestRoom Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | From DOE Reference Buildings
SmallHotel GuestRoom Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel GuestRoom Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel GuestRoom Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
SmallHotel HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
SmallHotel Infil | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Infil Half On | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
SmallHotel Laundry Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Laundry Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Laundry Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Laundry Gas | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Laundry Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Laundry Gas | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Laundry Light | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Laundry Occ | Occupancy |  | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Laundry Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Laundry Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Meeting Equip | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Meeting Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | From DOE Reference Buildings
SmallHotel Meeting Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Meeting Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Meeting Occ | Occupancy |  | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Meeting Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Meeting Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Office Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Reference Buildings
SmallHotel Office Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Office Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Office Equip | Equipment |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Reference Buildings
SmallHotel Office Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
SmallHotel Office Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Office Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Office Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Reference Buildings
SmallHotel Office Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Office Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Office Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Reference Buildings
SmallHotel StaffLounge Equip | Equipment |  | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | From DOE Reference Buildings
SmallHotel StaffLounge Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel StaffLounge Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel StaffLounge Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05 | From DOE Reference Buildings
SmallHotel StaffLounge Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel StaffLounge Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel StaffLounge Light | Lighting |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05 | From DOE Reference Buildings
SmallHotel StaffLounge Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel StaffLounge Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel StaffLounge Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel StaffLounge Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Storage Light | Lighting |  | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Reference Buildings
SmallHotel Storage Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Storage Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel UnitHeater ClgSP Sch | Thermostat Setpoint |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 40 | [23 empty] | From DOE Reference Buildings
SmallHotel UnitHeater HtgSP Sch | Thermostat Setpoint |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
SmallHotel Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
StripMall Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
StripMall Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | From DOE Reference Buildings
StripMall Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
StripMall Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
StripMall Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | From DOE Reference Buildings
StripMall Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | From DOE Reference Buildings
StripMall Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
StripMall Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
StripMall Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
StripMall Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
StripMall Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
StripMall Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | From DOE Reference Buildings
StripMall Bldg Occ | Occupancy |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
StripMall Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
StripMall Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | From DOE Reference Buildings
StripMall ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | From DOE Reference Buildings
StripMall ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
StripMall ClgSetp | Thermostat Setpoint | C | Sun | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
StripMall ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | From DOE Reference Buildings
StripMall Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
StripMall Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
StripMall Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
StripMall Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
StripMall HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
StripMall HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
StripMall HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
StripMall HtgSetp | Thermostat Setpoint | C | Sun | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
StripMall HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
StripMall Infil Half On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Reference Buildings
StripMall Infil Half On | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
StripMall Infil Half On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
StripMall Infil Half On | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | From DOE Reference Buildings
StripMall Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SuperMarket Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
SuperMarket Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | From DOE Reference Buildings
SuperMarket Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SuperMarket Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SuperMarket Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.15 | 0.15 | From DOE Reference Buildings
SuperMarket Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | From DOE Reference Buildings
SuperMarket Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
SuperMarket Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SuperMarket Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SuperMarket Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
SuperMarket Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
SuperMarket Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0 | 0 | From DOE Reference Buildings
SuperMarket Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SuperMarket Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SuperMarket Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | From DOE Reference Buildings
SuperMarket Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | From DOE Reference Buildings
SuperMarket Bldg Swh | Service Water Heating |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | From DOE Reference Buildings
SuperMarket Bldg Swh | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | From DOE Reference Buildings
SuperMarket Bldg Swh | Service Water Heating |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | From DOE Reference Buildings
SuperMarket ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | From DOE Reference Buildings
SuperMarket ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
SuperMarket Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SuperMarket Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
SuperMarket Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SuperMarket Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
SuperMarket HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
SuperMarket HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
SuperMarket Infil Half On | Infiltration |  | Default¦SmrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | From DOE Reference Buildings
SuperMarket Infil Half On | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SuperMarket Infil Half On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
SuperMarket Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Warehouse Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Warehouse Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Warehouse Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Warehouse Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.24 | 0.24 | 0.24 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Warehouse Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Warehouse Bldg Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Warehouse ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
Warehouse ClgSetp | Thermostat Setpoint | C | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
Warehouse ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
Warehouse ClgSetp FineStorage | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Reference Buildings
Warehouse Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Warehouse Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Warehouse Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Warehouse Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Warehouse HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | From DOE Reference Buildings
Warehouse HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
Warehouse HtgSetp | Thermostat Setpoint | C | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 15.5 | [23 empty] | From DOE Reference Buildings
Warehouse HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | From DOE Reference Buildings
Warehouse HtgSetp BulkStorage | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 7.2 | [23 empty] | From DOE Reference Buildings
Warehouse HtgSetp FineStorage | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
Warehouse Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
ApartmentHighRise Activity Schedule | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 95 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise All Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise All On | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise Ambient Temp Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise APT_DHW_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29 | From DOE Prototype Buildings
ApartmentHighRise BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
ApartmentHighRise BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise CLGSETP_DESIGN_OFF_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise CLGSETP_OFF_SCH_No_Optimum | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 29.4 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise CLGSETP_OFF_SCH_No_Optimum | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
ApartmentHighRise CLGSETP_OFF_SCH_No_Setback | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 23.9 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise CLGSETP_OFF_SCH_No_Setback | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
ApartmentHighRise CLGSETP_OFF_SCH_Yes_Optimum | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 29.4 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise CLGSETP_OFF_SCH_Yes_Optimum | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
ApartmentHighRise CLGSETP_OFF_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 29.4 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise CLGSETP_OFF_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
ApartmentHighRise COMPACT HVAC-ALWAYS 0 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise COMPACT HVAC-ALWAYS 1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise COMPACT HVAC-ALWAYS 4 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
ApartmentHighRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise EQP_APT_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58 | From DOE Prototype Buildings
ApartmentHighRise EQP_OFF_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise EQP_OFF_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | From DOE Prototype Buildings
ApartmentHighRise Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise Exterior_Ltg_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_DESIGN_OFF_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_No_Optimum | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_No_Optimum | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentHighRise INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0 | From DOE Prototype Buildings
ApartmentHighRise INF_APT_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise INF_COR_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise INF_OFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise LTG_APT_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.06 | 0.13 | 0.14 | 0.13 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.14 | 0.2 | 0.27 | 0.32 | 0.32 | 0.22 | 0.12 | 0.05 | From DOE Prototype Buildings
ApartmentHighRise LTG_COR_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise LTG_OFF_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.18 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise LTG_OFF_SCH | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise LTG_OFF_SCH | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise LTG_OFF_SCH | Unknown |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | From DOE Prototype Buildings
ApartmentHighRise N CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise N HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise OCC_APT_SCH | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1 | From DOE Prototype Buildings
ApartmentHighRise OCC_OFF_SCH | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise OCC_OFF_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
ApartmentHighRise PLANT LOOP HIGH TEMP SCHEDULE | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANT LOOP LOW TEMP SCHEDULE | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 20 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown |  | Wknd¦Wkdy | 2014-10-18 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown |  | Wknd¦Wkdy | 2014-01-01 | 2014-05-08 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTHEATINGONSCHED | Unknown |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTHEATINGONSCHED | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTHEATINGONSCHED | Unknown |  | Wknd¦Wkdy | 2014-10-18 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTHEATINGONSCHED | Unknown |  | Wknd¦Wkdy | 2014-01-01 | 2014-05-08 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise S CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise S HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SHW Latent fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SHW Sensible fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SHW SUPPLY TEMP SCHED | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SHW TARGET TEMP SCHED | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
ApartmentHighRise Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SupplyFanSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 2 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown |  | Wkdy | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise Activity Schedule | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 95 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise All Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise All On | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise APT_DHW_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29 | From DOE Prototype Buildings
ApartmentMidRise BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
ApartmentMidRise BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.4 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_No_Setback | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.9 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_No_Setback | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.4 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
ApartmentMidRise COMPACT HVAC-ALWAYS 0 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise COMPACT HVAC-ALWAYS 1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise COMPACT HVAC-ALWAYS 18.3333338190008 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.3333 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise COMPACT HVAC-ALWAYS 4 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise Constant Mains Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
ApartmentMidRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise EQP_APT_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58 | From DOE Prototype Buildings
ApartmentMidRise EQP_OFF_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise EQP_OFF_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | From DOE Prototype Buildings
ApartmentMidRise Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise Exterior_Ltg_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
ApartmentMidRise Hot Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentMidRise INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0 | From DOE Prototype Buildings
ApartmentMidRise INF_APT_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise INF_COR_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise INF_OFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise LTG_APT_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.06 | 0.13 | 0.14 | 0.13 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.14 | 0.2 | 0.27 | 0.32 | 0.32 | 0.22 | 0.12 | 0.05 | From DOE Prototype Buildings
ApartmentMidRise LTG_COR_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise LTG_OFF_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.18 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise LTG_OFF_SCH | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise LTG_OFF_SCH | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise LTG_OFF_SCH | Unknown |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | From DOE Prototype Buildings
ApartmentMidRise N CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise N HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise OCC_APT_SCH | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1 | From DOE Prototype Buildings
ApartmentMidRise OCC_OFF_SCH | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise OCC_OFF_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
ApartmentMidRise S CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise S HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
ApartmentMidRise Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
Hospital AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_ELEVATORS | Elevator |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital BLDG_ELEVATORS | Elevator |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_EXTD_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_EXTD_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_EQUIP_EXTD_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_EQUIP_EXTD_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_EXTD_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXAM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXAM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXAM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXAM_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXAM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXTD_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXTD_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXTD_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXTD_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXTD_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_OA_FRAC_SCH | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_OA_FRAC_SCH | OA Air |  | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_OCC_EXTD_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_OCC_EXTD_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_OCC_EXTD_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_OCC_EXTD_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_OCC_EXTD_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_SWH_EXTD_SCH | Service Water Heating |  | Default¦WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
Hospital BLDG_SWH_EXTD_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
Hospital BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0 | 0 | From DOE Prototype Buildings
Hospital CLGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
Hospital CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
Hospital CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital Cool-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
Hospital CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
Hospital Dishwashing Booster Setpoint Temp Schedule | Service Water Heating | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
Hospital Dishwashing Booster Water Inlet Temp Schedule | Service Water Heating | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital ER_Exam1_Mult4_Flr_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Exam1_Mult4_Flr_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Exam1_Mult4_Flr_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Exam1_Mult4_Flr_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Exam3_Mult4_Flr_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Exam3_Mult4_Flr_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Exam3_Mult4_Flr_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Exam3_Mult4_Flr_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital ER_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital ER_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma1_Flr_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma1_Flr_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma1_Flr_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma1_Flr_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma2_Flr_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma2_Flr_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma2_Flr_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma2_Flr_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Triage_Mult4_Flr_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Triage_Mult4_Flr_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Triage_Mult4_Flr_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Triage_Mult4_Flr_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital Heat-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
Hospital Hours_of_operation | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital HTGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
Hospital Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50 | [23 empty] | From DOE Prototype Buildings
Hospital HVACOperationSchd | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82 | [23 empty] | From DOE Prototype Buildings
Hospital ICU_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital ICU_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital INFIL_SCH_PNNL | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
Hospital Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | From DOE Prototype Buildings
Hospital Kitchen_Exhaust_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
Hospital Kitchen_Flr_5 sub cat Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital Kitchen_Flr_5 sub cat Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital Kitchen_Flr_5 sub cat Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital Kitchen_Flr_5 sub catHot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
Hospital Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital Kitchen_SAT_SCH | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
Hospital Labs_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital Labs_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital Laundry Setpoint Temp Schedule | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
Hospital LAUNDRY_SWH_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital MaxRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital MinRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 40 | [23 empty] | From DOE Prototype Buildings
Hospital MinRelHumSetSch_addDI | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
Hospital MinRelHumSetSch_addDI_ICU | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 35 | [23 empty] | From DOE Prototype Buildings
Hospital OR1_Flr_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital OR1_Flr_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital OR1_Flr_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital OR1_Flr_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital OR2_Mult5_Flr_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital OR2_Mult5_Flr_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital OR2_Mult5_Flr_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital OR2_Mult5_Flr_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital OR3_Flr_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital OR3_Flr_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital OR3_Flr_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital OR3_Flr_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital OR4_Flr_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital OR4_Flr_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital OR4_Flr_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital OR4_Flr_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital OR_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital OR_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital OR_MinSA_Sched | Unknown |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital OR_MinSA_Sched | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital OR_MinSA_Sched | Unknown |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital OR_MinSA_Sched | Unknown |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital Patrms_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital Patrms_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PhysTherapy_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PhysTherapy_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PhysTherapy_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PhysTherapy_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital Radiology_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital Radiology_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital Radiology_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital Radiology_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital scheduleOSCBasementFloorTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital scheduleOSCBasementLowerWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital scheduleOSCBasementUpperWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital scheduleOSCBasementWallSurfaceTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
Hospital SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital Tower-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.1 | [23 empty] | From DOE Prototype Buildings
Hospital VAV_ER_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Prototype Buildings
Hospital VAV_ICU_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Prototype Buildings
Hospital VAV_LABS_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital VAV_OR_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Prototype Buildings
Hospital VAV_PATRMS_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Prototype Buildings
Hospital VAV_SAT_SCH | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
Hospital walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital walkin_occ_lght_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.104 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.26 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.156 | 0.156 | 0.156 | 0.156 | 0.156 | 0.156 | 0.156 | 0.1 | From DOE Prototype Buildings
Hospital WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
HotelLarge Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
HotelLarge Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
HotelLarge Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
HotelLarge Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
HotelLarge Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
HotelLarge Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
HotelLarge Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
HotelLarge Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
HotelLarge AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | From DOE Prototype Buildings
HotelLarge Base_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
HotelLarge Base_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
HotelLarge BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | From DOE Prototype Buildings
HotelLarge BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | From DOE Prototype Buildings
HotelLarge BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | From DOE Prototype Buildings
HotelLarge BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | From DOE Prototype Buildings
HotelLarge BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | From DOE Prototype Buildings
HotelLarge BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | From DOE Prototype Buildings
HotelLarge BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | From DOE Prototype Buildings
HotelLarge Booster Water Inlet Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Booster Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
HotelLarge CLGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
HotelLarge CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
HotelLarge CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Cool-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
HotelLarge CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
HotelLarge Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
HotelLarge ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Eqp_Sch | Equipment |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Eqp_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Eqp_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge ExerciseRoom_Eqp_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | From DOE Prototype Buildings
HotelLarge ExerciseRoom_Occ_Sch | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | From DOE Prototype Buildings
HotelLarge Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Exterior_Ltg_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
HotelLarge FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge FLR_3_DOAS_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.3 | 0.62 | 0.9 | 0.62 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.21 | 0.4 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.17 | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.62 | 0.9 | 0.43 | 0.43 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.19 | 0.48 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.17 | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Prototype Buildings
HotelLarge GuestRoom_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
HotelLarge GuestRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge GuestRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge GuestRoom_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | From DOE Prototype Buildings
HotelLarge GuestRoom_SWH_Sch | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | From DOE Prototype Buildings
HotelLarge GuestRoom_SWH_Sch | Service Water Heating |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | From DOE Prototype Buildings
HotelLarge Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Prototype Buildings
HotelLarge Hours_of_operation | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge HTGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
HotelLarge Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50 | [23 empty] | From DOE Prototype Buildings
HotelLarge HVACOperationSchd | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge INFIL_HALF_ON_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
HotelLarge INFIL_QUARTER_ON_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
HotelLarge INFIL_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | From DOE Prototype Buildings
HotelLarge Kitchen_Elec_Equip_SCH | Equipment |  | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
HotelLarge Kitchen_Elec_Equip_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen_Elec_Equip_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen_Exhaust_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen_Gas_Equip_SCH | Equipment |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | From DOE Prototype Buildings
HotelLarge Kitchen_Gas_Equip_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen_Gas_Equip_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
HotelLarge Laundry Setpoint Temp Schedule | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Elec_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Elec_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Elec_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Gas_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Gas_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Gas_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge LaundryRoom_Occ_Sch | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge LaundryRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge LaundryRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge LaundryRoom_SWH_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge LAUNDRY_SWH_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
HotelLarge Lobby_Eqp_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21 | From DOE Prototype Buildings
HotelLarge Lobby_Eqp_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Lobby_Eqp_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Lobby_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelLarge Lobby_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Lobby_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Lobby_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelLarge MaxRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge MeetingRoom_Eqp_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge MeetingRoom_Occ_Sch | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge MeetingRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge MeetingRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge MinOA_MotorizedDamper_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge MinRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
HotelLarge N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelLarge N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelLarge N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelLarge N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelLarge Off During Unoccupied Period | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Office_Eqp_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Prototype Buildings
HotelLarge Office_Eqp_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Office_Eqp_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Office_Eqp_Sch | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Prototype Buildings
HotelLarge Office_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
HotelLarge Office_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Office_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Office_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
HotelLarge PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_6 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_6 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_6 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_6 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_6 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_6 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_5_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_5_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_5_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_5_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_6_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_6_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_6_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_6_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelLarge S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelLarge S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelLarge S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelLarge scheduleOSCBasementFloorTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge scheduleOSCBasementLowerWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge scheduleOSCBasementUpperWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge scheduleOSCBasementWallSurfaceTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
HotelLarge Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
HotelLarge Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
HotelLarge SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge SWHSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
HotelLarge SWHSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge SWHSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.156 | 0.156 | 0.104 | 0.104 | 0.104 | 0.104 | 0.156 | 0.208 | 0.208 | 0.156 | 0.156 | 0.156 | 0.156 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.26 | 0.364 | 0.416 | 0.312 | 0.26 | 0.156 | From DOE Prototype Buildings
HotelLarge walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge walkin_occ_lght_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.104 | 0.104 | 0.052 | 0.052 | 0.052 | 0.052 | 0.156 | 0.156 | 0.208 | 0.208 | 0.156 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.312 | 0.364 | 0.364 | 0.364 | 0.312 | 0.156 | From DOE Prototype Buildings
HotelLarge walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.104 | 0.078 | 0.052 | 0.052 | 0.052 | 0.104 | 0.208 | 0.26 | 0.208 | 0.208 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.312 | 0.416 | 0.468 | 0.416 | 0.312 | 0.156 | From DOE Prototype Buildings
HotelLarge WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall Activity_Sch | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 132 | [23 empty] | From DOE Prototype Buildings
HotelSmall Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall Adva_EmployeeLounge_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 26.667 | 26.667 | 26.667 | 26.667 | From DOE Prototype Buildings
HotelSmall Adva_EmployeeLounge_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.333 | 18.333 | 18.333 | 18.333 | From DOE Prototype Buildings
HotelSmall Adva_ExerciseCenter_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 26.667 | From DOE Prototype Buildings
HotelSmall Adva_ExerciseCenter_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.333 | From DOE Prototype Buildings
HotelSmall Adva_MeetingRoom_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | From DOE Prototype Buildings
HotelSmall Adva_MeetingRoom_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | From DOE Prototype Buildings
HotelSmall Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall AlwaysOff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall AlwaysOff_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall AlwaysOn | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall AlwaysOn_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall Base_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall Base_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
HotelSmall BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_EXERCENTER_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_LAUNDRY_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MECHROOM_SCH | Lighting |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MECHROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MECHROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_RESTROOM_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_STAIR_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_STORAGE_SCH | Lighting |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_STORAGE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_STORAGE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall CommonArea_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.889 | [23 empty] | From DOE Prototype Buildings
HotelSmall CommonArea_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall CommonArea_Infil_Sch | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
HotelSmall CommonArea_Infil_Sch | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall CommonArea_Infil_Sch | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall COMPACT HVAC-ALWAYS 0 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall COMPACT HVAC-ALWAYS 1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall COMPACT HVAC-ALWAYS 4 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
HotelSmall ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
HotelSmall ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelSmall ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Eqp_Sch | Equipment |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Eqp_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Eqp_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall ExerciseCenter_Eqp_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | From DOE Prototype Buildings
HotelSmall ExerciseCenter_Occ_Sch | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | From DOE Prototype Buildings
HotelSmall Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall Exterior_Ltg_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.3 | 0.62 | 0.9 | 0.62 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.21 | 0.4 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.09 | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.62 | 0.9 | 0.43 | 0.43 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.19 | 0.48 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.09 | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | From DOE Prototype Buildings
HotelSmall GuestRoom_Infil_Sch | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Infil_Sch | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Infil_Sch | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77 | From DOE Prototype Buildings
HotelSmall GuestRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1 | From DOE Prototype Buildings
HotelSmall GuestRoom_SHW_Sch | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | From DOE Prototype Buildings
HotelSmall GuestRoom_SHW_Sch | Service Water Heating |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | From DOE Prototype Buildings
HotelSmall Heat Exchanger Supply Air Temp Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 14 | [23 empty] | From DOE Prototype Buildings
HotelSmall INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0 | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Elec_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Elec_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Elec_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Gas_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Gas_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Gas_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall LaundryRoom_Occ_Sch | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall LaundryRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall LaundryRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall LaundryRoom_SHW_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall Lobby_Eqp_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21 | From DOE Prototype Buildings
HotelSmall Lobby_Eqp_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall Lobby_Eqp_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall Lobby_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelSmall Lobby_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall Lobby_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall Lobby_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelSmall MeetingRoom_Eqp_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall MeetingRoom_Occ_Sch | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall MeetingRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall MeetingRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall MinOA_MotorizedDamper_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall Off During Unoccupied Period | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall Office_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
HotelSmall Office_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall Office_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall Office_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
HotelSmall OFF_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Prototype Buildings
HotelSmall OFF_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall OFF_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall OFF_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Prototype Buildings
HotelSmall PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall SemiHeated_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 7.2 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHW Latent fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHW Laundry Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHW Sensible fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHW Shower Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHWSys Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.1 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHWSysLaundry Water Heater Setpoint Temperature Schedule | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHWSysLaundry-Loop-Temp-Schedule | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHWSysShower Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHWSysShower-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelSmall Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
HotelSmall Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall VacGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.333 | [23 empty] | From DOE Prototype Buildings
HotelSmall VacGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.889 | [23 empty] | From DOE Prototype Buildings
OfficeLarge ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
OfficeLarge AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeLarge ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
OfficeLarge BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OfficeLarge BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
OfficeLarge BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | From DOE Prototype Buildings
OfficeLarge BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeLarge CLGSETP_DC_SCH | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLGSETP_DC_SCH | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 27 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦WntrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Cool-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_bottom sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_bottom sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_bottom sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_bottom sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_mid sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_mid sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_mid sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_mid sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_top sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_top sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_top sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_top sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
OfficeLarge DataCenter_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge DataCenter_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge DC_MinRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
OfficeLarge ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
OfficeLarge Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge EXTERIOR_LIGHT_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Heat-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Hours_of_operation | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Hours_of_operation | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge Hours_of_operation | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge HTGSETP_DC_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HVACOperationSchd | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge HVACOperationSchd | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge HVACOperationSchd | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82 | [23 empty] | From DOE Prototype Buildings
OfficeLarge INFIL_HALF_ON_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge INFIL_HALF_ON_SCH | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge INFIL_HALF_ON_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge INFIL_SCH | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge INFIL_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge INFIL_SCH_PNNL | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge INFIL_SCH_PNNL | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge INFIL_SCH_PNNL | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge MinOA_MotorizedDamper_Sched | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge PLANT LOOP HIGH TEMP SCHEDULE | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.33 | [23 empty] | From DOE Prototype Buildings
OfficeLarge PLANT LOOP LOW TEMP SCHEDULE | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 5 | [23 empty] | From DOE Prototype Buildings
OfficeLarge PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge scheduleOSCBasementFloorTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge scheduleOSCBasementLowerWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge scheduleOSCBasementUpperWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge scheduleOSCBasementWallSurfaceTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
OfficeLarge SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeLarge SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeLarge SupplyFanSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Tower-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
OfficeMedium AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_ELEVATORS | Elevator |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.69 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_ELEVATORS | Elevator |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_ELEVATORS | Elevator |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦WntrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Cool-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_bottom sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_bottom sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_bottom sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_bottom sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_mid sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_mid sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_mid sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_mid sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_top sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_top sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_top sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_top sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.69 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
OfficeMedium Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Heat-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Hours_of_operation | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Hours_of_operation | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium Hours_of_operation | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HVACOperationSchd | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HVACOperationSchd | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium HVACOperationSchd | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium INFIL_SCH_PNNL | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium INFIL_SCH_PNNL | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeMedium INFIL_SCH_PNNL | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Prototype Buildings
OfficeMedium MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium MinOA_MotorizedDamper_Sched | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
OfficeMedium SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
OfficeSmall AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeSmall ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
OfficeSmall BLDG_LIGHT_SCH | Lighting |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.23 | 0.42 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.42 | 0.42 | 0.32 | 0.32 | 0.23 | 0.18 | From DOE Prototype Buildings
OfficeSmall BLDG_OCC_SCH | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0.11 | 0.11 | 0.11 | 0.11 | 0.05 | 0 | From DOE Prototype Buildings
OfficeSmall BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 0.55 | 0.64 | 0.64 | 0.82 | 1 | 0.91 | 0.55 | 0.55 | 0.73 | 0.37 | 0.37 | 0.18 | 0.27 | 0.09 | 0 | 0 | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
OfficeSmall CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Core_ZN Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Core_ZN Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Core_ZN Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Core_ZN Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 48.8 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
OfficeSmall Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HVACOperationSchd | Operation |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HVACOperationSchd | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeSmall HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeSmall INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeSmall INFIL_QUARTER_ON_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall INFIL_QUARTER_ON_SCH | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeSmall INFIL_QUARTER_ON_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeSmall MinOA_MotorizedDamper_Sched | OA Air |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall MinOA_MotorizedDamper_Sched | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeSmall MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
OfficeSmall SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
OfficeSmall SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeSmall SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeSmall WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare AHU-1_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare AHU-1_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare AHU-1_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare BLDG_CAV_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_CAV_SCH_HUMID | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare BLDG_ELEVATORS | Elevator |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_ELEVATORS | Elevator |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH | Equipment |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH | Equipment |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH_BASE | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH_BASE | Equipment |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH_BASE | Equipment |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_TOILET_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_TOILET_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_TOILET_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OA_FRAC_SCH | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OA_FRAC_SCH | OA Air |  | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OA_SCH | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OA_SCH | OA Air |  | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OCC_SCH | Occupancy |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OCC_SCH | Occupancy |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | From DOE Prototype Buildings
OutPatientHealthCare CAV_SAT_SCH | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 11.1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 25 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 22.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 25 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 23.9 | 23.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 25 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 23.9 | 23.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
OutPatientHealthCare Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Room Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Room Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Room Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Room Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 1 humidity sched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 PACU Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 PACU Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 PACU Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 PACU Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Step Down Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Step Down Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Step Down Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Step Down Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 2 X-Ray Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 2 X-Ray Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 2 X-Ray Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 2 X-Ray Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare HeatSys1 Loop Setpoint Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Hours_of_operation | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 18.3 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 18.3 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 19.4 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Prototype Buildings
OutPatientHealthCare Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare HVACOperationSchd | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OutPatientHealthCare INFIL_HALF_ON_SCH | Infiltration |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare INFIL_HALF_ON_SCH | Infiltration |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare INFIL_SCH | Infiltration |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare INFIL_SCH | Infiltration |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare MaxRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare MinOA_MotorizedDamper_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare MinRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 40 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare MinRelHumSetSch_addDI | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare OR_CLGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | From DOE Prototype Buildings
OutPatientHealthCare OR_HTGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.3 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare OR_MinSA_Sched | Unknown |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare OR_MinSA_Sched | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare OR_MinSA_Sched | Unknown |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
OutPatientHealthCare PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 11.1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare SWHSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare SWHSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare SWHSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare VAV_SAT_SCH | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_EQUIP_SCH | Equipment |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | From DOE Prototype Buildings
RestaurantFastFood BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.29 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH | Lighting |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH | Lighting |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_SCH | Lighting |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2 | From DOE Prototype Buildings
RestaurantFastFood BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35 | From DOE Prototype Buildings
RestaurantFastFood BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | From DOE Prototype Buildings
RestaurantFastFood BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.1 | 0.72 | 0.6 | 0.98 | 0.92 | 0.25 | 0.25 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0 | From DOE Prototype Buildings
RestaurantFastFood BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.1 | 0.72 | 0.6 | 0.98 | 0.92 | 0.25 | 0.25 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0.15 | From DOE Prototype Buildings
RestaurantFastFood BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.33 | 0.13 | 0.1 | 0.72 | 0.31 | 0.98 | 0.92 | 0.22 | 0.31 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0.15 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 28.33 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 26.11 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 28.33 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 28.9 | 27.8 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 28.33 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood DOOR_INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.258 | 0.258 | 0.363 | 0.558 | 0.558 | 0.363 | 0.258 | 0.363 | 0.462 | 0.558 | 0.65 | 0.74 | 0.462 | 0.258 | 0.258 | From DOE Prototype Buildings
RestaurantFastFood DOOR_INFIL_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood DOOR_INFIL_SCH | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood DOOR_INFIL_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.462 | 0.258 | 0.462 | 0.558 | 0.558 | 0.462 | 0.363 | 0.363 | 0.363 | 0.74 | 0.915 | 0.74 | 0.65 | 0.558 | 0.363 | From DOE Prototype Buildings
RestaurantFastFood DOOR_INFIL_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.462 | 0.462 | 0.462 | 0.258 | 0.558 | 0.829 | 0.74 | 0.462 | 0.258 | 0.363 | 0.558 | 0.829 | 0.829 | 0.829 | 0.558 | 0.363 | 0.258 | From DOE Prototype Buildings
RestaurantFastFood Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood FF_GAS_EQUIP_SCH | Equipment |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | From DOE Prototype Buildings
RestaurantFastFood FF_GAS_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood FF_GAS_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.29 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Hours_of_operation | Operation |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.22 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 16.7 | 17.8 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.22 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood HVACOperationSchd | Operation |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood INFIL_SCH_PNNL | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
RestaurantFastFood Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.53051 | 0 | 0 | 0 | 0 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | From DOE Prototype Buildings
RestaurantFastFood Kitchen Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Kitchen Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Kitchen Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Kitchen Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RestaurantFastFood Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
RestaurantFastFood Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Kitchen_Exhaust_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood MinOA_FFKitch_Sched | OA Air |  | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood MinOA_FFKitch_Sched | OA Air |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood MinOA_MotorizedDamper_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood SHWSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood SHWSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.241 | 0.241 | 0.345 | 0.542 | 0.542 | 0.345 | 0.241 | 0.345 | 0.445 | 0.542 | 0.637 | 0.73 | 0.445 | 0.241 | 0.241 | From DOE Prototype Buildings
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.445 | 0.241 | 0.445 | 0.542 | 0.542 | 0.445 | 0.345 | 0.345 | 0.345 | 0.73 | 0.911 | 0.73 | 0.637 | 0.542 | 0.345 | From DOE Prototype Buildings
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.445 | 0.445 | 0.445 | 0.241 | 0.542 | 0.821 | 0.73 | 0.445 | 0.241 | 0.345 | 0.542 | 0.821 | 0.821 | 0.821 | 0.542 | 0.345 | 0.241 | From DOE Prototype Buildings
RestaurantFastFood walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.312 | 0.312 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.26 | 0.156 | From DOE Prototype Buildings
RestaurantFastFood walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood walkin_occ_lght_SCH | Occupancy |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.26 | 0.26 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.26 | 0.156 | From DOE Prototype Buildings
RestaurantFastFood WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_EQUIP_SCH | Equipment |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | From DOE Prototype Buildings
RestaurantSitDown BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.29 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_SCH | Lighting |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2 | From DOE Prototype Buildings
RestaurantSitDown BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35 | From DOE Prototype Buildings
RestaurantSitDown BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | From DOE Prototype Buildings
RestaurantSitDown BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | From DOE Prototype Buildings
RestaurantSitDown BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | From DOE Prototype Buildings
RestaurantSitDown Booster Water Inlet Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Booster Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 26 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 28.9 | 27.8 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Prototype Buildings
RestaurantSitDown CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown DOOR_INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.258 | 0.258 | 0.363 | 0.558 | 0.558 | 0.363 | 0.258 | 0.363 | 0.462 | 0.558 | 0.65 | 0.74 | 0.462 | 0.258 | 0.258 | From DOE Prototype Buildings
RestaurantSitDown DOOR_INFIL_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown DOOR_INFIL_SCH | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown DOOR_INFIL_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.462 | 0.258 | 0.462 | 0.558 | 0.558 | 0.462 | 0.363 | 0.363 | 0.363 | 0.74 | 0.915 | 0.74 | 0.65 | 0.558 | 0.363 | From DOE Prototype Buildings
RestaurantSitDown DOOR_INFIL_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.462 | 0.462 | 0.462 | 0.258 | 0.558 | 0.829 | 0.74 | 0.462 | 0.258 | 0.363 | 0.558 | 0.829 | 0.829 | 0.829 | 0.558 | 0.363 | 0.258 | From DOE Prototype Buildings
RestaurantSitDown Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Hours_of_operation | Operation |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 19 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 16.7 | 17.8 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 19 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HVACOperationSchd | Operation |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown INFIL_HALF_ON_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
RestaurantSitDown INFIL_SCH_PNNL | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
RestaurantSitDown Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.93371 | 0 | 0 | 0 | 0 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | From DOE Prototype Buildings
RestaurantSitDown Kitchen Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Kitchen Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Kitchen Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Kitchen Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RestaurantSitDown Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
RestaurantSitDown Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Kitchen_Exhaust_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown MaxRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown MinOA_FFKitch_Sched | OA Air |  | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | From DOE Prototype Buildings
RestaurantSitDown MinOA_FFKitch_Sched | OA Air |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.65 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown MinOA_MotorizedDamper_Sched | OA Air |  | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown MinOA_SDKitch_Sched | OA Air |  | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown MinOA_SDKitch_Sched | OA Air |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown MinRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Rest_GAS_EQUIP_SCH | Equipment |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | From DOE Prototype Buildings
RestaurantSitDown Rest_GAS_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Rest_GAS_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.29 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown SWHSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown SWHSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown SWHSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.241 | 0.241 | 0.345 | 0.542 | 0.542 | 0.345 | 0.241 | 0.345 | 0.445 | 0.542 | 0.637 | 0.73 | 0.445 | 0.241 | 0.241 | From DOE Prototype Buildings
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.445 | 0.241 | 0.445 | 0.542 | 0.542 | 0.445 | 0.345 | 0.345 | 0.345 | 0.73 | 0.911 | 0.73 | 0.637 | 0.542 | 0.345 | From DOE Prototype Buildings
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.445 | 0.445 | 0.445 | 0.241 | 0.542 | 0.821 | 0.73 | 0.445 | 0.241 | 0.345 | 0.542 | 0.821 | 0.821 | 0.821 | 0.542 | 0.345 | 0.241 | From DOE Prototype Buildings
RestaurantSitDown walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.312 | 0.312 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.26 | 0.156 | From DOE Prototype Buildings
RestaurantSitDown walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown walkin_occ_lght_SCH | Occupancy |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.26 | 0.26 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.26 | 0.156 | From DOE Prototype Buildings
RestaurantSitDown WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
RetailStandalone AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
RetailStandalone ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_ELEVATORS | Elevator |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_ELEVATORS | Elevator |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | From DOE Prototype Buildings
RetailStandalone BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | From DOE Prototype Buildings
RetailStandalone BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
RetailStandalone Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone FrontEntry_CoilSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone FrontEntry_FanSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone FRONT_ENTRY_COOLING | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 100 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Hot Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Hours_of_operation | Operation |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone Hours_of_operation | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone Hours_of_operation | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | C | WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50 | [23 empty] | From DOE Prototype Buildings
RetailStandalone HVACOperationSchd | Operation |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone HVACOperationSchd | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone HVACOperationSchd | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RetailStandalone INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone INFIL_HALF_ON_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_HALF_ON_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone INFIL_HALF_ON_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_HALF_ON_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone INFIL_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH_PNNL | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH_PNNL | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH_PNNL | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
RetailStandalone SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
RetailStripmall AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
RetailStripmall ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
RetailStripmall CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Hot Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RetailStripmall INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Fri¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_EQUIP_SCH | Equipment |  | Default¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | From DOE Prototype Buildings
RetailStripmall Type1_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_EQUIP_SCH | Equipment |  | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | From DOE Prototype Buildings
RetailStripmall Type1_FAN_SCH | Unknown |  | Default¦SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type1_FAN_SCH | Unknown |  | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_Infil_SCH | Infiltration |  | Default¦SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
RetailStripmall Type1_Infil_SCH | Infiltration |  | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
RetailStripmall Type1_LIGHT_SCH | Lighting |  | Default¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | From DOE Prototype Buildings
RetailStripmall Type1_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_LIGHT_SCH | Lighting |  | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | From DOE Prototype Buildings
RetailStripmall Type1_MinOA_MotorizedDamper_SCH | OA Air |  | Default¦SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type1_MinOA_MotorizedDamper_SCH | OA Air |  | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type1_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.6 | 0.4 | 0.4 | 0.3 | 0.6 | 0.6 | 0.4 | 0.4 | 0.3 | 0.2 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type1_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_OCC_SCH | Occupancy |  | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.2 | 0.6 | 0.4 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.2 | From DOE Prototype Buildings
RetailStripmall Type1_OCC_SCH | Occupancy |  | Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type1_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.16 | 0.1 | From DOE Prototype Buildings
RetailStripmall Type1_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.23 | 0.32 | 0.41 | 0.65 | 0.6 | 0.55 | 0.45 | 0.5 | 0.46 | 0.47 | 0.34 | 0.33 | 0.23 | 0.13 | From DOE Prototype Buildings
RetailStripmall Type1_SWH_SCH | Service Water Heating |  | SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.62 | 0.6 | 0.55 | 0.45 | 0.5 | 0.46 | 0.47 | 0.34 | 0.33 | 0.23 | 0.13 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_FAN_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_FAN_SCH | Unknown |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_FAN_SCH | Unknown |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_Infil_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type2_Infil_SCH | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type2_Infil_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type2_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_MinOA_MotorizedDamper_SCH | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_MinOA_MotorizedDamper_SCH | OA Air |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_MinOA_MotorizedDamper_SCH | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.2 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.4 | 0.3 | 0.3 | 0.3 | 0.05 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.3 | 0.2 | 0.2 | 0.5 | 0.5 | 0.2 | 0.05 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.14 | 0.29 | 0.33 | 0.4 | 0.36 | 0.37 | 0.35 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.62 | 0.6 | 0.5 | 0.48 | 0.47 | 0.34 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_FAN_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_FAN_SCH | Unknown |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_FAN_SCH | Unknown |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_Infil_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type3_Infil_SCH | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type3_Infil_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type3_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_MinOA_MotorizedDamper_SCH | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_MinOA_MotorizedDamper_SCH | OA Air |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_MinOA_MotorizedDamper_SCH | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.43 | 0.46 | 0.5 | 0.69 | 0.34 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.58 | 0.71 | 0.74 | 0.77 | 0.8 | 0.74 | 0.54 | 0.11 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.43 | 0.46 | 0.71 | 0.5 | 0.69 | 0.54 | 0.71 | 0.34 | 0.26 | 0.11 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.25 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Latent fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Sensible fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.35 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Wknd | 2014-06-16 | 2014-09-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Wknd | 2014-01-01 | 2014-06-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Sat | 2014-09-16 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Sun¦Sat | 2014-06-16 | 2014-09-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Sun¦Sat | 2014-01-01 | 2014-06-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Booster Water Inlet Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Booster Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_Setup | Thermostat Setpoint | C | Default¦WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_Setup | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1.1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CoolingCoilAvailSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary FAN_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Hours_of_operation | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Hours_of_operation | Operation |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_Setback | Thermostat Setpoint | C | Default¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_Setback | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 65 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HVACOperationSchd | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HVACOperationSchd | Operation |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary INFIL_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolPrimary INFIL_SCH_PNNL | Infiltration |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary INFIL_SCH_PNNL | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.02 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.02 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.02 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary MinOA_Kitchen_Sched | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary MinOA_Kitchen_Sched | Equipment |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary PlantOnSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary ReheatCoilAvailSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary SHWSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary SHWSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary VAV-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Latent fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Sensible fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Hot Supply Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Latent fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Sensible fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_ELEVATORS | Elevator |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_ELEVATORS | Elevator |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.35 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Wknd | 2014-06-16 | 2014-09-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Wknd | 2014-01-01 | 2014-06-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Sat | 2014-09-16 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Sun¦Sat | 2014-06-16 | 2014-09-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Sun¦Sat | 2014-01-01 | 2014-06-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Booster Water Inlet Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Booster Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC_1_5 | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC_1_5 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC_1_5 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC_2_6 | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC_2_6 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC_2_6 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC_3_7 | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC_3_7 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC_3_7 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC_4_8 | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC_4_8 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC_4_8 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC_5_9 | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC_5_9 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC_5_9 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_Setup | Thermostat Setpoint | C | Default¦WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_Setup | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1.1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CoolingCoilAvailSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary FAN_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Hours_of_operation | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Hours_of_operation | Operation |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC_1_5 | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC_1_5 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC_1_5 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC_2_6 | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC_2_6 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC_2_6 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC_3_7 | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC_3_7 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC_3_7 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC_4_8 | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC_4_8 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC_4_8 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC_5_9 | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC_5_9 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC_5_9 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_Setback | Thermostat Setpoint | C | Default¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_Setback | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 65 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HVACOperationSchd | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HVACOperationSchd | Operation |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary INFIL_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolSecondary INFIL_SCH_PNNL | Infiltration |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary INFIL_SCH_PNNL | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH_DCV | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.02 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.02 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.02 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary PlantOnSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ReheatCoilAvailSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary SHWSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary SHWSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary VAV-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse Always Off Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse Always On Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.18 | [23 empty] | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.42 | 0.77 | 0.77 | 0.77 | 0.77 | 0.68 | 0.77 | 0.77 | 0.77 | 0.77 | 0.61 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.6 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Warehouse BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse BLDG_OCC_SCH | Occupancy |  | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Warehouse Bulk Storage Heating Setpoint Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 10 | [23 empty] | From DOE Prototype Buildings
Warehouse COMPACT HVAC-ALWAYS 1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse COMPACT HVAC-ALWAYS 4 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
Warehouse Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
Warehouse Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse Exterior_Ltg_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
Warehouse FanSched | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse FanSched | Unknown |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse FanSched | Unknown |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Warehouse Fine Storage Cooling Setpoint Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
Warehouse Fine Storage Heating Setpoint Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
Warehouse Hot Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Warehouse INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Warehouse MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse MinOA_MotorizedDamper_Sched | OA Air |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Warehouse MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse OA Damper Always ON Schedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse OA Damper Off during off hrs Schedule | OA Air |  | Default¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse OA Damper Off during off hrs Schedule | OA Air |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse OA Damper Off during off hrs Schedule | OA Air |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Warehouse Office Activity Schedule | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 131.85 | [23 empty] | From DOE Prototype Buildings
Warehouse Office_Plug_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Prototype Buildings
Warehouse Office_Plug_SCH | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse Office_Plug_SCH | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse Office_Plug_SCH | Unknown |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
Warehouse ZoneControlSchedule | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings

## Lookups
These lookups are used to help users avoid input mistakes on other tabs. Please do not edit or delete existing entries or rename tables. You may add entries at the bottom of the list, but please avoid near-duplicates.
Intended Surface Type Lookup | Standards Construction Type Lookup | Building Type Lookup | Space Type Lookup | Lighting Standards Lookup | Ventilation Standards Lookup | Material Type Lookup
Name | Name | Name | Name | Name | Name | Name
AtticFloor | Mass | FullServiceRestaurant | Dining | ASHRAE 90.1-1999 | ASHRAE 62.1-1999 | StandardOpaqueMaterial
AtticWall | SteelFramed | Hospital | Kitchen | ASHRAE 90.1-2001 | ASHRAE 62.1-2004 | AirGap
AtticRoof | WoodFramed | LargeHotel | Corridor | ASHRAE 90.1-2004 | ASHRAE 62.1-2007 | StandardGlazing
DemisingFloor | IEAD | MidriseApartment | ER_Exam | ASHRAE 90.1-2007 | GGHC v2.2 | MasslessOpaqueMaterial
DemisingWall | View | Office | ER_NurseStn | ASHRAE 189.1-2009 | AIA 2001 | SimpleGlazing
DemisingRoof | Daylight | Outpatient | ER_Trauma | ASHRAE 90.1-2010 |  | Gas
ExteriorFloor | Swinging | PrimarySchool | ER_Triage
ExteriorWall | NonSwinging | QuickServiceRestaurant | ICU_NurseStn
ExteriorRoof | Heated | Retail | ICU_Open
ExteriorWindow | Unheated | SecondarySchool | ICU_PatRm
ExteriorDoor | RollUp | SmallHotel | Lab
GlassDoor | Sliding | StripMall | Lobby
GroundContactFloor | Metal | SuperMarket | NurseStn
GroundContactWall | Nonmetal framing (all) | Warehouse | Office
GroundContactRoof | Metal framing (curtainwall/storefront) | SmallOffice | OR
InteriorFloor | Metal framing (entrance door) |  | PatCorridor
InteriorWall | Metal framing (all other) |  | PatRoom
InteriorCeiling |  |  | PhysTherapy
InteriorPartition |  |  | Radiology
InteriorWindow |  |  | Banquet
InteriorDoor |  |  | Cafe
OverheadDoor |  |  | GuestRoom
Skylight |  |  | Laundry
TubularDaylightDome |  |  | Mechanical
TubularDaylightDiffuser |  |  | Retail
Storage
WholeBuilding
Apartment
BreakRoom
ClosedOffice
Conference
Elec/MechRoom
IT_Room
OpenOffice
PrintRoom
Restroom
Stair
Vending
WholeBuilding - Lg Office
WholeBuilding - Md Office
WholeBuilding - Sm Office
Anesthesia
BioHazard
CleanWork
DressingRoom
Exam
Hall
Janitor
LockerRoom
Lounge
MedGas
MRI
MRI_Control
NurseStation
PACU
PhysicalTherapy
PreOp
ProcedureRoom
Soil Work
Toilet
Xray
Cafeteria
Classroom
Gym
Library
Back_Space
Entry
Point_of_Sale
Auditorium
Exercise
GuestLounge
Meeting
PublicRestroom
StaffLounge
Deli/Bakery
DryStorage
Sales/Produce
Bulk
Fine
Attic
Plenum