## Information
Worksheet | Description
"Constants" | List of contants used in all the worksheets
"BldgAreas" | List of areas of each archetype per vintage for the various fuel sources. This list does not include buildings not modelled.
"BldgEUI" | List of Energy-Use Intensities for all the archetypes for each of the vintages for building fuel consumption, DES fuel consumption, heating electricity consumption, and non-heating electricity consumption. Each ECM has an applicability index, which represents the portion of the total archetype vintage area across the base that the ECM is applicable for.
"ECMBldgAreas" | The ECM applicability index from worksheet "BldgEUI" is used to find the actual area of the archetype per vintage the ECM is applicable for. These areas would be the same as those in "BldgAreas" when the applicability index is 1.
"BaseBldgEnergy" | The areas for the archetype by vintage are used to find the fuel and electricity use for the archetype across the base for each ECM.
"BaseTotalEnergy" | The base wide fuel and electricity consumptions for each archetype from "BaseBldgEnergy" is used to find the total energy consumption for the base for each of the ECMs.
"ECMSuccessScores" | Four criteria are used to assign a probability of success score for each ECM. This score is used to find the total score for the ECM along with the energy, GHG, and cost scores.
"BaseECMScores" | The base wide percent reductions in energy and GHG are used to assign an energy and GHG score for the ECMs. The payback years for each of the ECM is used to assign a cost score. A total score is then calculated for each ECM using weighting factors for energy score, GHG score, cost score, and success score.
"BldgECMScores" | The percent reductions in energy and GHG for each archetype per vintage are used to assign an energy and GHG score for each ECM. The payback years are used to assign a cost score. All of the four scores are then summed together using weighting factors to get the total ECM score.

## arch
1A | Hanger
1B | Air Terminal
2A | Training Building
2B | DayCare
3A | Active Warehouse
3B | Storage Warehouse
4A | Hotel-Type Accommodation
4B | Dormitory
4C | Barracks
4D | Bunkhouse (Accom.)
4E | Seasonal Barracks
5A | Gym and Fitness Centre
5B | Sports with Arena
5C | Sports with Pool
5D | Club House
5E | Recreation Complex
6A | Office
6B | Small Office (<600 m2)
7A | Food Services
7B | Food Services Small (<600 m2)
8A | Waterworks/Sewage
8B | Vehicle Garage
9A | Maintenance Shop
9B | Small Shop (<1000 m2)
10A | Medical Facilities
11A | Retail Buildings
11B | Retail Buildings with Office
12A | Religious Bldgs
13A | Control Tower
13B | Firehall
13C | Communications & Control Bdg
14A | Museum
15A | Sheds (Heated)
15B | Sheds (Not Heated)

## Constants
Building Heating Efficiency | 0.8
Building DES Heating Efficiency | 0.8
DES Boiler Efficiency | 0.55
Electricity Fuel Cost Ratio | 5
Natural Gas GHG factor | 183 | g/kWh
Electricity GHG factor | 110 | g/kWh
Score Energy Reduction Weighting Factor | 0.35
Score GHG Reduction Weighting Factor | 0.35
Score Cost Reduction Weighting Factor | 0.15
Score Probability of Success Weighting Factor | 0.15
Future growth of base area | 1 | %
Future improvements in V1 EUI | 1 | %
Elec 2014 Cost ($/kWh) | 0.113
Gas 2014 Cost ($/kWh) | 0.0162
Inflation (%) | 0.02
Elec Annual Escalation (real %) | 0.04
Gas Annual Escalation (real %) | 0.02
Note on A13: Lubun, Mike: from sample bill and emails
Note on A14: Lubun, Mike: based on 4.5/GJ

## Area
Total area across the base for the archetype buildings per vintage
|  | Area | Percent of Total | post-2004 Area |  | 1980-2004 Area |  | 1960-1979 Area |  | pre-1960 Area
|  | m2 | % | m2 | % | m2 | % | m2 | % | m2 | %
1A | Hanger | 74957 | 28.4971 |  |  | 6551 |  | 6231 |  | 62176
1B | Air Terminal | 718 | 0.27297 |  |  | 718
2A | Training Building | 13531 | 5.1442 | 1869 |  | 4831 |  |  |  | 6831
2B | DayCare | 0 | 0
3A | Active Warehouse | 0 | 0
3B | Storage Warehouse (8b in master) | 20983 | 7.9773 | 1431 |  | 16388 |  | 2093 |  | 1072
4A | Hotel-Type Accommodation | 0 | 0
4B | Dormitory | 0 | 0
4C | Barracks | 20067 | 7.6291 | [6 empty] | 20067
4D | Bunkhouse (Accom.) | 151 | 0.057407 |  |  | 151
4E | Seasonal Barracks | 4543 | 1.7272 |  |  | 4543
5A | Gym and Fitness Centre | 0 | 0
5B | Sports with Arena | 3111 | 1.1827 |  |  | 3111
5C | Sports with Pool | 0 | 0
5D | Club House | 1059 | 0.40261 |  |  | 664 |  | 101 |  | 294
5E | Recreation Complex | 12613 | 4.7952 |  |  | 12613
6A | Office | 37676 | 14.3236 |  |  | 17683 |  | 3480 |  | 16513
6B | Small Office (<600 m2) | 6006 | 2.2834 | 501 |  | 4356 |  | 1148
7A | Food Services | 10012 | 3.8064 | [6 empty] | 10012
7B | Food Services Small (<600 m2) | 893 | 0.3395 |  |  | 893
8A | Waterworks/Sewage | 2433 | 0.92498 | 58 |  | 2038 |  | 303 |  | 34
8B | Vehicle Garage (3a in master) | 17501 | 6.6535 |  |  | 12254 |  |  |  | 5246
9A | Maintenance Shop | 14970 | 5.6913 |  |  | 10986 |  |  |  | 3983
9B | Small Shop (<1000 m2) | 7157 | 2.7209 |  |  | 4869 |  | 724 |  | 1565
10A | Medical Facilities | 0 | 0
11A | Retail Buildings | 7926 | 3.0133 |  |  | 650 |  | 7034 |  | 242
11B | Retail Buildings with Office | 0 | 0
12A | Religious Bldgs | 1049 | 0.39881 | [6 empty] | 1049
13A | Control Tower | 0 | 0
13B | Firehall | 1289 | 0.49005 | [6 empty] | 1289
13C | Communications & Control Bdg | 303 | 0.11519 | 124 |  | 179
14A | Museum | 0 | 0
15A | Sheds (Heated) | 551 | 0.20948 | 50 |  | 384 |  | 102 |  | 15
15B | Sheds (Not Heated) | 3535 | 1.3439 | 117 |  | 3132 |  | 265 |  | 21
| Total | 263034 |  | 4150 | 1.5777 | 106994 | 40.6769 | 21481 | 8.1666 | 130409 | 49.5788

## HtgArea
Type | Arch | Vintage | Total Area (m2) | Space DES Area (m2) | Space Gas Area (m2) | Space Elec Area (m2) | Water DES Area (m2) | Water Gas Area (m2) | Water Elec Area (m2)
1A | Hanger | pre-1960 | 62176 | 62176
|  | 1960-1979 | 6231 |  | 6231
|  | 1980-2004 | 7269 |  | 7269
2A | Training | pre-1960 | 6832 | 3118 | 3714
|  | 1980-2004 | 4831 | 4831
|  | 2005-2014 | 1869 |  | 1869
3B | Storage | pre-1960 | 330 | 249 | 81
|  | 1960-1979 | 833 | 326 | 507
|  | 1980-2004 | 10451 | 1702 | 8006 | 743
|  | 2005-2014 | 501 |  | 428 | 73
4C | Barracks | pre-1960 | 20067 | 20067
5E | Rec Centre | pre-1960 | 294 |  | 294
|  | 1960-1979 | 101 |  | 101
|  | 1980-2004 | 15831 |  | 15831
6A | Office | pre-1960 | 15698 | 9687 | 6011
|  | 1960-1979 | 3480 |  | 3480
|  | 1980-2004 | 17682 | 11024 | 6658
6B | Small Office | 1960-1979 | 1149 |  | 1137 | 12
|  | 1980-2004 | 4359 |  | 3455 | 904
|  | 2005-2014 | 501 |  | 501
7A | Food Services | pre-1960 | 10012 | 10012
8B | Vehicle Garage | pre-1960 | 5221 | 3443 | 1778
|  | 1980-2004 | 12146 |  | 12146
9A | Maintenance Shop | pre-1960 | 3983 | 1504 | 2479
|  | 1980-2004 | 10986 | 7670 | 3316
9B | Maintenance Shop-Small | pre-1960 | 1564 | 805 | 759
|  | 1960-1979 | 724 |  | 724
|  | 1980-2004 | 4871 | 1050 | 3821
13B | Firehall | pre-1960 | 1289 | 1289
Note on F1: Lubun, Mike: includes propane
Note on B2: Lubun, Mike: includes air terminal area
Note on B12: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B13: Lubun, Mike: includes curling and clubhouse
Note on B22: Lubun, Mike: excludes small food areas for mapleflag and summer cadets

## baseEUI
Type | Arch | Vintage |  | ECM Applicability (1 =Yes, 0 =No) | Space Heating Load (kWh/m2) | Space DES Consumption (kWh/m2) | Space Gas Consumption (kWh/m2) | Space Elec Consumption (kWh/m2) | Water Gas Consumption (kWh/m2) | Water Elec Consumption (kWh/m2) | Elec Consumption (kWh/m2) | Building EUI (kWh/m2) | Total Gas Savings (kWh/m2) | Total Elec Savings (kWh/m2) | Total Energy Savings (kWh/m2) | Total Gas Cost ($/m2) | Total Elec Cost ($/m2) | Total Energy Cost ($/m2) | Total Gas Savings ($/m2) | Total Elec Savings ($/m2) | Total Energy Savings ($/m2) | ECM Cost ($/m2) | Payback (yrs)
1A | Hanger | pre-1960 | baseline |  | 352.4484 | 0 | 440.5605 | 0 | 5.309 | 0 | 79.8644 | 525.7339 |  |  |  | 7.2231 | 9.0247 | 16.2478
1A | Hanger | 1960-1979 | baseline |  | 341.1255 | 0 | 426.4069 | 0 | 5.309 | 0 | 78.8625 | 510.5784 |  |  |  | 6.9938 | 8.9115 | 15.9053
1A | Hanger | 1980-2004 | baseline |  | 216.9386 | 0 | 271.1732 | 0 | 5.309 | 0 | 73.5061 | 349.9883 |  |  |  | 4.479 | 8.3062 | 12.7852
2A | Training | pre-1960 | baseline |  | 409.6861 | 0 | 512.1076 | 0 | 0 | 7.2427 | 78.1247 | 597.475 |  |  |  | 8.2961 | 9.6465 | 17.9427
2A | Training | 1980-2004 | baseline |  | 239.5897 | 0 | 299.4871 | 0 | 0 | 7.2427 | 67.9074 | 374.6373 |  |  |  | 4.8517 | 8.492 | 13.3437
2A | Training | 2005-2014 | baseline |  | 167.1125 | 0 | 208.8906 | 0 | 0 | 7.2427 | 64.812 | 280.9453 |  |  |  | 3.384 | 8.1422 | 11.5262
3B | Storage | pre-1960 | baseline |  | 259.8336 | 0 | 324.792 | 0 | 0 | 0 | 44.7913 | 369.5833 |  |  |  | 5.2616 | 5.0614 | 10.323
3B | Storage | 1960-1979 | baseline |  | 235.9158 | 0 | 294.8947 | 0 | 0 | 0 | 43.5767 | 338.4714 |  |  |  | 4.7773 | 4.9242 | 9.7015
3B | Storage | 1980-2004 | baseline |  | 143.0258 | 0 | 178.7822 | 0 | 0 | 0 | 38.8999 | 217.6821 |  |  |  | 2.8963 | 4.3957 | 7.292
3B | Storage | 2005-2014 | baseline |  | 85.4162 | 0 | 106.7703 | 0 | 0 | 0 | 35.6851 | 142.4554 |  |  |  | 1.7297 | 4.0324 | 5.7621
4C | Barracks | pre-1960 | baseline |  | 92.5407 | 0 | 115.6759 | 0 | 29.0853 | 0 | 33.6964 | 178.4576 |  |  |  | 2.3451 | 3.8077 | 6.1528
5E | Rec Centre | 1980-2004 | baseline |  | 289.9153 | 0 | 347.134 | 12.2081 | 20.994 | 0 | 86.4088 | 466.7449 |  |  |  | 5.9637 | 11.1437 | 17.1074
6A | Office | pre-1960 | baseline |  | 346.7971 | 0 | 433.4963 | 0 | 42.0362 | 0 | 111.3137 | 586.8461 |  |  |  | 7.7036 | 12.5784 | 20.2821
6A | Office | 1960-1979 | baseline |  | 322.294 | 0 | 402.8675 | 0 | 42.0353 | 0 | 108.6217 | 553.5245 |  |  |  | 7.2074 | 12.2743 | 19.4817
6A | Office | 1980-2004 | baseline |  | 231.0518 | 0 | 288.8147 | 0 | 42.0345 | 0 | 98.4153 | 429.2646 |  |  |  | 5.3598 | 11.1209 | 16.4807
6B | Small Office | 1960-1979 | baseline |  | 105.2576 | 0 | 129.8638 | 1.3666 | 0 | 5.73 | 54.8924 | 191.8528 |  |  |  | 2.1038 | 7.0048 | 9.1085
6B | Small Office | 1980-2004 | baseline |  | 58.7825 | 0 | 71.8531 | 1.3001 | 0 | 5.581 | 48.8047 | 127.5388 |  |  |  | 1.164 | 6.2925 | 7.4565
6B | Small Office | 2005-2014 | baseline |  | 32.0981 | 0 | 38.0761 | 1.6371 | 0 | 5.4548 | 45.4318 | 90.6 |  |  |  | 0.61683 | 5.9352 | 6.552
7A | Food Services | pre-1960 | baseline |  | 489.0534 | 0 | 611.3167 | 0 | 0 | 51.5821 | 145.4186 | 808.3174 |  |  |  | 9.9033 | 22.2611 | 32.1644
8B | Vehicle Garage | pre-1960 | baseline |  | 155.5356 | 0 | 194.4195 | 0 | 0 | 1.2143 | 42.281 | 237.9148 |  |  |  | 3.1496 | 4.915 | 8.0646
8B | Vehicle Garage | 1980-2004 | baseline |  | 107.7458 | 0 | 134.6823 | 0 | 0 | 1.2143 | 35.5742 | 171.4709 |  |  |  | 2.1819 | 4.1571 | 6.339
9A | Maintenance Shop | pre-1960 | baseline |  | 551.7236 | 0 | 689.6545 | 0 | 0 | 2.619 | 107.7621 | 800.0356 |  |  |  | 11.1724 | 12.4731 | 23.6455
9A | Maintenance Shop | 1980-2004 | baseline |  | 321.1088 | 0 | 401.386 | 0 | 0 | 2.619 | 78.9056 | 482.9106 |  |  |  | 6.5025 | 9.2123 | 15.7147
9B | Maintenance Shop-Small | pre-1960 | baseline |  | 599.9046 | 0 | 749.8808 | 0 | 4.6581 | 0 | 121.3605 | 875.8994 |  |  |  | 12.2235 | 13.7137 | 25.9373
9B | Maintenance Shop-Small | 1960-1979 | baseline |  | 556.137 | 0 | 695.1713 | 0 | 4.6581 | 0 | 117.4572 | 817.2866 |  |  |  | 11.3372 | 13.2727 | 24.6099
9B | Maintenance Shop-Small | 1980-2004 | baseline |  | 296.9115 | 0 | 371.1393 | 0 | 4.6581 | 0 | 93.8509 | 469.6483 |  |  |  | 6.0879 | 10.6051 | 16.6931
13B | Firehall | pre-1960 | baseline |  | 424.3909 | 0 | 530.4886 | 0 | 0 | 22.2562 | 172.4007 | 725.1454 |  |  |  | 8.5939 | 21.9962 | 30.5901
1A | Hanger | pre-1960 | infil_reduce | 1 | 203.4758 | 0 | 254.3448 | 0 | 5.309 | 0 | 73.734 | 333.3878 | 186.2158 | 6.1304 | 192.3461 | 4.2064 | 8.3319 | 12.5383 | 3.0167 | 0.69273 | 3.7094 | 15.0673 | 4.0619
1A | Hanger | 1960-1979 | infil_reduce | 1 | 206.7433 | 0 | 258.4292 | 0 | 5.309 | 0 | 73.3176 | 337.0557 | 167.9778 | 5.5449 | 173.5226 | 4.2726 | 8.2849 | 12.5574 | 2.7212 | 0.62657 | 3.3478 | 15.0673 | 4.5007
1A | Hanger | 1980-2004 | infil_reduce | 1 | 173.1748 | 0 | 216.4685 | 0 | 5.309 | 0 | 71.8651 | 293.6426 | 54.7047 | 1.641 | 56.3458 | 3.5928 | 8.1208 | 11.7136 | 0.88622 | 0.18544 | 1.0717 | 13.829 | 12.9044
2A | Training | pre-1960 | infil_reduce | 1 | 225.7539 | 0 | 282.1923 | 0 | 0 | 7.2427 | 69.1672 | 358.6023 | 229.9152 | 8.9575 | 238.8727 | 4.5715 | 8.6343 | 13.2058 | 3.7246 | 1.0122 | 4.7368 | 31.4713 | 6.644
2A | Training | 1980-2004 | infil_reduce | 1 | 185.6313 | 0 | 232.0392 | 0 | 0 | 7.2427 | 66.9374 | 306.2193 | 67.448 | 0.97 | 68.418 | 3.759 | 8.3824 | 12.1414 | 1.0927 | 0.10961 | 1.2023 | 28.055 | 23.3351
2A | Training | 2005-2014 | infil_reduce | 0 | 0 | 0 | [5 empty] | 0 | 208.8906 | 72.0547 | 280.9453 | 0 | 0 | 0 | 3.384 | 8.1422 | 11.5262 | 0 | n/a
3B | Storage | pre-1960 | infil_reduce | 1 | 135.1468 | 0 | 168.9335 | 0 | 0 | 0 | 38.5228 | 207.4564 | 155.8585 | 6.2684 | 162.1269 | 2.7367 | 4.3531 | 7.0898 | 2.5249 | 0.70833 | 3.2332 | 31.9035 | 9.8673
3B | Storage | 1960-1979 | infil_reduce | 1 | 173.7773 | 0 | 217.2216 | 0 | 0 | 0 | 40.4195 | 257.6411 | 77.6731 | 3.1572 | 80.8303 | 3.519 | 4.5674 | 8.0864 | 1.2583 | 0.35677 | 1.6151 | 31.9035 | 19.7536
3B | Storage | 1980-2004 | infil_reduce | 1 | 127.528 | 0 | 159.41 | 0 | 0 | 0 | 38.1285 | 197.5386 | 19.3722 | 0.77132 | 20.1435 | 2.5824 | 4.3085 | 6.891 | 0.31383 | 0.087159 | 0.40099 | 28.6291 | 71.3961
3B | Storage | 2005-2014 | infil_reduce | 0 | 0 | 0 | [5 empty] | 0 | 106.7703 | 35.6851 | 142.4554 | 0 | 0 | 0 | 1.7297 | 4.0324 | 5.7621 | 0 | n/a
4C | Barracks | pre-1960 | infil_reduce | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144.7611 | 33.6964 | 178.4576 | 0 | 0 | 0 | 2.3451 | 3.8077 | 6.1528 | 30.5872 | 4.9712 | ??
5E | Rec Centre | 1980-2004 | infil_reduce | 1 | 260.849 | 0 | 315.429 | 8.5057 | 20.9929 | 0 | 83.4759 | 428.4036 | 31.7061 | 6.6353 | 38.3414 | 5.45 | 10.3939 | 15.844 | 0.51364 | 0.74979 | 1.2634 | 8.9471 | 7.0816
6A | Office | pre-1960 | infil_reduce | 1 | 209.5642 | 0 | 261.9553 | 0 | 42.0337 | 0 | 100.7303 | 404.7193 | 171.5435 | 10.5834 | 182.1269 | 4.9246 | 11.3825 | 16.3071 | 2.779 | 1.1959 | 3.9749 | 15.9378 | 4.0096
6A | Office | 1960-1979 | infil_reduce | 1 | 241.8326 | 0 | 302.2908 | 0 | 42.0345 | 0 | 102.5146 | 446.8399 | 100.5775 | 6.1071 | 106.6846 | 5.5781 | 11.5842 | 17.1622 | 1.6294 | 0.6901 | 2.3195 | 15.9378 | 6.8714
6A | Office | 1980-2004 | infil_reduce | 1 | 194.135 | 0 | 242.6687 | 0 | 42.0337 | 0 | 97.3395 | 382.042 | 46.1468 | 1.0758 | 47.2226 | 4.6122 | 10.9994 | 15.6115 | 0.74758 | 0.12157 | 0.86914 | 14.5953 | 16.7927
6B | Small Office | 1960-1979 | infil_reduce | 1 | 63.5894 | 0 | 77.8789 | 1.2863 | 0 | 5.5855 | 50.4327 | 135.1834 | 51.985 | 4.6844 | 56.6694 | 1.2616 | 6.4754 | 7.737 | 0.84216 | 0.52934 | 1.3715 | 63.2815 | 46.1405
6B | Small Office | 1980-2004 | infil_reduce | 1 | 38.5755 | 0 | 46.365 | 1.4835 | 0 | 5.4915 | 46.8786 | 100.2187 | 25.488 | 1.832 | 27.3201 | 0.75111 | 6.0855 | 6.8366 | 0.41291 | 0.20702 | 0.61993 | 57.4522 | 92.6758
6B | Small Office | 2005-2014 | infil_reduce | 0 | 0 | 0 | [5 empty] | 0 | 38.0761 | 52.5238 | 90.6 | 0 | 0 | 0 | 0.61683 | 5.9352 | 6.552 | 0 | n/a
7A | Food Services | pre-1960 | infil_reduce | 1 | 272.1073 | 0 | 340.1341 | 0 | 0 | 51.5811 | 136.0806 | 527.7958 | 271.1826 | 9.339 | 280.5216 | 5.5102 | 21.2058 | 26.7159 | 4.3932 | 1.0553 | 5.4485 | 32.6308 | 5.989
8B | Vehicle Garage | pre-1960 | infil_reduce | 1 | 98.0305 | 0 | 122.5381 | 0 | 0 | 1.2143 | 34.3977 | 158.1502 | 71.8814 | 7.8832 | 79.7646 | 1.9851 | 4.0242 | 6.0093 | 1.1645 | 0.8908 | 2.0553 | 29.6245 | 14.4139
8B | Vehicle Garage | 1980-2004 | infil_reduce | 1 | 89.1579 | 0 | 111.4473 | 0 | 0 | 1.2143 | 33.0284 | 145.69 | 23.235 | 2.5459 | 25.7809 | 1.8054 | 3.8694 | 5.6749 | 0.37641 | 0.28769 | 0.66409 | 27.3743 | 41.2207
9A | Maintenance Shop | pre-1960 | infil_reduce | 1 | 354.4085 | 0 | 443.0106 | 0 | 0 | 2.619 | 83.9459 | 529.5755 | 246.6438 | 23.8162 | 270.4601 | 7.1768 | 9.7818 | 16.9586 | 3.9956 | 2.6912 | 6.6869 | 38.4114 | 5.7443
9A | Maintenance Shop | 1980-2004 | infil_reduce | 1 | 262.4175 | 0 | 328.0219 | 0 | 0 | 2.619 | 71.5941 | 402.235 | 73.3641 | 7.3115 | 80.6756 | 5.314 | 8.3861 | 13.7 | 1.1885 | 0.8262 | 2.0147 | 34.8418 | 17.2938
9B | Maintenance Shop-Small | pre-1960 | infil_reduce | 1 | 332.8676 | 0 | 416.0845 | 0 | 4.6581 | 0 | 97.4926 | 518.2352 | 333.7962 | 23.8679 | 357.6642 | 6.816 | 11.0167 | 17.8327 | 5.4075 | 2.6971 | 8.1046 | 50.8157 | 6.27
9B | Maintenance Shop-Small | 1960-1979 | infil_reduce | 1 | 315.7123 | 0 | 394.6404 | 0 | 4.6581 | 0 | 95.9529 | 495.2514 | 300.5309 | 21.5043 | 322.0352 | 6.4686 | 10.8427 | 17.3113 | 4.8686 | 2.43 | 7.2986 | 50.8157 | 6.9624
9B | Maintenance Shop-Small | 1980-2004 | infil_reduce | 1 | 217.4162 | 0 | 271.7703 | 0 | 4.6581 | 0 | 86.7479 | 363.1763 | 99.369 | 7.1029 | 106.472 | 4.4781 | 9.8025 | 14.2807 | 1.6098 | 0.80263 | 2.4124 | 46.6018 | 19.3175
13B | Firehall | pre-1960 | infil_reduce | 1 | 192.5857 | 0 | 240.7321 | 0 | 0 | 22.2562 | 156.6583 | 419.6466 | 289.7566 | 15.7423 | 305.4989 | 3.8999 | 20.2173 | 24.1172 | 4.6941 | 1.7789 | 6.4729 | 73.9232 | 11.4203
1A | Hanger | pre-1960 | exhaust_fans_occ_control | 1 | 352.4467 | 0 | 440.5583 | 0 | 5.309 | 0 | 79.0191 | 524.8864 | 0.0022128 | 0.84529 | 0.84751 | 7.2231 | 8.9292 | 16.1522 | 3.5848e-05 | 0.095518 | 0.095554 | 0.58676 | 6.1406
1A | Hanger | 1960-1979 | exhaust_fans_occ_control | 1 | 341.1241 | 0 | 426.4052 | 0 | 5.309 | 0 | 78.0172 | 509.7313 | 0.0017703 | 0.84529 | 0.84706 | 6.9938 | 8.8159 | 15.8097 | 2.8678e-05 | 0.095518 | 0.095547 | 0.58676 | 6.141
1A | Hanger | 1980-2004 | exhaust_fans_occ_control | 1 | 216.9371 | 0 | 271.1714 | 0 | 5.309 | 0 | 72.6608 | 349.1412 | 0.0017703 | 0.84529 | 0.84706 | 4.479 | 8.2107 | 12.6897 | 2.8678e-05 | 0.095518 | 0.095547 | 0.58676 | 6.141
2A | Training | pre-1960 | exhaust_fans_occ_control | 0 | 409.6861 | 0 | 512.1076 | 0 | 0 | 7.2427 | 78.1247 | 597.475 | 0 | 0 | 0 | 8.2961 | 9.6465 | 17.9427 | 0 | 0 | 0 | 0.40743 | n/a
2A | Training | 1980-2004 | exhaust_fans_occ_control | 0 | 239.5897 | 0 | 299.4871 | 0 | 0 | 7.2427 | 67.9074 | 374.6373 | 0 | 0 | 0 | 4.8517 | 8.492 | 13.3437 | 0 | 0 | 0 | 0.40743 | n/a
2A | Training | 2005-2014 | exhaust_fans_occ_control | 0 | 167.1125 | 0 | 208.8906 | 0 | 0 | 7.2427 | 64.812 | 280.9453 | 0 | 0 | 0 | 3.384 | 8.1422 | 11.5262 | 0 | 0 | 0 | 0.40743 | n/a
3B | Storage | pre-1960 | exhaust_fans_occ_control | 0 | 259.8336 | 0 | 324.792 | 0 | 0 | 0 | 44.7913 | 369.5833 | 0 | 0 | 0 | 5.2616 | 5.0614 | 10.323 | 0 | 0 | 0 | 0.64368 | n/a
3B | Storage | 1960-1979 | exhaust_fans_occ_control | 0 | 235.9158 | 0 | 294.8947 | 0 | 0 | 0 | 43.5767 | 338.4714 | 0 | 0 | 0 | 4.7773 | 4.9242 | 9.7015 | 0 | 0 | 0 | 0.64368 | n/a
3B | Storage | 1980-2004 | exhaust_fans_occ_control | 0 | 143.0258 | 0 | 178.7822 | 0 | 0 | 0 | 38.8999 | 217.6821 | 0 | 0 | 0 | 2.8963 | 4.3957 | 7.292 | 0 | 0 | 0 | 0.64368 | n/a
3B | Storage | 2005-2014 | exhaust_fans_occ_control | 0 | 85.4162 | 0 | 106.7703 | 0 | 0 | 0 | 35.6851 | 142.4554 | 0 | 0 | 0 | 1.7297 | 4.0324 | 5.7621 | 0 | 0 | 0 | 0.64368 | n/a
4C | Barracks | pre-1960 | exhaust_fans_occ_control | 0 | 0 | 0 | [5 empty] | 0 | 144.7611 | 33.6964 | 178.4576 | 0 | 0 | 0 | 2.3451 | 3.8077 | 6.1528 | 1.1337 | n/a
5E | Rec Centre | 1980-2004 | exhaust_fans_occ_control | 1 | 0 | 0 | [5 empty] | 0 | 368.128 | 98.6169 | 466.7449 | 0 | 0 | 0 | 5.9637 | 11.1437 | 17.1074 | 0.47808 | 0.027946
6A | Office | pre-1960 | exhaust_fans_occ_control | 1 | 346.7971 | 0 | 433.4963 | 0 | 42.0362 | 0 | 95.1977 | 570.7301 | 0 | 16.116 | 16.116 | 7.7036 | 10.7573 | 18.461 | 0 | 1.8211 | 1.8211 | 1.5432 | 0.8474
6A | Office | 1960-1979 | exhaust_fans_occ_control | 1 | 322.294 | 0 | 402.8675 | 0 | 42.0353 | 0 | 92.5057 | 537.4085 | 0 | 16.116 | 16.116 | 7.2074 | 10.4531 | 17.6606 | 0 | 1.8211 | 1.8211 | 1.5432 | 0.8474
6A | Office | 1980-2004 | exhaust_fans_occ_control | 1 | 231.0518 | 0 | 288.8147 | 0 | 42.0345 | 0 | 82.2993 | 413.1486 | 0 | 16.116 | 16.116 | 5.3598 | 9.2998 | 14.6596 | 0 | 1.8211 | 1.8211 | 1.5432 | 0.8474
6B | Small Office | 1960-1979 | exhaust_fans_occ_control | 1 | 105.2576 | 0 | 129.8638 | 1.3666 | 0 | 5.73 | 52.8127 | 189.7731 | 0 | 2.0797 | 2.0797 | 2.1038 | 6.7697 | 8.8735 | 0 | 0.235 | 0.235 | 2.5813 | 10.9843
6B | Small Office | 1980-2004 | exhaust_fans_occ_control | 1 | 58.7825 | 0 | 71.8531 | 1.3001 | 0 | 5.581 | 46.725 | 125.4591 | 0 | 2.0797 | 2.0797 | 1.164 | 6.0575 | 7.2215 | 0 | 0.235 | 0.235 | 2.5813 | 10.9843
6B | Small Office | 2005-2014 | exhaust_fans_occ_control | 1 | 32.0981 | 0 | 38.0761 | 1.6371 | 0 | 5.4548 | 43.3521 | 88.5203 | 0 | 2.0797 | 2.0797 | 0.61683 | 5.7002 | 6.317 | 0 | 0.235 | 0.235 | 2.5813 | 10.9843
7A | Food Services | pre-1960 | exhaust_fans_occ_control | 1 | 489.0501 | 0 | 611.3126 | 0 | 0 | 51.5821 | 133.3458 | 796.2404 | 0.004125 | 12.0728 | 12.077 | 9.9033 | 20.8968 | 30.8001 | 6.6825e-05 | 1.3642 | 1.3643 | 2.6416 | 1.9363
8B | Vehicle Garage | pre-1960 | exhaust_fans_occ_control | 1 | 155.5356 | 0 | 194.4195 | 0 | 0 | 1.2143 | 42.1719 | 237.8058 | 0 | 0.10905 | 0.10905 | 3.1496 | 4.9026 | 8.0522 | 0 | 0.012322 | 0.012322 | 0.33205 | 26.9472
8B | Vehicle Garage | 1980-2004 | exhaust_fans_occ_control | 1 | 107.7458 | 0 | 134.6823 | 0 | 0 | 1.2143 | 35.4652 | 171.3618 | 0 | 0.10905 | 0.10905 | 2.1819 | 4.1448 | 6.3266 | 0 | 0.012322 | 0.012322 | 0.33205 | 26.9472
9A | Maintenance Shop | pre-1960 | exhaust_fans_occ_control | 1 | 551.0742 | 0 | 688.8427 | 0 | 0 | 2.619 | 106.691 | 798.1528 | 0.81175 | 1.0711 | 1.8828 | 11.1593 | 12.352 | 23.5113 | 0.01315 | 0.12103 | 0.13418 | 1.1735 | 8.7452
9A | Maintenance Shop | 1980-2004 | exhaust_fans_occ_control | 1 | 320.9162 | 0 | 401.1453 | 0 | 0 | 2.619 | 77.517 | 481.2813 | 0.24073 | 1.3886 | 1.6293 | 6.4986 | 9.0554 | 15.5539 | 0.0038999 | 0.15691 | 0.16081 | 1.1735 | 7.2972
9B | Maintenance Shop-Small | pre-1960 | exhaust_fans_occ_control | 0 | 599.9046 | 0 | 749.8808 | 0 | 4.6581 | 0 | 121.3605 | 875.8994 | 0 | 0 | 0 | 12.2235 | 13.7137 | 25.9373 | 0 | 0 | 0 | 0.81311 | n/a
9B | Maintenance Shop-Small | 1960-1979 | exhaust_fans_occ_control | 0 | 556.137 | 0 | 695.1713 | 0 | 4.6581 | 0 | 117.4572 | 817.2866 | 0 | 0 | 0 | 11.3372 | 13.2727 | 24.6099 | 0 | 0 | 0 | 0.81311 | n/a
9B | Maintenance Shop-Small | 1980-2004 | exhaust_fans_occ_control | 0 | 296.9115 | 0 | 371.1393 | 0 | 4.6581 | 0 | 93.8509 | 469.6483 | 0 | 0 | 0 | 6.0879 | 10.6051 | 16.6931 | 0 | 0 | 0 | 0.81311 | n/a
13B | Firehall | pre-1960 | exhaust_fans_occ_control | 0 | 0 | 0 | [5 empty] | 0 | 530.4886 | 194.6568 | 725.1454 | 0 | 0 | 0 | 8.5939 | 21.9962 | 30.5901 | 2.4794 | n/a
1A | Hanger | pre-1960 | boiler_reset | 1 | 284.383 | 0 | 355.4787 | 0 | 5.309 | 0 | 78.9381 | 439.7259 | 85.0818 | 0.92628 | 86.0081 | 5.8448 | 8.92 | 14.7648 | 1.3783 | 0.10467 | 1.483 | 0.149 | 0.10047
1A | Hanger | 1960-1979 | boiler_reset | 1 | 276.0575 | 0 | 345.0719 | 0 | 5.309 | 0 | 78.0079 | 428.3887 | 81.3351 | 0.85459 | 82.1896 | 5.6762 | 8.8149 | 14.4911 | 1.3176 | 0.096569 | 1.4142 | 0.149 | 0.10536
1A | Hanger | 1980-2004 | boiler_reset | 1 | 172.5339 | 0 | 215.6674 | 0 | 5.309 | 0 | 73.0251 | 294.0015 | 55.5058 | 0.48107 | 55.9868 | 3.5798 | 8.2518 | 11.8316 | 0.89919 | 0.05436 | 0.95355 | 0.149 | 0.15625
2A | Training | pre-1960 | boiler_reset | 1 | 253.852 | 0 | 317.315 | 0 | 0 | 7.2427 | 78.5181 | 403.0758 | 194.7926 | -0.39341 | 194.3992 | 5.1405 | 9.691 | 14.8315 | 3.1556 | -0.044455 | 3.1112 | 0.25865 | 0.083135
2A | Training | 1980-2004 | boiler_reset | 1 | 151.7565 | 0 | 189.6956 | 0 | 0 | 7.2427 | 68.2723 | 265.2106 | 109.7916 | -0.36488 | 109.4267 | 3.0731 | 8.5332 | 11.6063 | 1.7786 | -0.041231 | 1.7374 | 0.25865 | 0.14887
2A | Training | 2005-2014 | boiler_reset | 1 | 104.0331 | 0 | 130.0414 | 0 | 0 | 7.2427 | 65.0252 | 202.3093 | 78.8492 | -0.21322 | 78.636 | 2.1067 | 8.1663 | 10.2729 | 1.2774 | -0.024094 | 1.2533 | 0.25865 | 0.20638
3B | Storage | pre-1960 | boiler_reset | 0 | 0 | 0 | [5 empty] | 0 | 324.792 | 44.7913 | 369.5833 | 0 | 0 | 0 | 5.2616 | 5.0614 | 10.323 | 0.81725 | n/a
3B | Storage | 1960-1979 | boiler_reset | 0 | 0 | 0 | [5 empty] | 0 | 294.8947 | 43.5767 | 338.4714 | 0 | 0 | 0 | 4.7773 | 4.9242 | 9.7015 | 0.81725 | n/a
3B | Storage | 1980-2004 | boiler_reset | 0 | 0 | 0 | [5 empty] | 0 | 178.7822 | 38.8999 | 217.6821 | 0 | 0 | 0 | 2.8963 | 4.3957 | 7.292 | 0.81725 | n/a
3B | Storage | 2005-2014 | boiler_reset | 0 | 0 | 0 | [5 empty] | 0 | 106.7703 | 35.6851 | 142.4554 | 0 | 0 | 0 | 1.7297 | 4.0324 | 5.7621 | 0.81725 | n/a
4C | Barracks | pre-1960 | boiler_reset | 1 | 57.6024 | 0 | 72.003 | 0 | 29.0848 | 0 | 33.6959 | 134.7837 | 43.6734 | 0.00050544 | 43.6739 | 1.6376 | 3.8076 | 5.4453 | 0.70751 | 5.7115e-05 | 0.70757 | 0.23991 | 0.33906
5E | Rec Centre | 1980-2004 | boiler_reset | 1 | 265.1675 | 0 | 316.0536 | 12.3246 | 20.994 | 0 | 86.3064 | 435.6786 | 31.0804 | -0.014095 | 31.0663 | 5.4602 | 11.1453 | 16.6055 | 0.5035 | -0.0015927 | 0.50191 | 0.075874 | 0.15117
6A | Office | pre-1960 | boiler_reset | 1 | 239.9131 | 0 | 299.8913 | 0 | 42.0362 | 0 | 111.1219 | 453.0494 | 133.605 | 0.19176 | 133.7968 | 5.5392 | 12.5568 | 18.096 | 2.1644 | 0.021669 | 2.1861 | 0.27991 | 0.12804
6A | Office | 1960-1979 | boiler_reset | 1 | 223.5497 | 0 | 279.4372 | 0 | 42.0353 | 0 | 108.4519 | 429.9244 | 123.4303 | 0.16982 | 123.6001 | 5.2079 | 12.2551 | 17.4629 | 1.9996 | 0.01919 | 2.0188 | 0.27991 | 0.13865
6A | Office | 1980-2004 | boiler_reset | 1 | 158.7354 | 0 | 198.4192 | 0 | 42.0345 | 0 | 98.521 | 338.9747 | 90.3955 | -0.10563 | 90.2899 | 3.8954 | 11.1329 | 15.0282 | 1.4644 | -0.011936 | 1.4525 | 0.27991 | 0.19271
6B | Small Office | 1960-1979 | boiler_reset | 0 | 105.2576 | 0 | 129.8638 | 1.3666 | 0 | 5.73 | 54.8924 | 191.8528 | 0 | 0 | 0 | 2.1038 | 7.0048 | 9.1085 | 0 | 0 | 0 | 1.6387 | n/a
6B | Small Office | 1980-2004 | boiler_reset | 0 | 58.7825 | 0 | 71.8531 | 1.3001 | 0 | 5.581 | 48.8047 | 127.5388 | 0 | 0 | 0 | 1.164 | 6.2925 | 7.4565 | 0 | 0 | 0 | 1.6387 | n/a
6B | Small Office | 2005-2014 | boiler_reset | 0 | 32.0981 | 0 | 38.0761 | 1.6371 | 0 | 5.4548 | 45.4318 | 90.6 | 0 | 0 | 0 | 0.61683 | 5.9352 | 6.552 | 0 | 0 | 0 | 1.6387 | n/a
7A | Food Services | pre-1960 | boiler_reset | 1 | 381.7671 | 0 | 477.2088 | 0 | 0 | 51.5821 | 145.4176 | 674.2085 | 134.1079 | 0.0010312 | 134.1089 | 7.7308 | 22.261 | 29.9917 | 2.1725 | 0.00011653 | 2.1727 | 0.37266 | 0.17152
8B | Vehicle Garage | pre-1960 | boiler_reset | 1 | 94.8217 | 0 | 118.5272 | 0 | 0 | 1.2143 | 42.2787 | 162.0202 | 75.8924 | 0.0022254 | 75.8946 | 1.9201 | 4.9147 | 6.8349 | 1.2295 | 0.00025147 | 1.2297 | 0.42159 | 0.34283
8B | Vehicle Garage | 1980-2004 | boiler_reset | 1 | 66.0235 | 0 | 82.5293 | 0 | 0 | 1.2143 | 35.5742 | 119.3179 | 52.153 | 0 | 52.153 | 1.337 | 4.1571 | 5.4941 | 0.84488 | 0 | 0.84488 | 0.42159 | 0.49899
9A | Maintenance Shop | pre-1960 | boiler_reset | 1 | 341.0968 | 0 | 426.371 | 0 | 0 | 2.619 | 107.7168 | 536.7068 | 263.2835 | 0.045355 | 263.3288 | 6.9072 | 12.4679 | 19.3751 | 4.2652 | 0.0051252 | 4.2703 | 0.49663 | 0.1163
9A | Maintenance Shop | 1980-2004 | boiler_reset | 1 | 201.017 | 0 | 251.2713 | 0 | 0 | 2.619 | 78.8975 | 332.7877 | 150.1148 | 0.0081407 | 150.1229 | 4.0706 | 9.2114 | 13.282 | 2.4319 | 0.0009199 | 2.4328 | 0.49663 | 0.20414
9B | Maintenance Shop-Small | pre-1960 | boiler_reset | 1 | 367.9072 | 0 | 459.884 | 0 | 4.6581 | 0 | 121.3605 | 585.9026 | 289.9968 | 0 | 289.9968 | 7.5256 | 13.7137 | 21.2393 | 4.6979 | 0 | 4.6979 | 1.0324 | 0.21975
9B | Maintenance Shop-Small | 1960-1979 | boiler_reset | 1 | 340.7079 | 0 | 425.8849 | 0 | 4.6581 | 0 | 117.4572 | 548.0002 | 269.2864 | 0 | 269.2864 | 6.9748 | 13.2727 | 20.2475 | 4.3624 | 0 | 4.3624 | 1.0324 | 0.23665
9B | Maintenance Shop-Small | 1980-2004 | boiler_reset | 1 | 181.4913 | 0 | 226.8642 | 0 | 4.6581 | 0 | 93.8539 | 325.3762 | 144.2752 | -0.0030072 | 144.2721 | 3.7507 | 10.6055 | 14.3561 | 2.3373 | -0.00033981 | 2.3369 | 1.0324 | 0.44176
13B | Firehall | pre-1960 | boiler_reset | 1 | 307.2806 | 0 | 384.1007 | 0 | 0 | 22.2562 | 172.4037 | 578.7606 | 146.3879 | -0.0030467 | 146.3849 | 6.2224 | 21.9966 | 28.219 | 2.3715 | -0.00034428 | 2.3711 | 1.0493 | 0.44255
1A | Hanger | pre-1960 | cooling_cop_3_0 | 1 | 352.4484 | 0 | 440.5605 | 0 | 5.309 | 0 | 79.7414 | 525.6109 | 0 | 0.12303 | 0.12303 | 7.2231 | 9.0108 | 16.2339 | 0 | 0.013903 | 0.013903 | 2.5825 | 185.7569
1A | Hanger | 1960-1979 | cooling_cop_3_0 | 1 | 341.1255 | 0 | 426.4069 | 0 | 5.309 | 0 | 78.7589 | 510.4748 | 0 | 0.10356 | 0.10356 | 6.9938 | 8.8998 | 15.8936 | 0 | 0.011702 | 0.011702 | 2.5825 | 220.6856
1A | Hanger | 1980-2004 | cooling_cop_3_0 | 1 | 216.9386 | 0 | 271.1732 | 0 | 5.309 | 0 | 73.4614 | 349.9436 | 0 | 0.044699 | 0.044699 | 4.479 | 8.3011 | 12.7802 | 0 | 0.005051 | 0.005051 | 2.5825 | 511.2913
2A | Training | pre-1960 | cooling_cop_3_0 | 1 | 409.6861 | 0 | 512.1076 | 0 | 0 | 7.2427 | 77.2666 | 596.6168 | 0 | 0.85813 | 0.85813 | 8.2961 | 9.5495 | 17.8457 | 0 | 0.096969 | 0.096969 | 5.5 | 56.7191
2A | Training | 1980-2004 | cooling_cop_3_0 | 1 | 239.5897 | 0 | 299.4871 | 0 | 0 | 7.2427 | 67.3916 | 374.1215 | 0 | 0.51578 | 0.51578 | 4.8517 | 8.4337 | 13.2854 | 0 | 0.058283 | 0.058283 | 5.5 | 94.3667
2A | Training | 2005-2014 | cooling_cop_3_0 | 0 | 167.1125 | 0 | 208.8906 | 0 | 0 | 7.2427 | 64.812 | 280.9453 | 0 | 0 | 0 | 3.384 | 8.1422 | 11.5262 | 0 | 0 | 0 | 5.5 | n/a
3B | Storage | pre-1960 | cooling_cop_3_0 | 0 | 0 | 0 | [5 empty] | 0 | 324.792 | 44.7913 | 369.5833 | 0 | 0 | 0 | 5.2616 | 5.0614 | 10.323 | 0 | n/a
3B | Storage | 1960-1979 | cooling_cop_3_0 | 0 | 0 | 0 | [5 empty] | 0 | 294.8947 | 43.5767 | 338.4714 | 0 | 0 | 0 | 4.7773 | 4.9242 | 9.7015 | 0 | n/a
3B | Storage | 1980-2004 | cooling_cop_3_0 | 0 | 0 | 0 | [5 empty] | 0 | 178.7822 | 38.8999 | 217.6821 | 0 | 0 | 0 | 2.8963 | 4.3957 | 7.292 | 0 | n/a
3B | Storage | 2005-2014 | cooling_cop_3_0 | 0 | 0 | 0 | [5 empty] | 0 | 106.7703 | 35.6851 | 142.4554 | 0 | 0 | 0 | 1.7297 | 4.0324 | 5.7621 | 0 | n/a
4C | Barracks | pre-1960 | cooling_cop_3_0 | 1 | 92.5407 | 0 | 115.6759 | 0 | 29.0853 | 0 | 33.2713 | 178.0325 | 0 | 0.42508 | 0.42508 | 2.3451 | 3.7597 | 6.1048 | 0 | 0.048034 | 0.048034 | 3.8261 | 79.6552
5E | Rec Centre | 1980-2004 | cooling_cop_3_0 | 0 | 289.914 | 0 | 347.134 | 12.2081 | 20.994 | 0 | 86.1903 | 466.5265 | 0 | 0.21847 | 0.21847 | 5.9637 | 11.119 | 17.0827 | 0 | 0.024688 | 0.024688 | 3.542 | n/a
6A | Office | pre-1960 | cooling_cop_3_0 | 1 | 346.7971 | 0 | 433.4963 | 0 | 42.0362 | 0 | 105.2115 | 580.7439 | 0 | 6.1022 | 6.1022 | 7.7036 | 11.8889 | 19.5925 | 0 | 0.68955 | 0.68955 | 6.0544 | 8.7802
6A | Office | 1960-1979 | cooling_cop_3_0 | 1 | 322.294 | 0 | 402.8675 | 0 | 42.0353 | 0 | 102.8697 | 547.7725 | 0 | 5.752 | 5.752 | 7.2074 | 11.6243 | 18.8317 | 0 | 0.64998 | 0.64998 | 6.0544 | 9.3148
6A | Office | 1980-2004 | cooling_cop_3_0 | 1 | 231.0518 | 0 | 288.8147 | 0 | 42.0345 | 0 | 96.297 | 427.1463 | 0 | 2.1183 | 2.1183 | 5.3598 | 10.8816 | 16.2413 | 0 | 0.23937 | 0.23937 | 6.0544 | 25.2933
6B | Small Office | 1960-1979 | cooling_cop_3_0 | 1 | 105.2576 | 0 | 129.8638 | 1.3666 | 0 | 5.73 | 54.0555 | 191.0159 | 0 | 0.83691 | 0.83691 | 2.1038 | 6.9102 | 9.014 | 0 | 0.094571 | 0.094571 | 29.5377 | 312.3324
6B | Small Office | 1980-2004 | cooling_cop_3_0 | 1 | 58.7825 | 0 | 71.8531 | 1.3001 | 0 | 5.581 | 48.4264 | 127.1605 | 0 | 0.37833 | 0.37833 | 1.164 | 6.2497 | 7.4138 | 0 | 0.042751 | 0.042751 | 29.5377 | 690.917
6B | Small Office | 2005-2014 | cooling_cop_3_0 | 0 | 32.0981 | 0 | 38.0761 | 1.6371 | 0 | 5.4548 | 45.4318 | 90.6 | 0 | 0 | 0 | 0.61683 | 5.9352 | 6.552 | 0 | 0 | 0 | 29.5377 | n/a
7A | Food Services | pre-1960 | cooling_cop_3_0 | 1 | 489.0534 | 0 | 611.3167 | 0 | 0 | 51.5821 | 144.2182 | 807.117 | 0 | 1.2004 | 1.2004 | 9.9033 | 22.1254 | 32.0288 | 0 | 0.13564 | 0.13564 | 7.9245 | 58.4217
8B | Vehicle Garage | pre-1960 | cooling_cop_3_0 | 0 | 0 | 0 | [5 empty] | 0 | 194.4195 | 43.4953 | 237.9148 | 0 | 0 | 0 | 3.1496 | 4.915 | 8.0646 | 0 | n/a
8B | Vehicle Garage | 1980-2004 | cooling_cop_3_0 | 0 | 0 | 0 | [5 empty] | 0 | 134.6823 | 36.7886 | 171.4709 | 0 | 0 | 0 | 2.1819 | 4.1571 | 6.339 | 0 | n/a
9A | Maintenance Shop | pre-1960 | cooling_cop_3_0 | 1 | 551.7236 | 0 | 689.6545 | 0 | 0 | 2.619 | 107.6109 | 799.8844 | 0 | 0.15118 | 0.15118 | 11.1724 | 12.456 | 23.6284 | 0 | 0.017084 | 0.017084 | 2.6401 | 154.5384
9A | Maintenance Shop | 1980-2004 | cooling_cop_3_0 | 1 | 321.1088 | 0 | 401.386 | 0 | 0 | 2.619 | 78.8358 | 482.8408 | 0 | 0.069778 | 0.069778 | 6.5025 | 9.2044 | 15.7068 | 0 | 0.0078849 | 0.0078849 | 2.6401 | 334.8333
9B | Maintenance Shop-Small | pre-1960 | cooling_cop_3_0 | 1 | 599.9046 | 0 | 749.8808 | 0 | 4.6581 | 0 | 121.0147 | 875.5536 | 0 | 0.34582 | 0.34582 | 12.2235 | 13.6747 | 25.8982 | 0 | 0.039078 | 0.039078 | 11.165 | 285.7103
9B | Maintenance Shop-Small | 1960-1979 | cooling_cop_3_0 | 1 | 556.137 | 0 | 695.1713 | 0 | 4.6581 | 0 | 117.1084 | 816.9377 | 0 | 0.34883 | 0.34883 | 11.3372 | 13.2332 | 24.5705 | 0 | 0.039418 | 0.039418 | 11.165 | 283.2473
9B | Maintenance Shop-Small | 1980-2004 | cooling_cop_3_0 | 1 | 296.9115 | 0 | 371.1393 | 0 | 4.6581 | 0 | 93.6975 | 469.4949 | 0 | 0.15337 | 0.15337 | 6.0879 | 10.5878 | 16.6757 | 0 | 0.01733 | 0.01733 | 11.165 | 644.2487
13B | Firehall | pre-1960 | cooling_cop_3_0 | 1 | 424.3909 | 0 | 530.4886 | 0 | 0 | 22.2562 | 171.9619 | 724.7067 | 0 | 0.43873 | 0.43873 | 8.5939 | 21.9466 | 30.5406 | 0 | 0.049576 | 0.049576 | 12.6096 | 254.3502
1A | Hanger | pre-1960 | dcv_enabled | 1 | 302.596 | 0 | 378.245 | 0 | 5.309 | 0 | 79.7834 | 463.3375 | 62.3155 | 0.080989 | 62.3965 | 6.2136 | 9.0155 | 15.2291 | 1.0095 | 0.0091518 | 1.0187 | 10.2739 | 10.0856
1A | Hanger | 1960-1979 | dcv_enabled | 1 | 291.4367 | 0 | 364.2959 | 0 | 5.309 | 0 | 78.7677 | 448.3726 | 62.111 | 0.094708 | 62.2057 | 5.9876 | 8.9008 | 14.8884 | 1.0062 | 0.010702 | 1.0169 | 10.2739 | 10.1031
1A | Hanger | 1980-2004 | dcv_enabled | 1 | 168.3749 | 0 | 210.4686 | 0 | 5.309 | 0 | 73.3911 | 289.1687 | 60.7046 | 0.11507 | 60.8196 | 3.4956 | 8.2932 | 11.7888 | 0.98341 | 0.013002 | 0.99642 | 10.2739 | 10.3108
2A | Training | pre-1960 | dcv_enabled | 1 | 349.1731 | 0 | 436.4664 | 0 | 0 | 7.2427 | 78.1172 | 521.8263 | 75.6411 | 0.0075077 | 75.6486 | 7.0708 | 9.6457 | 16.7164 | 1.2254 | 0.00084837 | 1.2262 | 9.4965 | 7.7444
2A | Training | 1980-2004 | dcv_enabled | 1 | 180.5621 | 0 | 225.7027 | 0 | 0 | 7.2427 | 68.0005 | 300.9459 | 73.7845 | -0.093096 | 73.6914 | 3.6564 | 8.5025 | 12.1589 | 1.1953 | -0.01052 | 1.1848 | 9.4965 | 8.0153
2A | Training | 2005-2014 | dcv_enabled | 1 | 105.7119 | 0 | 132.1398 | 0 | 0 | 7.2427 | 65.0312 | 204.4137 | 76.7508 | -0.21923 | 76.5316 | 2.1407 | 8.167 | 10.3076 | 1.2434 | -0.024773 | 1.2186 | 9.4965 | 7.793
3B | Storage | pre-1960 | dcv_enabled | 0 | 259.8336 | 0 | 324.792 | 0 | 0 | 0 | 44.7913 | 369.5833 | 0 | 0 | 0 | 5.2616 | 5.0614 | 10.323 | 0 | 0 | 0 | 0.73185 | n/a
3B | Storage | 1960-1979 | dcv_enabled | 0 | 235.9158 | 0 | 294.8947 | 0 | 0 | 0 | 43.5767 | 338.4714 | 0 | 0 | 0 | 4.7773 | 4.9242 | 9.7015 | 0 | 0 | 0 | 0.73185 | n/a
3B | Storage | 1980-2004 | dcv_enabled | 0 | 143.0258 | 0 | 178.7822 | 0 | 0 | 0 | 38.8999 | 217.6821 | 0 | 0 | 0 | 2.8963 | 4.3957 | 7.292 | 0 | 0 | 0 | 0.73185 | n/a
3B | Storage | 2005-2014 | dcv_enabled | 0 | 85.4162 | 0 | 106.7703 | 0 | 0 | 0 | 35.6851 | 142.4554 | 0 | 0 | 0 | 1.7297 | 4.0324 | 5.7621 | 0 | 0 | 0 | 0.73185 | n/a
4C | Barracks | pre-1960 | dcv_enabled | 1 | 89.2662 | 0 | 111.5828 | 0 | 29.0853 | 0 | 33.8607 | 174.5287 | 4.0931 | -0.16427 | 3.9288 | 2.2788 | 3.8263 | 6.1051 | 0.066308 | -0.018562 | 0.047746 | 16.1131 | 337.4778 | ??
5E | Rec Centre | 1980-2004 | dcv_enabled | 1 | 213.888 | 0 | 252.562 | 11.8377 | 20.9938 | 0 | 87.3939 | 372.7874 | 94.5723 | -0.61468 | 93.9576 | 4.4316 | 11.2132 | 15.6448 | 1.5321 | -0.069459 | 1.4626 | 2.1743 | 1.4866
6A | Office | pre-1960 | dcv_enabled | 1 | 298.0951 | 0 | 372.6189 | 0 | 42.0362 | 0 | 111.36 | 526.015 | 60.8774 | -0.046315 | 60.8311 | 6.7174 | 12.5837 | 19.3011 | 0.98621 | -0.0052336 | 0.98098 | 12.7836 | 13.0314
6A | Office | 1960-1979 | dcv_enabled | 1 | 274.0328 | 0 | 342.541 | 0 | 42.0353 | 0 | 108.677 | 493.2533 | 60.3265 | -0.055253 | 60.2713 | 6.2301 | 12.2805 | 18.5106 | 0.97729 | -0.0062436 | 0.97105 | 12.7836 | 13.1647
6A | Office | 1980-2004 | dcv_enabled | 1 | 181.7284 | 0 | 227.1605 | 0 | 42.0345 | 0 | 98.5185 | 367.7136 | 61.6542 | -0.10319 | 61.551 | 4.361 | 11.1326 | 15.4936 | 0.9988 | -0.011661 | 0.98714 | 12.7836 | 12.9501
6B | Small Office | 1960-1979 | dcv_enabled | 0 | 105.2576 | 0 | 129.8638 | 1.3666 | 0 | 5.73 | 54.8924 | 191.8528 | 0 | 0 | 0 | 2.1038 | 7.0048 | 9.1085 | 0 | 0 | 0 | 23.4795 | n/a
6B | Small Office | 1980-2004 | dcv_enabled | 0 | 58.7825 | 0 | 71.8531 | 1.3001 | 0 | 5.581 | 48.8047 | 127.5388 | 0 | 0 | 0 | 1.164 | 6.2925 | 7.4565 | 0 | 0 | 0 | 23.4795 | n/a
6B | Small Office | 2005-2014 | dcv_enabled | 0 | 32.0981 | 0 | 38.0761 | 1.6371 | 0 | 5.4548 | 45.4318 | 90.6 | 0 | 0 | 0 | 0.61683 | 5.9352 | 6.552 | 0 | 0 | 0 | 23.4795 | n/a
7A | Food Services | pre-1960 | dcv_enabled | 1 | 340.3381 | 0 | 425.4226 | 0 | 0 | 51.5821 | 147.4914 | 624.4961 | 185.8941 | -2.0728 | 183.8213 | 6.8918 | 22.4953 | 29.3872 | 3.0115 | -0.23423 | 2.7773 | 3.0035 | 1.0815
8B | Vehicle Garage | pre-1960 | dcv_enabled | 1 | 134.8005 | 0 | 168.5007 | 0 | 0 | 1.2143 | 42.2535 | 211.9685 | 25.9188 | 0.027447 | 25.9463 | 2.7297 | 4.9119 | 7.6416 | 0.41989 | 0.0031015 | 0.42299 | 3.7753 | 8.9254
8B | Vehicle Garage | 1980-2004 | dcv_enabled | 1 | 87.4333 | 0 | 109.2916 | 0 | 0 | 1.2143 | 35.5097 | 146.0157 | 25.3907 | 0.064537 | 25.4552 | 1.7705 | 4.1498 | 5.9203 | 0.41133 | 0.0072927 | 0.41862 | 3.7753 | 9.0185
9A | Maintenance Shop | pre-1960 | dcv_enabled | 1 | 423.5692 | 0 | 529.4615 | 0 | 0 | 2.619 | 107.5714 | 639.6519 | 160.193 | 0.19073 | 160.3837 | 8.5773 | 12.4515 | 21.0288 | 2.5951 | 0.021552 | 2.6167 | 4.8921 | 1.8696
9A | Maintenance Shop | 1980-2004 | dcv_enabled | 1 | 215.5103 | 0 | 269.3878 | 0 | 0 | 2.619 | 78.58 | 350.5868 | 131.9982 | 0.32563 | 132.3238 | 4.3641 | 9.1755 | 13.5396 | 2.1384 | 0.036796 | 2.1752 | 4.8921 | 2.2491
9B | Maintenance Shop-Small | pre-1960 | dcv_enabled | 0 | 599.9046 | 0 | 749.8808 | 0 | 4.6581 | 0 | 121.3605 | 875.8994 | 0 | 0 | 0 | 12.2235 | 13.7137 | 25.9373 | 0 | 0 | 0 | 8.3204 | n/a
9B | Maintenance Shop-Small | 1960-1979 | dcv_enabled | 0 | 556.137 | 0 | 695.1713 | 0 | 4.6581 | 0 | 117.4572 | 817.2866 | 0 | 0 | 0 | 11.3372 | 13.2727 | 24.6099 | 0 | 0 | 0 | 8.3204 | n/a
9B | Maintenance Shop-Small | 1980-2004 | dcv_enabled | 0 | 296.9115 | 0 | 371.1393 | 0 | 4.6581 | 0 | 93.8509 | 469.6483 | 0 | 0 | 0 | 6.0879 | 10.6051 | 16.6931 | 0 | 0 | 0 | 8.3204 | n/a
13B | Firehall | pre-1960 | dcv_enabled | 0 | 424.3909 | 0 | 530.4886 | 0 | 0 | 22.2562 | 172.4007 | 725.1454 | 0 | 0 | 0 | 8.5939 | 21.9962 | 30.5901 | 0 | 0 | 0 | 9.5044 | n/a
1A | Hanger | pre-1960 | economizers_enabled | 1 | 352.4544 | 0 | 440.5681 | 0 | 5.309 | 0 | 79.8494 | 525.7264 | -0.0075236 | 0.015047 | 0.0075236 | 7.2232 | 9.023 | 16.2462 | -0.00012188 | 0.0017003 | 0.0015784 | 0.4406 | 279.1382
1A | Hanger | 1960-1979 | economizers_enabled | 1 | 341.1316 | 0 | 426.4145 | 0 | 5.309 | 0 | 78.8483 | 510.5717 | -0.0075236 | 0.014162 | 0.0066384 | 6.9939 | 8.9099 | 15.9038 | -0.00012188 | 0.0016003 | 0.0014784 | 0.4406 | 298.0226
1A | Hanger | 1980-2004 | economizers_enabled | 1 | 216.9446 | 0 | 271.1807 | 0 | 5.309 | 0 | 73.4893 | 349.979 | -0.0075236 | 0.016817 | 0.0092938 | 4.4791 | 8.3043 | 12.7834 | -0.00012188 | 0.0019004 | 0.0017785 | 0.4406 | 247.7416
2A | Training | pre-1960 | economizers_enabled | 1 | 409.7185 | 0 | 512.1481 | 0 | 0 | 7.2427 | 77.6555 | 597.0463 | -0.040542 | 0.46923 | 0.42869 | 8.2968 | 9.5935 | 17.8903 | -0.00065678 | 0.053023 | 0.052367 | 1.5297 | 29.212
2A | Training | 1980-2004 | economizers_enabled | 1 | 239.6131 | 0 | 299.5164 | 0 | 0 | 7.2427 | 66.9292 | 373.6883 | -0.02928 | 0.97826 | 0.94898 | 4.8522 | 8.3814 | 13.2336 | -0.00047434 | 0.11054 | 0.11007 | 1.5297 | 13.8979
2A | Training | 2005-2014 | economizers_enabled | 1 | 167.1503 | 0 | 208.9379 | 0 | 0 | 7.2427 | 63.5342 | 279.7148 | -0.047299 | 1.2778 | 1.2305 | 3.3848 | 7.9978 | 11.3826 | -0.00076624 | 0.14439 | 0.14363 | 1.5297 | 10.6507
3B | Storage | pre-1960 | economizers_enabled | 0 | 0 | 0 | [5 empty] | 0 | 324.792 | 44.7913 | 369.5833 | 0 | 0 | 0 | 5.2616 | 5.0614 | 10.323 | 0 | n/a
3B | Storage | 1960-1979 | economizers_enabled | 0 | 0 | 0 | [5 empty] | 0 | 294.8947 | 43.5767 | 338.4714 | 0 | 0 | 0 | 4.7773 | 4.9242 | 9.7015 | 0 | n/a
3B | Storage | 1980-2004 | economizers_enabled | 0 | 0 | 0 | [5 empty] | 0 | 178.7822 | 38.8999 | 217.6821 | 0 | 0 | 0 | 2.8963 | 4.3957 | 7.292 | 0 | n/a
3B | Storage | 2005-2014 | economizers_enabled | 0 | 0 | 0 | [5 empty] | 0 | 106.7703 | 35.6851 | 142.4554 | 0 | 0 | 0 | 1.7297 | 4.0324 | 5.7621 | 0 | n/a
4C | Barracks | pre-1960 | economizers_enabled | 1 | 92.6305 | 0 | 115.7881 | 0 | 29.0853 | 0 | 33.2845 | 178.1578 | -0.11221 | 0.41194 | 0.29973 | 2.3469 | 3.7611 | 6.1081 | -0.0018178 | 0.046549 | 0.044731 | 1.0642 | 23.7905
5E | Rec Centre | 1980-2004 | economizers_enabled | 1 | 289.994 | 0 | 347.2336 | 12.211 | 20.994 | 0 | 86.3652 | 466.8037 | -0.099547 | 0.040744 | -0.058803 | 5.9653 | 11.1391 | 17.1044 | -0.0016127 | 0.004604 | 0.0029914 | 0.67312 | 225.0183
6A | Office | pre-1960 | economizers_enabled | 1 | 346.8146 | 0 | 433.5183 | 0 | 42.0362 | 0 | 111.1633 | 586.7178 | -0.021939 | 0.15032 | 0.12838 | 7.704 | 12.5615 | 20.2654 | -0.00035541 | 0.016986 | 0.016631 | 2.0693 | 124.4267
6A | Office | 1960-1979 | economizers_enabled | 1 | 322.3076 | 0 | 402.8845 | 0 | 42.0353 | 0 | 108.4828 | 553.4026 | -0.017063 | 0.13895 | 0.12188 | 7.2077 | 12.2586 | 19.4663 | -0.00027643 | 0.015701 | 0.015424 | 2.0693 | 134.1591
6A | Office | 1980-2004 | economizers_enabled | 1 | 231.0758 | 0 | 288.8448 | 0 | 42.0345 | 0 | 98.2358 | 429.1151 | -0.030064 | 0.17957 | 0.14951 | 5.3602 | 11.1006 | 16.4609 | -0.00048704 | 0.020292 | 0.019805 | 2.0693 | 104.4866
6B | Small Office | 1960-1979 | economizers_enabled | 0 | 105.2576 | 0 | 129.8638 | 1.3666 | 0 | 5.73 | 54.8924 | 191.8528 | 0 | 0 | 0 | 2.1038 | 7.0048 | 9.1085 | 0 | 0 | 0 | 9.6918 | n/a
6B | Small Office | 1980-2004 | economizers_enabled | 0 | 58.7825 | 0 | 71.8531 | 1.3001 | 0 | 5.581 | 48.8047 | 127.5388 | 0 | 0 | 0 | 1.164 | 6.2925 | 7.4565 | 0 | 0 | 0 | 9.6918 | n/a
6B | Small Office | 2005-2014 | economizers_enabled | 0 | 32.0981 | 0 | 38.0761 | 1.6371 | 0 | 5.4548 | 45.4318 | 90.6 | 0 | 0 | 0 | 0.61683 | 5.9352 | 6.552 | 0 | 0 | 0 | 9.6918 | n/a
7A | Food Services | pre-1960 | economizers_enabled | 1 | 489.0657 | 0 | 611.3322 | 0 | 0 | 51.5821 | 145.0175 | 807.9317 | -0.015469 | 0.40116 | 0.38569 | 9.9036 | 22.2157 | 32.1193 | -0.00025059 | 0.045331 | 0.04508 | 1.8808 | 41.7222
8B | Vehicle Garage | pre-1960 | economizers_enabled | 1 | 155.7932 | 0 | 194.7415 | 0 | 0 | 1.2143 | 42.1022 | 238.058 | -0.32195 | 0.17878 | -0.14317 | 3.1548 | 4.8948 | 8.0496 | -0.0052155 | 0.020202 | 0.014986 | 1.5958 | 106.4857
8B | Vehicle Garage | 1980-2004 | economizers_enabled | 1 | 108.0372 | 0 | 135.0465 | 0 | 0 | 1.2143 | 35.3747 | 171.6356 | -0.36423 | 0.19955 | -0.16468 | 2.1878 | 4.1346 | 6.3223 | -0.0059005 | 0.022549 | 0.016648 | 1.5958 | 95.8546
9A | Maintenance Shop | pre-1960 | economizers_enabled | 1 | 551.8194 | 0 | 689.7743 | 0 | 0 | 2.619 | 107.6353 | 800.0286 | -0.11978 | 0.12676 | 0.0069778 | 11.1743 | 12.4587 | 23.6331 | -0.0019405 | 0.014324 | 0.012384 | 0.62662 | 50.6007
9A | Maintenance Shop | 1980-2004 | economizers_enabled | 1 | 321.3219 | 0 | 401.6523 | 0 | 0 | 2.619 | 78.7695 | 483.0409 | -0.26632 | 0.13607 | -0.13025 | 6.5068 | 9.1969 | 15.7037 | -0.0043143 | 0.015375 | 0.011061 | 0.62662 | 56.6508
9B | Maintenance Shop-Small | pre-1960 | economizers_enabled | 1 | 600.0081 | 0 | 750.0101 | 0 | 4.6581 | 0 | 121.2131 | 875.8813 | -0.12931 | 0.14735 | 0.018043 | 12.2256 | 13.6971 | 25.9227 | -0.0020948 | 0.016651 | 0.014556 | 1.5264 | 104.8666
9B | Maintenance Shop-Small | 1960-1979 | economizers_enabled | 1 | 556.279 | 0 | 695.3487 | 0 | 4.6581 | 0 | 117.2798 | 817.2866 | -0.17742 | 0.17742 | -7.1054e-14 | 11.3401 | 13.2526 | 24.5927 | -0.0028743 | 0.020049 | 0.017175 | 1.5264 | 88.8773
9B | Maintenance Shop-Small | 1980-2004 | economizers_enabled | 1 | 297.2242 | 0 | 371.5303 | 0 | 4.6581 | 0 | 93.4599 | 469.6483 | -0.39093 | 0.39093 | -4.6896e-13 | 6.0943 | 10.561 | 16.6552 | -0.0063331 | 0.044175 | 0.037842 | 1.5264 | 40.3366
13B | Firehall | pre-1960 | economizers_enabled | 1 | 424.9856 | 0 | 531.232 | 0 | 0 | 22.2562 | 171.8126 | 725.3008 | -0.7434 | 0.58801 | -0.15538 | 8.606 | 21.9298 | 30.5357 | -0.012043 | 0.066446 | 0.054403 | 1.5515 | 28.5195
1A | Hanger | pre-1960 | fans_to_variable | 1 | 349.7615 | 0 | 437.2019 | 0 | 5.309 | 0 | 82.091 | 524.6019 | 3.3586 | -2.2265 | 1.1321 | 7.1687 | 9.2763 | 16.445 | 0.054409 | -0.2516 | -0.19719 | 0.35108 | -1.7804
1A | Hanger | 1960-1979 | fans_to_variable | 1 | 338.6019 | 0 | 423.2523 | 0 | 5.309 | 0 | 80.9567 | 509.518 | 3.1546 | -2.0942 | 1.0604 | 6.9427 | 9.1481 | 16.0908 | 0.051104 | -0.23665 | -0.18554 | 0.35108 | -1.8922
1A | Hanger | 1980-2004 | fans_to_variable | 1 | 215.3496 | 0 | 269.187 | 0 | 5.309 | 0 | 74.9028 | 349.3988 | 1.9862 | -1.3967 | 0.58949 | 4.4468 | 8.464 | 12.9109 | 0.032177 | -0.15783 | -0.12565 | 0.35108 | -2.7941
2A | Training | pre-1960 | fans_to_variable | 1 | 401.9429 | 0 | 502.4286 | 0 | 0 | 7.2427 | 84.4988 | 594.1701 | 9.679 | -6.3741 | 3.3049 | 8.1393 | 10.3668 | 18.5061 | 0.1568 | -0.72027 | -0.56347 | 2.0443 | -3.6281
2A | Training | 1980-2004 | fans_to_variable | 1 | 237.2671 | 0 | 296.5839 | 0 | 0 | 7.2427 | 70.3159 | 374.1425 | 2.9032 | -2.4085 | 0.49476 | 4.8047 | 8.7641 | 13.5688 | 0.047032 | -0.27216 | -0.22513 | 2.0443 | -9.0808
2A | Training | 2005-2014 | fans_to_variable | 1 | 163.1076 | 0 | 203.8844 | 0 | 0 | 7.2427 | 68.3354 | 279.4625 | 5.0062 | -3.5234 | 1.4828 | 3.3029 | 8.5403 | 11.8433 | 0.0811 | -0.39814 | -0.31704 | 2.0443 | -6.4481
3B | Storage | pre-1960 | fans_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 324.792 | 44.7913 | 369.5833 | 0 | 0 | 0 | 5.2616 | 5.0614 | 10.323 | 0 | n/a
3B | Storage | 1960-1979 | fans_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 294.8947 | 43.5767 | 338.4714 | 0 | 0 | 0 | 4.7773 | 4.9242 | 9.7015 | 0 | n/a
3B | Storage | 1980-2004 | fans_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 178.7822 | 38.8999 | 217.6821 | 0 | 0 | 0 | 2.8963 | 4.3957 | 7.292 | 0 | n/a
3B | Storage | 2005-2014 | fans_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 106.7703 | 35.6851 | 142.4554 | 0 | 0 | 0 | 1.7297 | 4.0324 | 5.7621 | 0 | n/a
4C | Barracks | pre-1960 | fans_to_variable | 1 | 91.0264 | 0 | 113.783 | 0 | 29.0853 | 0 | 35.3305 | 178.1988 | 1.8929 | -1.6341 | 0.25879 | 2.3145 | 3.9923 | 6.3068 | 0.030665 | -0.18465 | -0.15399 | 0.78215 | -5.0793
5E | Rec Centre | 1980-2004 | fans_to_variable | 1 | 289.914 | 0 | 343.8287 | 12.1969 | 20.994 | 0 | 90.4254 | 467.4451 | 3.3053 | -4.0054 | -0.70013 | 5.9101 | 11.5963 | 17.5065 | 0.053546 | -0.45261 | -0.39907 | 0.9445 | -2.3668
6A | Office | pre-1960 | fans_to_variable | 1 | 345.3293 | 0 | 431.6616 | 0 | 42.0362 | 0 | 112.7567 | 586.4545 | 1.8347 | -1.4431 | 0.39165 | 7.6739 | 12.7415 | 20.4154 | 0.029723 | -0.16307 | -0.13335 | 1.5209 | -11.4058
6A | Office | 1960-1979 | fans_to_variable | 1 | 320.9621 | 0 | 401.2026 | 0 | 42.0353 | 0 | 109.951 | 553.1889 | 1.6649 | -1.3293 | 0.33558 | 7.1805 | 12.4245 | 19.6049 | 0.026971 | -0.15021 | -0.12324 | 1.5209 | -12.3409
6A | Office | 1980-2004 | fans_to_variable | 1 | 230.0527 | 0 | 287.5658 | 0 | 42.0345 | 0 | 99.4286 | 429.029 | 1.2489 | -1.0132 | 0.23564 | 5.3395 | 11.2354 | 16.575 | 0.020232 | -0.1145 | -0.094265 | 1.5209 | -16.1345
6B | Small Office | 1960-1979 | fans_to_variable | 1 | 102.5236 | 0 | 126.4749 | 1.3436 | 0 | 5.73 | 58.811 | 192.3595 | 3.3889 | -3.8957 | -0.50673 | 2.0489 | 7.445 | 9.4939 | 0.054901 | -0.44021 | -0.38531 | 7.1233 | -18.4872
6B | Small Office | 1980-2004 | fans_to_variable | 1 | 57.2041 | 0 | 69.9087 | 1.2772 | 0 | 5.581 | 51.3131 | 128.0799 | 1.9444 | -2.4855 | -0.54113 | 1.1325 | 6.5734 | 7.7059 | 0.031499 | -0.28086 | -0.24936 | 7.1233 | -28.5658
6B | Small Office | 2005-2014 | fans_to_variable | 1 | 30.9135 | 0 | 36.6385 | 1.6027 | 0 | 5.4548 | 47.672 | 91.3681 | 1.4377 | -2.2058 | -0.76813 | 0.59354 | 6.1844 | 6.778 | 0.02329 | -0.24925 | -0.22596 | 7.1233 | -31.5241
7A | Food Services | pre-1960 | fans_to_variable | 1 | 484.3632 | 0 | 605.4541 | 0 | 0 | 51.5821 | 150.1737 | 807.2098 | 5.8627 | -4.7551 | 1.1076 | 9.8084 | 22.7984 | 32.6068 | 0.094975 | -0.53733 | -0.44235 | 1.6199 | -3.6621
8B | Vehicle Garage | pre-1960 | fans_to_variable | 1 | 151.9957 | 0 | 189.9946 | 0 | 0 | 1.2143 | 44.8981 | 236.107 | 4.4249 | -2.6171 | 1.8078 | 3.0779 | 5.2107 | 8.2886 | 0.071683 | -0.29573 | -0.22405 | 1.3744 | -6.1346
8B | Vehicle Garage | 1980-2004 | fans_to_variable | 1 | 105.4088 | 0 | 131.7611 | 0 | 0 | 1.2143 | 37.3754 | 170.3508 | 2.9212 | -1.8011 | 1.1201 | 2.1345 | 4.3606 | 6.4952 | 0.047324 | -0.20353 | -0.1562 | 1.3744 | -8.7992
9A | Maintenance Shop | pre-1960 | fans_to_variable | 1 | 542.3148 | 0 | 677.8935 | 0 | 0 | 2.619 | 114.9643 | 795.4768 | 11.761 | -7.2022 | 4.5588 | 10.9819 | 13.2869 | 24.2688 | 0.19053 | -0.81385 | -0.62332 | 0.63051 | -1.0115
9A | Maintenance Shop | 1980-2004 | fans_to_variable | 1 | 316.123 | 0 | 395.1537 | 0 | 0 | 2.619 | 82.8399 | 480.6126 | 6.2323 | -3.9343 | 2.298 | 6.4015 | 9.6569 | 16.0583 | 0.10096 | -0.44457 | -0.34361 | 0.63051 | -1.835
9B | Maintenance Shop-Small | pre-1960 | fans_to_variable | 1 | 597.4556 | 0 | 746.8195 | 0 | 4.6581 | 0 | 123.6008 | 875.0784 | 3.0613 | -2.2403 | 0.82096 | 12.1739 | 13.9669 | 26.1408 | 0.049593 | -0.25316 | -0.20357 | 2.9202 | -14.3451
9B | Maintenance Shop-Small | 1960-1979 | fans_to_variable | 1 | 553.8901 | 0 | 692.3626 | 0 | 4.6581 | 0 | 119.5502 | 816.5709 | 2.8087 | -2.093 | 0.71571 | 11.2917 | 13.5092 | 24.8009 | 0.045501 | -0.23651 | -0.19101 | 2.9202 | -15.2883
9B | Maintenance Shop-Small | 1980-2004 | fans_to_variable | 1 | 295.7158 | 0 | 369.6448 | 0 | 4.6581 | 0 | 95.0387 | 469.3416 | 1.4946 | -1.1878 | 0.30673 | 6.0637 | 10.7394 | 16.8031 | 0.024212 | -0.13423 | -0.11001 | 2.9202 | -26.5438
13B | Firehall | pre-1960 | fans_to_variable | 1 | 421.7781 | 0 | 527.2226 | 0 | 0 | 22.2562 | 175.3712 | 724.8499 | 3.2661 | -2.9705 | 0.29553 | 8.541 | 22.3319 | 30.8729 | 0.05291 | -0.33567 | -0.28276 | 1.3322 | -4.7115
1A | Hanger | pre-1960 | hrv_enabled | 1 | 311.2455 | 0 | 389.0569 | 0 | 5.309 | 0 | 81.2505 | 475.6164 | 51.5037 | -1.3861 | 50.1176 | 6.3887 | 9.1813 | 15.57 | 0.83436 | -0.15663 | 0.67773 | 29.124 | 42.973
1A | Hanger | 1960-1979 | hrv_enabled | 1 | 300.1156 | 0 | 375.1445 | 0 | 5.309 | 0 | 80.2455 | 460.6989 | 51.2625 | -1.383 | 49.8795 | 6.1633 | 9.0677 | 15.2311 | 0.83045 | -0.15628 | 0.67417 | 29.124 | 43.1997
1A | Hanger | 1980-2004 | hrv_enabled | 1 | 176.7709 | 0 | 220.9636 | 0 | 5.309 | 0 | 74.9644 | 301.2369 | 50.2096 | -1.4582 | 48.7514 | 3.6656 | 8.471 | 12.1366 | 0.8134 | -0.16478 | 0.64861 | 29.124 | 44.902
2A | Training | pre-1960 | hrv_enabled | 1 | 348.9888 | 0 | 436.2359 | 0 | 0 | 7.2427 | 79.6683 | 523.1469 | 75.8716 | -1.5436 | 74.328 | 7.067 | 9.8209 | 16.888 | 1.2291 | -0.17443 | 1.0547 | 68.7247 | 65.1607
2A | Training | 1980-2004 | hrv_enabled | 1 | 181.8198 | 0 | 227.2748 | 0 | 0 | 7.2427 | 69.7491 | 304.2666 | 72.2124 | -1.8416 | 70.3707 | 3.6819 | 8.7001 | 12.3819 | 1.1698 | -0.20811 | 0.96173 | 68.7247 | 71.4591
2A | Training | 2005-2014 | hrv_enabled | 1 | 108.7474 | 0 | 135.9342 | 0 | 0 | 7.2427 | 66.9952 | 210.1722 | 72.9564 | -2.1832 | 70.7731 | 2.2021 | 8.3889 | 10.591 | 1.1819 | -0.24671 | 0.93519 | 68.7247 | 73.4877
3B | Storage | pre-1960 | hrv_enabled | 0 | 259.8336 | 0 | 324.792 | 0 | 0 | 0 | 44.7913 | 369.5833 | 0 | 0 | 0 | 5.2616 | 5.0614 | 10.323 | 0 | 0 | 0 | 0 | n/a
3B | Storage | 1960-1979 | hrv_enabled | 0 | 235.9158 | 0 | 294.8947 | 0 | 0 | 0 | 43.5767 | 338.4714 | 0 | 0 | 0 | 4.7773 | 4.9242 | 9.7015 | 0 | 0 | 0 | 0 | n/a
3B | Storage | 1980-2004 | hrv_enabled | 0 | 143.0258 | 0 | 178.7822 | 0 | 0 | 0 | 38.8999 | 217.6821 | 0 | 0 | 0 | 2.8963 | 4.3957 | 7.292 | 0 | 0 | 0 | 0 | n/a
3B | Storage | 2005-2014 | hrv_enabled | 0 | 85.4162 | 0 | 106.7703 | 0 | 0 | 0 | 35.6851 | 142.4554 | 0 | 0 | 0 | 1.7297 | 4.0324 | 5.7621 | 0 | 0 | 0 | 0 | n/a
4C | Barracks | pre-1960 | hrv_enabled | 1 | 85.3452 | 0 | 106.6815 | 0 | 29.0853 | 0 | 36.258 | 172.0248 | 8.9944 | -2.5616 | 6.4328 | 2.1994 | 4.0972 | 6.2966 | 0.14571 | -0.28946 | -0.14375 | 68.0537 | -473.4147
5E | Rec Centre | 1980-2004 | hrv_enabled | 1 | 289.914 | 0 | 223.1576 | 11.3996 | 20.9938 | 0 | 91.3632 | 346.9142 | 123.9767 | -4.1459 | 119.8307 | 3.9553 | 11.6122 | 15.5675 | 2.0084 | -0.46849 | 1.5399 | 63.1328 | 40.9972
6A | Office | pre-1960 | hrv_enabled | 1 | 294.9697 | 0 | 368.7122 | 0 | 42.0362 | 0 | 118.0188 | 528.7671 | 64.7841 | -6.7051 | 58.079 | 6.6541 | 13.3361 | 19.9902 | 1.0495 | -0.75768 | 0.29183 | 91.7023 | 314.2369
6A | Office | 1960-1979 | hrv_enabled | 1 | 270.8534 | 0 | 338.5668 | 0 | 42.0353 | 0 | 115.3431 | 495.9452 | 64.3007 | -6.7214 | 57.5793 | 6.1658 | 13.0338 | 19.1995 | 1.0417 | -0.75951 | 0.28216 | 91.7023 | 325.0046
6A | Office | 1980-2004 | hrv_enabled | 1 | 178.3872 | 0 | 222.984 | 0 | 42.0337 | 0 | 105.2919 | 370.3096 | 65.8315 | -6.8766 | 58.9549 | 4.2933 | 11.898 | 16.1913 | 1.0665 | -0.77705 | 0.28942 | 91.7023 | 316.8493
6B | Small Office | 1960-1979 | hrv_enabled | 1 | 105.2576 | 0 | 129.8638 | 1.3666 | 0 | 5.73 | 54.8924 | 191.8528 | 0 | 0 | 0 | 2.1038 | 7.0048 | 9.1085 | 0 | 0 | 0 | 286.0017 | #DIV/0!
6B | Small Office | 1980-2004 | hrv_enabled | 1 | 58.7825 | 0 | 71.8531 | 1.3001 | 0 | 5.581 | 48.8047 | 127.5388 | 0 | 0 | 0 | 1.164 | 6.2925 | 7.4565 | 0 | 0 | 0 | 286.0017 | #DIV/0!
6B | Small Office | 2005-2014 | hrv_enabled | 1 | 32.0981 | 0 | 38.0761 | 1.6371 | 0 | 5.4548 | 45.4318 | 90.6 | 0 | 0 | 0 | 0.61683 | 5.9352 | 6.552 | 0 | 0 | 0 | 286.0017 | #DIV/0!
7A | Food Services | pre-1960 | hrv_enabled | 1 | 305.995 | 0 | 382.4937 | 0 | 0 | 51.5821 | 153.9801 | 588.0558 | 228.823 | -8.5614 | 220.2616 | 6.1964 | 23.2285 | 29.4249 | 3.7069 | -0.96744 | 2.7395 | 115.2653 | 42.0754
8B | Vehicle Garage | pre-1960 | hrv_enabled | 1 | 138.4313 | 0 | 173.0391 | 0 | 0 | 1.2143 | 45.7519 | 220.0053 | 21.3805 | -3.4709 | 17.9095 | 2.8032 | 5.3072 | 8.1104 | 0.34636 | -0.39222 | -0.045852 | 72.1933 | -1574.4943
8B | Vehicle Garage | 1980-2004 | hrv_enabled | 1 | 90.9014 | 0 | 113.6268 | 0 | 0 | 1.2143 | 39.0363 | 153.8774 | 21.0555 | -3.462 | 17.5935 | 1.8408 | 4.5483 | 6.3891 | 0.3411 | -0.39121 | -0.050109 | 72.1933 | -1440.7128
9A | Maintenance Shop | pre-1960 | hrv_enabled | 1 | 476.9853 | 0 | 596.2317 | 0 | 0 | 2.619 | 118.6288 | 717.4794 | 93.4228 | -10.8667 | 82.5561 | 9.659 | 13.701 | 23.36 | 1.5134 | -1.2279 | 0.28551 | 71.7222 | 251.204
9A | Maintenance Shop | 1980-2004 | hrv_enabled | 1 | 243.0054 | 0 | 303.7568 | 0 | 0 | 2.619 | 89.7281 | 396.1039 | 97.6292 | -10.8225 | 86.8068 | 4.9209 | 10.4352 | 15.3561 | 1.5816 | -1.2229 | 0.35865 | 71.7222 | 199.9774
9B | Maintenance Shop-Small | pre-1960 | hrv_enabled | 1 | 589.1919 | 0 | 736.4898 | 0 | 4.6581 | 0 | 123.7452 | 864.8931 | 13.3909 | -2.3847 | 11.0063 | 12.0066 | 13.9832 | 25.9898 | 0.21693 | -0.26947 | -0.052537 | 52.7023 | -1003.1548
9B | Maintenance Shop-Small | 1960-1979 | hrv_enabled | 1 | 545.3858 | 0 | 681.7322 | 0 | 4.6581 | 0 | 119.8719 | 806.2623 | 13.4391 | -2.4148 | 11.0243 | 11.1195 | 13.5455 | 24.6651 | 0.21771 | -0.27287 | -0.055155 | 52.7023 | -955.5272
9B | Maintenance Shop-Small | 1980-2004 | hrv_enabled | 1 | 286.1049 | 0 | 357.6311 | 0 | 4.6581 | 0 | 96.2656 | 458.5548 | 13.5082 | -2.4148 | 11.0935 | 5.8691 | 10.878 | 16.7471 | 0.21883 | -0.27287 | -0.054035 | 52.7023 | -975.3412
13B | Firehall | pre-1960 | hrv_enabled | 1 | 368.5388 | 0 | 460.6735 | 0 | 0 | 22.2562 | 177.7172 | 660.6468 | 69.8152 | -5.3165 | 64.4987 | 7.4629 | 22.597 | 30.0599 | 1.131 | -0.60076 | 0.53024 | 99.2201 | 187.1224
1A | Hanger | pre-1960 | lights_reduce_70p | 1 | 365.6102 | 0 | 457.0128 | 0 | 5.309 | 0 | 63.0811 | 525.4029 | -16.4523 | 16.7833 | 0.33104 | 7.4896 | 7.1282 | 14.6178 | -0.26653 | 1.8965 | 1.63 | 20.8178 | 12.7718
1A | Hanger | 1960-1979 | lights_reduce_70p | 1 | 354.0424 | 0 | 442.5529 | 0 | 5.309 | 0 | 62.0907 | 509.9526 | -16.146 | 16.7718 | 0.62578 | 7.2554 | 7.0162 | 14.2716 | -0.26157 | 1.8952 | 1.6336 | 20.8178 | 12.7432
1A | Hanger | 1980-2004 | lights_reduce_70p | 1 | 228.8824 | 0 | 286.1031 | 0 | 5.309 | 0 | 56.7237 | 348.1357 | -14.9299 | 16.7824 | 1.8526 | 4.7209 | 6.4098 | 11.1307 | -0.24186 | 1.8964 | 1.6545 | 20.8178 | 12.5822
2A | Training | pre-1960 | lights_reduce_70p | 1 | 421.5345 | 0 | 526.9181 | 0 | 0 | 7.2427 | 65.5492 | 599.71 | -14.8105 | 12.5754 | -2.2351 | 8.5361 | 8.2255 | 16.7616 | -0.23993 | 1.421 | 1.1811 | 43.3261 | 36.683
2A | Training | 1980-2004 | lights_reduce_70p | 1 | 248.6915 | 0 | 310.8644 | 0 | 0 | 7.2427 | 54.2238 | 372.3309 | -11.3772 | 13.6836 | 2.3064 | 5.036 | 6.9457 | 11.9817 | -0.18431 | 1.5462 | 1.3619 | 43.3261 | 31.8122
2A | Training | 2005-2014 | lights_reduce_70p | 1 | 175.3692 | 0 | 219.2115 | 0 | 0 | 7.2427 | 49.7748 | 276.2289 | -10.3209 | 15.0372 | 4.7164 | 3.5512 | 6.443 | 9.9942 | -0.1672 | 1.6992 | 1.532 | 43.3261 | 28.2806
3B | Storage | pre-1960 | lights_reduce_70p | 1 | 266.8377 | 0 | 333.5471 | 0 | 0 | 0 | 36.4765 | 370.0236 | -8.7551 | 8.3147 | -0.44034 | 5.4035 | 4.1218 | 9.5253 | -0.14183 | 0.93956 | 0.79773 | 20.8673 | 26.1583
3B | Storage | 1960-1979 | lights_reduce_70p | 1 | 242.7172 | 0 | 303.3965 | 0 | 0 | 0 | 35.2447 | 338.6412 | -8.5018 | 8.332 | -0.16981 | 4.915 | 3.9827 | 8.8977 | -0.13773 | 0.94151 | 0.80379 | 20.8673 | 25.9613
3B | Storage | 1980-2004 | lights_reduce_70p | 1 | 149.6292 | 0 | 187.0365 | 0 | 0 | 0 | 30.5823 | 217.6188 | -8.2543 | 8.3176 | 0.063317 | 3.03 | 3.4558 | 6.4858 | -0.13372 | 0.93989 | 0.80617 | 20.8673 | 25.8845
3B | Storage | 2005-2014 | lights_reduce_70p | 1 | 91.6467 | 0 | 114.5583 | 0 | 0 | 0 | 27.356 | 141.9143 | -7.788 | 8.3291 | 0.54108 | 1.8558 | 3.0912 | 4.9471 | -0.12617 | 0.94119 | 0.81502 | 20.8673 | 25.6033
4C | Barracks | pre-1960 | lights_reduce_70p | 1 | 97.0238 | 0 | 121.2797 | 0 | 29.0853 | 0 | 28.829 | 179.194 | -5.6039 | 4.8674 | -0.73643 | 2.4359 | 3.2577 | 5.6936 | -0.090782 | 0.55002 | 0.45924 | 23.1299 | 50.3659
5E | Rec Centre | 1980-2004 | lights_reduce_70p | 1 | 289.914 | 0 | 357.9201 | 13.1386 | 20.9951 | 0 | 70.2406 | 462.2944 | -10.7872 | 15.2377 | 4.4505 | 6.1384 | 9.4219 | 15.5603 | -0.17475 | 1.7219 | 1.5471 | 18.4207 | 11.9065
6A | Office | pre-1960 | lights_reduce_70p | 1 | 357.9309 | 0 | 447.4136 | 0 | 42.0362 | 0 | 99.9779 | 589.4276 | -13.9173 | 11.3358 | -2.5815 | 7.9291 | 11.2975 | 19.2266 | -0.22546 | 1.2809 | 1.0555 | 24.3276 | 23.0487
6A | Office | 1960-1979 | lights_reduce_70p | 1 | 332.7186 | 0 | 415.8982 | 0 | 42.0353 | 0 | 97.238 | 555.1716 | -13.0308 | 11.3837 | -1.647 | 7.4185 | 10.9879 | 18.4064 | -0.2111 | 1.2864 | 1.0753 | 24.3276 | 22.6248
6A | Office | 1980-2004 | lights_reduce_70p | 1 | 224.1296 | 0 | 280.1619 | 0 | 42.0345 | 0 | 83.0006 | 405.197 | 8.6528 | 15.4148 | 24.0676 | 5.2196 | 9.3791 | 14.5986 | 0.14018 | 1.7419 | 1.882 | 24.3276 | 12.9262
6B | Small Office | 1960-1979 | lights_reduce_70p | 1 | 110.0159 | 0 | 136.19 | 1.0639 | 0 | 5.7346 | 46.1266 | 189.1151 | -6.3262 | 9.0639 | 2.7377 | 2.2063 | 5.9805 | 8.1868 | -0.10248 | 1.0242 | 0.92174 | 34.5708 | 37.5061
6B | Small Office | 1980-2004 | lights_reduce_70p | 1 | 62.968 | 0 | 77.3744 | 1.0685 | 0 | 5.5878 | 39.9839 | 124.0146 | -5.5213 | 9.0456 | 3.5242 | 1.2535 | 5.2703 | 6.5238 | -0.089446 | 1.0221 | 0.9327 | 34.5708 | 37.0652
6B | Small Office | 2005-2014 | lights_reduce_70p | 1 | 35.6026 | 0 | 42.9899 | 1.2107 | 0 | 5.4617 | 36.0882 | 85.7504 | -4.9137 | 9.7632 | 4.8495 | 0.69644 | 4.8319 | 5.5284 | -0.079602 | 1.1032 | 1.0236 | 34.5708 | 33.7723
7A | Food Services | pre-1960 | lights_reduce_70p | 1 | 513.0188 | 0 | 641.2735 | 0 | 0 | 51.5821 | 120.0127 | 812.8683 | -29.9568 | 25.4059 | -4.5509 | 10.3886 | 19.3902 | 29.7788 | -0.4853 | 2.8709 | 2.3856 | 43.484 | 18.228
8B | Vehicle Garage | pre-1960 | lights_reduce_70p | 1 | 161.679 | 0 | 202.0987 | 0 | 0 | 1.2143 | 37.2292 | 240.5423 | -7.6792 | 5.0517 | -2.6275 | 3.274 | 4.3441 | 7.6181 | -0.1244 | 0.57085 | 0.44644 | 11.5244 | 25.814
8B | Vehicle Garage | 1980-2004 | lights_reduce_70p | 1 | 113.6524 | 0 | 142.0655 | 0 | 0 | 1.2143 | 30.5411 | 173.8209 | -7.3832 | 5.0332 | -2.3501 | 2.3015 | 3.5884 | 5.8898 | -0.11961 | 0.56875 | 0.44914 | 11.5244 | 25.6588
9A | Maintenance Shop | pre-1960 | lights_reduce_70p | 1 | 563.1634 | 0 | 703.9542 | 0 | 0 | 2.619 | 96.7582 | 803.3314 | -14.2997 | 11.0039 | -3.2958 | 11.4041 | 11.2296 | 22.6337 | -0.23166 | 1.2434 | 1.0118 | 23.6537 | 23.3781
9A | Maintenance Shop | 1980-2004 | lights_reduce_70p | 1 | 331.8006 | 0 | 414.7507 | 0 | 0 | 2.619 | 68.068 | 485.4377 | -13.3647 | 10.8376 | -2.5271 | 6.719 | 7.9876 | 14.7066 | -0.21651 | 1.2247 | 1.0081 | 23.6537 | 23.4627
9B | Maintenance Shop-Small | pre-1960 | lights_reduce_70p | 1 | 618.1161 | 0 | 772.6451 | 0 | 4.6581 | 0 | 105.0195 | 882.3227 | -22.7643 | 16.341 | -6.4233 | 12.5923 | 11.8672 | 24.4595 | -0.36878 | 1.8465 | 1.4777 | 26.0721 | 17.6431
9B | Maintenance Shop-Small | 1960-1979 | lights_reduce_70p | 1 | 574.0237 | 0 | 717.5296 | 0 | 4.6581 | 0 | 101.1132 | 823.3009 | -22.3583 | 16.344 | -6.0143 | 11.6994 | 11.4258 | 23.1252 | -0.36221 | 1.8469 | 1.4847 | 26.0721 | 17.5609
9B | Maintenance Shop-Small | 1980-2004 | lights_reduce_70p | 1 | 313.9248 | 0 | 392.406 | 0 | 4.6581 | 0 | 77.6121 | 474.6763 | -21.2667 | 16.2387 | -5.028 | 6.4324 | 8.7702 | 15.2026 | -0.34452 | 1.835 | 1.4905 | 26.0721 | 17.4927
13B | Firehall | pre-1960 | lights_reduce_70p | 1 | 449.8833 | 0 | 562.3541 | 0 | 0 | 22.2562 | 144.8554 | 729.4657 | -31.8655 | 27.5452 | -4.3202 | 9.1101 | 18.8836 | 27.9937 | -0.51622 | 3.1126 | 2.5964 | 17.2864 | 6.6579
1A | Hanger | pre-1960 | plug_loads_90_percent | 1 | 352.9621 | 0 | 441.2027 | 0 | 5.309 | 0 | 79.2537 | 525.7653 | -0.64216 | 0.61074 | -0.031422 | 7.2335 | 8.9557 | 16.1892 | -0.010403 | 0.069013 | 0.05861 | 3.4016 | 58.0383
1A | Hanger | 1960-1979 | plug_loads_90_percent | 1 | 341.6286 | 0 | 427.0358 | 0 | 5.309 | 0 | 78.2544 | 510.5992 | -0.62888 | 0.60808 | -0.0208 | 7.004 | 8.8427 | 15.8467 | -0.010188 | 0.068713 | 0.058525 | 3.4016 | 58.1226
1A | Hanger | 1980-2004 | plug_loads_90_percent | 1 | 217.3794 | 0 | 271.7242 | 0 | 5.309 | 0 | 72.8985 | 349.9317 | -0.55099 | 0.60764 | 0.056648 | 4.4879 | 8.2375 | 12.7255 | -0.008926 | 0.068663 | 0.059737 | 3.4016 | 56.9435
2A | Training | pre-1960 | plug_loads_90_percent | 1 | 410.6032 | 0 | 513.254 | 0 | 0 | 7.2427 | 77.0894 | 597.5861 | -1.1464 | 1.0353 | -0.11111 | 8.3147 | 9.5295 | 17.8442 | -0.018572 | 0.11699 | 0.098419 | 3.1443 | 31.9478
2A | Training | 1980-2004 | plug_loads_90_percent | 1 | 240.1387 | 0 | 300.1733 | 0 | 0 | 7.2427 | 66.7175 | 374.1335 | -0.68621 | 1.19 | 0.50377 | 4.8628 | 8.3575 | 13.2203 | -0.011117 | 0.13447 | 0.12335 | 3.1443 | 25.4904
2A | Training | 2005-2014 | plug_loads_90_percent | 1 | 167.7371 | 0 | 209.6714 | 0 | 0 | 7.2427 | 63.5567 | 280.4708 | -0.7808 | 1.2553 | 0.47449 | 3.3967 | 8.0003 | 11.397 | -0.012649 | 0.14185 | 0.1292 | 3.1443 | 24.3365
3B | Storage | pre-1960 | plug_loads_90_percent | 1 | 260.0431 | 0 | 325.0539 | 0 | 0 | 0 | 44.5351 | 369.589 | -0.2619 | 0.25615 | -0.0057561 | 5.2659 | 5.0325 | 10.2983 | -0.0042428 | 0.028945 | 0.024702 | 0.24231 | 9.8096
3B | Storage | 1960-1979 | plug_loads_90_percent | 1 | 236.1184 | 0 | 295.148 | 0 | 0 | 0 | 43.3206 | 338.4686 | -0.25327 | 0.25615 | 0.0028781 | 4.7814 | 4.8952 | 9.6766 | -0.004103 | 0.028945 | 0.024842 | 0.24231 | 9.7543
3B | Storage | 1980-2004 | plug_loads_90_percent | 1 | 143.2238 | 0 | 179.0298 | 0 | 0 | 0 | 38.6408 | 217.6706 | -0.24751 | 0.25903 | 0.011512 | 2.9003 | 4.3664 | 7.2667 | -0.0040097 | 0.02927 | 0.02526 | 0.24231 | 9.5927
3B | Storage | 2005-2014 | plug_loads_90_percent | 1 | 85.6004 | 0 | 107.0005 | 0 | 0 | 0 | 35.4289 | 142.4295 | -0.23024 | 0.25615 | 0.025903 | 1.7334 | 4.0035 | 5.7369 | -0.00373 | 0.028945 | 0.025215 | 0.24231 | 9.61
4C | Barracks | pre-1960 | plug_loads_90_percent | 1 | 92.9556 | 0 | 116.1945 | 0 | 29.0853 | 0 | 33.2764 | 178.5561 | -0.51859 | 0.42002 | -0.098562 | 2.3535 | 3.7602 | 6.1138 | -0.0084011 | 0.047463 | 0.039062 | 5.335 | 136.5787
5E | Rec Centre | 1980-2004 | plug_loads_90_percent | 1 | 290.318 | 0 | 347.6097 | 12.2313 | 20.9942 | 0 | 85.7243 | 466.5595 | -0.47593 | 0.66137 | 0.18544 | 5.9714 | 11.069 | 17.0404 | -0.0077101 | 0.074735 | 0.067025 | 0.71989 | 10.7407
6A | Office | pre-1960 | plug_loads_90_percent | 1 | 348.2154 | 0 | 435.2693 | 0 | 42.0362 | 0 | 110.2704 | 587.5758 | -1.773 | 1.0433 | -0.72966 | 7.7323 | 12.4606 | 20.1929 | -0.028722 | 0.11789 | 0.089172 | 4.2326 | 47.4658
6A | Office | 1960-1979 | plug_loads_90_percent | 1 | 323.6162 | 0 | 404.5202 | 0 | 42.0353 | 0 | 107.5556 | 554.1112 | -1.6527 | 1.0661 | -0.58666 | 7.2342 | 12.1538 | 19.388 | -0.026774 | 0.12046 | 0.093691 | 4.2326 | 45.1763
6A | Office | 1980-2004 | plug_loads_90_percent | 1 | 231.3157 | 0 | 289.1446 | 0 | 42.0345 | 0 | 97.1023 | 428.2814 | -0.32989 | 1.3131 | 0.98318 | 5.3651 | 10.9726 | 16.3377 | -0.0053443 | 0.14838 | 0.14303 | 4.2326 | 29.5918
6B | Small Office | 1960-1979 | plug_loads_90_percent | 1 | 105.6263 | 0 | 130.3476 | 1.3482 | 0 | 5.73 | 54.1976 | 191.6235 | -0.48381 | 0.7131 | 0.22929 | 2.1116 | 6.9242 | 9.0358 | -0.0078376 | 0.08058 | 0.072742 | 7.774 | 106.8701
6B | Small Office | 1980-2004 | plug_loads_90_percent | 1 | 59.0811 | 0 | 72.2406 | 1.2886 | 0 | 5.581 | 48.1077 | 127.2178 | -0.3875 | 0.70851 | 0.32101 | 1.1703 | 6.2124 | 7.3827 | -0.0062775 | 0.080062 | 0.073784 | 7.774 | 105.361
6B | Small Office | 2005-2014 | plug_loads_90_percent | 1 | 32.3237 | 0 | 38.3811 | 1.6188 | 0 | 5.4548 | 44.6935 | 90.1482 | -0.30496 | 0.75666 | 0.4517 | 0.62177 | 5.8497 | 6.4715 | -0.0049403 | 0.085503 | 0.080562 | 7.774 | 96.4962
7A | Food Services | pre-1960 | plug_loads_90_percent | 1 | 490.427 | 0 | 613.0337 | 0 | 0 | 51.5821 | 144.1285 | 808.7443 | -1.717 | 1.2901 | -0.42694 | 9.9311 | 22.1153 | 32.0464 | -0.027816 | 0.14578 | 0.11796 | 0.99445 | 8.4301
8B | Vehicle Garage | pre-1960 | plug_loads_90_percent | 1 | 155.9641 | 0 | 194.9551 | 0 | 0 | 1.2143 | 41.9308 | 238.1003 | -0.53559 | 0.35013 | -0.18545 | 3.1583 | 4.8754 | 8.0337 | -0.0086765 | 0.039565 | 0.030889 | 1.25 | 40.4679
8B | Vehicle Garage | 1980-2004 | plug_loads_90_percent | 1 | 108.1761 | 0 | 135.2201 | 0 | 0 | 1.2143 | 35.216 | 171.6504 | -0.53781 | 0.35829 | -0.17952 | 2.1906 | 4.1166 | 6.3072 | -0.0087126 | 0.040487 | 0.031775 | 1.25 | 39.3395
9A | Maintenance Shop | pre-1960 | plug_loads_90_percent | 1 | 552.4316 | 0 | 690.5395 | 0 | 0 | 2.619 | 107.2562 | 800.4147 | -0.88501 | 0.50589 | -0.37912 | 11.1867 | 12.4159 | 23.6026 | -0.014337 | 0.057165 | 0.042828 | 1.6197 | 37.8197
9A | Maintenance Shop | 1980-2004 | plug_loads_90_percent | 1 | 321.7396 | 0 | 402.1745 | 0 | 0 | 2.619 | 78.416 | 483.2095 | -0.78849 | 0.48961 | -0.29888 | 6.5152 | 9.157 | 15.6722 | -0.012773 | 0.055325 | 0.042552 | 1.6197 | 38.0651
9B | Maintenance Shop-Small | pre-1960 | plug_loads_90_percent | 1 | 600.5614 | 0 | 750.7017 | 0 | 4.6581 | 0 | 120.717 | 876.0768 | -0.82096 | 0.64354 | -0.17742 | 12.2368 | 13.641 | 25.8778 | -0.0133 | 0.072719 | 0.05942 | 2.7549 | 46.3625
9B | Maintenance Shop-Small | 1960-1979 | plug_loads_90_percent | 1 | 556.7842 | 0 | 695.9802 | 0 | 4.6581 | 0 | 116.8197 | 817.458 | -0.80893 | 0.63752 | -0.17141 | 11.3503 | 13.2006 | 24.551 | -0.013105 | 0.07204 | 0.058935 | 2.7549 | 46.7438
9B | Maintenance Shop-Small | 1980-2004 | plug_loads_90_percent | 1 | 297.5177 | 0 | 371.8971 | 0 | 4.6581 | 0 | 93.2254 | 469.7806 | -0.75781 | 0.62549 | -0.13232 | 6.1002 | 10.5345 | 16.6347 | -0.012276 | 0.070681 | 0.058404 | 2.7549 | 47.1688
13B | Firehall | pre-1960 | plug_loads_90_percent | 1 | 426.5236 | 0 | 533.1545 | 0 | 0 | 22.2562 | 169.7653 | 725.1759 | -2.6659 | 2.6354 | -0.030467 | 8.6371 | 21.6984 | 30.3355 | -0.043187 | 0.2978 | 0.25461 | 3.0154 | 11.8429
1A | Hanger | pre-1960 | pump_fan_eff_ | 1 | 352.4484 | 0 | 440.5605 | 0 | 5.309 | 0 | 79.9029 | 525.7724 | 0 | -0.038503 | -0.038503 | 7.2231 | 9.029 | 16.2521 | 0 | -0.0043508 | -0.0043508 | 1.0673 | -245.2997
1A | Hanger | 1960-1979 | pump_fan_eff_ | 1 | 341.1255 | 0 | 426.4069 | 0 | 5.309 | 0 | 78.8992 | 510.6151 | 0 | -0.036733 | -0.036733 | 6.9938 | 8.9156 | 15.9094 | 0 | -0.0041508 | -0.0041508 | 1.0673 | -257.1214
1A | Hanger | 1980-2004 | pump_fan_eff_ | 1 | 216.9386 | 0 | 271.1732 | 0 | 5.309 | 0 | 73.5291 | 350.0113 | 0 | -0.023013 | -0.023013 | 4.479 | 8.3088 | 12.7878 | 0 | -0.0026005 | -0.0026005 | 1.0673 | -410.4053
2A | Training | pre-1960 | pump_fan_eff_ | 1 | 409.6861 | 0 | 512.1076 | 0 | 0 | 7.2427 | 78.1277 | 597.478 | 0 | -0.0030031 | -0.0030031 | 8.2961 | 9.6469 | 17.943 | 0 | -0.00033935 | -0.00033935 | 5.4142 | -15954.6139
2A | Training | 1980-2004 | pump_fan_eff_ | 1 | 239.5897 | 0 | 299.4871 | 0 | 0 | 7.2427 | 67.9104 | 374.6403 | 0 | -0.0030031 | -0.0030031 | 4.8517 | 8.4923 | 13.344 | 0 | -0.00033935 | -0.00033935 | 5.4142 | -15954.6139
2A | Training | 2005-2014 | pump_fan_eff_ | 1 | 167.1125 | 0 | 208.8906 | 0 | 0 | 7.2427 | 64.8135 | 280.9468 | 0 | -0.0015015 | -0.0015015 | 3.384 | 8.1424 | 11.5264 | 0 | -0.00016967 | -0.00016967 | 5.4142 | -31909.2278
3B | Storage | pre-1960 | pump_fan_eff_ | 0 | 0 | 0 | [5 empty] | 0 | 324.792 | 44.7913 | 369.5833 | 0 | 0 | 0 | 5.2616 | 5.0614 | 10.323 | 0 | n/a
3B | Storage | 1960-1979 | pump_fan_eff_ | 0 | 0 | 0 | [5 empty] | 0 | 294.8947 | 43.5767 | 338.4714 | 0 | 0 | 0 | 4.7773 | 4.9242 | 9.7015 | 0 | n/a
3B | Storage | 1980-2004 | pump_fan_eff_ | 0 | 0 | 0 | [5 empty] | 0 | 178.7822 | 38.8999 | 217.6821 | 0 | 0 | 0 | 2.8963 | 4.3957 | 7.292 | 0 | n/a
3B | Storage | 2005-2014 | pump_fan_eff_ | 0 | 0 | 0 | [5 empty] | 0 | 106.7703 | 35.6851 | 142.4554 | 0 | 0 | 0 | 1.7297 | 4.0324 | 5.7621 | 0 | n/a
4C | Barracks | pre-1960 | pump_fan_eff_ | 1 | 92.5407 | 0 | 115.6759 | 0 | 29.0853 | 0 | 33.7283 | 178.4894 | 0 | -0.031843 | -0.031843 | 2.3451 | 3.8113 | 6.1564 | 0 | -0.0035983 | -0.0035983 | 2.557 | -710.6312
5E | Rec Centre | 1980-2004 | pump_fan_eff_ | 1 | 289.914 | 0 | 347.134 | 12.2081 | 20.994 | 0 | 86.4271 | 466.7632 | 0 | -0.01828 | -0.01828 | 5.9637 | 11.1458 | 17.1094 | 0 | -0.0020656 | -0.0020656 | 2.8064 | -1358.6545
6A | Office | pre-1960 | pump_fan_eff_ | 1 | 346.7971 | 0 | 433.4963 | 0 | 42.0362 | 0 | 111.3689 | 586.9014 | 0 | -0.055253 | -0.055253 | 7.7036 | 12.5847 | 20.2883 | 0 | -0.0062436 | -0.0062436 | 2.4207 | -387.7039
6A | Office | 1960-1979 | pump_fan_eff_ | 1 | 322.294 | 0 | 402.8675 | 0 | 42.0353 | 0 | 108.6729 | 553.5757 | 0 | -0.05119 | -0.05119 | 7.2074 | 12.28 | 19.4875 | 0 | -0.0057845 | -0.0057845 | 2.4207 | -418.4741
6A | Office | 1980-2004 | pump_fan_eff_ | 1 | 231.0518 | 0 | 288.8147 | 0 | 42.0345 | 0 | 98.4543 | 429.3036 | 0 | -0.039002 | -0.039002 | 5.3598 | 11.1253 | 16.4851 | 0 | -0.0044072 | -0.0044072 | 2.4207 | -549.2473
6B | Small Office | 1960-1979 | pump_fan_eff_ | 1 | 105.2576 | 0 | 129.8638 | 1.3666 | 0 | 5.73 | 54.8924 | 191.8528 | 0 | 0 | 0 | 2.1038 | 7.0048 | 9.1085 | 0 | 0 | 0 | 2.988 | #DIV/0!
6B | Small Office | 1980-2004 | pump_fan_eff_ | 1 | 58.7825 | 0 | 71.8531 | 1.3001 | 0 | 5.581 | 48.8047 | 127.5388 | 0 | 0 | 0 | 1.164 | 6.2925 | 7.4565 | 0 | 0 | 0 | 2.988 | #DIV/0!
6B | Small Office | 2005-2014 | pump_fan_eff_ | 1 | 32.0981 | 0 | 38.0761 | 1.6371 | 0 | 5.4548 | 45.4318 | 90.6 | 0 | 0 | 0 | 0.61683 | 5.9352 | 6.552 | 0 | 0 | 0 | 2.988 | #DIV/0!
7A | Food Services | pre-1960 | pump_fan_eff_ | 1 | 489.0534 | 0 | 611.3167 | 0 | 0 | 51.5821 | 145.4877 | 808.3865 | 0 | -0.069094 | -0.069094 | 9.9033 | 22.2689 | 32.1722 | 0 | -0.0078076 | -0.0078076 | 4.1418 | -530.4889
8B | Vehicle Garage | pre-1960 | pump_fan_eff_ | 1 | 155.5356 | 0 | 194.4195 | 0 | 0 | 1.2143 | 42.3351 | 237.969 | 0 | -0.054152 | -0.054152 | 3.1496 | 4.9211 | 8.0707 | 0 | -0.0061192 | -0.0061192 | 1.4752 | -241.0809
8B | Vehicle Garage | 1980-2004 | pump_fan_eff_ | 1 | 107.7458 | 0 | 134.6823 | 0 | 0 | 1.2143 | 35.6121 | 171.5087 | 0 | -0.037832 | -0.037832 | 2.1819 | 4.1614 | 6.3432 | 0 | -0.0042751 | -0.0042751 | 1.4752 | -345.0766
9A | Maintenance Shop | pre-1960 | pump_fan_eff_ | 1 | 551.7236 | 0 | 689.6545 | 0 | 0 | 2.619 | 107.9179 | 800.1914 | 0 | -0.15584 | -0.15584 | 11.1724 | 12.4907 | 23.6631 | 0 | -0.01761 | -0.01761 | 2.7329 | -155.193
9A | Maintenance Shop | 1980-2004 | pump_fan_eff_ | 1 | 321.1088 | 0 | 401.386 | 0 | 0 | 2.619 | 78.994 | 482.999 | 0 | -0.088385 | -0.088385 | 6.5025 | 9.2223 | 15.7247 | 0 | -0.0099875 | -0.0099875 | 2.7329 | -273.6297
9B | Maintenance Shop-Small | pre-1960 | pump_fan_eff_ | 1 | 599.9046 | 0 | 749.8808 | 0 | 4.6581 | 0 | 121.5349 | 876.0738 | 0 | -0.17442 | -0.17442 | 12.2235 | 13.7334 | 25.957 | 0 | -0.019709 | -0.019709 | 4.8719 | -247.1914
9B | Maintenance Shop-Small | 1960-1979 | pump_fan_eff_ | 1 | 556.137 | 0 | 695.1713 | 0 | 4.6581 | 0 | 117.6196 | 817.4489 | 0 | -0.16239 | -0.16239 | 11.3372 | 13.291 | 24.6282 | 0 | -0.01835 | -0.01835 | 4.8719 | -265.5019
9B | Maintenance Shop-Small | 1980-2004 | pump_fan_eff_ | 1 | 296.9115 | 0 | 371.1393 | 0 | 4.6581 | 0 | 93.9441 | 469.7415 | 0 | -0.093222 | -0.093222 | 6.0879 | 10.6157 | 16.7036 | 0 | -0.010534 | -0.010534 | 4.8719 | -462.4871
13B | Firehall | pre-1960 | pump_fan_eff_ | 1 | 424.3909 | 0 | 530.4886 | 0 | 0 | 22.2562 | 172.4677 | 725.2125 | 0 | -0.067027 | -0.067027 | 8.5939 | 22.0038 | 30.5977 | 0 | -0.0075741 | -0.0075741 | 6.7105 | -885.9833
1A | Hanger | pre-1960 | pumps_to_variable | 1 | 352.4484 | 0 | 440.5605 | 0 | 5.3249 | 0 | 79.852 | 525.7375 | -0.015932 | 0.012392 | -0.0035405 | 7.2233 | 9.0233 | 16.2466 | -0.0002581 | 0.0014003 | 0.0011422 | 0.54928 | 480.9075
1A | Hanger | 1960-1979 | pumps_to_variable | 1 | 341.1255 | 0 | 426.4069 | 0 | 5.3249 | 0 | 78.8501 | 510.5819 | -0.015932 | 0.012392 | -0.0035405 | 6.9941 | 8.9101 | 15.9041 | -0.0002581 | 0.0014003 | 0.0011422 | 0.54928 | 480.9075
1A | Hanger | 1980-2004 | pumps_to_variable | 1 | 216.9386 | 0 | 271.1732 | 0 | 5.3249 | 0 | 73.4933 | 349.9914 | -0.015932 | 0.012834 | -0.0030979 | 4.4793 | 8.3047 | 12.784 | -0.0002581 | 0.0014503 | 0.0011922 | 0.54928 | 460.7343
2A | Training | pre-1960 | pumps_to_variable | 0 | 409.6861 | 0 | 512.1076 | 0 | 0 | 7.2427 | 78.1247 | 597.475 | 0 | 0 | 0 | 8.2961 | 9.6465 | 17.9427 | 0 | 0 | 0 | 2.2462 | n/a
2A | Training | 1980-2004 | pumps_to_variable | 0 | 239.5897 | 0 | 299.4871 | 0 | 0 | 7.2427 | 67.9074 | 374.6373 | 0 | 0 | 0 | 4.8517 | 8.492 | 13.3437 | 0 | 0 | 0 | 2.2462 | n/a
2A | Training | 2005-2014 | pumps_to_variable | 0 | 167.1125 | 0 | 208.8906 | 0 | 0 | 7.2427 | 64.812 | 280.9453 | 0 | 0 | 0 | 3.384 | 8.1422 | 11.5262 | 0 | 0 | 0 | 2.2462 | n/a
3B | Storage | pre-1960 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 324.792 | 44.7913 | 369.5833 | 0 | 0 | 0 | 5.2616 | 5.0614 | 10.323 | 0 | n/a
3B | Storage | 1960-1979 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 294.8947 | 43.5767 | 338.4714 | 0 | 0 | 0 | 4.7773 | 4.9242 | 9.7015 | 0 | n/a
3B | Storage | 1980-2004 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 178.7822 | 38.8999 | 217.6821 | 0 | 0 | 0 | 2.8963 | 4.3957 | 7.292 | 0 | n/a
3B | Storage | 2005-2014 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 106.7703 | 35.6851 | 142.4554 | 0 | 0 | 0 | 1.7297 | 4.0324 | 5.7621 | 0 | n/a
4C | Barracks | pre-1960 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 144.7611 | 33.6964 | 178.4576 | 0 | 0 | 0 | 2.3451 | 3.8077 | 6.1528 | 0 | n/a
5E | Rec Centre | 1980-2004 | pumps_to_variable | 1 | 292.546 | 0 | 350.4162 | 12.2079 | 21.0398 | 0 | 83.4962 | 467.1601 | -3.328 | 2.9128 | -0.41515 | 6.0176 | 10.8146 | 16.8321 | -0.053913 | 0.32915 | 0.27524 | 1.1188 | 4.065
6A | Office | pre-1960 | pumps_to_variable | 1 | 354.3141 | 0 | 442.8926 | 0 | 42.0362 | 0 | 103.7115 | 588.6402 | -9.3963 | 7.6022 | -1.7941 | 7.8558 | 11.7194 | 19.5752 | -0.15222 | 0.85904 | 0.70682 | 1.0319 | 1.4599
6A | Office | 1960-1979 | pumps_to_variable | 1 | 329.2604 | 0 | 411.5755 | 0 | 42.0353 | 0 | 101.5054 | 555.1163 | -8.708 | 7.1163 | -1.5918 | 7.3485 | 11.4701 | 18.8186 | -0.14107 | 0.80414 | 0.66307 | 1.0319 | 1.5562
6A | Office | 1980-2004 | pumps_to_variable | 1 | 236.7324 | 0 | 295.9156 | 0 | 42.0345 | 0 | 92.8559 | 430.806 | -7.1008 | 5.5594 | -1.5414 | 5.4748 | 10.4927 | 15.9675 | -0.11503 | 0.62822 | 0.51318 | 1.0319 | 2.0108
6B | Small Office | 1960-1979 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 129.8638 | 61.989 | 191.8528 | 0 | 0 | 0 | 2.1038 | 7.0048 | 9.1085 | 0 | n/a
6B | Small Office | 1980-2004 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 71.8531 | 55.6857 | 127.5388 | 0 | 0 | 0 | 1.164 | 6.2925 | 7.4565 | 0 | n/a
6B | Small Office | 2005-2014 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 38.0761 | 52.5238 | 90.6 | 0 | 0 | 0 | 0.61683 | 5.9352 | 6.552 | 0 | n/a
7A | Food Services | pre-1960 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 611.3167 | 197.0007 | 808.3174 | 0 | 0 | 0 | 9.9033 | 22.2611 | 32.1644 | 0 | n/a
8B | Vehicle Garage | pre-1960 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 194.4195 | 43.4953 | 237.9148 | 0 | 0 | 0 | 3.1496 | 4.915 | 8.0646 | 0 | n/a
8B | Vehicle Garage | 1980-2004 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 134.6823 | 36.7886 | 171.4709 | 0 | 0 | 0 | 2.1819 | 4.1571 | 6.339 | 0 | n/a
9A | Maintenance Shop | pre-1960 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 689.6545 | 110.3811 | 800.0356 | 0 | 0 | 0 | 11.1724 | 12.4731 | 23.6455 | 0 | n/a
9A | Maintenance Shop | 1980-2004 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 401.386 | 81.5246 | 482.9106 | 0 | 0 | 0 | 6.5025 | 9.2123 | 15.7147 | 0 | n/a
9B | Maintenance Shop-Small | pre-1960 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 754.5389 | 121.3605 | 875.8994 | 0 | 0 | 0 | 12.2235 | 13.7137 | 25.9373 | 0 | n/a
9B | Maintenance Shop-Small | 1960-1979 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 699.8294 | 117.4572 | 817.2866 | 0 | 0 | 0 | 11.3372 | 13.2727 | 24.6099 | 0 | n/a
9B | Maintenance Shop-Small | 1980-2004 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 375.7974 | 93.8509 | 469.6483 | 0 | 0 | 0 | 6.0879 | 10.6051 | 16.6931 | 0 | n/a
13B | Firehall | pre-1960 | pumps_to_variable | 0 | 0 | 0 | [5 empty] | 0 | 530.4886 | 194.6568 | 725.1454 | 0 | 0 | 0 | 8.5939 | 21.9962 | 30.5901 | 0 | n/a
1A | Hanger | pre-1960 | solar_dhw | 1 | 424.3909 | 0 | 530.4886 | 0 | 2.49 | 0 | 172.4007 | 705.3793 | -87.1091 | -92.5362 | -179.6454 | 8.6343 | 19.4813 | 28.1155 | -1.4112 | -10.4566 | -11.8678 | 9.0996 | -0.76675
1A | Hanger | 1960-1979 | solar_dhw | 1 | 489.0534 | 0 | 611.3167 | 0 | 2.49 | 0 | 144.2182 | 758.0249 | -182.0908 | -65.3558 | -247.4466 | 9.9437 | 16.2967 | 26.2403 | -2.9499 | -7.3852 | -10.3351 | 9.0996 | -0.88046
1A | Hanger | 1980-2004 | solar_dhw | 1 | 0 | 0 | 0 | 0 | 2.49 | 0 | 0 | 2.49 | 273.9922 | 73.5061 | 347.4983 | 0.040338 | 0 | 0.040338 | 4.4387 | 8.3062 | 12.7449 | 9.0996 | 0.71398
2A | Training | pre-1960 | solar_dhw | 1 | 262.8194 | 0 | 328.5243 | 0 | 0 | 4.32 | 133.3922 | 466.2364 | 183.5833 | -52.3448 | 131.2385 | 5.3221 | 15.5615 | 20.8836 | 2.974 | -5.915 | -2.9409 | 9.7459 | -3.3139
2A | Training | 1980-2004 | solar_dhw | 1 | 352.9621 | 0 | 441.2027 | 0 | 0 | 4.32 | 79.2537 | 524.7764 | -141.7155 | -8.4235 | -150.1391 | 7.1475 | 9.4438 | 16.5913 | -2.2958 | -0.95186 | -3.2477 | 9.7459 | -3.0009
2A | Training | 2005-2014 | solar_dhw | 1 | 341.6286 | 0 | 427.0358 | 0 | 0 | 4.32 | 78.2544 | 509.6102 | -218.1452 | -10.5197 | -228.6649 | 6.918 | 9.3309 | 16.2489 | -3.534 | -1.1887 | -4.7227 | 9.7459 | -2.0636
3B | Storage | pre-1960 | solar_dhw | 0 | 187.7871 | 0 | 234.7339 | 0 | 0 | 0 | 71.5465 | 306.2804 | 90.0581 | -26.7552 | 63.3029 | 3.8027 | 8.0847 | 11.8874 | 1.4589 | -3.0233 | -1.5644 | 0 | n/a
3B | Storage | 1960-1979 | solar_dhw | 0 | 332.8676 | 0 | 416.0845 | 0 | 0 | 0 | 97.4926 | 513.5771 | -121.1898 | -53.9158 | -175.1057 | 6.7406 | 11.0167 | 17.7572 | -1.9633 | -6.0925 | -8.0558 | 0 | n/a
3B | Storage | 1980-2004 | solar_dhw | 0 | 315.7123 | 0 | 394.6404 | 0 | 0 | 0 | 95.9529 | 490.5933 | -215.8581 | -57.053 | -272.9112 | 6.3932 | 10.8427 | 17.2359 | -3.4969 | -6.447 | -9.9439 | 0 | n/a
3B | Storage | 2005-2014 | solar_dhw | 0 | 217.4162 | 0 | 271.7703 | 0 | 0 | 0 | 86.7479 | 358.5182 | -165 | -51.0629 | -216.0628 | 4.4027 | 9.8025 | 14.2052 | -2.673 | -5.7701 | -8.4431 | 0 | n/a
4C | Barracks | pre-1960 | solar_dhw | 1 | 551.7236 | 0 | 689.6545 | 0 | 19.51 | 0 | 107.7621 | 816.9266 | -564.4034 | -74.0657 | -638.469 | 11.4885 | 12.1771 | 23.6656 | -9.1433 | -8.3694 | -17.5128 | 31.6446 | -1.8069
5E | Rec Centre | 1980-2004 | solar_dhw | 1 | 312.1978 | 0 | 390.2472 | 0 | 13.62 | 0 | 77.6217 | 481.4889 | -35.7392 | 20.9952 | -14.744 | 6.5426 | 8.7713 | 15.3139 | -0.57897 | 2.3725 | 1.7935 | 24.3043 | 13.5515
6A | Office | pre-1960 | solar_dhw | 1 | 105.2576 | 0 | 129.8638 | 1.3666 | 38.88 | 0 | 52.8127 | 222.9231 | 306.7886 | 57.1344 | 363.923 | 2.7337 | 6.1223 | 8.8559 | 4.97 | 6.4562 | 11.4262 | 10.5469 | 0.92305
6A | Office | 1960-1979 | solar_dhw | 1 | 58.7825 | 0 | 71.8531 | 1.3001 | 38.88 | 0 | 46.725 | 158.7582 | 334.1697 | 60.5966 | 394.7663 | 1.7939 | 5.4268 | 7.2207 | 5.4135 | 6.8474 | 12.261 | 10.5469 | 0.8602
6A | Office | 1980-2004 | solar_dhw | 1 | 32.0981 | 0 | 38.0761 | 1.6371 | 38.88 | 0 | 43.3521 | 121.9454 | 253.8931 | 53.4261 | 307.3192 | 1.2467 | 5.0838 | 6.3305 | 4.1131 | 6.0371 | 10.1502 | 10.5469 | 1.0391
6B | Small Office | 1960-1979 | solar_dhw | 1 | 294.9697 | 0 | 368.7122 | 0 | 0 | 0.8 | 118.0188 | 487.531 | -238.8484 | -56.8298 | -295.6782 | 5.9731 | 13.4265 | 19.3997 | -3.8693 | -6.4218 | -10.2911 | 19.8953 | -1.9332
6B | Small Office | 1980-2004 | solar_dhw | 1 | 270.8534 | 0 | 338.5668 | 0 | 0 | 0.8 | 115.3431 | 454.7099 | -266.7137 | -60.4573 | -327.1711 | 5.4848 | 13.1242 | 18.6089 | -4.3208 | -6.8317 | -11.1524 | 19.8953 | -1.7839
6B | Small Office | 2005-2014 | solar_dhw | 1 | 181.7284 | 0 | 227.1605 | 0 | 0 | 0.8 | 98.5185 | 326.479 | -189.0844 | -46.7947 | -235.8791 | 3.68 | 11.223 | 14.903 | -3.0632 | -5.2878 | -8.351 | 19.8953 | -2.3824
7A | Food Services | pre-1960 | solar_dhw | 1 | 289.9153 | 0 | 347.134 | 12.2081 | 0 | 35.34 | 86.1903 | 480.8725 | 264.1827 | 63.2623 | 327.445 | 5.6236 | 15.1124 | 20.736 | 4.2798 | 7.1486 | 11.4284 | 53.8331 | 4.7105
8B | Vehicle Garage | pre-1960 | solar_dhw | 1 | 206.4168 | 0 | 258.021 | 0 | 0 | 0.21 | 44.4142 | 302.6452 | -63.6015 | -1.1289 | -64.7304 | 4.1799 | 5.0425 | 9.2225 | -1.0303 | -0.12757 | -1.1579 | 9.0598 | -7.8243
8B | Vehicle Garage | 1980-2004 | solar_dhw | 1 | 85.4162 | 0 | 106.7703 | 0 | 0 | 0.21 | 35.6851 | 142.6654 | 27.912 | 0.89352 | 28.8055 | 1.7297 | 4.0561 | 5.7858 | 0.45217 | 0.10097 | 0.55314 | 9.0598 | 16.3789
9A | Maintenance Shop | pre-1960 | solar_dhw | 1 | 401.9429 | 0 | 502.4286 | 0 | 0 | 0.62 | 84.4988 | 587.5474 | 187.2259 | 25.2623 | 212.4882 | 8.1393 | 9.6184 | 17.7578 | 3.0331 | 2.8546 | 5.8877 | 12.4897 | 2.1213
9A | Maintenance Shop | 1980-2004 | solar_dhw | 1 | 239.5897 | 0 | 299.4871 | 0 | 0 | 0.62 | 67.9074 | 368.0146 | 101.8989 | 12.9972 | 114.896 | 4.8517 | 7.7436 | 12.5953 | 1.6508 | 1.4687 | 3.1194 | 12.4897 | 4.0038
9B | Maintenance Shop-Small | pre-1960 | solar_dhw | 1 | 167.5984 | 0 | 209.498 | 0 | 1.64 | 0 | 64.4734 | 275.6114 | 543.4009 | 56.8871 | 600.288 | 3.4204 | 7.2855 | 10.7059 | 8.8031 | 6.4282 | 15.2313 | 12.5338 | 0.8229
9B | Maintenance Shop-Small | 1960-1979 | solar_dhw | 1 | 155.5356 | 0 | 194.4195 | 0 | 1.64 | 0 | 42.281 | 238.3405 | 503.7699 | 75.1762 | 578.9461 | 3.1762 | 4.7777 | 7.9539 | 8.1611 | 8.4949 | 16.656 | 12.5338 | 0.75251
9B | Maintenance Shop-Small | 1980-2004 | solar_dhw | 1 | 107.7458 | 0 | 134.6823 | 0 | 1.64 | 0 | 35.5742 | 171.8965 | 239.4751 | 58.2766 | 297.7518 | 2.2084 | 4.0199 | 6.2283 | 3.8795 | 6.5853 | 10.4648 | 12.5338 | 1.1977
13B | Firehall | pre-1960 | solar_dhw | 1 | 92.5407 | 0 | 115.6759 | 0 | 0 | 18.86 | 33.6964 | 168.2323 | 414.8128 | 142.1004 | 556.9132 | 1.8739 | 5.9389 | 7.8128 | 6.72 | 16.0573 | 22.7773 | 12.7399 | 0.55933
1A | Hanger | pre-1960 | occupancy_setback | 1 | 311.6452 | 0 | 389.5565 | 0 | 5.3094 | 0 | 76.778 | 471.6439 | 51.0036 | 3.0864 | 54.09 | 6.3968 | 8.6759 | 15.0727 | 0.82626 | 0.34877 | 1.175 | 5.8832 | 5.0069
1A | Hanger | 1960-1979 | occupancy_setback | 1 | 299.3338 | 0 | 374.1673 | 0 | 5.3094 | 0 | 75.919 | 455.3957 | 52.2392 | 2.9435 | 55.1827 | 6.1475 | 8.5788 | 14.7264 | 0.84628 | 0.33261 | 1.1789 | 5.8832 | 4.9905
1A | Hanger | 1980-2004 | occupancy_setback | 1 | 187.7871 | 0 | 234.7339 | 0 | 5.3094 | 0 | 71.5465 | 311.5898 | 36.4388 | 1.9597 | 38.3985 | 3.8887 | 8.0847 | 11.9735 | 0.59031 | 0.22144 | 0.81175 | 5.8832 | 7.2475
2A | Training | pre-1960 | occupancy_setback | 1 | 367.2758 | 0 | 459.0947 | 0 | 0 | 7.2427 | 77.5203 | 543.8578 | 53.0128 | 0.60437 | 53.6172 | 7.4373 | 9.5782 | 17.0156 | 0.85881 | 0.068294 | 0.9271 | 5.438 | 5.8656
2A | Training | 1980-2004 | occupancy_setback | 1 | 204.5562 | 0 | 255.6953 | 0 | 0 | 7.2427 | 71.7994 | 334.7374 | 43.7918 | -3.892 | 39.8998 | 4.1423 | 8.9318 | 13.074 | 0.70943 | -0.4398 | 0.26963 | 5.438 | 20.1685
2A | Training | 2005-2014 | occupancy_setback | 1 | 137.1056 | 0 | 171.382 | 0 | 0 | 7.2427 | 66.5238 | 245.1484 | 37.5086 | -1.7118 | 35.7969 | 2.7764 | 8.3356 | 11.112 | 0.60764 | -0.19343 | 0.41421 | 5.438 | 13.1287
3B | Storage | pre-1960 | occupancy_setback | 1 | 228.8196 | 0 | 286.0245 | 0 | 0 | 0 | 45.7468 | 331.7713 | 38.7675 | -0.95552 | 37.812 | 4.6336 | 5.1694 | 9.803 | 0.62803 | -0.10797 | 0.52006 | 0.41909 | 0.80584
3B | Storage | 1960-1979 | occupancy_setback | 1 | 206.4168 | 0 | 258.021 | 0 | 0 | 0 | 44.4142 | 302.4352 | 36.8737 | -0.83752 | 36.0362 | 4.1799 | 5.0188 | 9.1987 | 0.59735 | -0.094639 | 0.50271 | 0.41909 | 0.83365
3B | Storage | 1980-2004 | occupancy_setback | 1 | 124.0628 | 0 | 155.0785 | 0 | 0 | 0 | 39.156 | 194.2345 | 23.7037 | -0.25615 | 23.4476 | 2.5123 | 4.4246 | 6.9369 | 0.384 | -0.028945 | 0.35506 | 0.41909 | 1.1803
3B | Storage | 2005-2014 | occupancy_setback | 1 | 72.6699 | 0 | 90.8373 | 0 | 0 | 0 | 35.7282 | 126.5656 | 15.9329 | -0.043171 | 15.8898 | 1.4716 | 4.0373 | 5.5089 | 0.25811 | -0.0048783 | 0.25324 | 0.41909 | 1.6549
4C | Barracks | pre-1960 | occupancy_setback | 1 | 99.8409 | 0 | 124.8012 | 0 | 29.0853 | 0 | 31.6479 | 185.5343 | -9.1253 | 2.0486 | -7.0767 | 2.493 | 3.5762 | 6.0692 | -0.14783 | 0.23149 | 0.083658 | 9.2269 | 110.2934
5E | Rec Centre | 1980-2004 | occupancy_setback | 1 | 359.4598 | 0 | 429.3114 | 16.0107 | 20.9885 | 0 | 84.2571 | 550.5677 | -82.1719 | -1.6509 | -83.8228 | 7.2949 | 11.3303 | 18.6251 | -1.3312 | -0.18655 | -1.5177 | 1.2451 | -0.82034
6A | Office | pre-1960 | occupancy_setback | 1 | 331.6473 | 0 | 414.5592 | 0 | 42.0345 | 0 | 116.3262 | 572.92 | 18.9388 | -5.0126 | 13.9262 | 7.3968 | 13.1449 | 20.5417 | 0.30681 | -0.56642 | -0.25961 | 7.3203 | -28.197
6A | Office | 1960-1979 | occupancy_setback | 1 | 306.7029 | 0 | 383.3786 | 0 | 42.0345 | 0 | 113.4442 | 538.8573 | 19.4897 | -4.8224 | 14.6672 | 6.8917 | 12.8192 | 19.7109 | 0.31573 | -0.54494 | -0.2292 | 7.3203 | -31.9381
6A | Office | 1980-2004 | occupancy_setback | 1 | 208.6074 | 0 | 260.7592 | 0 | 42.0329 | 0 | 98.6737 | 401.4658 | 28.0571 | -0.25839 | 27.7988 | 4.9052 | 11.1501 | 16.0554 | 0.45453 | -0.029198 | 0.42533 | 7.3203 | 17.2111
6B | Small Office | 1960-1979 | occupancy_setback | 1 | 90.5289 | 0 | 111.665 | 1.1969 | 0 | 5.746 | 56.8024 | 175.4103 | 18.1989 | -1.7564 | 16.4425 | 1.809 | 7.2032 | 9.0122 | 0.29482 | -0.19847 | 0.096352 | 13.4452 | 139.5433
6B | Small Office | 1980-2004 | occupancy_setback | 1 | 49.277 | 0 | 60.0973 | 1.1992 | 0 | 5.6016 | 50.0475 | 116.9455 | 11.7558 | -1.1625 | 10.5933 | 0.97358 | 6.4239 | 7.3974 | 0.19044 | -0.13136 | 0.05908 | 13.4452 | 227.5756
6B | Small Office | 2005-2014 | occupancy_setback | 1 | 25.8861 | 0 | 30.5921 | 1.4124 | 0 | 5.4732 | 45.6061 | 83.0838 | 7.4841 | 0.032101 | 7.5162 | 0.49559 | 5.9316 | 6.4272 | 0.12124 | 0.0036274 | 0.12487 | 13.4452 | 107.6741
7A | Food Services | pre-1960 | occupancy_setback | 1 | 454.773 | 0 | 568.4662 | 0 | 0 | 51.5821 | 148.5144 | 768.5627 | 42.8505 | -3.0958 | 39.7547 | 9.2092 | 22.6109 | 31.8201 | 0.69418 | -0.34983 | 0.34435 | 1.7199 | 4.9947
8B | Vehicle Garage | pre-1960 | occupancy_setback | 1 | 131.8315 | 0 | 164.7894 | 0 | 0 | 1.2143 | 45.5301 | 211.5338 | 29.6301 | -3.2491 | 26.381 | 2.6696 | 5.2821 | 7.9517 | 0.48001 | -0.36715 | 0.11286 | 2.1619 | 19.1561
8B | Vehicle Garage | 1980-2004 | occupancy_setback | 1 | 90.2379 | 0 | 112.7974 | 0 | 0 | 1.2143 | 37.9332 | 151.945 | 21.8849 | -2.359 | 19.5259 | 1.8273 | 4.4237 | 6.251 | 0.35454 | -0.26656 | 0.087973 | 2.1619 | 24.5745
9A | Maintenance Shop | pre-1960 | occupancy_setback | 1 | 483.2765 | 0 | 604.0956 | 0 | 0 | 2.619 | 116.0168 | 722.7314 | 85.5589 | -8.2547 | 77.3042 | 9.7863 | 13.4058 | 23.1922 | 1.3861 | -0.93278 | 0.45327 | 2.8014 | 6.1803
9A | Maintenance Shop | 1980-2004 | occupancy_setback | 1 | 278.8301 | 0 | 348.5377 | 0 | 0 | 2.619 | 82.8818 | 434.0384 | 52.8483 | -3.9762 | 48.8722 | 5.6463 | 9.6616 | 15.3079 | 0.85614 | -0.44931 | 0.40684 | 2.8014 | 6.8857
9B | Maintenance Shop-Small | pre-1960 | occupancy_setback | 1 | 528.6274 | 0 | 660.7842 | 0 | 4.6581 | 0 | 124.0579 | 789.5003 | 89.0965 | -2.6974 | 86.3991 | 10.7802 | 14.0185 | 24.7987 | 1.4434 | -0.30481 | 1.1386 | 4.7646 | 4.1848
9B | Maintenance Shop-Small | 1960-1979 | occupancy_setback | 1 | 485.7668 | 0 | 607.2084 | 0 | 4.6581 | 0 | 119.7877 | 731.6543 | 87.9628 | -2.3306 | 85.6323 | 9.9122 | 13.536 | 23.4483 | 1.425 | -0.26335 | 1.1616 | 4.7646 | 4.1016
9B | Maintenance Shop-Small | 1980-2004 | occupancy_setback | 1 | 257.046 | 0 | 321.3074 | 0 | 4.6581 | 0 | 94.0734 | 420.039 | 49.8319 | -0.22253 | 49.6093 | 5.2806 | 10.6303 | 15.9109 | 0.80728 | -0.025146 | 0.78213 | 4.7646 | 6.0918
13B | Firehall | pre-1960 | occupancy_setback | 1 | 494.3505 | 0 | 617.9381 | 0 | 0 | 22.2562 | 178.0096 | 818.2039 | -87.4495 | -5.609 | -93.0585 | 10.0106 | 22.63 | 32.6406 | -1.4167 | -0.63381 | -2.0505 | 5.5543 | -2.7087
1A | Hanger | pre-1960 | cold_deck_reset | 1 | 346.6555 | 0 | 433.3193 | 0 | 5.309 | 0 | 81.6803 | 520.3086 | 7.2412 | -1.8158 | 5.4254 | 7.1058 | 9.2299 | 16.3356 | 0.11731 | -0.20519 | -0.087882 | 1.1276 | -12.8308
1A | Hanger | 1960-1979 | cold_deck_reset | 1 | 335.0341 | 0 | 418.7926 | 0 | 5.309 | 0 | 80.6022 | 504.7038 | 7.6143 | -1.7397 | 5.8746 | 6.8704 | 9.108 | 15.9785 | 0.12335 | -0.19659 | -0.073236 | 1.1276 | -15.3966
1A | Hanger | 1980-2004 | cold_deck_reset | 1 | 211.1679 | 0 | 263.9599 | 0 | 5.309 | 0 | 74.5855 | 343.8544 | 7.2133 | -1.0794 | 6.1339 | 4.3622 | 8.4282 | 12.7903 | 0.11686 | -0.12197 | -0.0051174 | 1.1276 | -220.3422
2A | Training | pre-1960 | cold_deck_reset | 1 | 392.7222 | 0 | 490.9027 | 0 | 0 | 7.2427 | 82.2382 | 580.3836 | 21.2048 | -4.1135 | 17.0913 | 7.9526 | 10.1113 | 18.064 | 0.34352 | -0.46482 | -0.12131 | 3.9149 | -32.2728
2A | Training | 1980-2004 | cold_deck_reset | 1 | 227.802 | 0 | 284.7525 | 0 | 0 | 7.2427 | 69.695 | 361.6902 | 14.7347 | -1.7876 | 12.9471 | 4.613 | 8.694 | 13.307 | 0.2387 | -0.202 | 0.036704 | 3.9149 | 106.6606
2A | Training | 2005-2014 | cold_deck_reset | 1 | 159.2161 | 0 | 199.0202 | 0 | 0 | 7.2427 | 65.9712 | 272.2341 | 9.8704 | -1.1592 | 8.7112 | 3.2241 | 8.2732 | 11.4973 | 0.1599 | -0.13099 | 0.028912 | 3.9149 | 135.4071
3B | Storage | pre-1960 | cold_deck_reset | 0 | 259.8336 | 0 | 324.792 | 0 | 0 | 0 | 44.7913 | 369.5833 | 0 | 0 | 0 | 5.2616 | 5.0614 | 10.323 | 0 | 0 | 0 | 0 | n/a
3B | Storage | 1960-1979 | cold_deck_reset | 0 | 235.9158 | 0 | 294.8947 | 0 | 0 | 0 | 43.5767 | 338.4714 | 0 | 0 | 0 | 4.7773 | 4.9242 | 9.7015 | 0 | 0 | 0 | 0 | n/a
3B | Storage | 1980-2004 | cold_deck_reset | 0 | 143.0258 | 0 | 178.7822 | 0 | 0 | 0 | 38.8999 | 217.6821 | 0 | 0 | 0 | 2.8963 | 4.3957 | 7.292 | 0 | 0 | 0 | 0 | n/a
3B | Storage | 2005-2014 | cold_deck_reset | 0 | 85.4162 | 0 | 106.7703 | 0 | 0 | 0 | 35.6851 | 142.4554 | 0 | 0 | 0 | 1.7297 | 4.0324 | 5.7621 | 0 | 0 | 0 | 0 | n/a
4C | Barracks | pre-1960 | cold_deck_reset | 1 | 92.9297 | 0 | 116.1621 | 0 | 29.0989 | 0 | 35.0823 | 180.3434 | -0.49988 | -1.3859 | -1.8858 | 2.3532 | 3.9643 | 6.3175 | -0.0080981 | -0.15661 | -0.16471 | 2.7234 | -16.5349
5E | Rec Centre | 1980-2004 | cold_deck_reset | 1 | 288.813 | 0 | 345.5188 | 12.398 | 20.994 | 0 | 86.339 | 465.2498 | 1.6152 | -0.12003 | 1.4952 | 5.9375 | 11.1573 | 17.0948 | 0.026166 | -0.013563 | 0.012603 | 2.5839 | 205.0228
6A | Office | pre-1960 | cold_deck_reset | 1 | 273.7253 | 0 | 342.1566 | 0 | 42.0362 | 0 | 92.3294 | 476.5222 | 91.3397 | 18.9843 | 110.324 | 6.2239 | 10.4332 | 16.6571 | 1.4797 | 2.1452 | 3.6249 | 5.2958 | 1.4609
6A | Office | 1960-1979 | cold_deck_reset | 1 | 254.3497 | 0 | 317.9371 | 0 | 42.0353 | 0 | 90.8652 | 450.8376 | 84.9304 | 17.7565 | 102.6869 | 5.8316 | 10.2678 | 16.0993 | 1.3759 | 2.0065 | 3.3824 | 5.2958 | 1.5657
6A | Office | 1980-2004 | cold_deck_reset | 1 | 174.5065 | 0 | 218.1331 | 0 | 42.0345 | 0 | 85.699 | 345.8667 | 70.6816 | 12.7163 | 83.3979 | 4.2147 | 9.684 | 13.8987 | 1.145 | 1.4369 | 2.582 | 5.2958 | 2.051
6B | Small Office | 1960-1979 | cold_deck_reset | 0 | 74.9109 | 0 | 72.8964 | 16.5938 | 0 | 5.7827 | 57.6668 | 152.9397 | 56.9675 | -18.0544 | 38.9131 | 1.1809 | 9.0449 | 10.2258 | 0.92287 | -2.0401 | -1.1173 | 24.8031 | n/a
6B | Small Office | 1980-2004 | cold_deck_reset | 0 | 41.538 | 0 | 38.3972 | 10.8203 | 0 | 5.6383 | 50.5106 | 105.3663 | 33.4559 | -11.2834 | 22.1725 | 0.62203 | 7.5675 | 8.1896 | 0.54199 | -1.275 | -0.73304 | 24.8031 | n/a
6B | Small Office | 2005-2014 | cold_deck_reset | 0 | 22.5004 | 0 | 19.3637 | 7.0094 | 0 | 5.5007 | 46.5783 | 78.4521 | 18.7125 | -6.5646 | 12.1479 | 0.31369 | 6.677 | 6.9907 | 0.30314 | -0.7418 | -0.43866 | 24.8031 | n/a
7A | Food Services | pre-1960 | cold_deck_reset | 1 | 472.9147 | 0 | 591.1434 | 0 | 0 | 51.58 | 146.7407 | 789.4641 | 20.1733 | -1.32 | 18.8533 | 9.5765 | 22.4102 | 31.9868 | 0.32681 | -0.14916 | 0.17765 | 5.6406 | 31.7515
8B | Vehicle Garage | pre-1960 | cold_deck_reset | 0 | 155.5356 | 0 | 194.4195 | 0 | 0 | 1.2143 | 42.281 | 237.9148 | 0 | 0 | 0 | 3.1496 | 4.915 | 8.0646 | 0 | 0 | 0 | 4.1035 | n/a
8B | Vehicle Garage | 1980-2004 | cold_deck_reset | 0 | 107.7458 | 0 | 134.6823 | 0 | 0 | 1.2143 | 35.5742 | 171.4709 | 0 | 0 | 0 | 2.1819 | 4.1571 | 6.339 | 0 | 0 | 0 | 4.1035 | n/a
9A | Maintenance Shop | pre-1960 | cold_deck_reset | 1 | 552.1088 | 0 | 690.136 | 0 | 0 | 2.619 | 108.0191 | 800.7741 | -0.48147 | -0.25701 | -0.73848 | 11.1802 | 12.5021 | 23.6823 | -0.0077997 | -0.029043 | -0.036842 | 1.8792 | -51.007
9A | Maintenance Shop | 1980-2004 | cold_deck_reset | 1 | 321.5656 | 0 | 401.957 | 0 | 0 | 2.619 | 79.137 | 483.713 | -0.57101 | -0.23143 | -0.80244 | 6.5117 | 9.2384 | 15.7501 | -0.0092504 | -0.026151 | -0.035402 | 1.8792 | -53.0824
9B | Maintenance Shop-Small | pre-1960 | cold_deck_reset | 1 | 598.0739 | 0 | 747.5923 | 0 | 4.6581 | 0 | 126.1239 | 878.3743 | 2.2885 | -4.7634 | -2.4749 | 12.1865 | 14.252 | 26.4385 | 0.037073 | -0.53826 | -0.50119 | 3.9064 | -7.7943
9B | Maintenance Shop-Small | 1960-1979 | cold_deck_reset | 1 | 553.8203 | 0 | 692.2754 | 0 | 4.6581 | 0 | 121.8627 | 818.7962 | 2.8959 | -4.4055 | -1.5096 | 11.2903 | 13.7705 | 25.0608 | 0.046914 | -0.49782 | -0.45091 | 3.9064 | -8.6634
9B | Maintenance Shop-Small | 1980-2004 | cold_deck_reset | 1 | 296.3341 | 0 | 370.4176 | 0 | 4.6581 | 0 | 95.8326 | 470.9083 | 0.72172 | -1.9817 | -1.26 | 6.0762 | 10.8291 | 16.9053 | 0.011692 | -0.22394 | -0.21224 | 3.9064 | -18.4054
13B | Firehall | pre-1960 | cold_deck_reset | 1 | 377.869 | 0 | 472.3362 | 0 | 0 | 22.2562 | 174.0185 | 668.6108 | 58.1524 | -1.6178 | 56.5346 | 7.6518 | 22.179 | 29.8309 | 0.94207 | -0.18281 | 0.75926 | 3.9707 | 5.2297
1A | Hanger | pre-1960
1A | Hanger | 1960-1979
1A | Hanger | 1980-2004
2A | Training | pre-1960
2A | Training | 1980-2004
2A | Training | 2005-2014
3B | Storage | pre-1960
3B | Storage | 1960-1979
3B | Storage | 1980-2004
3B | Storage | 2005-2014
4C | Barracks | pre-1960
5E | Rec Centre | 1980-2004
6A | Office | pre-1960
6A | Office | 1960-1979
6A | Office | 1980-2004
6B | Small Office | 1960-1979
6B | Small Office | 1980-2004
6B | Small Office | 2005-2014
7A | Food Services | pre-1960
8B | Vehicle Garage | pre-1960
8B | Vehicle Garage | 1980-2004
9A | Maintenance Shop | pre-1960
9A | Maintenance Shop | 1980-2004
9B | Maintenance Shop-Small | pre-1960
9B | Maintenance Shop-Small | 1960-1979
9B | Maintenance Shop-Small | 1980-2004
13B | Firehall | pre-1960
1A | Hanger | pre-1960
1A | Hanger | 1960-1979
1A | Hanger | 1980-2004
2A | Training | pre-1960
2A | Training | 1980-2004
2A | Training | 2005-2014
3B | Storage | pre-1960
3B | Storage | 1960-1979
3B | Storage | 1980-2004
3B | Storage | 2005-2014
4C | Barracks | pre-1960
5E | Rec Centre | 1980-2004
6A | Office | pre-1960
6A | Office | 1960-1979
6A | Office | 1980-2004
6B | Small Office | 1960-1979
6B | Small Office | 1980-2004
6B | Small Office | 2005-2014
7A | Food Services | pre-1960
8B | Vehicle Garage | pre-1960
8B | Vehicle Garage | 1980-2004
9A | Maintenance Shop | pre-1960
9A | Maintenance Shop | 1980-2004
9B | Maintenance Shop-Small | pre-1960
9B | Maintenance Shop-Small | 1960-1979
9B | Maintenance Shop-Small | 1980-2004
13B | Firehall | pre-1960
1A | Hanger | pre-1960
1A | Hanger | 1960-1979
1A | Hanger | 1980-2004
2A | Training | pre-1960
2A | Training | 1980-2004
2A | Training | 2005-2014
3B | Storage | pre-1960
3B | Storage | 1960-1979
3B | Storage | 1980-2004
3B | Storage | 2005-2014
4C | Barracks | pre-1960
5E | Rec Centre | 1980-2004
6A | Office | pre-1960
6A | Office | 1960-1979
6A | Office | 1980-2004
6B | Small Office | 1960-1979
6B | Small Office | 1980-2004
6B | Small Office | 2005-2014
7A | Food Services | pre-1960
8B | Vehicle Garage | pre-1960
8B | Vehicle Garage | 1980-2004
9A | Maintenance Shop | pre-1960
9A | Maintenance Shop | 1980-2004
9B | Maintenance Shop-Small | pre-1960
9B | Maintenance Shop-Small | 1960-1979
9B | Maintenance Shop-Small | 1980-2004
13B | Firehall | pre-1960
1A | Hanger | pre-1960
1A | Hanger | 1960-1979
1A | Hanger | 1980-2004
2A | Training | pre-1960
2A | Training | 1980-2004
2A | Training | 2005-2014
3B | Storage | pre-1960
3B | Storage | 1960-1979
3B | Storage | 1980-2004
3B | Storage | 2005-2014
4C | Barracks | pre-1960
5E | Rec Centre | 1980-2004
6A | Office | pre-1960
6A | Office | 1960-1979
6A | Office | 1980-2004
6B | Small Office | 1960-1979
6B | Small Office | 1980-2004
6B | Small Office | 2005-2014
7A | Food Services | pre-1960
8B | Vehicle Garage | pre-1960
8B | Vehicle Garage | 1980-2004
9A | Maintenance Shop | pre-1960
9A | Maintenance Shop | 1980-2004
9B | Maintenance Shop-Small | pre-1960
9B | Maintenance Shop-Small | 1960-1979
9B | Maintenance Shop-Small | 1980-2004
13B | Firehall | pre-1960
1A | Hanger | pre-1960
1A | Hanger | 1960-1979
1A | Hanger | 1980-2004
2A | Training | pre-1960
2A | Training | 1980-2004
2A | Training | 2005-2014
3B | Storage | pre-1960
3B | Storage | 1960-1979
3B | Storage | 1980-2004
3B | Storage | 2005-2014
4C | Barracks | pre-1960
5E | Rec Centre | 1980-2004
6A | Office | pre-1960
6A | Office | 1960-1979
6A | Office | 1980-2004
6B | Small Office | 1960-1979
6B | Small Office | 1980-2004
6B | Small Office | 2005-2014
7A | Food Services | pre-1960
8B | Vehicle Garage | pre-1960
8B | Vehicle Garage | 1980-2004
9A | Maintenance Shop | pre-1960
9A | Maintenance Shop | 1980-2004
9B | Maintenance Shop-Small | pre-1960
9B | Maintenance Shop-Small | 1960-1979
9B | Maintenance Shop-Small | 1980-2004
13B | Firehall | pre-1960
Note on H1: Lubun, Mike: includes propane
Note on B2: Lubun, Mike: includes air terminal area
Note on B3: Lubun, Mike: includes air terminal area
Note on B4: Lubun, Mike: includes air terminal area
Note on B12: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B13: Lubun, Mike: excludes curling and clubhouse
Note on B20: Lubun, Mike: includes small food areas
Note on B29: Lubun, Mike: includes air terminal area
Note on B30: Lubun, Mike: includes air terminal area
Note on B31: Lubun, Mike: includes air terminal area
Note on B39: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B40: Lubun, Mike: includes curling and clubhouse
Note on B47: Lubun, Mike: includes small food areas
Note on B56: Lubun, Mike: includes air terminal area
Note on B57: Lubun, Mike: includes air terminal area
Note on B58: Lubun, Mike: includes air terminal area
Note on E59: Lubun, Mike: not modelled in basecase
Note on E60: Lubun, Mike: not modelled in basecase
Note on E61: Lubun, Mike: not modelled in basecase
Note on E62: Lubun, Mike: only on 1/2 hour per day
Note on E63: Lubun, Mike: only on 1/2 hour per day
Note on E64: Lubun, Mike: only on 1/2 hour per day
Note on E65: Lubun, Mike: only on 1/2 hour per day
Note on B66: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B67: Lubun, Mike: includes curling and clubhouse
Note on B74: Lubun, Mike: includes small food areas
Note on D79: Lubun, Mike: exhaust fans on same schedule as supply fans (interlock), ecm would not result in savings
Note on D80: Lubun, Mike: exhaust fans on same schedule as supply fans (interlock), ecm would not result in savings
Note on D81: Lubun, Mike: exhaust fans on same schedule as supply fans (interlock), ecm would not result in savings
Note on B83: Lubun, Mike: includes air terminal area
Note on B84: Lubun, Mike: includes air terminal area
Note on B85: Lubun, Mike: includes air terminal area
Note on B93: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B94: Lubun, Mike: includes curling and clubhouse
Note on D98: Lubun, Mike: forced air RTU only
Note on D99: Lubun, Mike: forced air RTU only
Note on D100: Lubun, Mike: forced air RTU only
Note on B101: Lubun, Mike: includes small food areas
Note on B110: Lubun, Mike: includes air terminal area
Note on B111: Lubun, Mike: includes air terminal area
Note on B112: Lubun, Mike: includes air terminal area
Note on B120: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B121: Lubun, Mike: includes curling and clubhouse
Note on B128: Lubun, Mike: includes small food areas
Note on B137: Lubun, Mike: includes air terminal area
Note on B138: Lubun, Mike: includes air terminal area
Note on B139: Lubun, Mike: includes air terminal area
Note on B147: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on D147: Lubun, Mike: full occupancy from 4 pm to 7 am, fans only run during 6 to 7 am and from 4 to 8 pm, therefore dcv savings would be zero
Note on B148: Lubun, Mike: includes curling and clubhouse
Note on D152: Lubun, Mike: does not have an air handler, no ventilation, simply gas furnaces in space,
Note on D153: Lubun, Mike: does not have an air handler, no ventilation, simply gas furnaces in space,
Note on D154: Lubun, Mike: does not have an air handler, no ventilation, simply gas furnaces in space,
Note on B155: Lubun, Mike: includes small food areas
Note on D160: Lubun, Mike: occupancy and fan schedules match, therefore DCV will not save energy
Note on D161: Lubun, Mike: occupancy and fan schedules match, therefore DCV will not save energy
Note on D162: Lubun, Mike: occupancy and fan schedules match, therefore DCV will not save energy
Note on D163: Lubun, Mike: occupancy and fan schedules match, therefore DCV will not save energy
Note on B164: Lubun, Mike: includes air terminal area
Note on B165: Lubun, Mike: includes air terminal area
Note on B166: Lubun, Mike: includes air terminal area
Note on B174: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B175: Lubun, Mike: includes curling and clubhouse
Note on D179: Lubun, Mike: no air handler, simply space furnaces and air conditioners
Note on D180: Lubun, Mike: no air handler, simply space furnaces and air conditioners
Note on D181: Lubun, Mike: no air handler, simply space furnaces and air conditioners
Note on B182: Lubun, Mike: includes small food areas
Note on B191: Lubun, Mike: includes air terminal area
Note on B192: Lubun, Mike: includes air terminal area
Note on B193: Lubun, Mike: includes air terminal area
Note on B201: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B202: Lubun, Mike: includes curling and clubhouse
Note on B209: Lubun, Mike: includes small food areas
Note on B218: Lubun, Mike: includes air terminal area
Note on B219: Lubun, Mike: includes air terminal area
Note on B220: Lubun, Mike: includes air terminal area
Note on B228: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B229: Lubun, Mike: includes curling and clubhouse
Note on B236: Lubun, Mike: includes small food areas
Note on B245: Lubun, Mike: includes air terminal area
Note on B246: Lubun, Mike: includes air terminal area
Note on B247: Lubun, Mike: includes air terminal area
Note on B255: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B256: Lubun, Mike: includes curling and clubhouse
Note on B263: Lubun, Mike: includes small food areas
Note on B272: Lubun, Mike: includes air terminal area
Note on B273: Lubun, Mike: includes air terminal area
Note on B274: Lubun, Mike: includes air terminal area
Note on B282: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B283: Lubun, Mike: includes curling and clubhouse
Note on B290: Lubun, Mike: includes small food areas
Note on B299: Lubun, Mike: includes air terminal area
Note on B300: Lubun, Mike: includes air terminal area
Note on B301: Lubun, Mike: includes air terminal area
Note on B309: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B310: Lubun, Mike: includes curling and clubhouse
Note on B317: Lubun, Mike: includes small food areas
Note on B326: Lubun, Mike: includes air terminal area
Note on B327: Lubun, Mike: includes air terminal area
Note on B328: Lubun, Mike: includes air terminal area
Note on B336: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B337: Lubun, Mike: includes curling and clubhouse
Note on B344: Lubun, Mike: includes small food areas
Note on B353: Lubun, Mike: includes air terminal area
Note on B354: Lubun, Mike: includes air terminal area
Note on B355: Lubun, Mike: includes air terminal area
Note on B363: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B364: Lubun, Mike: includes curling and clubhouse
Note on B371: Lubun, Mike: includes small food areas
Note on B380: Lubun, Mike: includes air terminal area
Note on B381: Lubun, Mike: includes air terminal area
Note on B382: Lubun, Mike: includes air terminal area
Note on B390: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B391: Lubun, Mike: includes curling and clubhouse
Note on B398: Lubun, Mike: includes small food areas
Note on B407: Lubun, Mike: includes air terminal area
Note on B408: Lubun, Mike: includes air terminal area
Note on B409: Lubun, Mike: includes air terminal area
Note on B417: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B418: Lubun, Mike: includes curling and clubhouse
Note on D422: Lubun, Mike: no air handler, therefore no control on the supply air
Note on D423: Lubun, Mike: no air handler, therefore no control on the supply air
Note on D424: Lubun, Mike: no air handler, therefore no control on the supply air
Note on B425: Lubun, Mike: includes small food areas
Note on B434: Lubun, Mike: includes air terminal area
Note on B435: Lubun, Mike: includes air terminal area
Note on B436: Lubun, Mike: includes air terminal area
Note on B444: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B445: Lubun, Mike: includes curling and clubhouse
Note on B452: Lubun, Mike: includes small food areas
Note on B461: Lubun, Mike: includes air terminal area
Note on B462: Lubun, Mike: includes air terminal area
Note on B463: Lubun, Mike: includes air terminal area
Note on B471: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B472: Lubun, Mike: includes curling and clubhouse
Note on B479: Lubun, Mike: includes small food areas
Note on B488: Lubun, Mike: includes air terminal area
Note on B489: Lubun, Mike: includes air terminal area
Note on B490: Lubun, Mike: includes air terminal area
Note on B498: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B499: Lubun, Mike: includes curling and clubhouse
Note on B506: Lubun, Mike: includes small food areas
Note on B515: Lubun, Mike: includes air terminal area
Note on B516: Lubun, Mike: includes air terminal area
Note on B517: Lubun, Mike: includes air terminal area
Note on B525: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B526: Lubun, Mike: includes curling and clubhouse
Note on B533: Lubun, Mike: includes small food areas
Note on B542: Lubun, Mike: includes air terminal area
Note on B543: Lubun, Mike: includes air terminal area
Note on B544: Lubun, Mike: includes air terminal area
Note on B552: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on B553: Lubun, Mike: includes curling and clubhouse
Note on B560: Lubun, Mike: includes small food areas

## h1a-hanger4
Archetype 1A - Hanger
Exemplar Building | Hanger4 | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 6423 | [5 empty] | Corresp.
Air Handling Units | AHU1 | AHU2 | AHU3 | AHU4 | AHU5 | AHU6 | Building
Rated Flow (l/sec) | 3000 | 7380 |  |  |  |  | Numbers
Heating Capacity (kW) | 138.71 | 341.71
Cooling Capacity (kW) | 51.85 | 139.04
Fan Estimated (hp) | 2.68 | 7
Pumps (hp) | <10 HP | 10-25 HP | 25+ HP |  |  | Exh Fan
|  | 1 |  |  |  | 5
Space Retrofits |  |  | Lighting Retrofit |  |  |  | DCV Retrofit |  |  | Plug Loads | T-Stat Retrofit
|  | Area (m2) | Light W/m2 | No. of Fixtures | Fixture (W) | Cost ($) | # of spaces | Apply Y/N | Cost ($) | Cost ($) | Cost ($)
AHU1
MF27 offices | Office-Cat2 | 17.41 | 20.4 | 5.4641 | 65 | 832.5864 | 1 | Y | 857 | 283.75 | 490.75
MF28 offices | Office-Cat2 | 121.1 | 20.4 | 38.0068 | 65 | 5791.2815 | 9 | Y | 7713 | 2553.75 | 4416.75
MZ17 offices | Office-Cat2 | 111.89 | 20.4 | 35.1162 | 65 | 5350.838 | 9 | Y | 7713 | 2553.75 | 4416.75
MZ15 offices | Office-Cat2 | 44.15 | 20.4 | 13.8563 | 65 | 2111.3549 | 5 | Y | 4285 | 1418.75 | 2453.75
MF30 shipping | Material Hdlg | 56.67 | 10.8 | 9.4159 | 65 | 1434.7536 | 1 | Y | 857 | 283.75 | 490.75
MZ18 corridor | Corridor | 70.75 | 8.6 | 9.3608 | 65 | 1426.3472 | 2 | N | 0 | 0 | 0
MF22 workshop | Shop-Machine | 49.59 | 26.9 | 3.3349 | 400 | 985.4711 | 1 | Y | 857 | 283.75 | 490.75
MF24 workshop | Shop-Machine | 37 | 26.9 | 2.4882 | 400 | 735.2779 | 1 | Y | 857 | 283.75 | 490.75
MZ20 storage | inactive Stor | 56.67 | 3.2 | 2.7899 | 65 | 425.1122 | 4 | N | 0 | 0 | 0
AHU2
MF12,MZ16,MZ8 | Washroom | 75.07 | 8.7 | 10.0478 | 65 | 1531.0382 | 6 | N | 0 | 0 | 0
MF10 offices | Office-Cat2 | 21.19 | 20.4 | 6.6504 | 65 | 1013.3547 | 2 | Y | 1714 | 567.5 | 981.5
MF11 offices | Office-Cat2 | 63.67 | 20.4 | 19.9826 | 65 | 3044.8463 | 5 | Y | 4285 | 1418.75 | 2453.75
MF13 lounge | Lounge | 15.72 | 7.5 | 1.8138 | 65 | 276.3848 | 1 | Y | 857 | 283.75 | 490.75
MF14 offices | Office-Cat2 | 65.87 | 20.4 | 20.673 | 65 | 3150.0554 | 3 | Y | 2571 | 851.25 | 1472.25
MF15 workshop | Shop-Machine | 85.65 | 26.9 | 5.76 | 400 | 1702.0689 | 2 | Y | 1714 | 567.5 | 981.5
MF1 tool crib | Material Hdlg | 93.06 | 10.8 | 15.4623 | 65 | 2356.0644 | 5 | Y | 4285 | 1418.75 | 2453.75
MF16 offices | Office-Cat2 | 17.56 | 20.4 | 5.5111 | 65 | 839.7597 | 1 | Y | 857 | 283.75 | 490.75
MF18 workshop | Shop-Machine | 128.7 | 26.9 | 8.6551 | 400 | 2557.5747 | 2 | Y | 1714 | 567.5 | 981.5
MF2 offices | Office-Cat2 | 83.43 | 20.4 | 26.1842 | 65 | 3989.8151 | 5 | Y | 4285 | 1418.75 | 2453.75
MF5 workshop | Shop-Machine | 37.47 | 26.9 | 2.5199 | 400 | 744.6179 | 1 | Y | 857 | 283.75 | 490.75
MF6 canteen | Lounge | 94.54 | 7.5 | 10.9085 | 65 | 1662.1768 | 1 | Y | 857 | 283.75 | 490.75
MF8 offices | Office-Cat2 | 26.18 | 20.4 | 8.2165 | 65 | 1251.988 | 2 | Y | 1714 | 567.5 | 981.5
MZ10 library | Library-Read | 24.22 | 20.4 | 7.6014 | 65 | 1158.2563 | 1 | Y | 857 | 283.75 | 490.75
MZ11 workshop | Shop-Machine | 134.5 | 26.9 | 9.0451 | 400 | 2672.8344 | 2 | Y | 1714 | 567.5 | 981.5
MZ3 offices | Office-Cat2 | 111.8 | 20.4 | 35.088 | 65 | 5346.534 | 12 | Y | 10284 | 3405 | 5889
MZ4 storage | Active Storage | 110.78 | 3.2 | 5.4538 | 65 | 831.0204 | 2 | N | 0 | 0 | 0
MZ9 lounge | Lounge | 65.42 | 7.5 | 7.5485 | 65 | 1150.1968 | 1 | Y | 857 | 283.75 | 490.75
MF25 lockers | Showers/Lockers | 40.1 | 8.6 | 5.3055 | 65 | 808.4314 | 2 | N | 0 | 0 | 0
MZ1 lockers | Showers/Lockers | 34.04 | 8.6 | 4.5038 | 65 | 686.2595 | 2 | N | 0 | 0 | 0
MZ13 lockers | Showers/Lockers | 34.2 | 8.6 | 4.5249 | 65 | 689.4852 | 2 | N | 0 | 0 | 0
MF3 offices | Office-Cat2 | 14.88 | 20.4 | 4.67 | 65 | 711.5959 | 2 | Y | 1714 | 567.5 | 981.5
MF31 workshop | Shop-Machine | 3473.48 | 26.9 | 233.5915 | 400 | 69026.2971 | 2 | Y | 1714 | 567.5 | 981.5
MF19,20,21,26 | Corridor | 110.33 | 8.6 | 14.5975 | 65 | 2224.2952 | 6 | N | 0 | 0 | 0
all | Stairway | 259.1 | 6.5 | 25.91 | 65 | 3948.0363 | 8 | N | 0 | 0 | 0
DS1-4 | inactive Stor | 130.05 | 3.2 | 6.4025 | 65 | 975.5751 | 4 | N | 0 | 0 | 0
MF7 storage | inactive Stor | 36.17 | 3.2 | 1.7807 | 65 | 271.3306 | 3 | N | 0 | 0 | 0
Total $ |  | 0 |  |  |  | 133712.9161 | 118 |  | 65989 | 21848.75 | 37787.75
Total $/m2 | [5 empty] | 20.8178 |  |  | 10.2739 | 3.4016 | 5.8832
AHU Retrofits | AHU1 | AHU2 | AHU3 | AHU4 | AHU5 | AHU6 | AHU7 | Total $ | $/m2
HRV Retrofit Cost | 48855 | 138208.75 | [5 empty] | 187063.75 | 29.124
COP Retrofit Cost | 5087.5 | 11500 | [5 empty] | 16587.5 | 2.5825
Economizer Cost | 1415 | 1415 | [5 empty] | 2830 | 0.4406
VFD Retrofit Cost | 1040 | 1215 | [5 empty] | 2255 | 0.35108
SAT Reset Cost | 3621.25 | 3621.25 | [5 empty] | 7242.5 | 1.1276
Building Retrofits | [7 empty] | Total $ | $/m2
Retro-commissioning | [7 empty] | 33120 | 5.1565
Boiler Hot Water Reset | [7 empty] | 957 | 0.149
Variable Speed Pumps | [7 empty] | 3528 | 0.54928
Exhaust Fan Control | [7 empty] | 3768.75 | 0.58676
Motor Upgrades | [7 empty] | 6855 | 1.0673
Renewables | Collector Area (m2) | No. of Panels | [5 empty] | Total $ | $/m2
Solar DHW | 28.17 | 10 | [5 empty] | 58446.8812 | 9.0996
Note on A8: Lubun, Mike: use an average of 2.13 W/l/sec (average of MNECB constant volume 1.65 W/L/sec and VAV 2.65 W/L/sec)
Note on E13: Lubun, Mike:

## h13a-19T
Archetype 13B - Firehall
Exemplar Building | B004 | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 912 | [5 empty] | Corresp.
Air Handling Units | AHU1 | AHU2 | AHU3 |  |  |  | Building
Rated Flow (l/sec) | 2410 | [5 empty] | Numbers
Heating Capacity (kW) | 178.62
Cooling Capacity (kW) | 58.2
Fan Estimated (hp) | 6.8811
Pumps (hp) | <10 HP | 10 to 25 | 25+ |  |  | Exh Fan
| 2 | 0 | 0 |  |  | 3
Space Retrofits |  |  | Lighting Retrofit |  |  |  | DCV Retrofit |  |  | Plug Loads | T-Stat Retrofit
|  | Area (m2) | Light W/m2 | No. of Fixtures | Fixture (W) | Cost ($) | # of spaces | Apply Y/N | Cost ($) | Cost ($) | Cost ($)
AHU1
storage-bulky | Storage-Bulky | 33.03 | 3.2 | 4.4209 | 65 | 610.0895 | 6 | N | 0 | 0 | 0
washroom | Washroom | 41.85 | 8.7 | 5.6015 | 65 | 773.0017 | 1 | N | 0 | 0 | 0
stairways | Stairway |  | 6.5 | 0 | 65 | 0 | 2 | N | 0 | 0 | 0
corridor | Corridor | 54.7 | 8.6 | 7.2372 | 65 | 998.7378 | 1 | N | 0 | 0 | 0
Conference | Meeting | 38.67 | 19.4 | 11.5415 | 65 | 1592.7281 | 1 | Y | 788 | 250 | 460.5
office | Office-Cat1 | 98.57 | 19.4 | 29.4194 | 65 | 4059.8708 | 8 | Y | 6304 | 2000 | 3684
mech room | M/E | 25.87 | 7.5 | 2.985 | 65 | 411.93 | 2 | N | 0 | 0 | 0
Shop | Shop-Machine | 84.5 | 26.9 | 5.6826 | 400 | 1630.9134 | 2 | N | 0 | 0 | 0
Food Prep | Kitchen | 9.01 | 15.1 | 2.0931 | 65 | 288.8467 | 1 | Y | 788 | 250 | 460.5
lounge | lounge | 40.77 | 7.5 | 4.7042 | 65 | 649.1838 | 1 | Y | 788 | 250 | 460.5
Fire Engine Room | Fire Engine | 481.11 | 8.6 | 16.5502 | 250 | 4749.9028 | 1 | N | 0 | 0 | 0
Total $ |  | 908.08 |  |  |  | 15765.2047 | 26 |  | 8668 | 2750 | 5065.5
Total $/m2 | [5 empty] | 17.2864 |  |  | 9.5044 | 3.0154 | 5.5543
AHU Retrofits | AHU1 | AHU2 | AHU3 | AHU4 | AHU5 | Total $ | $/m2
HRV Retrofit Cost | 90488.75 |  |  |  |  | 90488.75 | 99.2201
COP Retrofit Cost | 11500 |  |  |  |  | 11500 | 12.6096
Economizer Cost | 1415 |  |  |  |  | 1415 | 1.5515
VFD Retrofit Cost | 1215 |  |  |  |  | 1215 | 1.3322
SAT Reset Cost | 3621.25 |  |  |  |  | 3621.25 | 3.9707
Building Retrofits | [5 empty] | Total $ | $/m2
Retro-commissioning | [5 empty] | 11902.5 | 13.051
Boiler Hot Water Reset | [5 empty] | 957 | 1.0493
Variable Speed Pumps | [5 empty] | n/a
Exhaust Fan Control | [5 empty] | 2261.25 | 2.4794
Motor Upgrades | [5 empty] | 6120 | 6.7105
Renewables | Collector Area (m2) | No. of Panels |  |  |  | Total $ | $/m2
Solar DHW | 5.6 | 2 |  |  |  | 11618.8333 | 12.7399
Note on A8: Lubun, Mike: use an average of 2.13 W/l/sec (average of MNECB constant volume 1.65 W/L/sec and VAV 2.65 W/L/sec)
Note on E13: Lubun, Mike:
Note on A43: Lubun, Mike:

## h5a-B720
Archetype 5A - Sport and Fitness: Gymnasium
Exemplar Building | B720
Floor Area (m2) | 12613
Air Handling Units | AHU1 | AHU2 | AHU3 | AHU4_U | AHU4_L | CC | AHU5 | UH-Blu | UH-Red
Rated Flow (l/sec) | 1110 | 4190 | 2740 | 1590 | 1550 | 870 | 22150 | 19030 | 18700
Heating Capacity (kW) | 0 | 41.02 | 0 | 0 | 0 | 22.5 | 0 | 491.17 | 482.65
Cooling Capacity (kW) | 17.52 | 0 | 48.59 | 25.16 | 28.43 | 16 | 0 | 0 | 0
Fan Estimated (hp) | 0.5 | 2 | 1.25 | 1 | 0.75 | 0.5 | 10 | 10 | 10
Pumps (hp) | <10 HP | 10-25 HP | 25+ HP |  |  | Exh Fan
| 4 | 4 | 0 |  |  | 8
Space Retrofits |  |  | Lighting Retrofit |  |  |  | DCV Retrofit |  |  | Plug Loads | T-Stat Retrofit
|  | Area (m2) | Light W/m2 | No. of Fixtures | Fixture (W) | Cost ($) | # of spaces | Apply Y/N | Cost ($) | Cost ($) | Cost ($)
AHU1
MZ13 conference | Meeting | 80.53 | 19.4 | 24.0351 | 65 | 3662.3495 | 1 | Y | 857 | 283.75 | 490.75
MF23 corridor | Corridor | 435.76 | 8.6 | 57.6544 | 65 | 8785.0892 | 3 | N | 0 | 0 | 0
MF08-gym | gym | 200.14 | 13 | 10.4073 | 250 | 3075.3512 | 1 | Y | 857 | 283.75 | 490.75
MZ15, MZ12 | Office-Cat1 | 207.99 | 19.4 | 62.077 | 65 | 9458.9852 | 3 | Y | 2571 | 851.25 | 1472.25
MF11 stairways | Stairway | 22.97 | 6.5 | 2.297 | 65 | 350.0054 | 2 | N | 0 | 0 | 0
washroom | Washroom | 58.4 | 8.7 | 7.8166 | 65 | 1191.0568 | 4 | N | 0 | 0 | 0
AHU2 Gym
MF10 storage | storage-bulky | 80.56 | 3.2 | 3.966 | 65 | 604.3239 | 4 | N | 0 | 0 | 0
MF09 Stores | Retail-C | 154.78 | 35.5 | 84.5337 | 65 | 12880.8214 | 3 | Y | 2571 | 851.25 | 1472.25
MF21 corridor | Corridor | 37.14 | 8.6 | 4.9139 | 65 | 748.7567 | 3 | N | 0 | 0 | 0
MF19-gym | gym | 1587.6 | 13 | 82.5552 | 250 | 24395.0616 | 1 | Y | 857 | 283.75 | 490.75
MZ10 Shell | Gym | 621.01 | 13 | 32.2925 | 250 | 9542.4397 | 1 | Y | 857 | 283.75 | 490.75
AHU3
MZ12 washroom | Washroom | 6.84 | 8.7 | 0.91551 | 65 | 139.5005 | 2 | N | 0 | 0 | 0
MF13 Atria & Vestibule | Atria | 177.62 | 7.5 | 20.4946 | 65 | 3122.867 | 2 | N | 0 | 0 | 0
MF16 Observation | Assembly | 90.51 | 19.4 | 27.0138 | 65 | 4116.2207 | 1 | Y | 857 | 283.75 | 490.75
MZ11 corridor | Corridor | 151.24 | 8.6 | 20.0102 | 65 | 3049.0566 | 4 | N | 0 | 0 | 0
MF17 locker | Shower | 551.95 | 8.6 | 73.0272 | 65 | 11127.5243 | 2 | Y | 1714 | 567.5 | 981.5
MZ14 mech room | M/E | 30.4 | 7.5 | 3.5077 | 65 | 534.4846 | 2 | N | 0 | 0 | 0
MF16-fitness | gym | 459.25 | 13 | 23.881 | 250 | 7056.8355 | 2 | Y | 1714 | 567.5 | 981.5
AHU4 Lower
MF062, MF06 | Shower | 620.9 | 8.6 | 82.1498 | 65 | 12517.5828 | 4 | Y | 3428 | 1135 | 1963
AHU4 Upper
MZ2,MZ9- Observation | Assembly | 109.03 | 10.8 | 4.7101 | 250 | 1391.8334 | 2 | Y | 1714 | 567.5 | 981.5
MZ3 Spectators | Assembly | 337.12 | 10.8 | 14.5636 | 250 | 4303.5391 | 1 | Y | 857 | 283.75 | 490.75
MZ4,MZ7 Washrooms | Washroom | 128.86 | 8.7 | 17.2474 | 65 | 2628.0749 | 4 | N | 0 | 0 | 0
MZ5 Café | Kitchen | 51.41 | 15.1 | 11.9429 | 65 | 1819.8052 | 1 | Y | 857 | 283.75 | 490.75
MZ6 Dining | Fast Food | 93.5 | 14 | 20.1385 | 65 | 3068.5981 | 1 | Y | 857 | 283.75 | 490.75
MZ8 Physio | Therapy | 194.06 | 17.2 | 51.3513 | 65 | 7824.6485 | 1 | Y | 857 | 283.75 | 490.75
CC Squash Courts
MF20 Squash | gym | 384.25 | 13 | 19.981 | 250 | 5904.3855 | 4 | Y | 3428 | 1135 | 1963
AHU5 Pool
Pool | gym | 1196.41 | 13 | 62.2133 | 250 | 18384.0361 | 1 | Y | 857 | 283.75 | 490.75
MF03 | M/E | 170.72 | 7.5 | 19.6985 | 65 | 3001.5531 | 1 | N | 0 | 0 | 0
UH Blue Arena
Rink | gym | 1984.17 | 13 | 103.1768 | 250 | 30488.7562 | 1 | Y | 857 | 283.75 | 490.75
MF22 | M/E | 225.06 | 7.5 | 25.9685 | 65 | 3956.9443 | 1 | N | 0 | 0 | 0
MF04 storage | storage-bulky | 57.25 | 3.2 | 2.8185 | 65 | 429.4631 | 1 | N | 0 | 0 | 0
UH Red Arena
Rink | gym | 1982.17 | 13 | 103.0728 | 250 | 30458.0242 | 1 | Y | 857 | 283.75 | 490.75
MZ21 | M/E | 107.12 | 7.5 | 12.36 | 65 | 1883.355 | 1 | N | 0 | 0 | 0
MF15 storage | storage-bulky | 58.44 | 3.2 | 2.877 | 65 | 438.3899 | 1 | N | 0 | 0 | 0
Total $ |  | 0 |  |  |  | 232339.7192 | 67 |  | 27424 | 9080 | 15704
Total $/m2 | [5 empty] | 18.4207 |  |  | 2.1743 | 0.71989 | 1.2451
AHU Retrofits | AHU1 | AHU2 | AHU3 | AHU4_U | AHU4_L | CC | AHU5 | UH-Blu | UH-Red | Total $ | $/m2
HRV Retrofit Cost | 66168.75 | 138208.75 | 90488.75 | 90488.75 | 90488.75 | 66168.75 | 254281.25 |  |  | 796293.75 | 63.1328
COP Retrofit Cost | 5087.5 | 0 | 11500 | 11500 | 11500 | 5087.5 |  |  |  | 44675 | 3.542
Economizer Cost | 1415 | 1415 | 1415 | 1415 | 1415 | 1415 |  |  |  | 8490 | 0.67312
VFD Retrofit Cost | 1040 | 1040 | 1040 | 1040 | 1040 | 1040 | 1891 | 1891 | 1891 | 11913 | 0.9445
SAT Reset Cost | 3621.25 | 3621.25 | 3621.25 | 3621.25 | 3621.25 | 3621.25 | 3621.25 | 3621.25 | 3621.25 | 32591.25 | 2.5839
Building Retrofits | [9 empty] | Total $ | $/m2
Retro-commissioning | [9 empty] | 28980 | 2.2976
Boiler Hot Water Reset | [9 empty] | 957 | 0.075874
Variable Speed Pumps | [9 empty] | 14112 | 1.1188
Exhaust Fan Control | [9 empty] | 6030 | 0.47808
Motor Upgrades | [9 empty] | 35397.5 | 2.8064
Renewables | Collector Area (m2) | No. of Panels | [7 empty] | Total $ | $/m2
Solar DHW | 147.75 | 51 | [7 empty] | 306550.4688 | 24.3043
Note on A8: Lubun, Mike: use an average of 2.13 W/l/sec (average of MNECB constant volume 1.65 W/L/sec and VAV 2.65 W/L/sec)
Note on E13: Lubun, Mike:

## h6b-B96
Archetype 6A - Office
Exemplar Building | B96 | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 584 | [5 empty] | Corresp.
Air Handling Units | AHU1 | AHU2 | AHU3 | AHU4 | AHU5 |  | Building
Rated Flow (l/sec) | 370 | 310 | 520 | 640 |  |  | Numbers
Heating Capacity (kW) | 29.65 | 24.8 | 41.75 | 51.4
Cooling Capacity (kW) | 6.75 | 4.88 | 9.35 | 11.47
Fan Estimated (hp) | 0.33 | 0.25 | 0.5 | 0.6
Pumps (hp) | <10 HP | 10-25 HP | 25+ HP |  |  | Exh Fan
| 0 | 0 | 0 |  |  | 2
Space Retrofits |  |  | Lighting Retrofit |  |  |  | DCV Retrofit |  |  | Plug Loads | T-Stat Retrofit
|  | Area (m2) | Light W/m2 | No. of Fixtures | Fixture (W) | Cost ($) | # of spaces | Apply Y/N | Cost ($) | Cost ($) | Cost ($)
AHU1 - Furnace 1
Reception | Lobby | 26.66 | 10.8 | 4.4297 | 65 | 674.9697 | 1 | Y | 857 | 283.75 | 490.75
DCO-OPS | Office-Cat1 | 25.54 | 19.4 | 7.6227 | 65 | 1161.5101 | 1 | Y | 857 | 283.75 | 490.75
OPS O | Office-Cat1 | 16.38 | 19.4 | 4.8888 | 65 | 744.9309 | 1 | Y | 857 | 283.75 | 490.75
filing & storage | Storage-inact | 46.69 | 3.2 | 2.2986 | 65 | 350.2468 | 2 | N | 0 | 0 | 0
washrooms 1 | Washroom | 3.79 | 8.7 | 0.50728 | 65 | 77.2963 | 1 | N | 0 | 0 | 0
Coffee | lounge | 3.74 | 7.5 | 0.43154 | 65 | 65.7557 | 1 | Y | 857 | 283.75 | 490.75
AHU2 - Furnace 2
CC office | Office-Cat1 | 12.8 | 19.4 | 3.8203 | 65 | 582.1194 | 1 | Y | 857 | 283.75 | 490.75
Foyer | Lobby | 28.67 | 10.8 | 0 | 65 | 0 | 1 | Y | 857 | 283.75 | 490.75
Privacy Office | Office-Cat1 | 24.87 | 19.4 | 7.4227 | 65 | 1131.0398 | 1 | Y | 857 | 283.75 | 490.75
AHU3 - Furnace 3
corridor (all) | Corridor | 4.98 | 8.6 | 0.65889 | 65 | 100.3987 | 3 | N | 0 | 0 | 0
washrooms 2 | Washroom | 18.56 | 8.7 | 2.4842 | 65 | 378.5276 | 2 | N | 0 | 0 | 0
Work Area 3 | Office-Cat1 | 103.8 | 19.4 | 30.9803 | 65 | 4720.6244 | 2 | Y | 1714 | 567.5 | 981.5
Work Area 4 & Canteen | lounge | 68.89 | 7.5 | 7.9488 | 65 | 1211.2054 | 2 | Y | 1714 | 567.5 | 981.5
AHU4 - Furnace 4
Env. Office | Office-Cat1 | 17.95 | 19.4 | 5.3574 | 65 | 816.3315 | 1 | Y | 857 | 283.75 | 490.75
WLEO, Conference 1 | Meeting | 82.81 | 19.4 | 24.7156 | 65 | 3766.0395 | 2 | Y | 1714 | 567.5 | 981.5
Work Area 1 & 2 | Office-Cat1 | 84.68 | 19.4 | 25.2737 | 65 | 3851.0836 | 2 | Y | 1714 | 567.5 | 981.5
Vestibule | Corridor | 20.69 | 8.6 | 2.7374 | 65 | 417.1184 | 1 | N | 0 | 0 | 0
furnace & telecom | M/E | 7.97 | 7.5 | 0.91962 | 65 | 140.1264 | 2 | N | 0 | 0 | 0
Total $ |  | 0 |  |  |  | 20189.3241 | 27 |  | 13712 | 4540 | 7852
Total $/m2 | [5 empty] | 34.5708 |  |  | 23.4795 | 7.774 | 13.4452
AHU Retrofits | AHU1 | AHU2 | AHU3 | AHU4 | AHU5 | Total $ | $/m2
HRV Retrofit Cost | 41756.25 | 41756.25 | 41756.25 | 41756.25 |  | 167025 | 286.0017
COP Retrofit Cost | 4312.5 | 4312.5 | 4312.5 | 4312.5 |  | 17250 | 29.5377
Economizer Cost | 1415 | 1415 | 1415 | 1415 |  | 5660 | 9.6918
VFD Retrofit Cost | 1040 | 1040 | 1040 | 1040 |  | 4160 | 7.1233
SAT Reset Cost | 3621.25 | 3621.25 | 3621.25 | 3621.25 |  | 14485 | 24.8031
Building Retrofits | [5 empty] | Total $ | $/m2
Retro-commissioning | [5 empty] | 12161.25 | 20.8241
Boiler Hot Water Reset | [5 empty] | 957 | 1.6387
Variable Speed Pumps | [5 empty] | 0 | 0
Exhaust Fan Control | [5 empty] | 1507.5 | 2.5813
Motor Upgrades | [5 empty] | 1745 | 2.988
Renewables | Collector Area (m2) | No. of Panels |  |  |  | Total $ | $/m2
Solar DHW | 5.6 | 2 |  |  |  | 11618.8333 | 19.8953
Note on A8: Lubun, Mike: use an average of 2.13 W/l/sec (average of MNECB constant volume 1.65 W/L/sec and VAV 2.65 W/L/sec)
Note on E13: Lubun, Mike:

## h9b-688
Archetype 9B - Workshop
Exemplar Building | B688 | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 927 | [5 empty] | Corresp.
Air Handling Units | AHU1 | AHU2 | AHU3 | AHU4 |  |  | Building
Rated Flow (l/sec) | 2890 | 370 |  |  |  |  | Numbers
Heating Capacity (kW) | 0 | 0
Cooling Capacity (kW) | 52.3 | 6.2
Fan Estimated (hp) | 2.6 | 0.5
Pumps (hp) | <10 HP | 10-25 HP | 25+ HP |  |  | Exh Fan
| 1 | 0 | 0 |  |  | 1
Space Retrofits |  |  | Lighting Retrofit |  |  |  | DCV Retrofit |  |  | Plug Loads | T-Stat Retrofit
|  | Area (m2) | Light W/m2 | No. of Fixtures | Fixture (W) | Cost ($) | # of spaces | Apply Y/N | Cost ($) | Cost ($) | Cost ($)
AHU1
washroom | Washroom | 16.43 | 8.7 | 2.1991 | 65 | 335.0867 | 2 | N | 0 | 0 | 0
RM101,103,117,118,120 | M/E | 93.64 | 7.5 | 10.8046 | 65 | 1646.3533 | 5 | N | 0 | 0 | 0
112-113 AIM Labs | Labs | 114.87 | 24.8 | 43.8273 | 65 | 6678.1884 | 1 | Y | 857 | 283.75 | 490.75
116 Electronics Lab | Shop Elec | 28.33 | 26.9 | 1.9052 | 400 | 562.9844 | 1 | Y | 857 | 283.75 | 490.75
110 Chaff & Flare | Shop Elec | 17.89 | 26.9 | 1.2031 | 400 | 355.5168 | 1 | Y | 857 | 283.75 | 490.75
111 Weapons Assem | Shop-Machine | 406.66 | 26.9 | 27.3479 | 400 | 8081.3 | 2 | Y | 1714 | 567.5 | 981.5
115 Missile Test Cell | Shop-Machine | 45.61 | 26.9 | 3.0673 | 400 | 906.379 | 1 | Y | 857 | 283.75 | 490.75
119 Bottle Cleaning | Shop-Machine | 23.7 | 26.9 | 1.5938 | 400 | 470.9753 | 1 | Y | 857 | 283.75 | 490.75
106 Janitor | Storage | 4.36 | 3.2 | 0.21465 | 65 | 32.7067 | 1 | N | 0 | 0 | 0
Room 109 | Material Handling | 97.9 | 10.8 | 16.2665 | 65 | 2478.6021 | 1 | N | 0 | 0 | 0
AHU2
office 104 & 105 | Office-Cat1 | 51.03 | 19.4 | 15.2305 | 65 | 2320.7463 | 2 | Y | 1714 | 567.5 | 981.5
102 corridor | Corridor | 14.88 | 8.6 | 1.9687 | 65 | 299.9865 | 1 | N | 0 | 0 | 0
Total $ |  | 0 |  |  |  | 24168.8254 | 19 |  | 7713 | 2553.75 | 4416.75
Total $/m2 | [5 empty] | 26.0721 |  |  | 8.3204 | 2.7549 | 4.7646
AHU Retrofits | AHU1 | AHU2 | AHU3 | AHU4 | AHU5 | Total $ | $/m2
HRV Retrofit Cost | 48855 | 0 |  |  |  | 48855 | 52.7023
COP Retrofit Cost | 10350 | 0 |  |  |  | 10350 | 11.165
Economizer Cost | 1415 | 0 |  |  |  | 1415 | 1.5264
VFD Retrofit Cost | 2707 | 0 |  |  |  | 2707 | 2.9202
SAT Reset Cost | 3621.25 | 0 |  |  |  | 3621.25 | 3.9064
Building Retrofits | [5 empty] | Total $ | $/m2
Retro-commissioning | [5 empty] | 6210 | 6.699
Boiler Hot Water Reset | [5 empty] | 957 | 1.0324
Variable Speed Pumps | [5 empty] | 0 | 0
Exhaust Fan Control | [5 empty] | 753.75 | 0.81311
Motor Upgrades | [5 empty] | 4516.25 | 4.8719
Renewables | Collector Area (m2) | No. of Panels |  |  |  | Total $ | $/m2
Solar DHW | 5.6 | 2 |  |  |  | 11618.8333 | 12.5338
Note on A8: Lubun, Mike: use an average of 2.13 W/l/sec (average of MNECB constant volume 1.65 W/L/sec and VAV 2.65 W/L/sec)
Note on E13: Lubun, Mike:

## h3b-B782
Archetype 8B - Storage Warehouse
Exemplar Building | B782 | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 1171 | [5 empty] | Corresp.
Air Handling Units | AHU1 | AHU2 | AHU3 | AHU4 |  |  | Building
Rated Flow (l/sec) | [6 empty] | Numbers
Heating Capacity (kW)
Cooling Capacity (kW)
Fan Estimated (hp)
Pumps (hp) | <10 HP | 10-25 HP | 25+ HP |  |  | Exh Fan
|  |  | 0 |  |  | 1
Space Retrofits |  |  | Lighting Retrofit |  |  |  | DCV Retrofit |  |  | Plug Loads | T-Stat Retrofit
|  | Area (m2) | Light W/m2 | No. of Fixtures | Fixture (W) | Cost ($) | # of spaces | Apply Y/N | Cost ($) | Cost ($) | Cost ($)
AHU1
storage | Handling | 965.16 | 10.8 | 160.365 | 65 | 24435.6239 | 1 | Y | 857 | 283.75 | 490.75
Total $ |  | 0 |  |  |  | 24435.6239 | 1 |  | 857 | 283.75 | 490.75
Total $/m2 | [5 empty] | 20.8673 |  |  | 0.73185 | 0.24231 | 0.41909
AHU Retrofits | AHU1 | AHU2 | AHU3 | AHU4 | AHU5 | Total $ | $/m2
HRV Retrofit Cost | [5 empty] | 0 | 0
COP Retrofit Cost | [5 empty] | 0 | 0
Economizer Cost | [5 empty] | 0 | 0
VFD Retrofit Cost | [5 empty] | 0 | 0
SAT Reset Cost | [5 empty] | 0 | 0
Building Retrofits | [5 empty] | Total $ | $/m2
Retro-commissioning | [5 empty] | 258.75 | 0.22096
Boiler Hot Water Reset | [5 empty] | 957 | 0.81725
Variable Speed Pumps | [5 empty] | 0 | 0
Exhaust Fan Control | [5 empty] | 753.75 | 0.64368
Motor Upgrades | [5 empty] | 0 | 0
Renewables | Collector Area (m2) | No. of Panels |  |  |  | Total $ | $/m2
Solar DHW | 0 | 0 |  |  |  | 0 | 0
Note on A8: Lubun, Mike: use an average of 2.13 W/l/sec (average of MNECB constant volume 1.65 W/L/sec and VAV 2.65 W/L/sec)
Note on E13: Lubun, Mike:

## h7a-B40
Archetype 7A - Food Services/Dining
Exemplar Building | B40 | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 2568 | [5 empty] | Corresp.
Air Handling Units | AHU1 | AHU2 | AHU3 | AHU4 |  |  | Building
Rated Flow (l/sec) | 780 | 3060 | 2790 | 2320 |  |  | Numbers
Heating Capacity (kW) | 186.77 | 36.24 | 141.85 | 120.05
Cooling Capacity (kW) | 12.95 | 58.31 | 52.96 | 44.2
Fan Estimated (hp) | 0.75 | 2.75 | 2.5 | 2.5
Pumps (hp) | <10 HP | 10-25 HP | 25+ HP |  |  | Exh Fan
| 2 |  |  |  |  | 9
Space Retrofits |  |  | Lighting Retrofit |  |  |  | DCV Retrofit |  |  | Plug Loads | T-Stat Retrofit
|  | Area (m2) | Light W/m2 | No. of Fixtures | Fixture (W) | Cost ($) | # of spaces | Apply Y/N | Cost ($) | Cost ($) | Cost ($)
AHU1 (Food Office)
office | Office-Cat1 | 136.69 | 19.4 | 40.7967 | 65 | 6216.3983 | 2 | Y | 1714 | 567.5 | 981.5
Lobby | Lobby | 9.07 | 10.8 | 1.507 | 65 | 229.6315 | 2 | N | 0 | 0 | 0
AHU2 (North Mess)
Dining Area | Dining | 594.88 | 26.9 | 246.1888 | 65 | 37513.0184 | 1 | Y | 857 | 283.75 | 490.75
office | Office-Cat1 | 0 | 19.4 | 0 | 65 | 0 | 0 | Y | 0 | 0 | 0
stairways | Stairway | 0 | 6.5 | 0 | 65 | 0 | 3 | N | 0 | 0 | 0
Corridor | Corridor | 87.84 | 8.6 | 11.6219 | 65 | 1770.8882 | 4 | N | 0 | 0 | 0
AHU3 (South Mess)
Dining Area | Dining | 530.17 | 26.9 | 219.4088 | 65 | 33432.4182 | 2 | Y | 1714 | 567.5 | 981.5
Washrooms | Washrooms | 52.4 | 8.7 | 7.0135 | 65 | 1068.6879 | 2 | N | 0 | 0 | 0
Electrical/Mech | M/E | 0 | 7.5 | 0 | 65 | 0 | 1 | N | 0 | 0 | 0
office | Office-Cat1 | 32.16 | 19.4 | 9.5985 | 65 | 1462.575 | 2 | Y | 1714 | 567.5 | 981.5
AHU4 (Kitchen RTU)
Kitchen | Kitchen | 463.24 | 15.1 | 107.6142 | 65 | 16397.7161 | 1 | Y | 857 | 283.75 | 490.75
Storage | Storage-Hand | 29.96 | 10.8 | 4.978 | 65 | 758.5181 | 6 | N | 0 | 0 | 0
storage | storage-bulky | 599.32 | 3.2 | 29.505 | 65 | 4495.822 | 6 | N | 0 | 0 | 0
office | Office-Cat1 | 11.06 | 19.4 | 3.301 | 65 | 502.9875 | 1 | Y | 857 | 283.75 | 490.75
Corridor | Corridor | 109.35 | 8.6 | 14.4678 | 65 | 2204.5381 | 4 | N | 0 | 0 | 0
Washrooms | Washrooms | 39.94 | 8.7 | 5.3458 | 65 | 814.5686 | 2 | N | 0 | 0 | 0
Electrical/Mech | M/E | 223.16 | 7.5 | 25.7492 | 65 | 3923.539 | 2 | N | 0 | 0 | 0
locker and shower | locker | 43.43 | 8.6 | 5.7461 | 65 | 875.5655 | 1 | N | 0 | 0 | 0
Total $ |  | 2825.98 |  |  |  | 111666.8724 | 42 |  | 7713 | 2553.75 | 4416.75
Total $/m2 | [5 empty] | 43.484 |  |  | 3.0035 | 0.99445 | 1.7199
AHU Retrofits | AHU1 | AHU2 | AHU3 | AHU4 | AHU5 | Total $ | $/m2
HRV Retrofit Cost | 66168.75 | 90488.75 | 90488.75 | 48855 |  | 296001.25 | 115.2653
COP Retrofit Cost | 5087.5 | 5087.5 | 5087.5 | 5087.5 |  | 20350 | 7.9245
Economizer Cost | 1207.5 | 1207.5 | 1207.5 | 1207.5 |  | 4830 | 1.8808
VFD Retrofit Cost | 1040 | 1040 | 1040 | 1040 |  | 4160 | 1.6199
SAT Reset Cost | 3621.25 | 3621.25 | 3621.25 | 3621.25 |  | 14485 | 5.6406
Building Retrofits | [5 empty] | Total $ | $/m2
Retro-commissioning | [5 empty] | 16042.5 | 6.2471
Boiler Hot Water Reset | [5 empty] | 957 | 0.37266
Variable Speed Pumps | [5 empty] | 0 | 0
Exhaust Fan Control | [5 empty] | 6783.75 | 2.6416
Motor Upgrades | [5 empty] | 10636.25 | 4.1418
Renewables | Collector Area (m2) | No. of Panels |  |  |  | Total $ | $/m2
Solar DHW | 66.63 | 23 |  |  |  | 138243.3687 | 53.8331
Note on A8: Lubun, Mike: use an average of 2.13 W/l/sec (average of MNECB constant volume 1.65 W/L/sec and VAV 2.65 W/L/sec)
Note on E13: Lubun, Mike:

## h8a-B624
Archetype 3A - Vehicle Garage
Exemplar Building | B624 | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 2270 | [5 empty] | Corresp.
Air Handling Units | AHU1 | AHU2 | AHU3 |  |  |  | Building
Rated Flow (l/sec) | 1860 | 2180 | 490 |  |  |  | Numbers
Heating Capacity (kW) | 0 | 0 | 0
Cooling Capacity (kW) | 0 | 0 | 0
Fan Estimated (hp) | 1 | 1 | 0.5
Pumps (hp) | <10 | 10 to 25 | 25+ |  |  | Exh Fan
| 1 | 0 | 0 |  |  | 1
Space Retrofits |  |  | Lighting Retrofit |  |  |  | DCV Retrofit |  |  | Plug Loads | T-Stat Retrofit
|  | Area (m2) | Light W/m2 | No. of Fixtures | Fixture (W) | Cost ($) | # of spaces | Apply Y/N | Cost ($) | Cost ($) | Cost ($)
AHU1 - Supply
Supply | Auto | 611.39 | 10.8 | 16.5075 | 400 | 4877.9751 | 1 | Y | 857 | 283.75 | 490.75
Tool Crib, Battery | Storage | 106.66 | 3.2 | 5.251 | 65 | 800.1141 | 3 | N | 0 | 0 | 0
AHU2-Wash Bay & Shop
Main Shop | Auto | 657.27 | 10.8 | 17.7463 | 400 | 5244.0287 | 1 | Y | 857 | 283.75 | 490.75
Wash Bay | Machinery | 247.24 | 26.9 | 16.6269 | 400 | 4913.246 | 2 | Y | 1714 | 567.5 | 981.5
AHU3-Offices
washroom | Washroom | 83.66 | 8.7 | 11.1976 | 65 | 1706.2296 | 2 | N | 0 | 0 | 0
Back Office | Office | 58.52 | 19.4 | 17.466 | 65 | 2661.3771 | 2 | Y | 1714 | 567.5 | 981.5
Transport office | Office | 57.15 | 19.4 | 17.0571 | 65 | 2599.0721 | 2 | Y | 1714 | 567.5 | 981.5
Office | Office | 15.45 | 19.4 | 4.6112 | 65 | 702.6363 | 1 | Y | 857 | 283.75 | 490.75
Common Room | Lounge | 88.38 | 7.5 | 10.1977 | 65 | 1553.8734 | 1 | Y | 857 | 283.75 | 490.75
stairways | Stairway | 36.76 | 6.5 | 1 | 65 | 152.375 | 4 | N | 0 | 0 | 0
corridor | Corridor | 47.1 | 8.6 | 6.2317 | 65 | 949.5541 | 4 | N | 0 | 0 | 0
Total |  | 1764.74 |  |  |  | 26160.4814 | 23 |  | 8570 | 2837.5 | 4907.5
Total $/m2 | [5 empty] | 11.5244 |  |  | 3.7753 | 1.25 | 2.1619
AHU Retrofits | AHU1 | AHU2 | AHU3 | AHU4 | AHU5 | Total $ | $/m2
HRV Retrofit Cost | 48855 | 48855 | 66168.75 |  |  | 163878.75 | 72.1933
COP Retrofit Cost | 0 | 0 | 0 |  |  | 0 | 0
Economizer Cost | 1207.5 | 1207.5 | 1207.5 |  |  | 3622.5 | 1.5958
VFD Retrofit Cost | 1040 | 1040 | 1040 |  |  | 3120 | 1.3744
SAT Reset Cost | 3105 | 3105 | 3105 |  |  | 9315 | 4.1035
Building Retrofits | [5 empty] | Total $ | $/m2
Retro-commissioning | [5 empty] | 9832.5 | 4.3315
Boiler Hot Water Reset | [5 empty] | 957 | 0.42159
Variable Speed Pumps | [5 empty] | n/a
Exhaust Fan Control | [5 empty] | 753.75 | 0.33205
Motor Upgrades | [5 empty] | 3348.75 | 1.4752
Renewables | Collector Area (m2) | No. of Panels |  |  |  | Total $ | $/m2
Solar DHW | 11.6 | 4 |  |  |  | 20565.8333 | 9.0598
Note on A8: Lubun, Mike: use an average of 2.13 W/l/sec (average of MNECB constant volume 1.65 W/L/sec and VAV 2.65 W/L/sec)
Note on E13: Lubun, Mike:

## h6a-007
Archetype 6A - Office
Exemplar Building | B007 | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 3419 | [5 empty] | Corresp.
Air Handling Units | AHU1 | AHU2 | AHU3 | AHU4 | AHU5 |  | Building
Rated Flow (l/sec) | 840 | 620 | 890 | 1580 | 1420 |  | Numbers
Heating Capacity (kW) | 0 | 0 | 0 | 0 | 0
Cooling Capacity (kW) | 13.37 | 0 | 16.37 | 27.88 | 26
Fan Estimated (hp) | 0.75 | 0.5 | 0.75 | 1.5 | 1.3
Pumps (hp) | <10 HP | 10-25 HP | 25+ HP |  |  | Exh Fan
| 1 | 1 | 0 |  |  | 7
Space Retrofits |  |  | Lighting Retrofit |  |  |  | DCV Retrofit |  |  | Plug Loads | T-Stat Retrofit
|  | Area (m2) | Light W/m2 | No. of Fixtures | Fixture (W) | Cost ($) | # of spaces | Apply Y/N | Cost ($) | Cost ($) | Cost ($)
AHU1 - RTU1
Conference | Meeting | 36.72 | 19.4 | 4.9148 | 65 | 748.8973 | 1 | Y | 857 | 283.75 | 490.75
office 5,6,7 | Office-Cat1 | 120.36 | 19.4 | 35.9228 | 65 | 5473.7413 | 12 | Y | 10284 | 3405 | 5889
Planning | Office-Cat1 | 39.09 | 19.4 | 11.6669 | 65 | 1777.738 | 2 | Y | 1714 | 567.5 | 981.5
storage-inactive | Storage-inact | 42.34 | 3.2 | 2.0844 | 65 | 317.6151 | 3 | N | 0 | 0 | 0
Prevent. Maintenance | Shop-Machine | 54 | 26.9 | 3.6315 | 400 | 1073.1082 | 1 | Y | 857 | 283.75 | 490.75
AHU2 - RTU2
office 4 & ADP office | Office-Cat1 | 70.12 | 19.4 | 20.9281 | 65 | 3188.9228 | 4 | Y | 3428 | 1135 | 1963
ADP work and lockshop | Shop-Machine | 79.02 | 26.9 | 5.3141 | 400 | 1570.3151 | 1 | Y | 857 | 283.75 | 490.75
Computer room | Office-Comp | 17.71 | 22.6 | 6.1576 | 65 | 938.269 | 1 | Y | 857 | 283.75 | 490.75
AHU3 - RTU3
Canteen & Coffee | lounge | 208.23 | 7.5 | 24.0265 | 65 | 3661.0438 | 2 | Y | 1714 | 567.5 | 981.5
Kitchen | kitchen | 28.37 | 15.1 | 6.5906 | 65 | 1004.238 | 1 | Y | 857 | 283.75 | 490.75
AHU4
MZ offices 5,6,7,8 | Office-Cat1 | 193 | 19.4 | 57.6031 | 65 | 8777.2688 | 7 | Y | 5999 | 1986.25 | 3435.25
MZ GIS Records | Storage-inact | 16.57 | 3.2 | 0.81575 | 65 | 124.3005 | 2 | N | 0 | 0 | 0
Printing & Photocopy | Office-Comp | 61.6 | 22.6 | 21.4178 | 65 | 3263.5443 | 2 | Y | 1714 | 567.5 | 981.5
MZ Tool | Storage-inact | 131.2 | 3.2 | 6.4591 | 65 | 984.2018 | 5 | N | 0 | 0 | 0
MZ Cooler | Storage-inact | 16.6 | 3.2 | 0.81723 | 65 | 124.5255 | 2 | N | 0 | 0 | 0
Shipping/Receiving | Material Handling | 266.02 | 10.8 | 44.2002 | 65 | 6735.0125 | 2 | N | 0 | 0 | 0
CE Tool Control 1,2,3 | Storage-inact | 293.64 | 3.2 | 14.4561 | 65 | 2202.7518 | 3 | N | 0 | 0 | 0
Machine, Rm 1, 2 | Shop-Machine | 220.11 | 26.9 | 14.8024 | 400 | 4374.1085 | 3 | Y | 2571 | 851.25 | 1472.25
Paint Shop | Shop-Paint | 128.76 | 17.2 | 5.5367 | 400 | 1636.0889 | 1 | Y | 857 | 283.75 | 490.75
Carpenter Shop | Shop-Carpentry | 246.77 | 24.8 | 15.2997 | 400 | 4521.0732 | 1 | Y | 857 | 283.75 | 490.75
mech & valve room | M/E | 48.64 | 7.5 | 5.6123 | 65 | 855.1754 | 2 | N | 0 | 0 | 0
AHU5 VAV w/Reheat
MZ 3&4, Office 3 | Office-Cat1 | 460.2 | 19.4 | 137.352 | 65 | 20929.011 | 12 | Y | 10284 | 3405 | 5889
washrooms (all) | Washroom | 68.55 | 8.7 | 9.1752 | 65 | 1398.0641 | 4 | N | 0 | 0 | 0
stairways (all) | Stairway | 49.88 | 6.5 | 4.988 | 65 | 760.0465 | 4 | N | 0 | 0 | 0
corridor (all) | Corridor | 321.5 | 8.6 | 42.5369 | 65 | 6481.5637 | 8 | N | 0 | 0 | 0
vestibule 1,2 | Corridor | 12.67 | 8.6 | 1.6763 | 65 | 255.4321 | 2 | N | 0 | 0 | 0
Total $ |  | 0 |  |  |  | 83176.0572 | 88 |  | 43707 | 14471.25 | 25028.25
Total $/m2 | [5 empty] | 24.3276 |  |  | 12.7836 | 4.2326 | 7.3203
AHU Retrofits | AHU1 | AHU2 | AHU3 | AHU4 | AHU5 | Total $ | $/m2
HRV Retrofit Cost | 66168.75 | 66168.75 | 66168.75 | 48855 | 66168.75 | 313530 | 91.7023
COP Retrofit Cost | 0 | 0 | 0 | 10350 | 10350 | 20700 | 6.0544
Economizer Cost | 1415 | 1415 | 1415 | 1415 | 1415 | 7075 | 2.0693
VFD Retrofit Cost | 1040 | 1040 | 1040 | 1040 | 1040 | 5200 | 1.5209
SAT Reset Cost | 3621.25 | 3621.25 | 3621.25 | 3621.25 | 3621.25 | 18106.25 | 5.2958
Building Retrofits | [5 empty] | Total $ | $/m2
Retro-commissioning | [5 empty] | 29238.75 | 8.5518
Boiler Hot Water Reset | [5 empty] | 957 | 0.27991
Variable Speed Pumps | [5 empty] | 3528 | 1.0319
Exhaust Fan Control | [5 empty] | 5276.25 | 1.5432
Motor Upgrades | [5 empty] | 8276.25 | 2.4207
Renewables | Collector Area (m2) | No. of Panels |  |  |  | Total $ | $/m2 |  |  |  |  | a-
Solar DHW | 17.38 | 6 |  |  |  | 36059.8792 | 10.5469
Note on A8: Lubun, Mike: use an average of 2.13 W/l/sec (average of MNECB constant volume 1.65 W/L/sec and VAV 2.65 W/L/sec)
Note on E13: Lubun, Mike:

## h4c-B45
Archetype 4C - Barracks
Exemplar Building | B45 | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 3989 | [5 empty] | Corresp.
Air Handling Units | AHU1 | AHU2 | AHU3 | AHU4 |  |  | Building
Rated Flow (l/sec) | 1550 | 1840 | 2020 |  |  |  | Numbers
Heating Capacity (kW) | 93.46 | 71.66 | 85.37
Cooling Capacity (kW) | 27.21 | 33.64 | 36.07
Fan Estimated (hp) | 4.4256 | 5.2536 | 5.7676
Pumps (hp) | <10 HP | 10-25 HP | 25+ HP |  |  | Exh Fan
| 2 |  |  |  |  | 6
Space Retrofits |  |  | Lighting Retrofit |  |  |  | DCV Retrofit |  |  | Plug Loads | T-Stat Retrofit
|  | Area (m2) | Light W/m2 | No. of Fixtures | Fixture (W) | Cost ($) | # of spaces | Apply Y/N | Cost ($) | Cost ($) | Cost ($)
AHU1 ,AHU2,AHU3
dormitory | Dormitory | 2327.44 | 11.8 | 311.5189 | 65 | 47467.6912 | 75 | Y | 64275 | 21281.25 | 36806.25
washroom | Washroom | 492.07 | 8.7 | 65.8617 | 65 | 10035.673 | 21 | N | 0 | 0 | 0
stairways | Stairway | 195.52 | 6.5 | 19.552 | 65 | 2979.236 | 5 | N | 0 | 0 | 0
corridor | Corridor | 923.44 | 8.6 | 122.1782 | 65 | 18616.9056 | 6 | N | 0 | 0 | 0
showers | Showers | 0 | 8.6 | 0 | 65 | 0 | 0 | N | 0 | 0 | 0
mech/elec | M/E | 90.29 | 7.5 | 10.4181 | 65 | 1587.4545 | 1 | N | 0 | 0 | 0
storage | Storage-Bulky | 92.98 | 3.2 | 4.5775 | 65 | 697.493 | 8 | N | 0 | 0 | 0
laundry | Laundry-Wash | 478.5 | 9.7 | 71.4069 | 65 | 10880.6299 | 2 | N | 0 | 0 | 0
Total $ |  | 0 |  |  |  | 92265.0832 | 118 |  | 64275 | 21281.25 | 36806.25
Total $/m2 | [5 empty] | 23.1299 |  |  | 16.1131 | 5.335 | 9.2269
AHU Retrofits | AHU1 | AHU2 | AHU3 | AHU4 | AHU5 | Total $ | $/m2
HRV Retrofit Cost | 90488.75 | 90488.75 | 90488.75 |  |  | 271466.25 | 68.0537
COP Retrofit Cost | 5087.5 | 5087.5 | 5087.5 |  |  | 15262.5 | 3.8261
Economizer Cost | 1415 | 1415 | 1415 |  |  | 4245 | 1.0642
VFD Retrofit Cost | 1040 | 1040 | 1040 |  |  | 3120 | 0.78215
SAT Reset Cost | 3621.25 | 3621.25 | 3621.25 |  |  | 10863.75 | 2.7234
Building Retrofits | [5 empty] | Total $ | $/m2
Retro-commissioning | [5 empty] | 34413.75 | 8.6272
Boiler Hot Water Reset | [5 empty] | 957 | 0.23991
Variable Speed Pumps | [5 empty] | 0 | 0
Exhaust Fan Control | [5 empty] | 4522.5 | 1.1337
Motor Upgrades | [5 empty] | 10200 | 2.557
Renewables | Collector Area (m2) | No. of Panels |  |  |  | Total $ | $/m2
Solar DHW | 60.84 | 21 |  |  |  | 126230.325 | 31.6446
Note on A8: Lubun, Mike: use an average of 2.13 W/l/sec (average of MNECB constant volume 1.65 W/L/sec and VAV 2.65 W/L/sec)
Note on E13: Lubun, Mike:

## h9a-581
Archetype 9A - Workshop
Exemplar Building | B581 | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 1927 | [5 empty] | Corresp.
Air Handling Units | AHU1 | AHU2 | AHU3 | AHU4 | AHU5 |  | Building
Rated Flow (l/sec) | 4000 | 0 | 80 |  |  |  | Numbers
Heating Capacity (kW) | 0 |  | 0
Cooling Capacity (kW) | 9.92 | 0 | 0
Fan Estimated (hp) | 3.6 | 1.5 | 0.25
Pumps (hp) | <10 HP | 10 to 25 | 25+ |  |  | Exh Fan
| 1 |  |  |  |  | 3
Space Retrofits |  |  | Lighting Retrofit |  |  |  | DCV Retrofit |  |  | Plug Loads | T-Stat Retrofit
|  | Area (m2) | Light W/m2 | No. of Fixtures | Fixture (W) | Cost ($) | # of spaces | Apply Y/N | Cost ($) | Cost ($) | Cost ($)
AHU1 Office
office 1 | Office-Cat1 | 12.67 | 19.4 | 3.7815 | 65 | 576.2072 | 1 | Y | 857 | 283.75 | 490.75
office 2 | Office-Cat1 | 12.19 | 19.4 | 3.6382 | 65 | 554.3778 | 1 | Y | 857 | 283.75 | 490.75
library | Library-Read | 11.55 | 20.4 | 3.6249 | 65 | 552.3477 | 1 | Y | 857 | 283.75 | 490.75
washroom | Washroom |  | 8.7 | 0 | 65 | 0 |  | N | 0 | 0 | 0
stairways | Stairway | 4.23 | 6.5 | 0.423 | 65 | 64.4546 | 1 | N | 0 | 0 | 0
corridor | Corridor | 36.73 | 8.6 | 4.8597 | 65 | 740.4909 | 2 | N | 0 | 0 | 0
Common Room | M/E | 52.91 | 7.5 | 6.105 | 65 | 930.2494 | 1 | N | 0 | 0 | 0
Control Room | M/E | 26.89 | 7.5 | 3.1027 | 65 | 472.7727 | 1 | N | 0 | 0 | 0
AHU2 Workshop | [5 empty] | 0
Weld Shop | Shop-Welding | 52.44 | 12.9 | 1.6912 | 400 | 499.7466 | 1 | Y | 857 | 283.75 | 490.75
Main Workshop | Shop-Machine | 833.51 | 26.9 | 56.0535 | 400 | 16563.8233 | 2 | Y | 1714 | 567.5 | 981.5
Nozzle Testing | Shop-Machine | 12.8 | 26.9 | 0.8608 | 400 | 254.3664 | 1 | Y | 857 | 283.75 | 490.75
Washing Bay | Shop-Machine | 32.01 | 26.9 | 2.1527 | 400 | 636.1147 | 1 | Y | 857 | 283.75 | 490.75
AfterBurner Rm | Shop-Repair | 106.4 | 10.8 | 2.8728 | 400 | 848.9124 | 1 | Y | 857 | 283.75 | 490.75
Engine Prep | Shop-Repair | 365.66 | 10.8 | 9.8728 | 400 | 2917.4183 | 1 | Y | 857 | 283.75 | 490.75
Tool Crib | Active Storage | 110 | 3.2 | 5.4154 | 65 | 825.1692 | 1 | Y | 857 | 283.75 | 490.75
AHU3/4Mech Rooms
Mech Rooms 1&2 | M/E | 26.89 | 267.6 | 110.7041 | 65 | 16868.5314 | 2 | N | 0 | 0 | 0
MUA Locker Rooms
locker and shower | Locker | 108.73 | 8.6 | 14.3858 | 65 | 2192.0386 | 6 | N | 0 | 0 | 0
Closet | Active Storage | 11.15 | 3.2 | 0.54892 | 65 | 83.6422 | 2 | N | 0 | 0 | 0
Total $ |  | 1791.9 |  |  |  | 45580.6635 | 26 |  | 9427 | 3121.25 | 5398.25
Total $/m2 | [5 empty] | 23.6537 |  |  | 4.8921 | 1.6197 | 2.8014
AHU Retrofits | AHU1 | AHU2 | AHU3 | AHU4 | AHU5 | Total $ | $/m2
HRV Retrofit Cost | 138208.75 | 0 | 0 |  |  | 138208.75 | 71.7222
COP Retrofit Cost | 5087.5 | 0 | 0 |  |  | 5087.5 | 2.6401
Economizer Cost | 1207.5 | 0 | 0 |  |  | 1207.5 | 0.62662
VFD Retrofit Cost | 1215 | 0 | 0 |  |  | 1215 | 0.63051
SAT Reset Cost | 3621.25 | 0 | 0 |  |  | 3621.25 | 1.8792
Building Retrofits | [5 empty] | Total $ | $/m2
Retro-commissioning | [5 empty] | 10608.75 | 5.5053
Boiler Hot Water Reset | [5 empty] | 957 | 0.49663
Variable Speed Pumps | [5 empty] | 0 | 0
Exhaust Fan Control | [5 empty] | 2261.25 | 1.1735
Motor Upgrades | [5 empty] | 5266.25 | 2.7329
Renewables | Collector Area (m2) | No. of Panels |  |  |  | Total $ | $/m2
Solar DHW | 11.6 | 4 |  |  |  | 24067.5833 | 12.4897
Note on A8: Lubun, Mike: use an average of 2.13 W/l/sec (average of MNECB constant volume 1.65 W/L/sec and VAV 2.65 W/L/sec)
Note on E13: Lubun, Mike:

## h2a-34T
Archetype 2A - Training Centre
Exemplar Building | B172 | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 3700 | [5 empty] | Corresp. | B503 | B246 | B058a | B034
Air Handling Units | AHU1 | AHU2 | AHU3 | AHU4 |  |  | Building | B587 |  |  | B065
Rated Flow (l/sec) | 17390 | [5 empty] | Numbers
Heating Capacity (kW) | 0
Cooling Capacity (kW) | 414.49
Fan Estimated (hp) | 49.6524
Pumps (hp) | <10 HP | 10-25 HP | 25+ HP |  |  | Exh Fan
| 4 | 0 | 2 |  |  | 2
Space Retrofits |  |  | Lighting Retrofit |  |  |  | DCV Retrofit |  |  | Plug Loads | T-Stat Retrofit
|  | Area (m2) | Light W/m2 | No. of Fixtures | Fixture (W) | Cost ($) | # of spaces | Apply Y/N | Cost ($) | Cost ($) | Cost ($)
AHU1
Conference | Meeting | 96.01 | 19.4 | 12.8506 | 65 | 1958.1055 | 4 | Y | 3428 | 1135 | 1963
washroom | Washroom | 39.61 | 8.7 | 5.3016 | 65 | 807.8383 | 4 | N | 0 | 0 | 0
stairways | Stairway |  | 6.5 | 0 | 65 | 0 |  |  | 0 | 0 | 0
corridor | Corridor | 567.05 | 8.6 | 75.0251 | 65 | 11431.9461 | 8 | N | 0 | 0 | 0
office | Office-Cat2 | 152.87 | 20.4 | 47.9777 | 65 | 7310.5962 | 6 | Y | 5142 | 1702.5 | 2944.5
office | Office-Cat1 | 768.13 | 19.4 | 229.2573 | 65 | 34933.0752 | 10 | Y | 8570 | 2837.5 | 4907.5
mech room | M/E | 174.39 | 7.5 | 20.1219 | 65 | 3066.078 | 2 | N | 0 | 0 | 0
storage-inactive | Storage-inact |  | 6.5 | 0 | 65 | 0 |  |  | 0 | 0 | 0
Classroom | Classroom | 1999.94 | 21.5 | 661.5186 | 65 | 100798.899 | 21 | Y | 17997 | 5958.75 | 10305.75
Total $ |  | 3798 |  |  |  | 160306.5384 | 55 |  | 35137 | 11633.75 | 20120.75
Total $/m2 | [5 empty] | 43.3261 |  |  | 9.4965 | 3.1443 | 5.438
AHU Retrofits | AHU1 | AHU2 | AHU3 | AHU4 | AHU5 | Total $ | $/m2
HRV Retrofit Cost | 254281.25 |  |  |  |  | 254281.25 | 68.7247
COP Retrofit Cost | 20350 |  |  |  |  | 20350 | 5.5
Economizer Cost | 5660 |  |  |  |  | 5660 | 1.5297
VFD Retrofit Cost | 7564 |  |  |  |  | 7564 | 2.0443
SAT Reset Cost | 14485 |  |  |  |  | 14485 | 3.9149
Building Retrofits | [5 empty] | Total $ | $/m2
Retro-commissioning | [5 empty] | 19406.25 | 5.2449
Boiler Hot Water Reset | [5 empty] | 957 | 0.25865
Variable Speed Pumps | [5 empty] | 8311 | 2.2462
Exhaust Fan Control | [5 empty] | 1507.5 | 0.40743
Motor Upgrades | [5 empty] | 20032.5 | 5.4142
Renewables | Collector Area (m2) | No. of Panels |  |  |  | Total $ | $/m2
Solar DHW | 17.38 | 6 |  |  |  | 36059.8792 | 9.7459
Note on A8: Lubun, Mike: use an average of 2.13 W/l/sec (average of MNECB constant volume 1.65 W/L/sec and VAV 2.65 W/L/sec)
Note on E13: Lubun, Mike:

## ECMBldgAreas
Adjusted areas for the archetypes for all vintages accounting for the applicability index of the ECM under worksheet "BldgEUI"
1A-Hanger (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 0
Roof | 0 | 0 | 0 | 0 | 0
Windows | 0 | 0 | 0 | 0 | 0
Air tightness | 0 | 0 | 0 | 0 | 0
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0
T set back | 0 | 0 | 0 | 0 | 0
Lighting (30%) | 0 | 0 | 0 | 0 | 0
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0
HRV | 0 | 0 | 0 | 0 | 0
DCV | 0 | 0 | 0 | 0 | 0
Cold Deck Reset | 0 | 0 | 0 | 0 | 0
VSD | 0 | 0 | 0 | 0 | 0
VSP | 0 | 0 | 0 | 0 | 0
Solar Wall | 0 | 0 | 0 | 0 | 0
Solar DHW | 0 | 0 | 0 | 0 | 0
DB Economizer | 0 | 0 | 0 | 0 | 0
COP | 0 | 0 | 0 | 0 | 0
Retro-commissioning | 0 | 0 | 0 | 0 | 0
2A-Training Building (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 0
Roof | 0 | 0 | 0 | 0 | 0
Windows | 0 | 0 | 0 | 0 | 0
Air tightness | 0 | 0 | 0 | 0 | 0
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0
T set back | 0 | 0 | 0 | 0 | 0
Lighting (30%) | 0 | 0 | 0 | 0 | 0
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0
HRV | 0 | 0 | 0 | 0 | 0
DCV | 0 | 0 | 0 | 0 | 0
Cold Deck Reset | 0 | 0 | 0 | 0 | 0
VSD | 0 | 0 | 0 | 0 | 0
VSP | 0 | 0 | 0 | 0 | 0
Solar Wall | 0 | 0 | 0 | 0 | 0
Solar DHW | 0 | 0 | 0 | 0 | 0
DB Economizer | 0 | 0 | 0 | 0 | 0
COP | 0 | 0 | 0 | 0 | 0
Retro-commissioning | 0 | 0 | 0 | 0 | 0
3A-Active Warehouse (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 0
Roof | 0 | 0 | 0 | 0 | 0
Windows | 0 | 0 | 0 | 0 | 0
Air tightness | 0 | 0 | 0 | 0 | 0
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0
T set back | 0 | 0 | 0 | 0 | 0
Lighting (30%) | 0 | 0 | 0 | 0 | 0
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0
HRV | 0 | 0 | 0 | 0 | 0
DCV | 0 | 0 | 0 | 0 | 0
Cold Deck Reset | 0 | 0 | 0 | 0 | 0
VSD | 0 | 0 | 0 | 0 | 0
VSP | 0 | 0 | 0 | 0 | 0
Solar Wall | 0 | 0 | 0 | 0 | 0
Solar DHW | 0 | 0 | 0 | 0 | 0
DB Economizer | 0 | 0 | 0 | 0 | 0
COP | 0 | 0 | 0 | 0 | 0
Retro-commissioning | 0 | 0 | 0 | 0 | 0
3B-Storage Type Warehouse (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 893 | 0 | 0 | 893
Wall | 0 | 893 | 0 | 0 | 893
Roof | 0 | 893 | 0 | 0 | 893
Windows | 0 | 893 | 0 | 0 | 893
Air tightness | 0 | 893 | 0 | 0 | 893
T Reduction (2 DegC) | 0 | 893 | 0 | 0 | 893
T set back | 0 | 893 | 0 | 0 | 893
Lighting (30%) | 0 | 893 | 0 | 0 | 893
Occupancy Sensors (Lights/Plug Loads) | 0 | 893 | 0 | 0 | 893
HRV | 0 | 893 | 0 | 0 | 893
DCV | 0 | 893 | 0 | 0 | 893
Cold Deck Reset | 0 | 893 | 0 | 0 | 893
VSD | 0 | 893 | 0 | 0 | 893
VSP | 0 | 893 | 0 | 0 | 893
Solar Wall | 0 | 893 | 0 | 0 | 893
Solar DHW | 0 | 893 | 0 | 0 | 893
DB Economizer | 0 | 893 | 0 | 0 | 893
COP | 0 | 893 | 0 | 0 | 893
Retro-commissioning | 0 | 893 | 0 | 0 | 893
4A-Hotel Type Accomodation (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 2038 | 0 | 0 | 2038
Wall | 0 | 2038 | 0 | 0 | 2038
Roof | 0 | 2038 | 0 | 0 | 2038
Windows | 0 | 2038 | 0 | 0 | 2038
Air tightness | 0 | 2038 | 0 | 0 | 2038
T Reduction (2 DegC) | 0 | 2038 | 0 | 0 | 2038
T set back | 0 | 2038 | 0 | 0 | 2038
Lighting (30%) | 0 | 2038 | 0 | 0 | 2038
Occupancy Sensors (Lights/Plug Loads) | 0 | 2038 | 0 | 0 | 2038
HRV | 0 | 2038 | 0 | 0 | 2038
DCV | 0 | 2038 | 0 | 0 | 2038
Cold Deck Reset | 0 | 2038 | 0 | 0 | 2038
VSD | 0 | 2038 | 0 | 0 | 2038
VSP | 0 | 2038 | 0 | 0 | 2038
Solar Wall | 0 | 2038 | 0 | 0 | 2038
Solar DHW | 0 | 2038 | 0 | 0 | 2038
DB Economizer | 0 | 2038 | 0 | 0 | 2038
COP | 0 | 2038 | 0 | 0 | 2038
Retro-commissioning | 0 | 2038 | 0 | 0 | 2038
4B-Dormitory (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 12254 | 0 | 5246 | 17500
Wall | 0 | 12254 | 0 | 5246 | 17500
Roof | 0 | 12254 | 0 | 5246 | 17500
Windows | 0 | 12254 | 0 | 5246 | 17500
Air tightness | 0 | 12254 | 0 | 5246 | 17500
T Reduction (2 DegC) | 0 | 12254 | 0 | 5246 | 17500
T set back | 0 | 12254 | 0 | 5246 | 17500
Lighting (30%) | 0 | 12254 | 0 | 5246 | 17500
Occupancy Sensors (Lights/Plug Loads) | 0 | 12254 | 0 | 5246 | 17500
HRV | 0 | 12254 | 0 | 5246 | 17500
DCV | 0 | 12254 | 0 | 5246 | 17500
Cold Deck Reset | 0 | 12254 | 0 | 5246 | 17500
VSD | 0 | 12254 | 0 | 5246 | 17500
VSP | 0 | 12254 | 0 | 5246 | 17500
Solar Wall | 0 | 12254 | 0 | 5246 | 17500
Solar DHW | 0 | 12254 | 0 | 5246 | 17500
DB Economizer | 0 | 12254 | 0 | 5246 | 17500
COP | 0 | 12254 | 0 | 5246 | 17500
Retro-commissioning | 0 | 12254 | 0 | 5246 | 17500
4C-Barracks (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 10986 | 0 | 0 | 10986
Wall | 0 | 10986 | 0 | 0 | 10986
Roof | 0 | 10986 | 0 | 0 | 10986
Windows | 0 | 10986 | 0 | 0 | 10986
Air tightness | 0 | 10986 | 0 | 0 | 10986
T Reduction (2 DegC) | 0 | 10986 | 0 | 0 | 10986
T set back | 0 | 10986 | 0 | 0 | 10986
Lighting (30%) | 0 | 10986 | 0 | 0 | 10986
Occupancy Sensors (Lights/Plug Loads) | 0 | 10986 | 0 | 0 | 10986
HRV | 0 | 10986 | 0 | 0 | 10986
DCV | 0 | 10986 | 0 | 0 | 10986
Cold Deck Reset | 0 | 10986 | 0 | 0 | 10986
VSD | 0 | 10986 | 0 | 0 | 10986
VSP | 0 | 10986 | 0 | 0 | 10986
Solar Wall | 0 | 10986 | 0 | 0 | 10986
Solar DHW | 0 | 10986 | 0 | 0 | 10986
DB Economizer | 0 | 10986 | 0 | 0 | 10986
COP | 0 | 10986 | 0 | 0 | 10986
Retro-commissioning | 0 | 10986 | 0 | 0 | 10986
4D-Accomodation Building (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 4869 | 0 | 0 | 4869
Wall | 0 | 4869 | 0 | 0 | 4869
Roof | 0 | 4869 | 0 | 0 | 4869
Windows | 0 | 4869 | 0 | 0 | 4869
Air tightness | 0 | 4869 | 0 | 0 | 4869
T Reduction (2 DegC) | 0 | 4869 | 0 | 0 | 4869
T set back | 0 | 4869 | 0 | 0 | 4869
Lighting (30%) | 0 | 4869 | 0 | 0 | 4869
Occupancy Sensors (Lights/Plug Loads) | 0 | 4869 | 0 | 0 | 4869
HRV | 0 | 4869 | 0 | 0 | 4869
DCV | 0 | 4869 | 0 | 0 | 4869
Cold Deck Reset | 0 | 4869 | 0 | 0 | 4869
VSD | 0 | 4869 | 0 | 0 | 4869
VSP | 0 | 4869 | 0 | 0 | 4869
Solar Wall | 0 | 4869 | 0 | 0 | 4869
Solar DHW | 0 | 4869 | 0 | 0 | 4869
DB Economizer | 0 | 4869 | 0 | 0 | 4869
COP | 0 | 4869 | 0 | 0 | 4869
Retro-commissioning | 0 | 4869 | 0 | 0 | 4869
5A-Gym and Fitness Centre (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 0
Roof | 0 | 0 | 0 | 0 | 0
Windows | 0 | 0 | 0 | 0 | 0
Air tightness | 0 | 0 | 0 | 0 | 0
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0
T set back | 0 | 0 | 0 | 0 | 0
Lighting (30%) | 0 | 0 | 0 | 0 | 0
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0
HRV | 0 | 0 | 0 | 0 | 0
DCV | 0 | 0 | 0 | 0 | 0
Cold Deck Reset | 0 | 0 | 0 | 0 | 0
VSD | 0 | 0 | 0 | 0 | 0
VSP | 0 | 0 | 0 | 0 | 0
Solar Wall | 0 | 0 | 0 | 0 | 0
Solar DHW | 0 | 0 | 0 | 0 | 0
DB Economizer | 0 | 0 | 0 | 0 | 0
COP | 0 | 0 | 0 | 0 | 0
Retro-commissioning | 0 | 0 | 0 | 0 | 0
5C-Sports Centre (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 650 | 0 | 0 | 650
Wall | 0 | 650 | 0 | 0 | 650
Roof | 0 | 650 | 0 | 0 | 650
Windows | 0 | 650 | 0 | 0 | 650
Air tightness | 0 | 650 | 0 | 0 | 650
T Reduction (2 DegC) | 0 | 650 | 0 | 0 | 650
T set back | 0 | 650 | 0 | 0 | 650
Lighting (30%) | 0 | 650 | 0 | 0 | 650
Occupancy Sensors (Lights/Plug Loads) | 0 | 650 | 0 | 0 | 650
HRV | 0 | 650 | 0 | 0 | 650
DCV | 0 | 650 | 0 | 0 | 650
Cold Deck Reset | 0 | 650 | 0 | 0 | 650
VSD | 0 | 650 | 0 | 0 | 650
VSP | 0 | 650 | 0 | 0 | 650
Solar Wall | 0 | 650 | 0 | 0 | 650
Solar DHW | 0 | 650 | 0 | 0 | 650
DB Economizer | 0 | 650 | 0 | 0 | 650
COP | 0 | 650 | 0 | 0 | 650
Retro-commissioning | 0 | 650 | 0 | 0 | 650
` | 5D-Sports and Arena (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 0
Roof | 0 | 0 | 0 | 0 | 0
Windows | 0 | 0 | 0 | 0 | 0
Air tightness | 0 | 0 | 0 | 0 | 0
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0
T set back | 0 | 0 | 0 | 0 | 0
Lighting (30%) | 0 | 0 | 0 | 0 | 0
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0
HRV | 0 | 0 | 0 | 0 | 0
DCV | 0 | 0 | 0 | 0 | 0
Cold Deck Reset | 0 | 0 | 0 | 0 | 0
VSD | 0 | 0 | 0 | 0 | 0
VSP | 0 | 0 | 0 | 0 | 0
Solar Wall | 0 | 0 | 0 | 0 | 0
Solar DHW | 0 | 0 | 0 | 0 | 0
DB Economizer | 0 | 0 | 0 | 0 | 0
COP | 0 | 0 | 0 | 0 | 0
Retro-commissioning | 0 | 0 | 0 | 0 | 0
` | 6A-Office Building (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 0 | 0 | 1049 | 1049
Wall | 0 | 0 | 0 | 1049 | 1049
Roof | 0 | 0 | 0 | 1049 | 1049
Windows | 0 | 0 | 0 | 1049 | 1049
Air tightness | 0 | 0 | 0 | 1049 | 1049
T Reduction (2 DegC) | 0 | 0 | 0 | 1049 | 1049
T set back | 0 | 0 | 0 | 1049 | 1049
Lighting (30%) | 0 | 0 | 0 | 1049 | 1049
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 1049 | 1049
HRV | 0 | 0 | 0 | 1049 | 1049
DCV | 0 | 0 | 0 | 1049 | 1049
Cold Deck Reset | 0 | 0 | 0 | 1049 | 1049
VSD | 0 | 0 | 0 | 1049 | 1049
VSP | 0 | 0 | 0 | 1049 | 1049
Solar Wall | 0 | 0 | 0 | 1049 | 1049
Solar DHW | 0 | 0 | 0 | 1049 | 1049
DB Economizer | 0 | 0 | 0 | 1049 | 1049
COP | 0 | 0 | 0 | 1049 | 1049
Retro-commissioning | 0 | 0 | 0 | 1049 | 1049
` | 7A-Dining Hall (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 0
Roof | 0 | 0 | 0 | 0 | 0
Windows | 0 | 0 | 0 | 0 | 0
Air tightness | 0 | 0 | 0 | 0 | 0
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0
T set back | 0 | 0 | 0 | 0 | 0
Lighting (30%) | 0 | 0 | 0 | 0 | 0
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0
HRV | 0 | 0 | 0 | 0 | 0
DCV | 0 | 0 | 0 | 0 | 0
Cold Deck Reset | 0 | 0 | 0 | 0 | 0
VSD | 0 | 0 | 0 | 0 | 0
VSP | 0 | 0 | 0 | 0 | 0
Solar Wall | 0 | 0 | 0 | 0 | 0
Solar DHW | 0 | 0 | 0 | 0 | 0
DB Economizer | 0 | 0 | 0 | 0 | 0
COP | 0 | 0 | 0 | 0 | 0
Retro-commissioning | 0 | 0 | 0 | 0 | 0
` | 9A-Workshop Building (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 0 | 0 | 1289 | 1289
Wall | 0 | 0 | 0 | 1289 | 1289
Roof | 0 | 0 | 0 | 1289 | 1289
Windows | 0 | 0 | 0 | 1289 | 1289
Air tightness | 0 | 0 | 0 | 1289 | 1289
T Reduction (2 DegC) | 0 | 0 | 0 | 1289 | 1289
T set back | 0 | 0 | 0 | 1289 | 1289
Lighting (30%) | 0 | 0 | 0 | 1289 | 1289
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 1289 | 1289
HRV | 0 | 0 | 0 | 1289 | 1289
DCV | 0 | 0 | 0 | 1289 | 1289
Cold Deck Reset | 0 | 0 | 0 | 1289 | 1289
VSD | 0 | 0 | 0 | 1289 | 1289
VSP | 0 | 0 | 0 | 1289 | 1289
Solar Wall | 0 | 0 | 0 | 1289 | 1289
Solar DHW | 0 | 0 | 0 | 1289 | 1289
DB Economizer | 0 | 0 | 0 | 1289 | 1289
COP | 0 | 0 | 0 | 1289 | 1289
Retro-commissioning | 0 | 0 | 0 | 1289 | 1289
` | 11B-Retail Building (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 0
Roof | 0 | 0 | 0 | 0 | 0
Windows | 0 | 0 | 0 | 0 | 0
Air tightness | 0 | 0 | 0 | 0 | 0
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0
T set back | 0 | 0 | 0 | 0 | 0
Lighting (30%) | 0 | 0 | 0 | 0 | 0
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0
HRV | 0 | 0 | 0 | 0 | 0
DCV | 0 | 0 | 0 | 0 | 0
Cold Deck Reset | 0 | 0 | 0 | 0 | 0
VSD | 0 | 0 | 0 | 0 | 0
VSP | 0 | 0 | 0 | 0 | 0
Solar Wall | 0 | 0 | 0 | 0 | 0
Solar DHW | 0 | 0 | 0 | 0 | 0
DB Economizer | 0 | 0 | 0 | 0 | 0
COP | 0 | 0 | 0 | 0 | 0
Retro-commissioning | 0 | 0 | 0 | 0 | 0
` | 13B-Firehall (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 0
Roof | 0 | 0 | 0 | 0 | 0
Windows | 0 | 0 | 0 | 0 | 0
Air tightness | 0 | 0 | 0 | 0 | 0
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0
T set back | 0 | 0 | 0 | 0 | 0
Lighting (30%) | 0 | 0 | 0 | 0 | 0
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0
HRV | 0 | 0 | 0 | 0 | 0
DCV | 0 | 0 | 0 | 0 | 0
Cold Deck Reset | 0 | 0 | 0 | 0 | 0
VSD | 0 | 0 | 0 | 0 | 0
VSP | 0 | 0 | 0 | 0 | 0
Solar Wall | 0 | 0 | 0 | 0 | 0
Solar DHW | 0 | 0 | 0 | 0 | 0
DB Economizer | 0 | 0 | 0 | 0 | 0
COP | 0 | 0 | 0 | 0 | 0
Retro-commissioning | 0 | 0 | 0 | 0 | 0
Base Wide (m^2)
| V1 | V2 | V3 | V4 | Total
Base case | 0 | 31690 | 0 | 7584 | 39274
Wall | 0 | 31690 | 0 | 7584 | 39274
Roof | 0 | 31690 | 0 | 7584 | 39274
Windows | 0 | 31690 | 0 | 7584 | 39274
Air tightness | 0 | 31690 | 0 | 7584 | 39274
T Reduction (2 DegC) | 0 | 31690 | 0 | 7584 | 39274
T set back | 0 | 31690 | 0 | 7584 | 39274
Lighting (30%) | 0 | 31690 | 0 | 7584 | 39274
Occupancy Sensors (Lights/Plug Loads) | 0 | 31690 | 0 | 7584 | 39274
HRV | 0 | 31690 | 0 | 7584 | 39274
DCV | 0 | 31690 | 0 | 7584 | 39274
Cold Deck Reset | 0 | 31690 | 0 | 7584 | 39274
VSD | 0 | 31690 | 0 | 7584 | 39274
VSP | 0 | 31690 | 0 | 7584 | 39274
Solar Wall | 0 | 31690 | 0 | 7584 | 39274
Solar DHW | 0 | 31690 | 0 | 7584 | 39274
DB Economizer | 0 | 31690 | 0 | 7584 | 39274
COP | 0 | 31690 | 0 | 7584 | 39274
Retro-commissioning | 0 | 31690 | 0 | 7584 | 39274

## ecm$
Archetype 1A-Hanger ($/m2 floor area)
Exempler Building #607 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case
Wall Insulation: Additional RSI 1.32 on ext. | [7 empty] | 234.5388 |  |  |  | 234.5388 |  |  |  | 234.5388
Roof: Additional RSI 1.76 to 2.11 on exterior | [7 empty] | 198.0823 |  |  |  | 309.8852 |  |  |  | 309.8852
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 149.8765 |  |  |  | 125.7736 |  |  |  | 125.7736
Roof: Additional RSI 1.76 on ext, 2.11 on int. | [7 empty] | 295.9052 |  |  |  | 175.4 |  |  |  | 175.4
Windows: Double Glazed to Triple LowE |  |  |  | 87.3884 |  |  |  | 87.3884 |  |  |  | 87.3884 |  |  |  | 87.3884
Air tightness: vintage ACH to 0.27 ACH | [7 empty] | 14.7847 |  |  |  | 16.1877 |  |  |  | 16.1877
Heating setpoint reduction (2 DegC) |  |  |  | 1.1929 |  |  |  | 1.1929 |  |  |  | 1.1929 | 1.1929 | 1.1929 | 1.1929 | 1.1929
Temperature set back of 2 DegC afterhours |  |  |  | 1.1929 | 1.1929 | 1.1929 | 1.1929 | 1.1929 | 1.1929 | 1.1929 | 1.1929 | 1.1929 | 1.1929 | 1.1929 | 1.1929 | 1.1929
Lighting: 30% reduction from MNECB |  |  |  | 18.477 |  |  |  | 18.477 | 18.477 | 18.477 | 18.477 | 18.477 | 18.477 | 18.477 | 18.477 | 18.477
Occupancy Sensors (Lights/Plug Loads) |  |  |  | 0.64762 |  |  |  | 0.64762 | 0.64762 | 0.64762 | 0.64762 | 0.64762 | 0.64762 | 0.64762 | 0.64762 | 0.64762
HRV |  |  |  | 71.5384 |  |  |  | 71.5384 | 71.5384 | 71.5384 | 71.5384 | 71.5384 | 71.5384 | 71.5384 | 71.5384 | 71.5384
DCV for all occupied zones |  |  |  | 2.0413 |  |  |  | 2.0413 | 2.0413 | 2.0413 | 2.0413 | 2.0413 | 2.0413 | 2.0413 | 2.0413 | 2.0413
Cold Deck Reset to eliminate reheat |  |  |  | 1.984 |  |  |  | 1.984 | 1.984 | 1.984 | 1.984 | 1.984 | 1.984 | 1.984 | 1.984 | 1.984
VSD/VFD on large hp AHU |  |  |  | 0.94364 |  |  |  | 0.94364 | 0.94364 | 0.94364 | 0.94364 | 0.94364 | 0.94364 | 0.94364 | 0.94364 | 0.94364
VSP on large hp heating/cooling pumps |  |  |  | 3.0964 |  |  |  | 3.0964 | 3.0964 | 3.0964 | 3.0964 | 3.0964 | 3.0964 | 3.0964 | 3.0964 | 3.0964
Solar Wall for ventilation preheat | 3.2737 | 3.3996 | 1.2591 | 7.9324 | 3.2737 | 3.3996 | 1.2591 | 7.9324 | 3.2737 | 3.3996 | 1.2591 | 7.9324 | 3.2737 | 3.3996 | 1.2591 | 7.9324
Solar DHW |  |  |  | 5.2213 |  |  |  | 5.2213 | 5.2213 | 5.2213 | 5.2213 | 5.2213 | 5.2213 | 5.2213 | 5.2213 | 5.2213
Dry Bulb Economizer Control |  |  |  | 0.79411 |  |  |  | 0.79411 | 0.79411 | 0.79411 | 0.79411 | 0.79411 | 0.79411 | 0.79411 | 0.79411 | 0.79411
DX Cooling COP Upgrade to COP 4.0 |  |  |  | 1.0398 |  |  |  | 1.0398 | 1.0398 | 1.0398 | 1.0398 | 1.0398 | 1.0398 | 1.0398 | 1.0398 | 1.0398
Retro-commissioning on thermostats and AHU |  |  |  | 1.6457 |  |  |  | 1.6457 | 1.6457 | 1.6457 | 1.6457 | 1.6457 | 1.6457 | 1.6457 | 1.6457 | 1.6457
Archetype 2A-Training Building ($/m2 floor area)
Exempler Building #34 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case | 7.9414 | #REF! | 7.9414
Wall Insulation: Additional RSI 1.32 on ext. | 7.9414 | #REF! | 7.9414 |  |  |  |  | 123.1035 |  |  |  | 123.1035 |  |  |  | 123.1035
Roof: Additional RSI 1.76 to 2.11 on exterior | 7.9414 | #REF! | 7.9414 |  |  |  |  | 140.5233 |  |  |  | 219.8384 |  |  |  | 219.8384
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 106.3252 |  |  |  | 89.2262 |  |  |  | 89.2262
Roof: Additional RSI 1.76 on ext, 2.11 on int. | [7 empty] | 209.9207 |  |  |  | 124.4321 |  |  |  | 124.4321
Windows: Double Glazed to Triple LowE | 51.1264 | #REF! | 7.9414 | 43.1849 |  |  |  | 43.1849 |  |  |  | 43.1849 |  |  |  | 43.1849
Air tightness: vintage ACH to 0.27 ACH | 7.9414 | #REF! | 7.9414 |  |  |  |  | 24.9364 |  |  |  | 27.7885 |  |  |  | 27.7885
Heating setpoint reduction (2 DegC) | 12.9126 | #REF! | 7.9414 | 4.9712 |  |  |  | 4.9712 | 4.9712 | 4.9712 | 4.9712 | 4.9712 | 4.9712 | 4.9712 | 4.9712 | 4.9712
Temperature set back of 2 DegC afterhours | 12.9126 | #REF! | 7.9414 | 4.9712 | 4.9712 | 4.9712 | 4.9712 | 4.9712 | 4.9712 | 4.9712 | 4.9712 | 4.9712 | 4.9712 | 4.9712 | 4.9712 | 4.9712
Lighting: 30% reduction from MNECB | 46.1677 | #REF! | 7.9414 | 38.2262 |  |  |  | 38.2262 | 38.2262 | 38.2262 | 38.2262 | 38.2262 | 38.2262 | 38.2262 | 38.2262 | 38.2262
Occupancy Sensors (Lights/Plug Loads) | 10.6402 | #REF! | 7.9414 | 2.6988 |  |  |  | 2.7312 |  |  |  | 2.7312 |  |  |  | 2.7312
HRV | 70.2835 | #REF! | 7.9414 | 62.342 |  |  |  | 62.342 | 62.342 | 62.342 | 62.342 | 62.342 | 62.342 | 62.342 | 62.342 | 62.342
DCV for all occupied zones | 16.448 | #REF! | 7.9414 | 8.5066 |  |  |  | 8.5066 | 8.5066 | 8.5066 | 8.5066 | 8.5066 | 8.5066 | 8.5066 | 8.5066 | 8.5066
Cold Deck Reset to eliminate reheat | 11.2832 | #REF! | 7.9414 | 3.3418 |  |  |  | 3.3418 | 3.3418 | 3.3418 | 3.3418 | 3.3418 | 3.3418 | 3.3418 | 3.3418 | 3.3418
VSD/VFD on large hp AHU | 9.7529 | #REF! | 7.9414 | 1.8115 |  |  |  | 1.8115 | 1.8115 | 1.8115 | 1.8115 | 1.8115 | 1.8115 | 1.8115 | 1.8115 | 1.8115
VSP on large hp heating/cooling pumps | 9.8919 | #REF! | 7.9414 | 1.9505 |  |  |  | 1.9505 | 1.9505 | 1.9505 | 1.9505 | 1.9505 | 1.9505 | 1.9505 | 1.9505 | 1.9505
Solar Wall for ventilation preheat | 10.6187 | #REF! | 7.9414 | 2.6773 |  |  |  | 2.6773 |  |  |  | 2.6773 |  |  |  | 2.6773
Solar DHW | 17.7352 | #REF! | 7.9414 | 9.7937 |  |  |  | 9.7937 | 9.7937 | 9.7937 | 9.7937 | 9.7937 | 9.7937 | 9.7937 | 9.7937 | 9.7937
Dry Bulb Economizer Control | 9.279 | #REF! | 7.9414 | 1.3375 |  |  |  | 1.3375 | 1.3375 | 1.3375 | 1.3375 | 1.3375 | 1.3375 | 1.3375 | 1.3375 | 1.3375
DX Cooling COP Upgrade to COP 4.0 | 12.9546 | #REF! | 7.9414 | 5.0132 |  |  |  | 5.0132 | 5.0132 | 5.0132 | 5.0132 | 5.0132 | 5.0132 | 5.0132 | 5.0132 | 5.0132
Retro-commissioning on thermostats and AHU | 12.0291 | #REF! | 7.9414 | 4.0877 |  |  |  | 4.0877 | 4.0877 | 4.0877 | 4.0877 | 4.0877 | 4.0877 | 4.0877 | 4.0877 | 4.0877
10.73
Archetype 3A-Active Warehouse ($/m2 floor area)
Exempler Building #358 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case | 21.64 | #REF! | 21.64
Wall Insulation: Additional RSI 1.32 on ext. | 19.43 | #REF! | 19.43 |  |  |  |  | 154.4894 |  |  |  | 154.4894 |  |  |  | 154.4894
Roof: Additional RSI 1.76 to 2.11 on exterior | 19.83 | #REF! | 19.83 |  |  |  |  | 202.2334 |  |  |  | 316.3793 |  |  |  | 316.3793
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 153.0174 |  |  |  | 128.4093 |  |  |  | 128.4093
Roof: Additional RSI 1.76 on ext, 2.11 on int. | [7 empty] | 302.1063 |  |  |  | 179.0757 |  |  |  | 179.0757
Windows: Double Glazed to Triple LowE | 29.8725 | #REF! | 21.4 | 8.4725 |  |  |  | 8.4725 |  |  |  | 8.4725 |  |  |  | 8.4725
Air tightness: vintage ACH to 0.27 ACH | 21.64 | #REF! | 21.64 |  |  |  |  | 16.3416 |  |  |  | 17.7432 |  |  |  | 17.7432
Heating setpoint reduction (2 DegC) | 16.3556 | #REF! | 15.54 | 0.81557 |  |  |  | 0.81557 | 0.81557 | 0.81557 | 0.81557 | 0.81557 | 0.81557 | 0.81557 | 0.81557 | 0.81557
Temperature set back of 2 DegC afterhours | 22.4556 | #REF! | 21.64 | 0.81557 | 0.81557 | 0.81557 | 0.81557 | 0.81557 | 0.81557 | 0.81557 | 0.81557 | 0.81557 | 0.81557 | 0.81557 | 0.81557 | 0.81557
Lighting: 30% reduction from MNECB | 33.4349 | #REF! | 23.48 | 9.9549 |  |  |  | 9.9549 | 9.9549 | 9.9549 | 9.9549 | 9.9549 | 9.9549 | 9.9549 | 9.9549 | 9.9549
Occupancy Sensors (Lights/Plug Loads) | 22.0828 | #REF! | 21.64 | 0.44276 |  |  |  | 0.44276 | 0.44276 | 0.44276 | 0.44276 | 0.44276 | 0.44276 | 0.44276 | 0.44276 | 0.44276
HRV | 19.36 | #REF! | 19.36 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DCV for all occupied zones | 20.1856 | #REF! | 18.79 | 1.3956 |  |  |  | 1.3956 | 1.3956 | 1.3956 | 1.3956 | 1.3956 | 1.3956 | 1.3956 | 1.3956 | 1.3956
Cold Deck Reset to eliminate reheat | 23.7349 | #REF! | 21.64 | 2.0949 |  |  |  | 2.0949 | 2.0949 | 2.0949 | 2.0949 | 2.0949 | 2.0949 | 2.0949 | 2.0949 | 2.0949
VSD/VFD on large hp AHU | 27.16 | #REF! | 27.16 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VSP on large hp heating/cooling pumps | 21.64 | #REF! | 21.64 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Wall for ventilation preheat | 24.7271 | #REF! | 21.64 | 3.0871 |  |  |  | 3.0871 |  |  |  | 3.0871 |  |  |  | 3.0871
Solar DHW | 23.9781 | #REF! | 21.64 | 2.3381 |  |  |  | 2.3381 | 2.3381 | 2.3381 | 2.3381 | 2.3381 | 2.3381 | 2.3381 | 2.3381 | 2.3381
Dry Bulb Economizer Control | 22.538 | #REF! | 21.7 | 0.83796 |  |  |  | 0.83796 | 0.83796 | 0.83796 | 0.83796 | 0.83796 | 0.83796 | 0.83796 | 0.83796 | 0.83796
DX Cooling COP Upgrade to COP 4.0 | 22.6874 | #REF! | 21.64 | 1.0474 |  |  |  | 1.0474 | 1.0474 | 1.0474 | 1.0474 | 1.0474 | 1.0474 | 1.0474 | 1.0474 | 1.0474
Retro-commissioning on thermostats and AHU | 20.8841 | #REF! | 19.47 | 1.4141 |  |  |  | 1.4141 | 1.4141 | 1.4141 | 1.4141 | 1.4141 | 1.4141 | 1.4141 | 1.4141 | 1.4141
Archetype 3B-Warehouse ($/m2 floor area)
Exempler Building #239 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case | 0 | #REF! | 0
Wall Insulation: Additional RSI 1.32 on ext. | 0 | #REF! | 0 |  |  |  |  | 301.4226 |  |  |  | 301.4226 |  |  |  | 301.4226
Roof: Additional RSI 1.76 to 2.11 on exterior | [7 empty] | 222.4154 |  |  |  | 347.9526 |  |  |  | 347.9526
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 168.2878 |  |  |  | 141.224 |  |  |  | 141.224
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 0 | #REF! | 0 |  |  |  |  | 332.2551 |  |  |  | 196.9467 |  |  |  | 196.9467
Windows: Double Glazed to Triple LowE | 0 | #REF! | 0 | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Air tightness: vintage ACH to 0.27 ACH | 0 | #REF! | 0 |  |  |  |  | 87.1128 |  |  |  | 92.3112 |  |  |  | 92.3112
Heating setpoint reduction (2 DegC) | 1.6149 | #REF! | 0 | 1.6149 |  |  |  | 1.6149 | 1.6149 | 1.6149 | 1.6149 | 1.6149 | 1.6149 | 1.6149 | 1.6149 | 1.6149
Temperature set back of 2 DegC afterhours | 1.6149 | #REF! | 0 | 1.6149 | 1.6149 | 1.6149 | 1.6149 | 1.6149 | 1.6149 | 1.6149 | 1.6149 | 1.6149 | 1.6149 | 1.6149 | 1.6149 | 1.6149
Lighting: 30% reduction from MNECB | 7.8991 | #REF! | 0 | 7.8991 |  |  |  | 7.8991 | 7.8991 | 7.8991 | 7.8991 | 7.8991 | 7.8991 | 7.8991 | 7.8991 | 7.8991
Occupancy Sensors (Lights/Plug Loads) | 0.8767 | #REF! | 0 | 0.8767 |  |  |  | 0.8767 | 0.8767 | 0.8767 | 0.8767 | 0.8767 | 0.8767 | 0.8767 | 0.8767 | 0.8767
HRV | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DCV for all occupied zones | 2.7634 | #REF! | 0 | 2.7634 |  |  |  | 2.7634 | 2.7634 | 2.7634 | 2.7634 | 2.7634 | 2.7634 | 2.7634 | 2.7634 | 2.7634
Cold Deck Reset to eliminate reheat | 11.1271 | #REF! | 0 | 11.1271 |  |  |  | 11.1271 | 11.1271 | 11.1271 | 11.1271 | 11.1271 | 11.1271 | 11.1271 | 11.1271 | 11.1271
VSD/VFD on large hp AHU | 3.2403 | #REF! | 0 | 3.2403 |  |  |  | 3.2403 | 3.2403 | 3.2403 | 3.2403 | 3.2403 | 3.2403 | 3.2403 | 3.2403 | 3.2403
VSP on large hp heating/cooling pumps | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Wall for ventilation preheat | 7.1316 | #REF! | 0 | 7.1316 |  |  |  | 7.1316 | 7.1316 | 7.1316 | 7.1316 | 7.1316 | 7.1316 | 7.1316 | 7.1316 | 7.1316
Solar DHW | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dry Bulb Economizer Control | 4.4536 | #REF! | 0 | 4.4536 |  |  |  | 4.4536 | 4.4536 | 4.4536 | 4.4536 | 4.4536 | 4.4536 | 4.4536 | 4.4536 | 4.4536
DX Cooling COP Upgrade to COP 4.0 | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retro-commissioning on thermostats and AHU | 7.2591 | #REF! | 0 | 7.2591 |  |  |  | 7.2591 | 7.2591 | 7.2591 | 7.2591 | 7.2591 | 7.2591 | 7.2591 | 7.2591 | 7.2591
Archetype 4A-Hotel Accomodation ($/m2 floor area)
Exempler Building #414 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case | 0 | #REF! | 0
Wall Insulation: Additional RSI 1.32 on ext. | 0 | #REF! | 0 |  |  |  |  | 83.1481 |  |  |  | 83.1481 |  |  |  | 83.1481
Roof: Additional RSI 1.76 to 2.11 on exterior | [7 empty] | 105.2928 |  |  |  | 164.7228 |  |  |  | 164.7228
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 79.6684 |  |  |  | 66.8563 |  |  |  | 66.8563
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 0 | #REF! | 0 |  |  |  |  | 157.2915 |  |  |  | 93.2357 |  |  |  | 93.2357
Windows: Double Glazed to Triple LowE | 74.0905 | #REF! | 0 | 74.0905 |  |  |  | 74.0905 |  |  |  | 74.0905 |  |  |  | 74.0905
Air tightness: vintage ACH to 0.27 ACH | 0 | #REF! | 0 |  |  |  |  | 22.6608 |  |  |  | 24.8947 |  |  |  | 24.8947
Heating setpoint reduction (2 DegC) | 11.132 | #REF! | 0 | 11.132 |  |  |  | 11.132 | 11.132 | 11.132 | 11.132 | 11.132 | 11.132 | 11.132 | 11.132 | 11.132
Temperature set back of 2 DegC afterhours | 11.132 | #REF! | 0 | 11.132 |  |  |  | 11.132 | 11.132 | 11.132 | 11.132 | 11.132 | 11.132 | 11.132 | 11.132 | 11.132
Lighting: 30% reduction from MNECB | 18.4237 | #REF! | 0 | 18.4237 |  |  |  | 18.4237 | 18.4237 | 18.4237 | 18.4237 | 18.4237 | 18.4237 | 18.4237 | 18.4237 | 18.4237
Occupancy Sensors (Lights/Plug Loads) | 6.0434 | #REF! | 0 | 6.0434 |  |  |  | 6.0434 | 6.0434 | 6.0434 | 6.0434 | 6.0434 | 6.0434 | 6.0434 | 6.0434 | 6.0434
HRV | 65.0422 | #REF! | 0 | 65.0422 |  |  |  | 65.0422 | 65.0422 | 65.0422 | 65.0422 | 65.0422 | 65.0422 | 65.0422 | 65.0422 | 65.0422
DCV for all occupied zones | 19.0488 | #REF! | 0 | 19.0488 |  |  |  | 19.0488 | 19.0488 | 19.0488 | 19.0488 | 19.0488 | 19.0488 | 19.0488 | 19.0488 | 19.0488
Cold Deck Reset to eliminate reheat | 0.87162 | #REF! | 0 | 0.87162 |  |  |  | 0.87162 | 0.87162 | 0.87162 | 0.87162 | 0.87162 | 0.87162 | 0.87162 | 0.87162 | 0.87162
VSD/VFD on large hp AHU | 0.68345 | #REF! | 0 | 0.68345 |  |  |  | 0.68345 | 0.68345 | 0.68345 | 0.68345 | 0.68345 | 0.68345 | 0.68345 | 0.68345 | 0.68345
VSP on large hp heating/cooling pumps | 2.8893 | #REF! | 0 | 2.8893 |  |  |  | 2.8893 | 2.8893 | 2.8893 | 2.8893 | 2.8893 | 2.8893 | 2.8893 | 2.8893 | 2.8893
Solar Wall for ventilation preheat | 4.5622 | #REF! | 0 | 4.5622 |  |  |  | 4.5622 | 4.5622 | 4.5622 | 4.5622 | 4.5622 | 4.5622 | 4.5622 | 4.5622 | 4.5622
Solar DHW | 102.1793 | #REF! | 0 | 102.1793 |  |  |  | 102.1793 | 102.1793 | 102.1793 | 102.1793 | 102.1793 | 102.1793 | 102.1793 | 102.1793 | 102.1793
Dry Bulb Economizer Control | 0.34887 | #REF! | 0 | 0.34887 |  |  |  | 0.34887 | 0.34887 | 0.34887 | 0.34887 | 0.34887 | 0.34887 | 0.34887 | 0.34887 | 0.34887
DX Cooling COP Upgrade to COP 4.0 | 3.1975 | #REF! | 0 | 3.1975 |  |  |  | 3.1975 | 3.1975 | 3.1975 | 3.1975 | 3.1975 | 3.1975 | 3.1975 | 3.1975 | 3.1975
Retro-commissioning on thermostats and AHU | 11.4863 | #REF! | 0 | 11.4863 |  |  |  | 11.4863 | 11.4863 | 11.4863 | 11.4863 | 11.4863 | 11.4863 | 11.4863 | 11.4863 | 11.4863
Archetype 4B-Dormitory ($/m2 floor area)
Exempler Building #111 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case | 0 | #REF! | 0
Wall Insulation: Additional RSI 1.32 on ext. | 0 | #REF! | 0 |  |  |  |  | 175.5089 |  |  |  | 175.5089 |  |  |  | 175.5089
Roof: Additional RSI 1.76 to 2.11 on exterior | [7 empty] | 70.1836 |  |  |  | 109.7971 |  |  |  | 109.7971
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 53.1036 |  |  |  | 44.5635 |  |  |  | 44.5635
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 0 | #REF! | 0 |  |  |  |  | 104.8438 |  |  |  | 62.1469 |  |  |  | 62.1469
Windows: Double Glazed to Triple LowE | 128.8464 | #REF! | 0 | 128.8464 |  |  |  | 128.8464 |  |  |  | 128.8464 |  |  |  | 128.8464
Air tightness: vintage ACH to 0.27 ACH | 0 | #REF! | 0 |  |  |  |  | 31.4818 |  |  |  | 34.6528 |  |  |  | 34.6528
Heating setpoint reduction (2 DegC) | 14.326 | #REF! | 0 | 14.326 |  |  |  | 14.326 | 14.326 | 14.326 | 14.326 | 14.326 | 14.326 | 14.326 | 14.326 | 14.326
Temperature set back of 2 DegC afterhours | 14.326 | #REF! | 0 | 14.326 |  |  |  | 14.326 | 14.326 | 14.326 | 14.326 | 14.326 | 14.326 | 14.326 | 14.326 | 14.326
Lighting: 30% reduction from MNECB | 18.0825 | #REF! | 0 | 18.0825 |  |  |  | 18.0825 | 18.0825 | 18.0825 | 18.0825 | 18.0825 | 18.0825 | 18.0825 | 18.0825 | 18.0825
Occupancy Sensors (Lights/Plug Loads) | 7.7774 | #REF! | 0 | 7.7774 |  |  |  | 7.7774 | 7.7774 | 7.7774 | 7.7774 | 7.7774 | 7.7774 | 7.7774 | 7.7774 | 7.7774
HRV | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DCV for all occupied zones | 24.5143 | #REF! | 0 | 24.5143 |  |  |  | 24.5143 | 24.5143 | 24.5143 | 24.5143 | 24.5143 | 24.5143 | 24.5143 | 24.5143 | 24.5143
Cold Deck Reset to eliminate reheat | 1.371 | #REF! | 0 | 1.371 |  |  |  | 1.371 | 1.371 | 1.371 | 1.371 | 1.371 | 1.371 | 1.371 | 1.371 | 1.371
VSD/VFD on large hp AHU | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VSP on large hp heating/cooling pumps | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Wall for ventilation preheat | 0 | #REF! | 0
Solar DHW | 50.5115 | #REF! | 0 | 50.5115 |  |  |  | 50.5115 | 50.5115 | 50.5115 | 50.5115 | 50.5115 | 50.5115 | 50.5115 | 50.5115 | 50.5115
Dry Bulb Economizer Control | 0.54874 | #REF! | 0 | 0.54874 |  |  |  | 0.54874 | 0.54874 | 0.54874 | 0.54874 | 0.54874 | 0.54874 | 0.54874 | 0.54874 | 0.54874
DX Cooling COP Upgrade to COP 4.0 | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retro-commissioning on thermostats and AHU | 10.0173 | #REF! | 0 | 10.0173 |  |  |  | 10.0173 | 10.0173 | 10.0173 | 10.0173 | 10.0173 | 10.0173 | 10.0173 | 10.0173 | 10.0173
Archetype 4C-Barracks ($/m2 floor area)
Exempler Building #231 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case | 0 | #REF! | 0
Wall Insulation: Additional RSI 1.32 on ext. | 0 | #REF! | 0 |  |  |  |  | 238.1549 |  |  |  | 238.1549 |  |  |  | 238.1549
Roof: Additional RSI 1.76 to 2.11 on exterior | [7 empty] | 210.55 |  |  |  | 329.39 |  |  |  | 329.39
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 159.31 |  |  |  | 133.69 |  |  |  | 133.69
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 0 | #REF! | 0 |  |  |  |  | 314.53 |  |  |  | 186.44 |  |  |  | 186.44
Windows: Double Glazed to Triple LowE | 66.7681 | #REF! | 0 | 66.7681 |  |  |  | 66.7681 |  |  |  | 66.7681 |  |  |  | 66.7681
Air tightness: vintage ACH to 0.27 ACH | 0 | #REF! | 0 |  |  |  |  | 59.8662 |  |  |  | 66.5537 |  |  |  | 66.5537
Heating setpoint reduction (2 DegC) | 2.8288 | #REF! | 0 | 2.8288 |  |  |  | 2.8288 | 2.8288 | 2.8288 | 2.8288 | 2.8288 | 2.8288 | 2.8288 | 2.8288 | 2.8288
Temperature set back of 2 DegC afterhours | 2.8288 | #REF! | 0 | 2.8288 |  |  |  | 2.8288 | 2.8288 | 2.8288 | 2.8288 | 2.8288 | 2.8288 | 2.8288 | 2.8288 | 2.8288
Lighting: 30% reduction from MNECB | 18.4573 | #REF! | 0 | 18.4573 |  |  |  | 18.4573 | 18.4573 | 18.4573 | 18.4573 | 18.4573 | 18.4573 | 18.4573 | 18.4573 | 18.4573
Occupancy Sensors (Lights/Plug Loads) | 1.5357 | #REF! | 0 | 1.5357 |  |  |  | 1.5357 | 1.5357 | 1.5357 | 1.5357 | 1.5357 | 1.5357 | 1.5357 | 1.5357 | 1.5357
HRV | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DCV for all occupied zones | 4.8407 | #REF! | 0 | 4.8407 |  |  |  | 4.8407 | 4.8407 | 4.8407 | 4.8407 | 4.8407 | 4.8407 | 4.8407 | 4.8407 | 4.8407
Cold Deck Reset to eliminate reheat | 4.8729 | #REF! | 0 | 4.8729 |  |  |  | 4.8729 | 4.8729 | 4.8729 | 4.8729 | 4.8729 | 4.8729 | 4.8729 | 4.8729 | 4.8729
VSD/VFD on large hp AHU | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VSP on large hp heating/cooling pumps | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Wall for ventilation preheat | 6.2463 | #REF! | 0 | 6.2463 |  |  |  | 6.2463 | 6.2463 | 6.2463 | 6.2463 | 6.2463 | 6.2463 | 6.2463 | 6.2463 | 6.2463
Solar DHW | 81.6065 | #REF! | 0 | 81.6065 |  |  |  | 81.6065 | 81.6065 | 81.6065 | 81.6065 | 81.6065 | 81.6065 | 81.6065 | 81.6065 | 81.6065
Dry Bulb Economizer Control | 1.9504 | #REF! | 0 | 1.9504 |  |  |  | 1.9504 | 1.9504 | 1.9504 | 1.9504 | 1.9504 | 1.9504 | 1.9504 | 1.9504 | 1.9504
DX Cooling COP Upgrade to COP 4.0 | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retro-commissioning on thermostats and AHU | 4.1327 | #REF! | 0 | 4.1327 |  |  |  | 4.1327 | 4.1327 | 4.1327 | 4.1327 | 4.1327 | 4.1327 | 4.1327 | 4.1327 | 4.1327
Archetype 4D-Accomodation Bldg ($/m2 floor area)
Exempler Building #260 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case | 0 | #REF! | 0
Wall Insulation: Additional RSI 1.32 on ext. | 0 | #REF! | 0 |  |  |  |  | 379.4191 |  |  |  | 379.4191 |  |  |  | 379.4191
Roof: Additional RSI 1.76 to 2.11 on exterior | 0 | #REF! | 0 |  |  |  |  | 232.4361 |  |  |  | 363.6291 |  |  |  | 363.6291
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 175.8698 |  |  |  | 175.8698 |  |  |  | 147.5867
Roof: Additional RSI 1.76 on ext, 2.11 on int. | [7 empty] | 347.2245 |  |  |  | 205.8199 |  |  |  | 205.8199
Windows: Double Glazed to Triple LowE | 111.2726 | #REF! | 0 | 111.2726 |  |  |  | 111.2726 |  |  |  | 111.2726 |  |  |  | 111.2726
Air tightness: vintage ACH to 0.27 ACH | 0 | #REF! | 0 |  |  |  |  | 111.0801 |  |  |  | 121.2078 |  |  |  | 121.2078
Heating setpoint reduction (2 DegC) | 31.7976 | #REF! | 0 | 31.7976 |  |  |  | 31.7976 | 31.7976 | 31.7976 | 31.7976 | 31.7976 | 31.7976 | 31.7976 | 31.7976 | 31.7976
Temperature set back of 2 DegC afterhours | 31.7976 | #REF! | 0 | 31.7976 |  |  |  | 31.7976 | 31.7976 | 31.7976 | 31.7976 | 31.7976 | 31.7976 | 31.7976 | 31.7976 | 31.7976
Lighting: 30% reduction from MNECB | 18.5864 | #REF! | 0 | 18.5864 |  |  |  | 18.5864 | 18.5864 | 18.5864 | 18.5864 | 18.5864 | 18.5864 | 18.5864 | 18.5864 | 18.5864
Occupancy Sensors (Lights/Plug Loads) | 17.2625 | #REF! | 0 | 17.2625 |  |  |  | 17.2625 | 17.2625 | 17.2625 | 17.2625 | 17.2625 | 17.2625 | 17.2625 | 17.2625 | 17.2625
HRV | 468.774 | #REF! | 0 | 468.774 |  |  |  | 468.774 | 468.774 | 468.774 | 468.774 | 468.774 | 468.774 | 468.774 | 468.774 | 468.774
DCV for all occupied zones | 54.4115 | #REF! | 0 | 54.4115 |  |  |  | 54.4115 | 54.4115 | 54.4115 | 54.4115 | 54.4115 | 54.4115 | 54.4115 | 54.4115 | 54.4115
Cold Deck Reset to eliminate reheat | 24.344 | #REF! | 0 | 24.344 |  |  |  | 24.344 | 24.344 | 24.344 | 24.344 | 24.344 | 24.344 | 24.344 | 24.344 | 24.344
VSD/VFD on large hp AHU | 13.1963 | #REF! | 0 | 13.1963 |  |  |  | 13.1963 | 13.1963 | 13.1963 | 13.1963 | 13.1963 | 13.1963 | 13.1963 | 13.1963 | 13.1963
VSP on large hp heating/cooling pumps | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Wall for ventilation preheat | 28.0846 | #REF! | 0 | 28.0846 |  |  |  | 28.0846 | 28.0846 | 28.0846 | 28.0846 | 28.0846 | 28.0846 | 28.0846 | 28.0846 | 28.0846
Solar DHW | 122.3064 | #REF! | 0 | 122.3064 |  |  |  | 122.3064 | 122.3064 | 122.3064 | 122.3064 | 122.3064 | 122.3064 | 122.3064 | 122.3064 | 122.3064
Dry Bulb Economizer Control | 9.7437 | #REF! | 0 | 9.7437 |  |  |  | 9.7437 | 9.7437 | 9.7437 | 9.7437 | 9.7437 | 9.7437 | 9.7437 | 9.7437 | 9.7437
DX Cooling COP Upgrade to COP 4.0 | 36.5199 | #REF! | 0 | 36.5199 |  |  |  | 36.5199 | 36.5199 | 36.5199 | 36.5199 | 36.5199 | 36.5199 | 36.5199 | 36.5199 | 36.5199
Retro-commissioning on thermostats and AHU | 26.9986 | #REF! | 0 | 26.9986 |  |  |  | 26.9986 | 26.9986 | 26.9986 | 26.9986 | 26.9986 | 26.9986 | 26.9986 | 26.9986 | 26.9986
Archetype 5A-Gym/Fitness Centre ($/m2 floor area)
Exempler Building #58 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case | 0 | #REF! | 0
Wall Insulation: Additional RSI 1.32 on ext. | 0 | #REF! | 0 |  |  |  |  | 121.7849 |  |  |  | 121.7849 |  |  |  | 121.7849
Roof: Additional RSI 1.76 to 2.11 on exterior | 0 | #REF! | 0 |  |  |  |  | 169.2442 |  |  |  | 264.7701 |  |  |  | 264.7701
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 128.0565 |  |  |  | 107.4626 |  |  |  | 107.4626
Roof: Additional RSI 1.76 on ext, 2.11 on int. | [7 empty] | 252.8254 |  |  |  | 149.8641 |  |  |  | 149.8641
Windows: Double Glazed to Triple LowE | 35.4164 | #REF! | 0 | 35.4164 |  |  |  | 35.4164 |  |  |  | 35.4164 |  |  |  | 35.4164
Air tightness: vintage ACH to 0.27 ACH | 0 | #REF! | 0 |  |  |  |  | 10.4947 |  |  |  | 11.4477 |  |  |  | 11.4477
Heating setpoint reduction (2 DegC) | 1.9468 | #REF! | 0 | 1.9468 |  |  |  | 1.9468 | 1.9468 | 1.9468 | 1.9468 | 1.9468 | 1.9468 | 1.9468 | 1.9468 | 1.9468
Temperature set back of 2 DegC afterhours | 1.9468 | #REF! | 0 | 1.9468 |  |  |  | 1.9468 | 1.9468 | 1.9468 | 1.9468 | 1.9468 | 1.9468 | 1.9468 | 1.9468 | 1.9468
Lighting: 30% reduction from MNECB | 24.8076 | #REF! | 0 | 24.8076 |  |  |  | 24.8076 | 24.8076 | 24.8076 | 24.8076 | 24.8076 | 24.8076 | 24.8076 | 24.8076 | 24.8076
Occupancy Sensors (Lights/Plug Loads) | 1.0569 | #REF! | 0 | 1.0569 |  |  |  | 1.0569 | 1.0569 | 1.0569 | 1.0569 | 1.0569 | 1.0569 | 1.0569 | 1.0569 | 1.0569
HRV | 142.7667 | #REF! | 0 | 142.7667 |  |  |  | 142.7667 | 142.7667 | 142.7667 | 142.7667 | 142.7667 | 142.7667 | 142.7667 | 142.7667 | 142.7667
DCV for all occupied zones | 3.3314 | #REF! | 0 | 3.3314 |  |  |  | 3.3314 | 3.3314 | 3.3314 | 3.3314 | 3.3314 | 3.3314 | 3.3314 | 3.3314 | 3.3314
Cold Deck Reset to eliminate reheat | 2.5797 | #REF! | 0 | 2.5797 |  |  |  | 2.5797 | 2.5797 | 2.5797 | 2.5797 | 2.5797 | 2.5797 | 2.5797 | 2.5797 | 2.5797
VSD/VFD on large hp AHU | 1.6436 | #REF! | 0 | 1.6436 |  |  |  | 1.6436 | 1.6436 | 1.6436 | 1.6436 | 1.6436 | 1.6436 | 1.6436 | 1.6436 | 1.6436
VSP on large hp heating/cooling pumps | 2.0228 | #REF! | 0 | 2.0228 |  |  |  | 2.0228 | 2.0228 | 2.0228 | 2.0228 | 2.0228 | 2.0228 | 2.0228 | 2.0228 | 2.0228
Solar Wall for ventilation preheat | 4.409 | #REF! | 0 | 4.409 |  |  |  | 4.409 | 4.409 | 4.409 | 4.409 | 4.409 | 4.409 | 4.409 | 4.409 | 4.409
Solar DHW | 5.1842 | #REF! | 0 | 5.1842 |  |  |  | 5.1842 | 5.1842 | 5.1842 | 5.1842 | 5.1842 | 5.1842 | 5.1842 | 5.1842 | 5.1842
Dry Bulb Economizer Control | 1.0325 | #REF! | 0 | 1.0325 |  |  |  | 1.0325 | 1.0325 | 1.0325 | 1.0325 | 1.0325 | 1.0325 | 1.0325 | 1.0325 | 1.0325
DX Cooling COP Upgrade to COP 4.0 | 8.3447 | #REF! | 0 | 8.3447 |  |  |  | 8.3447 | 8.3447 | 8.3447 | 8.3447 | 8.3447 | 8.3447 | 8.3447 | 8.3447 | 8.3447
Retro-commissioning on thermostats and AHU | 2.5917 | #REF! | 0 | 2.5917 |  |  |  | 2.5917 | 2.5917 | 2.5917 | 2.5917 | 2.5917 | 2.5917 | 2.5917 | 2.5917 | 2.5917
Archetype 5C-Sports Centre ($/m2 floor area)
Exempler Building #362 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case | 0 | #REF! | 0
Wall Insulation: Additional RSI 1.32 on ext. | 0 | #REF! | 0 |  |  |  |  | 186.2082 |  |  |  | 186.2082 |  |  |  | 186.2082
Roof: Additional RSI 1.76 to 2.11 on exterior | 0 | #REF! | 0 |  |  |  |  | 187.7463 |  |  |  | 293.7153 |  |  |  | 293.7153
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 142.0559 |  |  |  | 119.2107 |  |  |  | 119.2107
Roof: Additional RSI 1.76 on ext, 2.11 on int. | [7 empty] | 280.4648 |  |  |  | 166.2476 |  |  |  | 166.2476
Windows: Double Glazed to Triple LowE | 44.6772 | #REF! | 0 | 44.6772 |  |  |  | 44.6772 |  |  |  | 44.6772 |  |  |  | 44.6772
Air tightness: vintage ACH to 0.27 ACH | 0 | #REF! | 0 |  |  |  |  | 18.0331 |  |  |  | 19.7443 |  |  |  | 19.7443
Heating setpoint reduction (2 DegC) | 2.2507 | #REF! | 0 | 2.2507 |  |  |  | 2.2507 | 2.2507 | 2.2507 | 2.2507 | 2.2507 | 2.2507 | 2.2507 | 2.2507 | 2.2507
Temperature set back of 2 DegC afterhours | 2.2507 | #REF! | 0 | 2.2507 |  |  |  | 2.2507 | 2.2507 | 2.2507 | 2.2507 | 2.2507 | 2.2507 | 2.2507 | 2.2507 | 2.2507
Lighting: 30% reduction from MNECB | 25.1382 | #REF! | 0 | 25.1382 |  |  |  | 25.1382 | 25.1382 | 25.1382 | 25.1382 | 25.1382 | 25.1382 | 25.1382 | 25.1382 | 25.1382
Occupancy Sensors (Lights/Plug Loads) | 1.2219 | #REF! | 0 | 1.2219 |  |  |  | 1.2219 | 1.2219 | 1.2219 | 1.2219 | 1.2219 | 1.2219 | 1.2219 | 1.2219 | 1.2219
HRV | 52.3135 | #REF! | 0 | 52.3135 |  |  |  | 52.3135 | 52.3135 | 52.3135 | 52.3135 | 52.3135 | 52.3135 | 52.3135 | 52.3135 | 52.3135
DCV for all occupied zones | 3.8514 | #REF! | 0 | 3.8514 |  |  |  | 3.8514 | 3.8514 | 3.8514 | 3.8514 | 3.8514 | 3.8514 | 3.8514 | 3.8514 | 3.8514
Cold Deck Reset to eliminate reheat | 3.1017 | #REF! | 0 | 3.1017 |  |  |  | 3.1017 | 3.1017 | 3.1017 | 3.1017 | 3.1017 | 3.1017 | 3.1017 | 3.1017 | 3.1017
VSD/VFD on large hp AHU | 1.0635 | #REF! | 0 | 1.0635 |  |  |  | 1.0635 | 1.0635 | 1.0635 | 1.0635 | 1.0635 | 1.0635 | 1.0635 | 1.0635 | 1.0635
VSP on large hp heating/cooling pumps | 6.8543 | #REF! | 0 | 6.8543 |  |  |  | 6.8543 | 6.8543 | 6.8543 | 6.8543 | 6.8543 | 6.8543 | 6.8543 | 6.8543 | 6.8543
Solar Wall for ventilation preheat | 11.044 | #REF! | 0 | 11.044 |  |  |  | 11.044 | 11.044 | 11.044 | 11.044 | 11.044 | 11.044 | 11.044 | 11.044 | 11.044
Solar DHW | 3.4629 | #REF! | 0 | 3.4629 |  |  |  | 3.4629 | 3.4629 | 3.4629 | 3.4629 | 3.4629 | 3.4629 | 3.4629 | 3.4629 | 3.4629
Dry Bulb Economizer Control | 1.5471 | #REF! | 0 | 1.5471 |  |  |  | 1.5471 | 1.5471 | 1.5471 | 1.5471 | 1.5471 | 1.5471 | 1.5471 | 1.5471 | 1.5471
DX Cooling COP Upgrade to COP 4.0 | 6.8948 | #REF! | 0 | 6.8948 |  |  |  | 6.8948 | 6.8948 | 6.8948 | 6.8948 | 6.8948 | 6.8948 | 6.8948 | 6.8948 | 6.8948
Retro-commissioning on thermostats and AHU | 4.0469 | #REF! | 0 | 4.0469 |  |  |  | 4.0469 | 4.0469 | 4.0469 | 4.0469 | 4.0469 | 4.0469 | 4.0469 | 4.0469 | 4.0469
Archetype 5D-Sports and Arena ($/m2 floor area)
Exempler Building #405 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case | 0 | #REF! | 0
Wall Insulation: Additional RSI 1.32 on ext. | 0 | #REF! | 0 |  |  |  |  | 454.1983 |  |  |  | 454.1983 |  |  |  | 454.1983
Roof: Additional RSI 1.76 to 2.11 on exterior | 0 | #REF! | 0 |  |  |  |  | 210.55 |  |  |  | 329.39 |  |  |  | 329.39
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 159.31 |  |  |  | 133.69 |  |  |  | 133.69
Roof: Additional RSI 1.76 on ext, 2.11 on int. | [7 empty] | 314.53 |  |  |  | 186.44 |  |  |  | 186.44
Windows: Double Glazed to Triple LowE | 45.7054 | #REF! | 0 | 45.7054 |  |  |  | 45.7054 |  |  |  | 45.7054 |  |  |  | 45.7054
Air tightness: vintage ACH to 0.27 ACH | 0 | #REF! | 0 |  |  |  |  | 51.5651 |  |  |  | 56.4157 |  |  |  | 56.4157
Heating setpoint reduction (2 DegC) | 0 | #REF! | 0
Temperature set back of 2 DegC afterhours | 0 | #REF! | 0
Lighting: 30% reduction from MNECB | 0 | #REF! | 0
Occupancy Sensors (Lights/Plug Loads) | 0 | #REF! | 0
HRV | 0 | #REF! | 0
DCV for all occupied zones | 0 | #REF! | 0
Cold Deck Reset to eliminate reheat | 0 | #REF! | 0
VSD/VFD on large hp AHU | 0 | #REF! | 0
VSP on large hp heating/cooling pumps | 0 | #REF! | 0
Solar Wall for ventilation preheat | 0 | #REF! | 0
Solar DHW | 0 | #REF! | 0
Dry Bulb Economizer Control | 0 | #REF! | 0
DX Cooling COP Upgrade to COP 4.0 | 0 | #REF! | 0
Retro-commissioning on thermostats and AHU | 0 | #REF! | 0
Archetype 6A-Office Building ($/m2 floor area)
Exempler Building #56 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case | 0 | #REF! | 0
Wall Insulation: Additional RSI 1.32 on ext. | 0 | #REF! | 0 |  |  |  |  | 237.8235 |  |  |  | 237.8235 |  |  |  | 237.8235
Roof: Additional RSI 1.76 to 2.11 on exterior | 0 | #REF! | 0 |  |  |  |  | 221.6735 |  |  |  | 346.7919 |  |  |  | 346.7919
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 167.7265 |  |  |  | 140.7529 |  |  |  | 140.7529
Roof: Additional RSI 1.76 on ext, 2.11 on int. | [7 empty] | 331.1469 |  |  |  | 196.2898 |  |  |  | 196.2898
Windows: Double Glazed to Triple LowE | 109.8959 | #REF! | 0 | 109.8959 |  |  |  | 109.8959 |  |  |  | 109.8959 |  |  |  | 109.8959
Air tightness: vintage ACH to 0.27 ACH | 0 | #REF! | 0 |  |  |  |  | 22.8156 |  |  |  | 24.8255 |  |  |  | 24.8255
Heating setpoint reduction (2 DegC) | 6.9111 | #REF! | 0 | 6.9111 |  |  |  | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111
Temperature set back of 2 DegC afterhours | 6.9111 | #REF! | 0 | 6.9111 |  |  |  | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111 | 6.9111
Lighting: 30% reduction from MNECB | 32.8859 | #REF! | 0 | 32.8859 |  |  |  | 32.8859 | 32.8859 | 32.8859 | 32.8859 | 32.8859 | 32.8859 | 32.8859 | 32.8859 | 32.8859
Occupancy Sensors (Lights/Plug Loads) | 3.752 | #REF! | 0 | 3.752 |  |  |  | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752 | 3.752
HRV | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DCV for all occupied zones | 11.8262 | #REF! | 0 | 11.8262 |  |  |  | 11.8262 | 11.8262 | 11.8262 | 11.8262 | 11.8262 | 11.8262 | 11.8262 | 11.8262 | 11.8262
Cold Deck Reset to eliminate reheat | 0.83544 | #REF! | 0 | 0.83544 |  |  |  | 0.83544 | 0.83544 | 0.83544 | 0.83544 | 0.83544 | 0.83544 | 0.83544 | 0.83544 | 0.83544
VSD/VFD on large hp AHU | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VSP on large hp heating/cooling pumps | 0.81885 | #REF! | 0 | 0.81885 |  |  |  | 0.81885 | 0.81885 | 0.81885 | 0.81885 | 0.81885 | 0.81885 | 0.81885 | 0.81885 | 0.81885
Solar Wall for ventilation preheat | 0 | #REF! | 0
Solar DHW | 11.1928 | #REF! | 0 | 11.1928 |  |  |  | 11.1928 | 11.1928 | 11.1928 | 11.1928 | 11.1928 | 11.1928 | 11.1928 | 11.1928 | 11.1928
Dry Bulb Economizer Control | 0.33439 | #REF! | 0 | 0.33439 |  |  |  | 0.33439 | 0.33439 | 0.33439 | 0.33439 | 0.33439 | 0.33439 | 0.33439 | 0.33439 | 0.33439
DX Cooling COP Upgrade to COP 4.0 | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retro-commissioning on thermostats and AHU | 5.2867 | #REF! | 0 | 5.2867 |  |  |  | 5.2867 | 5.2867 | 5.2867 | 5.2867 | 5.2867 | 5.2867 | 5.2867 | 5.2867 | 5.2867
Archetype 7A-Dining Hall ($/m2 floor area)
Exempler Building #120 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case | 0 | #REF! | 0
Wall Insulation: Additional RSI 1.32 on ext. | 0 | #REF! | 0 |  |  |  |  | 82.3316 |  |  |  | 82.3316 |  |  |  | 82.3316
Roof: Additional RSI 1.76 to 2.11 on exterior | 0 | #REF! | 0 |  |  |  |  | 186.134 |  |  |  | 291.193 |  |  |  | 291.193
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 140.836 |  |  |  | 118.1869 |  |  |  | 118.1869
Roof: Additional RSI 1.76 on ext, 2.11 on int. | [7 empty] | 278.0562 |  |  |  | 164.8199 |  |  |  | 164.8199
Windows: Double Glazed to Triple LowE | 37.3852 | #REF! | 0 | 37.3852 |  |  |  | 37.3852 |  |  |  | 37.3852 |  |  |  | 37.3852
Air tightness: vintage ACH to 0.27 ACH | 0 | #REF! | 0 |  |  |  |  | 20.2326 |  |  |  | 22.4599 |  |  |  | 22.4599
Heating setpoint reduction (2 DegC) | 2.138 | #REF! | 0 | 2.138 |  |  |  | 2.138 | 2.138 | 2.138 | 2.138 | 2.138 | 2.138 | 2.138 | 2.138 | 2.138
Temperature set back of 2 DegC afterhours | 2.138 | #REF! | 0 | 2.138 |  |  |  | 2.138 | 2.138 | 2.138 | 2.138 | 2.138 | 2.138 | 2.138 | 2.138 | 2.138
Lighting: 30% reduction from MNECB | 36.1831 | #REF! | 0 | 36.1831 |  |  |  | 36.1831 | 36.1831 | 36.1831 | 36.1831 | 36.1831 | 36.1831 | 36.1831 | 36.1831 | 36.1831
Occupancy Sensors (Lights/Plug Loads) | 1.1607 | #REF! | 0 | 1.1607 |  |  |  | 1.1607 | 1.1607 | 1.1607 | 1.1607 | 1.1607 | 1.1607 | 1.1607 | 1.1607 | 1.1607
HRV | 24.3291 | #REF! | 0 | 24.3291 |  |  |  | 24.3291 | 24.3291 | 24.3291 | 24.3291 | 24.3291 | 24.3291 | 24.3291 | 24.3291 | 24.3291
DCV for all occupied zones | 3.6584 | #REF! | 0 | 3.6584 |  |  |  | 3.6584 | 3.6584 | 3.6584 | 3.6584 | 3.6584 | 3.6584 | 3.6584 | 3.6584 | 3.6584
Cold Deck Reset to eliminate reheat | 2.7621 | #REF! | 0 | 2.7621 |  |  |  | 2.7621 | 2.7621 | 2.7621 | 2.7621 | 2.7621 | 2.7621 | 2.7621 | 2.7621 | 2.7621
VSD/VFD on large hp AHU | 0.3157 | #REF! | 0 | 0.3157 |  |  |  | 0.3157 | 0.3157 | 0.3157 | 0.3157 | 0.3157 | 0.3157 | 0.3157 | 0.3157 | 0.3157
VSP on large hp heating/cooling pumps | 3.9544 | #REF! | 0 | 3.9544 |  |  |  | 3.9544 | 3.9544 | 3.9544 | 3.9544 | 3.9544 | 3.9544 | 3.9544 | 3.9544 | 3.9544
Solar Wall for ventilation preheat | 3.2455 | #REF! | 0 | 3.2455 |  |  |  | 3.2455 | 3.2455 | 3.2455 | 3.2455 | 3.2455 | 3.2455 | 3.2455 | 3.2455 | 3.2455
Solar DHW | 15.419 | #REF! | 0 | 15.419 |  |  |  | 15.419 | 15.419 | 15.419 | 15.419 | 15.419 | 15.419 | 15.419 | 15.419 | 15.419
Dry Bulb Economizer Control | 0.96104 | #REF! | 0 | 0.96104 |  |  |  | 0.96104 | 0.96104 | 0.96104 | 0.96104 | 0.96104 | 0.96104 | 0.96104 | 0.96104 | 0.96104
DX Cooling COP Upgrade to COP 4.0 | 4.7588 | #REF! | 0 | 4.7588 |  |  |  | 4.7588 | 4.7588 | 4.7588 | 4.7588 | 4.7588 | 4.7588 | 4.7588 | 4.7588 | 4.7588
Retro-commissioning on thermostats and AHU | 3.4237 | #REF! | 0 | 3.4237 |  |  |  | 3.4237 | 3.4237 | 3.4237 | 3.4237 | 3.4237 | 3.4237 | 3.4237 | 3.4237 | 3.4237
Archetype 9A-Workshop ($/m2 floor area)
Exempler Building #152 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case | 374.29 | #REF! | 374.29
Wall Insulation: Additional RSI 1.32 on ext. | 363.84 | #REF! | 363.84 |  |  |  |  | 236.4727 |  |  |  | 236.4727 |  |  |  | 236.4727
Roof: Additional RSI 1.76 to 2.11 on exterior | 367.38 | #REF! | 367.38 |  |  |  |  | 214.1938 |  |  |  | 335.0904 |  |  |  | 335.0904
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 162.067 |  |  |  | 136.0036 |  |  |  | 136.0036
Roof: Additional RSI 1.76 on ext, 2.11 on int. | [7 empty] | 319.9733 |  |  |  | 189.6665 |  |  |  | 189.6665
Windows: Double Glazed to Triple LowE | 409.0651 | #REF! | 373.47 | 35.5951 |  |  |  | 35.5951 |  |  |  | 35.5951 |  |  |  | 35.5951
Air tightness: vintage ACH to 0.27 ACH | 374.29 | #REF! | 374.29 |  |  |  |  | 22.8663 |  |  |  | 24.7923 |  |  |  | 24.7923
Heating setpoint reduction (2 DegC) | 321.6135 | #REF! | 319.74 | 1.8735 |  |  |  | 1.8735 | 1.8735 | 1.8735 | 1.8735 | 1.8735 | 1.8735 | 1.8735 | 1.8735 | 1.8735
Temperature set back of 2 DegC afterhours | 332.6535 | #REF! | 330.78 | 1.8735 |  |  |  | 1.8735 | 1.8735 | 1.8735 | 1.8735 | 1.8735 | 1.8735 | 1.8735 | 1.8735 | 1.8735
Lighting: 30% reduction from MNECB | 407.6587 | #REF! | 388.2 | 19.4587 |  |  |  | 19.4587 | 19.4587 | 19.4587 | 19.4587 | 19.4587 | 19.4587 | 19.4587 | 19.4587 | 19.4587
Occupancy Sensors (Lights/Plug Loads) | 375.3071 | #REF! | 374.29 | 1.0171 |  |  |  | 1.0171 | 1.0171 | 1.0171 | 1.0171 | 1.0171 | 1.0171 | 1.0171 | 1.0171 | 1.0171
HRV | 457.3867 | #REF! | 369.27 | 88.1167 |  |  |  | 88.1167 | 88.1167 | 88.1167 | 88.1167 | 88.1167 | 88.1167 | 88.1167 | 88.1167 | 88.1167
DCV for all occupied zones | 377.4959 | #REF! | 374.29 | 3.2059 |  |  |  | 3.2059 | 3.2059 | 3.2059 | 3.2059 | 3.2059 | 3.2059 | 3.2059 | 3.2059 | 3.2059
Cold Deck Reset to eliminate reheat | 377.5173 | #REF! | 374.29 | 3.2273 |  |  |  | 3.2273 | 3.2273 | 3.2273 | 3.2273 | 3.2273 | 3.2273 | 3.2273 | 3.2273 | 3.2273
VSD/VFD on large hp AHU | 375.3966 | #REF! | 374.29 | 1.1066 |  |  |  | 1.1066 | 1.1066 | 1.1066 | 1.1066 | 1.1066 | 1.1066 | 1.1066 | 1.1066 | 1.1066
VSP on large hp heating/cooling pumps | 377.4532 | #REF! | 374.29 | 3.1632 |  |  |  | 3.1632 | 3.1632 | 3.1632 | 3.1632 | 3.1632 | 3.1632 | 3.1632 | 3.1632 | 3.1632
Solar Wall for ventilation preheat | 384.6321 | #REF! | 374.29 | 10.3421 |  |  |  | 10.3421 | 10.3421 | 10.3421 | 10.3421 | 10.3421 | 10.3421 | 10.3421 | 10.3421 | 10.3421
Solar DHW | 379.157 | #REF! | 371.05 | 8.107 |  |  |  | 8.107 | 8.107 | 8.107 | 8.107 | 8.107 | 8.107 | 8.107 | 8.107 | 8.107
Dry Bulb Economizer Control | 375.9829 | #REF! | 374.86 | 1.1229 |  |  |  | 1.1229 | 1.1229 | 1.1229 | 1.1229 | 1.1229 | 1.1229 | 1.1229 | 1.1229 | 1.1229
DX Cooling COP Upgrade to COP 4.0 | 380.2095 | #REF! | 374.29 | 5.9195 |  |  |  | 5.9195 | 5.9195 | 5.9195 | 5.9195 | 5.9195 | 5.9195 | 5.9195 | 5.9195 | 5.9195
Retro-commissioning on thermostats and AHU | 340.9992 | #REF! | 337.42 | 3.5792 |  |  |  | 3.5792 | 3.5792 | 3.5792 | 3.5792 | 3.5792 | 3.5792 | 3.5792 | 3.5792 | 3.5792
Archetype 11A-Retail Building ($/m2 floor area)
Exempler Building #119 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case | 0 | #REF! | 0
Wall Insulation: Additional RSI 1.32 on ext. | 0 | #REF! | 0 |  |  |  |  | 246.6607 |  |  |  | 246.6607 |  |  |  | 246.6607
Roof: Additional RSI 1.76 to 2.11 on exterior | [7 empty] | 210.55 |  |  |  | 329.39 |  |  |  | 329.39
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 159.31 |  |  |  | 133.69 |  |  |  | 133.69
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 0 | #REF! | 0 |  |  |  |  | 314.53 |  |  |  | 186.44 |  |  |  | 186.44
Windows: Double Glazed to Triple LowE | 186.2711 | #REF! | 0 | 186.2711 |  |  |  | 186.2711 |  |  |  | 186.2711 |  |  |  | 186.2711
Air tightness: vintage ACH to 0.27 ACH | 0 | #REF! | 0 |  |  |  |  | 58.3527 |  |  |  | 63.9352 |  |  |  | 63.9352
Heating setpoint reduction (2 DegC) | 12.9767 | #REF! | 0 | 12.9767 |  |  |  | 12.9767 | 12.9767 | 12.9767 | 12.9767 | 12.9767 | 12.9767 | 12.9767 | 12.9767 | 12.9767
Temperature set back of 2 DegC afterhours | 12.9767 | #REF! | 0 | 12.9767 |  |  |  | 12.9767 | 12.9767 | 12.9767 | 12.9767 | 12.9767 | 12.9767 | 12.9767 | 12.9767 | 12.9767
Lighting: 30% reduction from MNECB | 45.3263 | #REF! | 0 | 45.3263 |  |  |  | 45.3263 | 45.3263 | 45.3263 | 45.3263 | 45.3263 | 45.3263 | 45.3263 | 45.3263 | 45.3263
Occupancy Sensors (Lights/Plug Loads) | 7.0449 | #REF! | 0 | 7.0449 |  |  |  | 7.0449 | 7.0449 | 7.0449 | 7.0449 | 7.0449 | 7.0449 | 7.0449 | 7.0449 | 7.0449
HRV | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DCV for all occupied zones | 22.2055 | #REF! | 0 | 22.2055 |  |  |  | 22.2055 | 22.2055 | 22.2055 | 22.2055 | 22.2055 | 22.2055 | 22.2055 | 22.2055 | 22.2055
Cold Deck Reset to eliminate reheat | 22.3535 | #REF! | 0 | 22.3535 |  |  |  | 22.3535 | 22.3535 | 22.3535 | 22.3535 | 22.3535 | 22.3535 | 22.3535 | 22.3535 | 22.3535
VSD/VFD on large hp AHU | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VSP on large hp heating/cooling pumps | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Wall for ventilation preheat | 7.1634 | #REF! | 0 | 7.1634 |  |  |  | 7.1634 | 7.1634 | 7.1634 | 7.1634 | 7.1634 | 7.1634 | 7.1634 | 7.1634 | 7.1634
Solar DHW | 24.9568 | #REF! | 0 | 24.9568 |  |  |  | 24.9568 | 24.9568 | 24.9568 | 24.9568 | 24.9568 | 24.9568 | 24.9568 | 24.9568 | 24.9568
Dry Bulb Economizer Control | 8.947 | #REF! | 0 | 8.947 |  |  |  | 8.947 | 8.947 | 8.947 | 8.947 | 8.947 | 8.947 | 8.947 | 8.947 | 8.947
DX Cooling COP Upgrade to COP 4.0 | 0 | #REF! | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retro-commissioning on thermostats and AHU | 13.6107 | #REF! | 0 | 13.6107 |  |  |  | 13.6107 | 13.6107 | 13.6107 | 13.6107 | 13.6107 | 13.6107 | 13.6107 | 13.6107 | 13.6107
Archetype 13A-Firehall ($/m2 floor area)
Exempler Building #19 | V1: Post-2004 |  |  |  | V2: 1980-2004 |  |  |  | V3: 1960-1979 |  |  |  | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2) | Total Cost ($/m2)
Base case | 227.46 | #REF! | 227.46
Wall Insulation: Additional RSI 1.32 on ext. | 219.82 | #REF! | 219.82 |  |  |  |  | 212.3694 |  |  |  | 212.3694 |  |  |  | 212.3694
Roof: Additional RSI 1.76 to 2.11 on exterior | 215.04 | #REF! | 215.04 |  |  |  |  | 161.8078 |  |  |  | 253.1364 |  |  |  | 253.1364
Roof: Additional RSI 2.11 to 3.52 on interior | [7 empty] | 122.4298 |  |  |  | 102.7408 |  |  |  | 102.7408
Roof: Additional RSI 1.76 on ext, 2.11 on int. | [7 empty] | 241.7164 |  |  |  | 143.2792 |  |  |  | 143.2792
Windows: Double Glazed to Triple LowE | 278.1949 | #REF! | 226.6 | 51.5949 |  |  |  | 51.5949 |  |  |  | 51.5949 |  |  |  | 51.5949
Air tightness: vintage ACH to 0.27 ACH | 227.46 | #REF! | 227.46 |  |  |  |  | 49.7388 |  |  |  | 53.0997 |  |  |  | 53.0997
Heating setpoint reduction (2 DegC) | 186.5583 | #REF! | 180.98 | 5.5783 |  |  |  | 5.5783 | 5.5783 | 5.5783 | 5.5783 | 5.5783 | 5.5783 | 5.5783 | 5.5783 | 5.5783
Temperature set back of 2 DegC afterhours | 214.5883 | #REF! | 209.01 | 5.5783 |  |  |  | 5.5783 | 5.5783 | 5.5783 | 5.5783 | 5.5783 | 5.5783 | 5.5783 | 5.5783 | 5.5783
Lighting: 30% reduction from MNECB | 265.891 | #REF! | 248.53 | 17.361 |  |  |  | 17.361 | 17.361 | 17.361 | 17.361 | 17.361 | 17.361 | 17.361 | 17.361 | 17.361
Occupancy Sensors (Lights/Plug Loads) | 230.4884 | #REF! | 227.46 | 3.0284 |  |  |  | 3.0284 | 3.0284 | 3.0284 | 3.0284 | 3.0284 | 3.0284 | 3.0284 | 3.0284 | 3.0284
HRV | 259.7303 | #REF! | 179.44 | 80.2903 |  |  |  | 80.2903 | 80.2903 | 80.2903 | 80.2903 | 80.2903 | 80.2903 | 80.2903 | 80.2903 | 80.2903
DCV for all occupied zones | 237.0054 | #REF! | 227.46 | 9.5454 |  |  |  | 9.5454 | 9.5454 | 9.5454 | 9.5454 | 9.5454 | 9.5454 | 9.5454 | 9.5454 | 9.5454
Cold Deck Reset to eliminate reheat | 230.4994 | #REF! | 227.46 | 3.0394 |  |  |  | 3.0394 | 3.0394 | 3.0394 | 3.0394 | 3.0394 | 3.0394 | 3.0394 | 3.0394 | 3.0394
VSD/VFD on large hp AHU | 228.6581 | #REF! | 227.46 | 1.1981 |  |  |  | 1.1981 | 1.1981 | 1.1981 | 1.1981 | 1.1981 | 1.1981 | 1.1981 | 1.1981 | 1.1981
VSP on large hp heating/cooling pumps | 227.46 | #REF! | 227.46 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Wall for ventilation preheat | 236.418 | #REF! | 227.46 | 8.958 |  |  |  | 8.958 | 8.958 | 8.958 | 8.958 | 8.958 | 8.958 | 8.958 | 8.958 | 8.958
Solar DHW | 240.5137 | #REF! | 220.16 | 20.3537 |  |  |  | 20.3537 | 20.3537 | 20.3537 | 20.3537 | 20.3537 | 20.3537 | 20.3537 | 20.3537 | 20.3537
Dry Bulb Economizer Control | 228.6758 | #REF! | 227.46 | 1.2158 |  |  |  | 1.2158 | 1.2158 | 1.2158 | 1.2158 | 1.2158 | 1.2158 | 1.2158 | 1.2158 | 1.2158
DX Cooling COP Upgrade to COP 4.0 | 238.6044 | #REF! | 227.46 | 11.1444 |  |  |  | 11.1444 | 11.1444 | 11.1444 | 11.1444 | 11.1444 | 11.1444 | 11.1444 | 11.1444 | 11.1444
Retro-commissioning on thermostats and AHU | 213.3566 | #REF! | 206.29 | 7.0666 |  |  |  | 7.0666 | 7.0666 | 7.0666 | 7.0666 | 7.0666 | 7.0666 | 7.0666 | 7.0666 | 7.0666
Note on A14: khaddad: 10% reduction in lighting and plug loads
Note on A17: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A23: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A24: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A39: khaddad: 10% reduction in lighting and plug loads
Note on A42: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A48: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A49: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A64: khaddad: 10% reduction in lighting and plug loads
Note on A67: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A73: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A74: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A89: khaddad: 10% reduction in lighting and plug loads
Note on A92: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A98: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A99: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A114: khaddad: 10% reduction in lighting and plug loads
Note on A117: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A123: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A124: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A139: khaddad: 10% reduction in lighting and plug loads
Note on A142: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A148: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A149: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A164: khaddad: 10% reduction in lighting and plug loads
Note on A167: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A173: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A174: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A189: khaddad: 10% reduction in lighting and plug loads
Note on A192: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A198: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A199: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A214: khaddad: 10% reduction in lighting and plug loads
Note on A217: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A223: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A224: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A239: khaddad: 10% reduction in lighting and plug loads
Note on A242: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A248: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A249: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A264: khaddad: 10% reduction in lighting and plug loads
Note on A267: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A273: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A274: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A289: khaddad: 10% reduction in lighting and plug loads
Note on A292: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A298: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A299: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A314: khaddad: 10% reduction in lighting and plug loads
Note on A317: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A323: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A324: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A339: khaddad: 10% reduction in lighting and plug loads
Note on A342: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A348: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A349: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A364: khaddad: 10% reduction in lighting and plug loads
Note on A367: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A373: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A374: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A389: khaddad: 10% reduction in lighting and plug loads
Note on A392: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A398: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A399: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw

## Energy$
Archetype 1A: Hanger |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: # 607 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 1 | 1 | 10.6805 | 1.882 | 12.5625 | 17.115 | 2.6463 | 19.7613 | 17.4318 | 4.3826 | 21.8144 | 10.834 | 5.5362 | 16.3702 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 1 | 1 | 10.2101 | 1.8228 | 12.0329 | 16.6379 | 2.5136 | 19.1515 | 16.9521 | 4.1694 | 21.1215 | 10.3541 | 5.2094 | 15.5635 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 1 | 1 | 10.2101 | 1.8228 | 12.0329 | 16.6379 | 2.5136 | 19.1515 | 16.9521 | 4.1694 | 21.1215 | 10.3541 | 5.2094 | 15.5635 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 1 | 1 | 10.2101 | 1.8228 | 12.0329 | 16.6379 | 2.5136 | 19.1515 | 16.9521 | 4.1694 | 21.1215 | 10.3541 | 5.2094 | 15.5635 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 1 | 1 | 10.21 | 1.8136 | 12.0235 | 16.6244 | 2.2543 | 18.8787 | 16.9484 | 3.6653 | 20.6136 | 10.3514 | 4.816 | 15.1674 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 1 | 1 | 10.2016 | 1.8316 | 12.0332 | 16.6347 | 2.5995 | 19.2342 | 16.9523 | 4.3338 | 21.2861 | 10.3542 | 5.5169 | 15.8711 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 1 | 1 | 10.6805 | 1.882 | 12.5625 | 16.5236 | 2.4634 | 18.987 | 16.9514 | 4.1269 | 21.0783 | 10.3472 | 5.0893 | 15.4365 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 1 | 1 | 10.252 | 1.6873 | 11.9394 | 16.6255 | 2.377 | 19.0024 | 16.9424 | 3.9854 | 20.9279 | 10.3439 | 5.1787 | 15.5226 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 1 | 1 | 10.196 | 1.7483 | 11.9443 | 16.6313 | 2.4721 | 19.1035 | 16.9477 | 4.1347 | 21.0825 | 10.3497 | 5.3544 | 15.7041 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 1 | 1 | 8.6536 | 1.9748 | 10.6283 | 15.1784 | 2.7588 | 17.9372 | 15.5124 | 4.5201 | 20.0325 | 8.9152 | 5.629 | 14.5442 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 1 | 0 | 9.6124 | 1.882 | 11.4944 | 15.4035 | 2.6463 | 18.0498 | 15.6886 | 4.3826 | 20.0712 | 9.7506 | 5.5362 | 15.2868 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 1 | 1 | 10.3169 | 1.227 | 11.5439 | 16.6336 | 1.9242 | 18.5578 | 16.9514 | 4.3625 | 21.3139 | 10.3844 | 5.5193 | 15.9036 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 1 | 1 | 10.1662 | 1.2446 | 11.4108 | 16.6115 | 1.9212 | 18.5327 | 16.9447 | 4.3817 | 21.3265 | 10.3515 | 5.5347 | 15.8861 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 1 | 1 | 10.2615 | 1.8256 | 12.0871 | 16.602 | 2.631 | 19.233 | 16.9511 | 4.3826 | 21.3338 | 10.3531 | 5.5362 | 15.8893 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 1 | 1 | 10.6805 | 1.882 | 12.5625 | 16.6017 | 2.6481 | 19.2498 | 16.9499 | 4.3815 | 21.3314 | 10.3532 | 5.5345 | 15.8877 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 1 | 1 | 8.5778 | 1.882 | 10.4598 | 12.1567 | 2.784 | 14.9407 | 11.8733 | 4.5734 | 16.4467 | 10.3536 | 5.5362 | 15.8898 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 1 | 1 | 10.7169 | 1.7412 | 12.4581 | 17.1511 | 2.5055 | 19.6566 | 17.4675 | 4.2418 | 21.7093 | 10.8706 | 5.3954 | 16.266 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 1 | 1 | 10.6864 | 1.8468 | 12.5332 | 17.1206 | 2.6111 | 19.7317 | 17.437 | 4.3474 | 21.7845 | 10.8401 | 5.501 | 16.3411 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 1 | 1 | 10.2276 | 1.881 | 12.1086 | 16.5647 | 2.6425 | 19.2072 | 16.9477 | 4.3688 | 21.3166 | 10.3519 | 5.5171 | 15.869 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 1 | 1 | 10.6805 | 1.882 | 12.5625 | 16.3974 | 2.6435 | 19.0409 | 16.9342 | 4.3695 | 21.3036 | 10.3372 | 5.5362 | 15.8734 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 1 | 0 | 9.6124 | 1.6938 | 11.3062 | 15.4035 | 2.3817 | 17.7852 | 15.6886 | 3.9444 | 19.633 | 9.7506 | 4.9826 | 14.7331 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 2A: Training Building |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: # 34 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 1 | 1 | 7.4162 | 2.5757 | 9.9919 | 7.901 | 3.7651 | 11.666 | 9.2298 | 5.4798 | 14.7097 | 9.8231 | 6.4053 | 16.2284 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 1 | 1 | 7.4128 | 2.5075 | 9.9203 | 7.8377 | 3.5961 | 11.4338 | 9.0784 | 5.2914 | 14.3698 | 9.6039 | 6.1333 | 15.7372 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 1 | 1 | 7.4128 | 2.5075 | 9.9203 | 7.8377 | 3.5961 | 11.4338 | 9.0784 | 5.2914 | 14.3698 | 9.6039 | 6.1333 | 15.7372 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 1 | 1 | 7.4128 | 2.5075 | 9.9203 | 7.8377 | 3.5961 | 11.4338 | 9.0784 | 5.2914 | 14.3698 | 9.6039 | 6.1333 | 15.7372 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 1 | 1 | 7.3902 | 2.3856 | 9.7758 | 7.6275 | 3.2977 | 10.9252 | 7.9258 | 4.0086 | 11.9344 | 8.4773 | 4.8678 | 13.3451 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 1 | 1 | 7.4162 | 2.5629 | 9.9791 | 7.9021 | 3.7299 | 11.632 | 9.2129 | 5.4499 | 14.6628 | 9.7948 | 6.3561 | 16.1509 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 1 | 1 | 7.4162 | 2.5757 | 9.9919 | 7.8479 | 3.0871 | 10.9349 | 8.4908 | 4.2924 | 12.7832 | 8.5823 | 4.4173 | 12.9996 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 1 | 1 | 7.3416 | 2.0466 | 9.3882 | 7.8309 | 3.0809 | 10.9118 | 9.179 | 4.5909 | 13.7699 | 9.77 | 5.3975 | 15.1675 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 1 | 1 | 7.3529 | 2.1052 | 9.4581 | 7.8388 | 3.1559 | 10.9948 | 9.1846 | 4.7171 | 13.9018 | 9.7734 | 4.9458 | 14.7191 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 1 | 1 | 5.7099 | 2.7649 | 8.4748 | 6.3653 | 3.8151 | 10.1804 | 7.7857 | 5.6122 | 13.3979 | 8.3857 | 6.5414 | 14.9272 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 1 | 1 | 6.8817 | 2.5757 | 9.4574 | 7.3687 | 3.7651 | 11.1338 | 8.6965 | 5.4798 | 14.1763 | 9.2886 | 6.4053 | 15.6939 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 1 | 1 | 7.467 | 1.6367 | 9.1037 | 7.9179 | 2.7906 | 10.7085 | 9.2276 | 4.5064 | 13.734 | 9.822 | 5.4256 | 15.2475 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 1 | 1 | 7.4162 | 2.0733 | 9.4895 | 7.901 | 3.0377 | 10.9386 | 9.2298 | 4.4095 | 13.6393 | 9.7734 | 5.1498 | 14.9232 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 0 | 0 | 7.1936 | 2.5757 | 9.7692 | 7.6637 | 3.7651 | 11.4287 | 8.9519 | 5.4798 | 14.4317 | 9.8231 | 6.4053 | 16.2284 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 1 | 1 | 6.3266 | 2.7221 | 9.0487 | 6.533 | 3.9489 | 10.4819 | 6.8979 | 5.7933 | 12.6911 | 7.0626 | 6.7764 | 13.839 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 0 | 0 | 4.9449 | 2.5757 | 7.5205 | 5.4296 | 3.7649 | 9.1946 | 6.7585 | 5.4798 | 12.2384 | 7.3518 | 6.4053 | 13.7571 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 1 | 0 | 7.5021 | 2.5387 | 10.0408 | 7.9868 | 3.7281 | 11.715 | 9.3157 | 5.4429 | 14.7586 | 9.909 | 6.3684 | 16.2774 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 1 | 1 | 7.4286 | 2.5089 | 9.9375 | 7.9134 | 3.6983 | 11.6117 | 9.2423 | 5.4131 | 14.6554 | 9.8355 | 6.3386 | 16.1741 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 1 | 1 | 7.3823 | 2.5757 | 9.958 | 7.8727 | 3.7651 | 11.6378 | 9.2185 | 5.4798 | 14.6984 | 9.814 | 6.4053 | 16.2194 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 1 | 1 | 7.4162 | 2.5757 | 9.9919 | 7.8196 | 3.7649 | 11.5845 | 9.0615 | 5.4798 | 14.5413 | 9.57 | 6.4053 | 15.9753 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 1 | 1 | 7.2071 | 2.3309 | 9.538 | 7.6456 | 3.4014 | 11.047 | 8.84 | 4.9447 | 13.7847 | 9.3734 | 5.7778 | 15.1511 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 3A: Active Warehouse |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: # 358 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 1 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 3B: Storage Warehouse |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: # 239 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 1 | 1 | 2.9502 | 1.1687 | 4.1189 | 2.84 | 1.643 | 4.483 | 3.0614 | 2.4966 | 5.558 | 3.3764 | 3.2389 | 6.6153 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 1 | 1 | 2.9281 | 1.1176 | 4.0457 | 2.8047 | 1.5075 | 4.3122 | 3.0118 | 2.3323 | 5.3442 | 3.2872 | 2.943 | 6.2302 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 1 | 1 | 2.9281 | 1.1176 | 4.0457 | 2.8047 | 1.5075 | 4.3122 | 3.0118 | 2.3323 | 5.3442 | 3.2872 | 2.943 | 6.2302 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 1 | 1 | 2.9281 | 1.1176 | 4.0457 | 2.8047 | 1.5075 | 4.3122 | 3.0118 | 2.3323 | 5.3442 | 3.2872 | 2.943 | 6.2302 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 1 | 1 | 2.9171 | 1.103 | 4.0201 | 2.7772 | 1.4628 | 4.24 | 2.9656 | 2.2083 | 5.1739 | 3.1188 | 2.4802 | 5.599 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 1 | 0 | 2.9502 | 1.1687 | 4.1189 | 2.84 | 1.643 | 4.483 | 3.0614 | 2.4966 | 5.558 | 3.3764 | 3.2389 | 6.6153 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 1 | 0 | 2.9502 | 1.1687 | 4.1189 | 2.84 | 1.643 | 4.483 | 3.0614 | 2.4966 | 5.558 | 3.3764 | 3.2389 | 6.6153 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 1 | 1 | 2.7945 | 1.0322 | 3.8267 | 2.6703 | 1.4772 | 4.1475 | 2.8642 | 2.3064 | 5.1707 | 3.1414 | 3.0367 | 6.1781 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 0 | 0 | 2.9502 | 1.1687 | 4.1189 | 2.84 | 1.643 | 4.483 | 3.0614 | 2.4966 | 5.558 | 3.3764 | 3.2389 | 6.6153 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 1 | 1 | 2.5767 | 1.2006 | 3.7773 | 2.4643 | 1.6763 | 4.1407 | 2.6836 | 2.5313 | 5.2149 | 2.9911 | 3.2733 | 6.2644 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 1 | 0 | 2.9502 | 1.1687 | 4.1189 | 2.84 | 1.643 | 4.483 | 3.0614 | 2.4966 | 5.558 | 3.3764 | 3.2389 | 6.6153 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 1 | 0 | 2.9502 | 1.1687 | 4.1189 | 2.84 | 1.643 | 4.483 | 3.0614 | 2.4966 | 5.558 | 3.3764 | 3.2389 | 6.6153 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 1 | 0 | 2.9502 | 1.0524 | 4.0025 | 2.84 | 1.4786 | 4.3186 | 3.0614 | 2.2469 | 5.3084 | 3.3764 | 2.915 | 6.2915 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 0 | 0 | 2.8612 | 1.1687 | 4.0299 | 2.7538 | 1.643 | 4.3968 | 2.9696 | 2.4966 | 5.4662 | 3.2747 | 3.2389 | 6.5136 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 1 | 0 | 2.9502 | 1.1687 | 4.1189 | 2.84 | 1.643 | 4.483 | 3.0614 | 2.4966 | 5.558 | 3.3764 | 3.2389 | 6.6153 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 0 | 0 | 2.9502 | 1.1687 | 4.1189 | 2.84 | 1.643 | 4.483 | 3.0614 | 2.4966 | 5.558 | 3.3764 | 3.2389 | 6.6153 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 1 | 0 | 3.0069 | 1.0676 | 4.0745 | 2.8962 | 1.5419 | 4.4381 | 3.1177 | 2.3953 | 5.513 | 3.4329 | 3.1378 | 6.5707 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 1 | 1 | 2.9502 | 1.1687 | 4.1189 | 2.84 | 1.643 | 4.483 | 3.0614 | 2.4966 | 5.558 | 3.3764 | 3.2389 | 6.6153 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 1 | 0 | 2.9502 | 1.1687 | 4.1189 | 2.84 | 1.643 | 4.483 | 3.0614 | 2.4966 | 5.558 | 3.3764 | 3.2389 | 6.6153 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 1 | 0 | 2.9502 | 1.1687 | 4.1189 | 2.84 | 1.643 | 4.483 | 3.0614 | 2.4966 | 5.558 | 3.3764 | 3.2389 | 6.6153 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 1 | 0 | 2.9502 | 1.1687 | 4.1189 | 2.84 | 1.643 | 4.483 | 3.0614 | 2.4966 | 5.558 | 3.3764 | 3.2389 | 6.6153 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype: 4A: Hotel Accomodation |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: #414 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 1 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 1 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 1 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 4B: Dormitory |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: # 111 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 1 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 1 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 1 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 4C: Barracks |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: # 231 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 1 | 1 | 0 | 0 | 0 | 7.206 | 3.8673 | 11.0733 | 8.6829 | 5.6301 | 14.3131 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 1 | 1 | 0 | 0 | 0 | 7.0286 | 3.6703 | 10.6989 | 8.4445 | 5.3742 | 13.8187 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 1 | 1 | 0 | 0 | 0 | 6.8681 | 3.477 | 10.3451 | 7.5032 | 4.3126 | 11.8158 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 1 | 1 | 0 | 0 | 0 | 6.8681 | 3.477 | 10.3451 | 7.5032 | 4.3126 | 11.8158 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 1 | 1 | 0 | 0 | 0 | 6.8681 | 3.477 | 10.3451 | 7.5032 | 4.3126 | 11.8158 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 1 | 1 | 0 | 0 | 0 | 7.1766 | 3.8297 | 11.0063 | 8.6558 | 5.5961 | 14.2519 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 1 | 1 | 0 | 0 | 0 | 6.7235 | 3.2063 | 9.9298 | 7.7179 | 4.2982 | 12.0161 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 1 | 1 | 0 | 0 | 0 | 6.893 | 3.3076 | 10.2006 | 8.1914 | 4.8699 | 13.0613 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 1 | 1 | 0 | 0 | 0 | 6.8534 | 3.4462 | 10.2997 | 8.1563 | 5.0657 | 13.2221 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 1 | 1 | 0 | 0 | 0 | 6.0376 | 3.973 | 10.0106 | 7.5145 | 5.7408 | 13.2553 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 1 | 1 | 0 | 0 | 0 | 6.7337 | 3.8673 | 10.6009 | 8.2095 | 5.6301 | 13.8396 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 1 | 1 | 0 | 0 | 0 | 7.206 | 3.4589 | 10.6649 | 8.6829 | 5.2151 | 13.898 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 1 | 1 | 0 | 0 | 0 | 7.206 | 3.3911 | 10.5972 | 8.6829 | 5.1558 | 13.8387 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 0 | 0 | 0 | 0 | 0 | 7.206 | 3.8673 | 11.0733 | 8.6829 | 5.6301 | 14.3131 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 1 | 1 | 0 | 0 | 0 | 5.3405 | 4.0829 | 9.4235 | 5.71 | 5.9739 | 11.6839 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 0 | 0 | 0 | 0 | 0 | 7.206 | 3.8673 | 11.0733 | 8.6829 | 5.6301 | 14.3131 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 1 | 0 | 0 | 0 | 0 | 7.5733 | 3.7484 | 11.3216 | 9.0502 | 5.5112 | 14.5614 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 1 | 1 | 0 | 0 | 0 | 7.3032 | 3.4114 | 10.7146 | 8.7801 | 5.1743 | 13.9544 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 0 | 0 | 0 | 0 | 0 | 7.206 | 3.8673 | 11.0733 | 8.6829 | 5.6301 | 14.3131 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 0 | 0 | 0 | 0 | 0 | 7.206 | 3.8673 | 11.0733 | 8.6829 | 5.6301 | 14.3131 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 1 | 1 | 0 | 0 | 0 | 6.9563 | 3.5729 | 10.5292 | 8.2852 | 5.1595 | 13.4447 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 4D: Accommodation |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: # 260 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 1 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 1 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 1 | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 5A: Gym/Fitness Centre |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: # 58 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 1 | 1 | 0 | 0 | 0 | 9.8999 | 2.239 | 12.1389 | 0 | 0 | 0 | 12.334 | 4.8286 | 17.1625 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 1 | 1 | 0 | 0 | 0 | 9.7519 | 2.0914 | 11.8433 | 0 | 0 | 0 | 12.0345 | 4.5352 | 16.5697 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 1 | 1 | 0 | 0 | 0 | 9.3971 | 1.8136 | 11.2107 | 0 | 0 | 0 | 10.648 | 3.373 | 14.021 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 1 | 1 | 0 | 0 | 0 | 9.3971 | 1.8136 | 11.2107 | 0 | 0 | 0 | 10.648 | 3.373 | 14.021 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 1 | 1 | 0 | 0 | 0 | 9.3971 | 1.8136 | 11.2107 | 0 | 0 | 0 | 10.648 | 3.373 | 14.021 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 1 | 1 | 0 | 0 | 0 | 9.8841 | 2.2119 | 12.0961 | 0 | 0 | 0 | 12.3034 | 4.7826 | 17.086 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 1 | 1 | 0 | 0 | 0 | 9.4807 | 1.691 | 11.1717 | 0 | 0 | 0 | 10.8559 | 2.9505 | 13.8064 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 1 | 1 | 0 | 0 | 0 | 9.8163 | 1.7797 | 11.596 | 0 | 0 | 0 | 12.2356 | 4.0335 | 16.2691 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 1 | 1 | 0 | 0 | 0 | 9.8276 | 1.9163 | 11.7439 | 0 | 0 | 0 | 12.2469 | 4.1775 | 16.4244 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 1 | 1 | 0 | 0 | 0 | 7.7687 | 2.4554 | 10.2242 | 0 | 0 | 0 | 10.8819 | 5.0622 | 15.9441 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 1 | 1 | 0 | 0 | 0 | 9.1982 | 2.239 | 11.4372 | 0 | 0 | 0 | 11.6322 | 4.8286 | 16.4608 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 1 | 1 | 0 | 0 | 0 | 9.9135 | 2.0114 | 11.9249 | 0 | 0 | 0 | 12.3396 | 4.5927 | 16.9323 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 1 | 1 | 0 | 0 | 0 | 9.8999 | 1.9283 | 11.8282 | 0 | 0 | 0 | 12.334 | 4.1301 | 16.464 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 0 | 0 | 0 | 0 | 0 | 9.6027 | 2.239 | 11.8417 | 0 | 0 | 0 | 11.9633 | 4.8286 | 16.7919 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 1 | 0 | 0 | 0 | 0 | 8.5691 | 2.4179 | 10.9869 | 0 | 0 | 0 | 9.6078 | 4.4622 | 14.07 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 0 | 0 | 0 | 0 | 0 | 9.6106 | 2.239 | 11.8497 | 0 | 0 | 0 | 12.0447 | 4.8286 | 16.8732 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 1 | 0 | 0 | 0 | 0 | 9.9655 | 2.1423 | 12.1078 | 0 | 0 | 0 | 12.3995 | 4.7319 | 17.1314 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 1 | 1 | 0 | 0 | 0 | 9.9056 | 2.2045 | 12.1101 | 0 | 0 | 0 | 12.3396 | 4.7941 | 17.1337 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 1 | 1 | 0 | 0 | 0 | 9.5338 | 2.239 | 11.7728 | 0 | 0 | 0 | 11.9385 | 4.8286 | 16.767 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 1 | 1 | 0 | 0 | 0 | 9.5666 | 2.239 | 11.8056 | 0 | 0 | 0 | 11.926 | 4.8286 | 16.7546 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 1 | 1 | 0 | 0 | 0 | 9.6118 | 2.0218 | 11.6335 | 0 | 0 | 0 | 11.8017 | 4.3524 | 16.1541 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 5C: Sports Centre |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: # 362 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 1 | 1 | 0 | 0 | 0 | 10.2401 | 5.5982 | 15.8383 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 1 | 1 | 0 | 0 | 0 | 10.2016 | 5.467 | 15.6687 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 1 | 1 | 0 | 0 | 0 | 10.1734 | 5.1997 | 15.3731 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 1 | 1 | 0 | 0 | 0 | 10.1734 | 5.1997 | 15.3731 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 1 | 1 | 0 | 0 | 0 | 10.1734 | 5.1997 | 15.3731 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 1 | 1 | 0 | 0 | 0 | 10.2322 | 5.5375 | 15.7696 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 1 | 1 | 0 | 0 | 0 | 10.1836 | 5.0158 | 15.1994 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 1 | 1 | 0 | 0 | 0 | 10.196 | 5.0782 | 15.2742 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 1 | 1 | 0 | 0 | 0 | 10.2254 | 5.2799 | 15.5053 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 1 | 1 | 0 | 0 | 0 | 8.0806 | 5.7659 | 13.8465 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 1 | 1 | 0 | 0 | 0 | 9.3293 | 5.5982 | 14.9275 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 1 | 1 | 0 | 0 | 0 | 10.266 | 4.6058 | 14.8719 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 1 | 1 | 0 | 0 | 0 | 10.2887 | 3.403 | 13.6916 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 0 | 0 | 0 | 0 | 0 | 9.9327 | 5.5982 | 15.5309 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 1 | 0 | 0 | 0 | 0 | 9.636 | 5.6464 | 15.2824 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 0 | 0 | 0 | 0 | 0 | 10.1756 | 5.5982 | 15.7739 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 1 | 0 | 0 | 0 | 0 | 10.5 | 5.2925 | 15.7925 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 1 | 1 | 0 | 0 | 0 | 10.2435 | 5.5759 | 15.8193 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 1 | 1 | 0 | 0 | 0 | 10.2355 | 5.5982 | 15.8338 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 1 | 1 | 0 | 0 | 0 | 10.2401 | 5.5982 | 15.8383 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 1 | 1 | 0 | 0 | 0 | 10.1248 | 5.0565 | 15.1813 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 5D: Sports & Arena |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: # 405 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 6A: Office |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: # 56 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 1 | 1 | 10.3542 | 5.6104 | 15.9646 | 10.5644 | 6.2662 | 16.8305 | 9.9169 | 6.5382 | 16.455 | 9.9169 | 6.5382 | 16.455 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 1 | 0 | 10.3542 | 5.4785 | 15.8327 | 10.5644 | 6.0068 | 16.5712 | 9.9169 | 6.1345 | 16.0513 | 9.9169 | 6.5383 | 16.4552 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 1 | 0 | 10.3542 | 5.4468 | 15.801 | 10.5644 | 5.9958 | 16.5602 | 9.9169 | 6.2197 | 16.1365 | 9.9169 | 6.5382 | 16.455 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 1 | 0 | 10.3542 | 5.4468 | 15.801 | 10.5644 | 5.9958 | 16.5602 | 9.9169 | 6.2197 | 16.1365 | 9.9169 | 6.5382 | 16.455 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 1 | 0 | 10.3542 | 5.4468 | 15.801 | 10.5644 | 5.9958 | 16.5602 | 9.9169 | 6.2197 | 16.1365 | 9.9169 | 6.5382 | 16.455 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 1 | 0 | 10.3542 | 5.6104 | 15.9646 | 10.5644 | 6.2662 | 16.8305 | 9.9169 | 6.5382 | 16.455 | 9.9169 | 6.5382 | 16.455 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 1 | 0 | 10.3542 | 5.6104 | 15.9646 | 10.5226 | 6.0186 | 16.5412 | 9.7677 | 5.8338 | 15.6015 | 9.7677 | 5.8338 | 15.6015 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 1 | 0 | 10.3542 | 5.5647 | 15.9189 | 10.5802 | 6.0857 | 16.6659 | 9.9124 | 6.5199 | 16.4322 | 9.9124 | 6.5199 | 16.4322 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 1 | 0 | 10.3542 | 5.6104 | 15.9646 | 10.5644 | 6.2662 | 16.8305 | 9.9169 | 6.5382 | 16.455 | 9.9169 | 6.5382 | 16.455 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 1 | 0 | 9.0287 | 5.7183 | 14.747 | 9.1575 | 6.3831 | 15.5406 | 8.4953 | 6.6631 | 15.1584 | 8.4953 | 6.6631 | 15.1584 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 1 | 0 | 9.318 | 5.6104 | 14.9284 | 9.5078 | 6.2662 | 15.774 | 8.9247 | 6.5382 | 15.4629 | 9.9169 | 6.5382 | 16.455 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 1 | 0 | 9.3767 | 4.7503 | 14.1271 | 11.3667 | 4.5285 | 15.8952 | 10.048 | 4.7152 | 14.7631 | 10.048 | 4.7152 | 14.7631 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 1 | 0 | 10.0005 | 5.0494 | 15.0499 | 10.5644 | 5.6395 | 16.2039 | 9.9169 | 6.5382 | 16.455 | 9.9169 | 5.8796 | 15.7965 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 1 | 0 | 9.2615 | 5.6104 | 14.8719 | 10.2468 | 6.2662 | 16.513 | 9.6186 | 6.2112 | 15.8298 | 9.6186 | 6.2112 | 15.8298 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 1 | 0 | 10.3542 | 5.6104 | 15.9646 | 10.2932 | 6.295 | 16.5882 | 11.6074 | 6.3261 | 17.9335 | 11.6074 | 6.3261 | 17.9335 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 1 | 0 | 10.3542 | 5.6104 | 15.9646 | 10.266 | 6.307 | 16.573 | 9.7982 | 6.5411 | 16.3393 | 9.7982 | 6.5411 | 16.3393 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 1 | 0 | 10.3542 | 5.6104 | 15.9646 | 10.5644 | 6.2662 | 16.8305 | 9.9169 | 6.5382 | 16.455 | 9.9169 | 6.5382 | 16.455 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 1 | 1 | 9.9383 | 5.6104 | 15.5487 | 10.1485 | 6.2662 | 16.4147 | 9.501 | 6.5382 | 16.0392 | 9.501 | 6.5382 | 16.0392 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 1 | 0 | 10.3542 | 5.6104 | 15.9646 | 10.5644 | 6.2662 | 16.8305 | 9.9169 | 6.5382 | 16.455 | 9.9169 | 6.5382 | 16.455 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 1 | 0 | 10.3542 | 5.6104 | 15.9646 | 10.5644 | 6.2662 | 16.8305 | 9.9169 | 6.5382 | 16.455 | 9.9169 | 6.5382 | 16.455 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 1 | 0 | 10.3542 | 5.6104 | 15.9646 | 10.5644 | 6.2662 | 16.8305 | 9.9169 | 6.5382 | 16.455 | 9.9169 | 6.5382 | 16.455 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 7A: Dining Hall |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: # 120 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.749 | 5.9015 | 25.6505 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.7136 | 5.7418 | 25.4554 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.278 | 4.1741 | 23.452 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.278 | 4.1741 | 23.452 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.278 | 4.1741 | 23.452 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.7457 | 5.8598 | 25.6056 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6074 | 4.0771 | 23.6845 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.614 | 4.8951 | 24.5091 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.749 | 5.9015 | 25.6505 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6653 | 6.2124 | 22.8777 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.5377 | 5.9015 | 24.4392 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.8895 | 4.69 | 24.5795 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6711 | 4.2405 | 23.9116 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.1569 | 5.9015 | 25.0584 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.1082 | 6.293 | 22.4012 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.749 | 5.9015 | 25.6505 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.9852 | 5.8228 | 25.808 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.1885 | 5.9015 | 25.09 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.5197 | 5.9214 | 25.4411 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.1422 | 5.9015 | 25.0437 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.1015 | 5.3113 | 24.4129 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 9A: Workshop |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: # 152 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 1 | 1 | 14.2764 | 6.0635 | 20.3399 | 15.6539 | 6.9765 | 22.6304 | 0 | 0 | 0 | 22.5175 | 10.2463 | 32.7638 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 1 | 1 | 14.0708 | 5.8942 | 19.965 | 15.1657 | 6.7739 | 21.9396 | 0 | 0 | 0 | 21.5683 | 9.8313 | 31.3996 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 1 | 1 | 14.0538 | 5.9516 | 20.0054 | 15.1872 | 6.7795 | 21.9667 | 0 | 0 | 0 | 19.2563 | 8.822 | 28.0784 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 1 | 1 | 14.0538 | 5.9516 | 20.0054 | 15.1872 | 6.7795 | 21.9667 | 0 | 0 | 0 | 19.2563 | 8.822 | 28.0784 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 1 | 1 | 14.0538 | 5.9516 | 20.0054 | 15.1872 | 6.7795 | 21.9667 | 0 | 0 | 0 | 19.2563 | 8.822 | 28.0784 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 1 | 1 | 14.2742 | 6.0502 | 20.3244 | 15.6302 | 6.9427 | 22.5728 | 0 | 0 | 0 | 22.4938 | 10.2041 | 32.6978 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 1 | 1 | 14.2764 | 6.0635 | 20.3399 | 14.4866 | 6.2537 | 20.7403 | 0 | 0 | 0 | 17.9715 | 7.8492 | 25.8207 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 1 | 1 | 14.2086 | 5.1798 | 19.3884 | 15.5556 | 5.9799 | 21.5355 | 0 | 0 | 0 | 22.235 | 8.8664 | 31.1014 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 1 | 1 | 14.1928 | 5.3586 | 19.5514 | 15.5522 | 6.1834 | 21.7356 | 0 | 0 | 0 | 22.2802 | 9.1287 | 31.4089 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 1 | 1 | 12.03 | 6.2888 | 18.3188 | 13.7227 | 7.1704 | 20.8932 | 0 | 0 | 0 | 20.6202 | 10.4381 | 31.0584 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 1 | 1 | 13.3758 | 6.0635 | 19.4393 | 14.7522 | 6.9765 | 21.7287 | 0 | 0 | 0 | 21.6158 | 10.2463 | 31.8621 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 1 | 1 | 14.2595 | 5.9822 | 20.2416 | 15.6347 | 6.8524 | 22.4871 | 0 | 0 | 0 | 22.5028 | 10.0592 | 32.562 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 1 | 1 | 14.2764 | 5.4571 | 19.7336 | 15.6539 | 6.2788 | 21.9327 | 0 | 0 | 0 | 22.5175 | 9.2217 | 31.7392 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 0 | 0 | 13.847 | 6.0635 | 19.9105 | 15.1838 | 6.9765 | 22.1603 | 0 | 0 | 0 | 21.8418 | 10.2463 | 32.0881 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 1 | 0 | 10.4166 | 6.5823 | 16.9989 | 10.7711 | 7.6328 | 18.4039 | 0 | 0 | 0 | 17.6347 | 10.9026 | 28.5373 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 0 | 0 | 14.2764 | 6.0635 | 20.3399 | 15.1137 | 6.9765 | 22.0903 | 0 | 0 | 0 | 21.9774 | 10.2463 | 32.2237 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 1 | 0 | 14.4414 | 5.7784 | 20.2198 | 15.8189 | 6.6914 | 22.5103 | 0 | 0 | 0 | 22.6825 | 9.9612 | 32.6437 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 1 | 1 | 14.2877 | 6.011 | 20.2987 | 15.6652 | 6.924 | 22.5892 | 0 | 0 | 0 | 22.5288 | 10.1938 | 32.7227 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 1 | 1 | 14.2493 | 6.0727 | 20.322 | 15.6268 | 6.9892 | 22.6159 | 0 | 0 | 0 | 22.4836 | 10.276 | 32.7596 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 1 | 1 | 14.2764 | 6.0635 | 20.3399 | 15.1544 | 6.9765 | 22.131 | 0 | 0 | 0 | 21.4203 | 10.2463 | 31.6666 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 1 | 1 | 13.7487 | 5.4662 | 19.2149 | 14.9883 | 6.2882 | 21.2765 | 0 | 0 | 0 | 21.1649 | 9.2309 | 30.3958 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 11A: Retail Building |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: # 119 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.0422 | 7.964 | 32.0061 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7864 | 7.509 | 31.2954 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7156 | 6.1859 | 29.9015 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7156 | 6.1859 | 29.9015 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7156 | 6.1859 | 29.9015 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.9766 | 7.7547 | 31.7313 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.4775 | 5.0944 | 28.5719 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7274 | 6.924 | 30.6514 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.2225 | 6.7409 | 29.9634 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.7129 | 8.2008 | 29.9137 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1526 | 7.964 | 31.1166 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.835 | 6.6495 | 30.4845 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.8019 | 5.5872 | 29.3891 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.5696 | 7.964 | 31.5335 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.2168 | 7.964 | 31.1808 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.0422 | 7.964 | 32.0061 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.2306 | 7.8011 | 32.0318 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.2983 | 7.964 | 31.2623 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.8748 | 7.9702 | 31.845 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.5515 | 7.964 | 31.5155 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.6384 | 7.1675 | 29.8059 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 13B: Firehall |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Energy Cost |  |  | 2013 Total Energy Cost |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings |  |  | ECM 2013 Energy Savings
Exempler Building: # 19 |  |  |  | V1: Post 2004 |  |  | V2:1980-2004 |  |  | V3:1960-1979 |  |  | V4: pre-1960 |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: pre 1960: Total Area $ |  |  | Sum: All Areas $ |  |  | V1: Post 2004: Total Area $ |  |  | V2: 1980-2004: Total Area $ |  |  | V3: 1960-1979: Total Area $ |  |  | V4: Pre 1960: Total Area $ |  |  | Sum: All Areas $
ECM | ECM Applicability Index | ECM Modelled Index | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $/m2 | Gas $/m2 | Total $/m2 | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case | 1 | 1 | 18.054 | 3.6849 | 21.7389 | 0 | 0 | 0 | 20.8191 | 9.1506 | 29.9697 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Wall Insulation: Additional RSI 1.32 on ext. | 1 | 1 | 17.9873 | 3.5611 | 21.5484 | 0 | 0 | 0 | 20.6666 | 8.9139 | 29.5805 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | 1 | 1 | 17.9376 | 3.4836 | 21.4213 | 0 | 0 | 0 | 19.7208 | 7.5275 | 27.2483 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | 1 | 1 | 17.9376 | 3.4836 | 21.4213 | 0 | 0 | 0 | 19.7208 | 7.5275 | 27.2483 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 1 | 1 | 17.9376 | 3.4836 | 21.4213 | 0 | 0 | 0 | 19.7208 | 7.5275 | 27.2483 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | 1 | 1 | 18.0472 | 3.6709 | 21.7182 | 0 | 0 | 0 | 20.7965 | 9.1081 | 29.9046 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | 1 | 1 | 18.054 | 3.6849 | 21.7389 | 0 | 0 | 0 | 19.2145 | 5.4688 | 24.6833 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | 1 | 1 | 17.9512 | 2.9319 | 20.8831 | 0 | 0 | 0 | 20.6078 | 7.689 | 28.2968 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | 1 | 1 | 17.9907 | 3.386 | 21.3767 | 0 | 0 | 0 | 20.7005 | 8.5066 | 29.2071 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | 1 | 1 | 14.8154 | 4.0262 | 18.8416 | 0 | 0 | 0 | 17.6201 | 9.5267 | 27.1468 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | 1 | 1 | 16.4596 | 3.6849 | 20.1444 | 0 | 0 | 0 | 19.2247 | 9.1506 | 28.3753 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | 1 | 1 | 18.2258 | 2.9069 | 21.1327 | 0 | 0 | 0 | 20.9061 | 8.3466 | 29.2527 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | 1 | 1 | 18.054 | 2.9478 | 21.0018 | 0 | 0 | 0 | 20.8191 | 7.3205 | 28.1396 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | 0 | 0 | 17.5116 | 3.6849 | 21.1965 | 0 | 0 | 0 | 20.1897 | 9.1506 | 29.3403 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | 1 | 0 | 17.1123 | 3.8114 | 20.9238 | 0 | 0 | 0 | 18.4024 | 9.4754 | 27.8777 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | 0 | 0 | 17.3839 | 3.6849 | 21.0688 | 0 | 0 | 0 | 20.149 | 9.1506 | 29.2996 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | 1 | 0 | 18.619 | 3.3908 | 22.0098 | 0 | 0 | 0 | 21.3841 | 8.8565 | 30.2407 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | 1 | 1 | 18.0732 | 3.5666 | 21.6398 | 0 | 0 | 0 | 20.8383 | 9.0323 | 29.8706 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | 1 | 1 | 17.8868 | 3.6849 | 21.5716 | 0 | 0 | 0 | 20.5536 | 9.1507 | 29.7043 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | 1 | 1 | 18.054 | 3.6849 | 21.7389 | 0 | 0 | 0 | 20.6406 | 9.1506 | 29.7912 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | 1 | 1 | 17.8416 | 3.3419 | 21.1835 | 0 | 0 | 0 | 20.331 | 8.2612 | 28.5921 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2013 Savings $
| V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | -2500 | #REF! | #REF! | -3000 | #REF! | #REF! | -4000 | #REF! | #REF! | -5000 | #REF! | #REF! | -14500 | #REF! | #REF!
Solar DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Present Value of Energy Savings Accrued to 2018 (Real Elec Escalation = 4%/yr, Real Gas Escalation = 2%/yr, Inflation = Discount = 1%/yr)
| V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | -2754.9 | #REF! | #REF! | -3305.8801 | #REF! | #REF! | -4407.8401 | #REF! | #REF! | -5509.8001 | #REF! | #REF! | -15978.4203 | #REF! | #REF!
Solar DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Present Value of Energy Savings Accrued to 2023 (Real Elec Escalation = 2%/yr, Real Gas Escalation = 3%/yr, Inflation = Discount = 1%/yr)
| V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | -3035.7897 | #REF! | #REF! | -3642.9476 | #REF! | #REF! | -4857.2635 | #REF! | #REF! | -6071.5794 | #REF! | #REF! | -17607.5803 | #REF! | #REF!
Solar DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Present Value of Energy Savings Accrued to 2028 (Real Elec Escalation = 4%/yr, Real Gas Escalation = 2%/yr, Inflation = Discount = 1%/yr)
| V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | -3345.3189 | #REF! | #REF! | -4014.3827 | #REF! | #REF! | -5352.5102 | #REF! | #REF! | -6690.6378 | #REF! | #REF! | -19402.8495 | #REF! | #REF!
Solar DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Present Value of Energy Savings Accrued to 2033 (Real Elec Escalation = 4%/yr, Real Gas Escalation = 2%/yr, Inflation = Discount = 1%/yr)
| V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | -3686.4077 | #REF! | #REF! | -4423.6892 | #REF! | #REF! | -5898.2523 | #REF! | #REF! | -7372.8153 | #REF! | #REF! | -21381.1644 | #REF! | #REF!
Solar DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 3A: Active Warehouse | 2013 Savings $
Exempler: # 358 | V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 3A: Active Warehouse | Present Value of Energy Savings Accrued to 2018 (Real Elec Escalation = 4%/yr, Real Gas Escalation = 2%/yr, Inflation = Discount = 1%/yr)
Exempler: # 358 | V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 3A: Active Warehouse | Present Value of Energy Savings Accrued to 2023 (Real Elec Escalation = 2%/yr, Real Gas Escalation = 3%/yr, Inflation = Discount = 1%/yr)
Exempler: # 358 | V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 3A: Active Warehouse | Present Value of Energy Savings Accrued to 2028 (Real Elec Escalation = 4%/yr, Real Gas Escalation = 2%/yr, Inflation = Discount = 1%/yr)
Exempler: # 358 | V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 3A: Active Warehouse | Present Value of Energy Savings Accrued to 2033 (Real Elec Escalation = 4%/yr, Real Gas Escalation = 2%/yr, Inflation = Discount = 1%/yr)
Exempler: # 358 | V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 1A: Hanger | 2013 Savings $
Exempler: # 607 | V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 1A: Hanger | Present Value of Energy Savings Accrued to 2018 (Real Elec Escalation = 4%/yr, Real Gas Escalation = 2%/yr, Inflation = Discount = 1%/yr)
Exempler: # 607 | V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 1A: Hanger | Present Value of Energy Savings Accrued to 2023 (Real Elec Escalation = 2%/yr, Real Gas Escalation = 3%/yr, Inflation = Discount = 1%/yr)
Exempler: # 607 | V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 1A: Hanger | Present Value of Energy Savings Accrued to 2028 (Real Elec Escalation = 4%/yr, Real Gas Escalation = 2%/yr, Inflation = Discount = 1%/yr)
Exempler: # 607 | V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 1A: Hanger | Present Value of Energy Savings Accrued to 2033 (Real Elec Escalation = 4%/yr, Real Gas Escalation = 2%/yr, Inflation = Discount = 1%/yr)
Exempler: # 607 | V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 to 2.11 on exterior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 1.76 on ext, 2.11 on int. | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Archetype 1A: Hanger | Present Value of Energy Savings Accrued to 2033 (Real Elec Escalation = 4%/yr, Real Gas Escalation = 2%/yr, Inflation = Discount = 1%/yr)
Exempler: # 607 | V1: Post 2004 |  |  | V2: 1980 -2004 |  |  | V3: 1960-1979 |  |  | V4: Pre-1960 |  |  | All Vintages
ECM | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $ | Elec $ | Gas $ | Total $
Base case
Heating setpoint reduction (2 DegC) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total | [12 empty] | #REF! | #REF! | #REF!
Note on A14: khaddad: 10% reduction in lighting and plug loads
Note on A17: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A23: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A24: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A39: khaddad: 10% reduction in lighting and plug loads
Note on A42: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A48: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A49: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A64: khaddad: 10% reduction in lighting and plug loads
Note on A67: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A73: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A74: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A89: khaddad: 10% reduction in lighting and plug loads
Note on A92: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A98: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A99: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A114: khaddad: 10% reduction in lighting and plug loads
Note on A117: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A123: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A124: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A139: khaddad: 10% reduction in lighting and plug loads
Note on A142: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A148: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A149: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A164: khaddad: 10% reduction in lighting and plug loads
Note on A167: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A173: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A174: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A189: khaddad: 10% reduction in lighting and plug loads
Note on A192: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A198: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A199: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A214: khaddad: 10% reduction in lighting and plug loads
Note on A217: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A223: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A224: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A239: khaddad: 10% reduction in lighting and plug loads
Note on A242: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A248: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A249: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A264: khaddad: 10% reduction in lighting and plug loads
Note on A267: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A273: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A274: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A289: khaddad: 10% reduction in lighting and plug loads
Note on A292: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A298: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A299: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A314: khaddad: 10% reduction in lighting and plug loads
Note on A317: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A323: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A324: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A339: khaddad: 10% reduction in lighting and plug loads
Note on A342: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A348: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A349: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A364: khaddad: 10% reduction in lighting and plug loads
Note on A367: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A373: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A374: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A389: khaddad: 10% reduction in lighting and plug loads
Note on A392: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A398: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A399: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A414: khaddad: 10% reduction in lighting and plug loads
Note on A417: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A423: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A424: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A440: khaddad: 10% reduction in lighting and plug loads
Note on A443: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A449: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A450: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A465: khaddad: 10% reduction in lighting and plug loads
Note on A468: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A474: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A475: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A490: khaddad: 10% reduction in lighting and plug loads
Note on A493: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A499: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A500: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A515: khaddad: 10% reduction in lighting and plug loads
Note on A518: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A524: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A525: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A540: khaddad: 10% reduction in lighting and plug loads
Note on A543: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A549: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A550: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A566: khaddad: 10% reduction in lighting and plug loads
Note on A569: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A575: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A576: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A591: khaddad: 10% reduction in lighting and plug loads
Note on A594: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A600: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A601: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A616: khaddad: 10% reduction in lighting and plug loads
Note on A619: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A625: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A626: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A641: khaddad: 10% reduction in lighting and plug loads
Note on A644: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A650: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A651: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A666: khaddad: 10% reduction in lighting and plug loads
Note on A669: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A675: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A676: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A692: khaddad: 10% reduction in lighting and plug loads
Note on A695: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A701: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A702: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A717: khaddad: 10% reduction in lighting and plug loads
Note on A720: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A726: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A727: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A742: khaddad: 10% reduction in lighting and plug loads
Note on A745: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A751: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A752: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A767: khaddad: 10% reduction in lighting and plug loads
Note on A770: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A776: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A777: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A786: khaddad: 10% reduction in lighting and plug loads
Note on A788: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A792: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A793: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw

## Bldg$EUI
Archetype 1A-Hanger (kWh/m2 floor area)
Exempler Building #607 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $
Base case
Wall Insulation: Additional RSI 1.32 on ext. |  |  |  | 0 | 0 | #REF! |  |  |  | 234.5388 | 384.6063 | #REF! |  |  |  | 234.5388 | 338.4835 | #REF! |  |  |  | 234.5388 | 290.7558 | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | 0 | #REF! |  |  |  | 149.8765 | 245.7736 | #REF! |  |  |  | 125.7736 | 181.5149 | #REF! |  |  |  | 125.7736 | 155.9204 | #REF!
Windows: Double Glazed to Triple LowE |  |  |  | 87.3884 | 165.1113 | #REF! |  |  |  | 87.3884 | 165.7857 | #REF! |  |  |  | 87.3884 | 165.4024 | #REF! |  |  |  | 87.3884 | 175.1041 | #REF!
Air tightness: vintage ACH to 0.27 ACH |  |  |  | 0 | n/a | #REF! |  |  |  | 14.7847 | 19.095 | #REF! |  |  |  | 16.1877 | 21.9917 | #REF! |  |  |  | 16.1877 | 17.3383 | #REF!
Heating setpoint reduction (2 DegC) |  |  |  | 1.1929 | 1.9144 | #REF! |  |  |  | 1.1929 | 1.572 | #REF! |  |  |  | 1.1929 | 1.3455 | #REF! |  |  |  | 1.1929 | 1.4074 | #REF!
Temperature set back of 2 DegC afterhours |  |  |  | 1.1929 | 1.9297 | #REF! |  |  |  | 1.1929 | 1.8134 | #REF! |  |  |  | 1.1929 | 1.6298 | #REF! |  |  |  | 1.1929 | 1.791 | #REF!
Lighting: 30% reduction from MNECB |  |  |  | 18.477 | 9.5531 | #REF! |  |  |  | 18.477 | 10.1296 | #REF! |  |  |  | 18.477 | 10.369 | #REF! |  |  |  | 18.477 | 10.1191 | #REF!
Occupancy Sensors (Lights/Plug Loads) |  |  |  | 0.64762 | 0.60636 | #REF! |  |  |  | 0.64762 | 0.37839 | #REF! |  |  |  | 0.64762 | 0.37151 | #REF! |  |  |  | 0.64762 | 0.59776 | #REF!
HRV |  |  |  | 71.5384 | 70.2305 | #REF! |  |  |  | 71.5384 | 59.4418 | #REF! |  |  |  | 71.5384 | 142.9366 | #REF! |  |  |  | 71.5384 | 153.3337 | #REF!
DCV for all occupied zones |  |  |  | 2.0413 | 1.7725 | #REF! |  |  |  | 2.0413 | 1.6615 | #REF! |  |  |  | 2.0413 | 4.1834 | #REF! |  |  |  | 2.0413 | 4.2172 | #REF!
Cold Deck Reset to eliminate reheat |  |  |  | 1.984 | 4.1736 | #REF! |  |  |  | 1.984 | 3.7555 | #REF! |  |  |  | 1.984 | 4.1278 | #REF! |  |  |  | 1.984 | 4.1256 | #REF!
VSD/VFD on large hp AHU |  |  |  | 0.94364 | n/a | #REF! |  |  |  | 0.94364 | 1.8448 | #REF! |  |  |  | 0.94364 | 1.9537 | #REF! |  |  |  | 0.94364 | 1.9558 | #REF!
VSP on large hp heating/cooling pumps |  |  |  | 3.0964 | 1.4726 | #REF! |  |  |  | 3.0964 | 0.64233 | #REF! |  |  |  | 3.0964 | 0.57686 | #REF! |  |  |  | 3.0964 | 6.4459 | #REF!
Solar Wall for ventilation preheat | 3.2737 | 3.3996 | 1.2591 | 7.9324 | 75.9914 | #REF! | 3.2737 | 3.3996 | 1.2591 | 7.9324 | 75.7874 | #REF! | 3.2737 | 3.3996 | 1.2591 | 7.9324 | 75.4934 | #REF! | 3.2737 | 3.3996 | 1.2591 | 7.9324 | 76.1593 | #REF!
Solar DHW |  |  |  | 5.2213 | 178.3756 | #REF! |  |  |  | 5.2213 | 176.6794 | #REF! |  |  |  | 5.2213 | 174.2757 | #REF! |  |  |  | 5.2213 | 179.7888 | #REF!
Dry Bulb Economizer Control |  |  |  | 0.79411 | 1.7496 | #REF! |  |  |  | 0.79411 | 1.4332 | #REF! |  |  |  | 0.79411 | 1.595 | #REF! |  |  |  | 0.79411 | 1.5845 | #REF!
DX Cooling COP Upgrade to COP 4.0 |  |  |  | 1.0398 | n/a | #REF! |  |  |  | 1.0398 | 1.4434 | #REF! |  |  |  | 1.0398 | 2.0356 | #REF! |  |  |  | 1.0398 | 2.0932 | #REF!
Retro-commissioning on thermostats and AHU |  |  |  | 1.6457 | 1.31 | #REF! |  |  |  | 1.6457 | 0.83277 | #REF! |  |  |  | 1.6457 | 0.75439 | #REF! |  |  |  | 1.6457 | 1.0053 | #REF!
Archetype 2A-Training Building (kWh/m2 floor area)
Exempler Building #34 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $
Base case | 7.9414 | 6.3532 | 7.9414
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | 6.3532 | 7.9414 | 0 | 0 | #REF! |  |  |  | 123.1035 | 530.0563 | #REF! |  |  |  | 123.1035 | 362.2544 | #REF! |  |  |  | 123.1035 | 250.6086 | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | 0 | #REF! |  |  |  | 106.3252 | 457.8129 | #REF! |  |  |  | 89.2262 | 262.5642 | #REF! |  |  |  | 89.2262 | 181.6427 | #REF!
Windows: Double Glazed to Triple LowE | #REF! | 3415.25 | 7.9414 | 43.1849 | 3374.349 | #REF! |  |  |  | 43.1849 | 1269.2487 | #REF! |  |  |  | 43.1849 | 920.3947 | #REF! |  |  |  | 43.1849 | 557.2391 | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #VALUE! | 7.9414 | 0 | n/a | #REF! |  |  |  | 24.9364 | 34.1089 | #REF! |  |  |  | 27.7885 | 14.4245 | #REF! |  |  |  | 27.7885 | 8.6064 | #REF!
Heating setpoint reduction (2 DegC) | #REF! | 18.565 | 7.9414 | 4.9712 | 8.2349 | #REF! |  |  |  | 4.9712 | 6.5914 | #REF! |  |  |  | 4.9712 | 5.2899 | #REF! |  |  |  | 4.9712 | 4.6858 | #REF!
Temperature set back of 2 DegC afterhours | #REF! | 19.6441 | 7.9414 | 4.9712 | 9.314 | #REF! |  |  |  | 4.9712 | 7.4056 | #REF! |  |  |  | 4.9712 | 6.1532 | #REF! |  |  |  | 4.9712 | 3.2937 | #REF!
Lighting: 30% reduction from MNECB | #REF! | 62.1313 | 7.9414 | 38.2262 | 25.1972 | #REF! |  |  |  | 38.2262 | 25.731 | #REF! |  |  |  | 38.2262 | 29.1406 | #REF! |  |  |  | 38.2262 | 29.3759 | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | 13.5615 | 7.9414 | 2.6988 | 5.0493 | #REF! |  |  |  | 2.7312 | 5.1316 | #REF! |  |  |  | 2.7312 | 5.1207 | #REF! |  |  |  | 2.7312 | 5.1099 | #REF!
HRV | #REF! | 126.4237 | 7.9414 | 62.342 | 70.1969 | #REF! |  |  |  | 62.342 | 65.1105 | #REF! |  |  |  | 62.342 | 63.8935 | #REF! |  |  |  | 62.342 | 63.5556 | #REF!
DCV for all occupied zones | #REF! | 30.0916 | 7.9414 | 8.5066 | 16.9332 | #REF! |  |  |  | 8.5066 | 11.6948 | #REF! |  |  |  | 8.5066 | 7.9476 | #REF! |  |  |  | 8.5066 | 6.5174 | #REF!
Cold Deck Reset to eliminate reheat | #REF! | 24.0383 | 7.9414 | 3.3418 | 15.0117 | #REF! |  |  |  | 3.3418 | 14.0824 | #REF! |  |  |  | 3.3418 | 12.0216 | #REF! |  |  |  | 3.3418 | n/a | #REF!
VSD/VFD on large hp AHU | #REF! | 9.723 | 7.9414 | 1.8115 | 1.9207 | #REF! |  |  |  | 1.8115 | 1.5298 | #REF! |  |  |  | 1.8115 | 0.89742 | #REF! |  |  |  | 1.8115 | 0.75811 | #REF!
VSP on large hp heating/cooling pumps | #REF! | 8.7028 | 7.9414 | 1.9505 | 0.78926 | #REF! |  |  |  | 1.9505 | 0.78921 | #REF! |  |  |  | 1.9505 | 0.78926 | #REF! |  |  |  | 1.9505 | 0.78926 | #REF!
Solar Wall for ventilation preheat | #REF! | -46.2053 | 7.9414 | 2.6773 | -54.7003 | #REF! |  |  |  | 2.6773 | -54.7003 | #REF! |  |  |  | 2.6773 | -54.7003 | #REF! |  |  |  | 2.6773 | -54.7003 | #REF!
Solar DHW | #REF! | 194.5052 | 7.9414 | 9.7937 | 180.3171 | #REF! |  |  |  | 9.7937 | 180.3171 | #REF! |  |  |  | 9.7937 | 180.3171 | #REF! |  |  |  | 9.7937 | 180.3171 | #REF!
Dry Bulb Economizer Control | #REF! | 46.8788 | 7.9414 | 1.3375 | 39.4556 | #REF! |  |  |  | 1.3375 | 47.3468 | #REF! |  |  |  | 1.3375 | 118.3669 | #REF! |  |  |  | 1.3375 | 147.9586 | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #VALUE! | 7.9414 | 5.0132 | n/a | #REF! |  |  |  | 5.0132 | 61.4946 | #REF! |  |  |  | 5.0132 | 29.7747 | #REF! |  |  |  | 5.0132 | 19.8055 | #REF!
Retro-commissioning on thermostats and AHU | #REF! | 18.6303 | 7.9414 | 4.0877 | 9.007 | #REF! |  |  |  | 4.0877 | 6.6029 | #REF! |  |  |  | 4.0877 | 4.4194 | #REF! |  |  |  | 4.0877 | 3.7943 | #REF!
Archetype 3A-Active Warehouse (kWh/m2 floor area)
Exempler Building #358 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $
Base case | 21.64 | 17.312 | 21.64
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | 19.43 | 0 | #REF! | #REF! |  |  |  | 154.4894 | #REF! | #REF! |  |  |  | 154.4894 |  | #REF! |  |  |  | 154.4894 | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | #REF! | #REF! |  |  |  | 153.0174 | #REF! | #REF! |  |  |  | 128.4093 |  | #REF! |  |  |  | 128.4093 | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | 21.4 | 8.4725 | #REF! | #REF! |  |  |  | 8.4725 | #REF! | #REF! |  |  |  | 8.4725 |  | #REF! |  |  |  | 8.4725 | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | 21.64 | 0 | #REF! | #REF! |  |  |  | 16.3416 | #REF! | #REF! |  |  |  | 17.7432 |  | #REF! |  |  |  | 17.7432 | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | 15.54 | 0.81557 | #REF! | #REF! |  |  |  | 0.81557 | #REF! | #REF! |  |  |  | 0.81557 |  | #REF! |  |  |  | 0.81557 | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | 21.64 | 0.81557 | #REF! | #REF! |  |  |  | 0.81557 | #REF! | #REF! |  |  |  | 0.81557 |  | #REF! |  |  |  | 0.81557 | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | 23.48 | 9.9549 | #REF! | #REF! |  |  |  | 9.9549 | #REF! | #REF! |  |  |  | 9.9549 |  | #REF! |  |  |  | 9.9549 | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | 21.64 | 0.44276 | #REF! | #REF! |  |  |  | 0.44276 | #REF! | #REF! |  |  |  | 0.44276 |  | #REF! |  |  |  | 0.44276 | #REF! | #REF!
HRV | #REF! | #REF! | 19.36 | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! |  |  |  | 0 |  | #REF! |  |  |  | 0 | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | 18.79 | 1.3956 | #REF! | #REF! |  |  |  | 1.3956 | #REF! | #REF! |  |  |  | 1.3956 |  | #REF! |  |  |  | 1.3956 | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | 21.64 | 2.0949 | #REF! | #REF! |  |  |  | 2.0949 | #REF! | #REF! |  |  |  | 2.0949 |  | #REF! |  |  |  | 2.0949 | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | 27.16 | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! |  |  |  | 0 |  | #REF! |  |  |  | 0 | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | 21.64 | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! |  |  |  | 0 |  | #REF! |  |  |  | 0 | #REF! | #REF!
Solar Wall for ventilation preheat | #REF! | #REF! | 21.64 | 3.0871 | #REF! | #REF! |  |  |  | 3.0871 | #REF! | #REF! |  |  |  | 3.0871 |  | #REF! |  |  |  | 3.0871 | #REF! | #REF!
Solar DHW | #REF! | #REF! | 21.64 | 2.3381 | #REF! | #REF! |  |  |  | 2.3381 | #REF! | #REF! |  |  |  | 2.3381 |  | #REF! |  |  |  | 2.3381 | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | 21.7 | 0.83796 | #REF! | #REF! |  |  |  | 0.83796 | #REF! | #REF! |  |  |  | 0.83796 |  | #REF! |  |  |  | 0.83796 | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | 21.64 | 1.0474 | #REF! | #REF! |  |  |  | 1.0474 | #REF! | #REF! |  |  |  | 1.0474 |  | #REF! |  |  |  | 1.0474 | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | 19.47 | 1.4141 | #REF! | #REF! |  |  |  | 1.4141 | #REF! | #REF! |  |  |  | 1.4141 |  | #REF! |  |  |  | 1.4141 | #REF! | #REF!
Archetype 3B-Storage Type Warehouse (kWh/m2 floor area)
Exempler Building #239 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $
Base case | 0 | 0 | 0
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | 0 | 0 | 0 | 0 | #REF! |  |  |  | 301.4226 | 1764.7307 | #REF! |  |  |  | 301.4226 | 1409.539 | #REF! |  |  |  | 301.4226 | 782.6146 | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | 0 | #REF! |  |  |  | 168.2878 | 985.27 | #REF! |  |  |  | 141.224 | 660.4042 | #REF! |  |  |  | 141.224 | 366.6744 | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 87.1128 | n/a | #REF! |  |  |  | 92.3112 | n/a | #REF! |  |  |  | 92.3112 | n/a | #REF!
Heating setpoint reduction (2 DegC) | #REF! | 6.8184 | 0 | 1.6149 | 5.5265 | #REF! |  |  |  | 1.6149 | 4.8134 | #REF! |  |  |  | 1.6149 | 4.1691 | #REF! |  |  |  | 1.6149 | 3.6938 | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #VALUE! | 0 | 1.6149 | n/a | #REF! |  |  |  | 1.6149 | n/a | #REF! |  |  |  | 1.6149 | n/a | #REF! |  |  |  | 1.6149 | n/a | #REF!
Lighting: 30% reduction from MNECB | #REF! | 29.4419 | 0 | 7.8991 | 23.1227 | #REF! |  |  |  | 7.8991 | 23.0726 | #REF! |  |  |  | 7.8991 | 23.02 | #REF! |  |  |  | 7.8991 | 22.5091 | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #VALUE! | 0 | 0.8767 | n/a | #REF! |  |  |  | 0.8767 | n/a | #REF! |  |  |  | 0.8767 | n/a | #REF! |  |  |  | 0.8767 | n/a | #REF!
HRV | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
DCV for all occupied zones | #REF! | 25.9571 | 0 | 2.7634 | 23.7464 | #REF! |  |  |  | 2.7634 | 16.8029 | #REF! |  |  |  | 2.7634 | 11.0693 | #REF! |  |  |  | 2.7634 | 8.5328 | #REF!
Cold Deck Reset to eliminate reheat | #REF! | 133.9286 | 0 | 11.1271 | 125.0269 | #REF! |  |  |  | 11.1271 | 129.1073 | #REF! |  |  |  | 11.1271 | 121.234 | #REF! |  |  |  | 11.1271 | 109.4109 | #REF!
VSD/VFD on large hp AHU | #REF! | #VALUE! | 0 | 3.2403 | n/a | #REF! |  |  |  | 3.2403 | n/a | #REF! |  |  |  | 3.2403 | n/a | #REF! |  |  |  | 3.2403 | n/a | #REF!
VSP on large hp heating/cooling pumps | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Solar Wall for ventilation preheat | #REF! | 166.4379 | 0 | 7.1316 | 160.7326 | #REF! |  |  |  | 7.1316 | 158.7604 | #REF! |  |  |  | 7.1316 | 158.4761 | #REF! |  |  |  | 7.1316 | 159.8921 | #REF!
Solar DHW | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Dry Bulb Economizer Control | #REF! | #VALUE! | 0 | 4.4536 | n/a | #REF! |  |  |  | 4.4536 | n/a | #REF! |  |  |  | 4.4536 | n/a | #REF! |  |  |  | 4.4536 | n/a | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #VALUE! | 0 | 7.2591 | n/a | #REF! |  |  |  | 7.2591 | n/a | #REF! |  |  |  | 7.2591 | n/a | #REF! |  |  |  | 7.2591 | n/a | #REF!
Archetype 4A-Hotel Type Accomodation (kWh/m2 floor area)
Exempler Building #414 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $
Base case | 0 | 0 | 0
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | 0 | 0 | #REF! | #REF! |  |  |  | 83.1481 | #REF! | #REF! |  |  |  | 83.1481 | #REF! | #REF! |  |  |  | 83.1481 | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | #REF! | #REF! |  |  |  | 79.6684 | #REF! | #REF! |  |  |  | 66.8563 | #REF! | #REF! |  |  |  | 66.8563 | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | 0 | 74.0905 | #REF! | #REF! |  |  |  | 74.0905 | #REF! | #REF! |  |  |  | 74.0905 | #REF! | #REF! |  |  |  | 74.0905 | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | 0 | 0 | #REF! | #REF! |  |  |  | 22.6608 | #REF! | #REF! |  |  |  | 24.8947 | #REF! | #REF! |  |  |  | 24.8947 | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | 0 | 11.132 | #REF! | #REF! |  |  |  | 11.132 | #REF! | #REF! |  |  |  | 11.132 | #REF! | #REF! |  |  |  | 11.132 | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | 0 | 11.132 | #REF! | #REF! |  |  |  | 11.132 | #REF! | #REF! |  |  |  | 11.132 | #REF! | #REF! |  |  |  | 11.132 | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | 0 | 18.4237 | #REF! | #REF! |  |  |  | 18.4237 | #REF! | #REF! |  |  |  | 18.4237 | #REF! | #REF! |  |  |  | 18.4237 | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | 0 | 6.0434 | #REF! | #REF! |  |  |  | 6.0434 | #REF! | #REF! |  |  |  | 6.0434 | #REF! | #REF! |  |  |  | 6.0434 | #REF! | #REF!
HRV | #REF! | #REF! | 0 | 65.0422 | #REF! | #REF! |  |  |  | 65.0422 | #REF! | #REF! |  |  |  | 65.0422 | #REF! | #REF! |  |  |  | 65.0422 | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | 0 | 19.0488 | #REF! | #REF! |  |  |  | 19.0488 | #REF! | #REF! |  |  |  | 19.0488 | #REF! | #REF! |  |  |  | 19.0488 | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | 0 | 0.87162 | #REF! | #REF! |  |  |  | 0.87162 | #REF! | #REF! |  |  |  | 0.87162 | #REF! | #REF! |  |  |  | 0.87162 | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | 0 | 0.68345 | #REF! | #REF! |  |  |  | 0.68345 | #REF! | #REF! |  |  |  | 0.68345 | #REF! | #REF! |  |  |  | 0.68345 | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | 0 | 2.8893 | #REF! | #REF! |  |  |  | 2.8893 | #REF! | #REF! |  |  |  | 2.8893 | #REF! | #REF! |  |  |  | 2.8893 | #REF! | #REF!
Solar Wall for ventilation preheat | #REF! | #REF! | 0 | 4.5622 | #REF! | #REF! |  |  |  | 4.5622 | #REF! | #REF! |  |  |  | 4.5622 | #REF! | #REF! |  |  |  | 4.5622 | #REF! | #REF!
Solar DHW | #REF! | #REF! | 0 | 102.1793 | #REF! | #REF! |  |  |  | 102.1793 | #REF! | #REF! |  |  |  | 102.1793 | #REF! | #REF! |  |  |  | 102.1793 | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | 0 | 0.34887 | #REF! | #REF! |  |  |  | 0.34887 | #REF! | #REF! |  |  |  | 0.34887 | #REF! | #REF! |  |  |  | 0.34887 | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | 0 | 3.1975 | #REF! | #REF! |  |  |  | 3.1975 | #REF! | #REF! |  |  |  | 3.1975 | #REF! | #REF! |  |  |  | 3.1975 | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | 0 | 11.4863 | #REF! | #REF! |  |  |  | 11.4863 | #REF! | #REF! |  |  |  | 11.4863 | #REF! | #REF! |  |  |  | 11.4863 | #REF! | #REF!
Archetype 4B-Dormitory (kWh/m2 floor area)
Exempler Building #111 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $
Base case | 0 | 0 | 0
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | 0 | 0 | #REF! | #REF! |  |  |  | 175.5089 | #REF! | #REF! |  |  |  | 175.5089 | #REF! | #REF! |  |  |  | 175.5089 | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | #REF! | #REF! |  |  |  | 53.1036 | #REF! | #REF! |  |  |  | 44.5635 | #REF! | #REF! |  |  |  | 44.5635 | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | 0 | 128.8464 | #REF! | #REF! |  |  |  | 128.8464 | #REF! | #REF! |  |  |  | 128.8464 | #REF! | #REF! |  |  |  | 128.8464 | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | 0 | 0 | #REF! | #REF! |  |  |  | 31.4818 | #REF! | #REF! |  |  |  | 34.6528 | #REF! | #REF! |  |  |  | 34.6528 | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | 0 | 14.326 | #REF! | #REF! |  |  |  | 14.326 | #REF! | #REF! |  |  |  | 14.326 | #REF! | #REF! |  |  |  | 14.326 | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | 0 | 14.326 | #REF! | #REF! |  |  |  | 14.326 | #REF! | #REF! |  |  |  | 14.326 | #REF! | #REF! |  |  |  | 14.326 | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | 0 | 18.0825 | #REF! | #REF! |  |  |  | 18.0825 | #REF! | #REF! |  |  |  | 18.0825 | #REF! | #REF! |  |  |  | 18.0825 | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | 0 | 7.7774 | #REF! | #REF! |  |  |  | 7.7774 | #REF! | #REF! |  |  |  | 7.7774 | #REF! | #REF! |  |  |  | 7.7774 | #REF! | #REF!
HRV | #REF! | #REF! | 0 | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | 0 | 24.5143 | #REF! | #REF! |  |  |  | 24.5143 | #REF! | #REF! |  |  |  | 24.5143 | #REF! | #REF! |  |  |  | 24.5143 | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | 0 | 1.371 | #REF! | #REF! |  |  |  | 1.371 | #REF! | #REF! |  |  |  | 1.371 | #REF! | #REF! |  |  |  | 1.371 | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | 0 | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | 0 | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF!
Solar Wall for ventilation preheat | #REF! | #REF! | 0 | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF!
Solar DHW | #REF! | #REF! | 0 | 50.5115 | #REF! | #REF! |  |  |  | 50.5115 | #REF! | #REF! |  |  |  | 50.5115 | #REF! | #REF! |  |  |  | 50.5115 | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | 0 | 0.54874 | #REF! | #REF! |  |  |  | 0.54874 | #REF! | #REF! |  |  |  | 0.54874 | #REF! | #REF! |  |  |  | 0.54874 | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | 0 | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | 0 | 10.0173 | #REF! | #REF! |  |  |  | 10.0173 | #REF! | #REF! |  |  |  | 10.0173 | #REF! | #REF! |  |  |  | 10.0173 | #REF! | #REF!
Archetype 4C-Barracks (kWh/m2 floor area)
Exempler Building #231 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $
Base case | 0 | 0 | 0
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 238.1549 | 636.094 | #REF! |  |  |  | 238.1549 | 481.7145 | #REF! |  |  |  | 238.1549 | n/a | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | n/a | #REF! |  |  |  | 159.31 | 218.7939 | #REF! |  |  |  | 133.69 | 53.5345 | #REF! |  |  |  | 133.69 | n/a | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #VALUE! | 0 | 66.7681 | n/a | #REF! |  |  |  | 66.7681 | 997.0749 | #REF! |  |  |  | 66.7681 | 1092.0531 | #REF! |  |  |  | 66.7681 | n/a | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 59.8662 | 52.3548 | #REF! |  |  |  | 66.5537 | 28.9744 | #REF! |  |  |  | 66.5537 | n/a | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #VALUE! | 0 | 2.8288 | n/a | #REF! |  |  |  | 2.8288 | 3.2414 | #REF! |  |  |  | 2.8288 | 2.2598 | #REF! |  |  |  | 2.8288 | n/a | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #VALUE! | 0 | 2.8288 | n/a | #REF! |  |  |  | 2.8288 | 3.6567 | #REF! |  |  |  | 2.8288 | 2.5929 | #REF! |  |  |  | 2.8288 | n/a | #REF!
Lighting: 30% reduction from MNECB | #REF! | #VALUE! | 0 | 18.4573 | n/a | #REF! |  |  |  | 18.4573 | 17.3694 | #REF! |  |  |  | 18.4573 | 17.4492 | #REF! |  |  |  | 18.4573 | n/a | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #VALUE! | 0 | 1.5357 | n/a | #REF! |  |  |  | 1.5357 | 3.2514 | #REF! |  |  |  | 1.5357 | 3.2436 | #REF! |  |  |  | 1.5357 | n/a | #REF!
HRV | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | 0 | #REF! |  |  |  | 0 | 0 | #REF! |  |  |  | 0 | n/a | #REF!
DCV for all occupied zones | #REF! | #VALUE! | 0 | 4.8407 | n/a | #REF! |  |  |  | 4.8407 | 10.1669 | #REF! |  |  |  | 4.8407 | 10.2051 | #REF! |  |  |  | 4.8407 | n/a | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #VALUE! | 0 | 4.8729 | n/a | #REF! |  |  |  | 4.8729 | n/a | #REF! |  |  |  | 4.8729 | n/a | #REF! |  |  |  | 4.8729 | n/a | #REF!
VSD/VFD on large hp AHU | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | 0 | #REF! |  |  |  | 0 | 0 | #REF! |  |  |  | 0 | n/a | #REF!
VSP on large hp heating/cooling pumps | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Solar Wall for ventilation preheat | #REF! | #VALUE! | 0 | 6.2463 | n/a | #REF! |  |  |  | 6.2463 | -25.152 | #REF! |  |  |  | 6.2463 | -25.152 | #REF! |  |  |  | 6.2463 | n/a | #REF!
Solar DHW | #REF! | #VALUE! | 0 | 81.6065 | n/a | #REF! |  |  |  | 81.6065 | 227.5138 | #REF! |  |  |  | 81.6065 | 227.5138 | #REF! |  |  |  | 81.6065 | n/a | #REF!
Dry Bulb Economizer Control | #REF! | #VALUE! | 0 | 1.9504 | n/a | #REF! |  |  |  | 1.9504 | n/a | #REF! |  |  |  | 1.9504 | n/a | #REF! |  |  |  | 1.9504 | n/a | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #VALUE! | 0 | 4.1327 | n/a | #REF! |  |  |  | 4.1327 | 7.5957 | #REF! |  |  |  | 4.1327 | 4.7591 | #REF! |  |  |  | 4.1327 | n/a | #REF!
Archetype 4D-Accomodation Building (kWh/m2 floor area)
Exempler Building #260 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m^2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m^2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m^2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m^2) | Current Payback (yrs) | Total m2 Principal Required $
Base case | 0 | 0 | 0
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #REF! | 0 | 0 | #REF! | #REF! |  |  |  | 379.4191 | #REF! | #REF! |  |  |  | 379.4191 | #REF! | #REF! |  |  |  | 379.4191 | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | #REF! | #REF! |  |  |  | 175.8698 | #REF! | #REF! |  |  |  | 175.8698 | #REF! | #REF! |  |  |  | 147.5867 | #REF! | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #REF! | 0 | 111.2726 | #REF! | #REF! |  |  |  | 111.2726 | #REF! | #REF! |  |  |  | 111.2726 | #REF! | #REF! |  |  |  | 111.2726 | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #REF! | 0 | 0 | #REF! | #REF! |  |  |  | 111.0801 | #REF! | #REF! |  |  |  | 121.2078 | #REF! | #REF! |  |  |  | 121.2078 | #REF! | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #REF! | 0 | 31.7976 | #REF! | #REF! |  |  |  | 31.7976 | #REF! | #REF! |  |  |  | 31.7976 | #REF! | #REF! |  |  |  | 31.7976 | #REF! | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #REF! | 0 | 31.7976 | #REF! | #REF! |  |  |  | 31.7976 | #REF! | #REF! |  |  |  | 31.7976 | #REF! | #REF! |  |  |  | 31.7976 | #REF! | #REF!
Lighting: 30% reduction from MNECB | #REF! | #REF! | 0 | 18.5864 | #REF! | #REF! |  |  |  | 18.5864 | #REF! | #REF! |  |  |  | 18.5864 | #REF! | #REF! |  |  |  | 18.5864 | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #REF! | 0 | 17.2625 | #REF! | #REF! |  |  |  | 17.2625 | #REF! | #REF! |  |  |  | 17.2625 | #REF! | #REF! |  |  |  | 17.2625 | #REF! | #REF!
HRV | #REF! | #REF! | 0 | 468.774 | #REF! | #REF! |  |  |  | 468.774 | #REF! | #REF! |  |  |  | 468.774 | #REF! | #REF! |  |  |  | 468.774 | #REF! | #REF!
DCV for all occupied zones | #REF! | #REF! | 0 | 54.4115 | #REF! | #REF! |  |  |  | 54.4115 | #REF! | #REF! |  |  |  | 54.4115 | #REF! | #REF! |  |  |  | 54.4115 | #REF! | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #REF! | 0 | 24.344 | #REF! | #REF! |  |  |  | 24.344 | #REF! | #REF! |  |  |  | 24.344 | #REF! | #REF! |  |  |  | 24.344 | #REF! | #REF!
VSD/VFD on large hp AHU | #REF! | #REF! | 0 | 13.1963 | #REF! | #REF! |  |  |  | 13.1963 | #REF! | #REF! |  |  |  | 13.1963 | #REF! | #REF! |  |  |  | 13.1963 | #REF! | #REF!
VSP on large hp heating/cooling pumps | #REF! | #REF! | 0 | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF!
Solar Wall for ventilation preheat | #REF! | #REF! | 0 | 28.0846 | #REF! | #REF! |  |  |  | 28.0846 | #REF! | #REF! |  |  |  | 28.0846 | #REF! | #REF! |  |  |  | 28.0846 | #REF! | #REF!
Solar DHW | #REF! | #REF! | 0 | 122.3064 | #REF! | #REF! |  |  |  | 122.3064 | #REF! | #REF! |  |  |  | 122.3064 | #REF! | #REF! |  |  |  | 122.3064 | #REF! | #REF!
Dry Bulb Economizer Control | #REF! | #REF! | 0 | 9.7437 | #REF! | #REF! |  |  |  | 9.7437 | #REF! | #REF! |  |  |  | 9.7437 | #REF! | #REF! |  |  |  | 9.7437 | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #REF! | 0 | 36.5199 | #REF! | #REF! |  |  |  | 36.5199 | #REF! | #REF! |  |  |  | 36.5199 | #REF! | #REF! |  |  |  | 36.5199 | #REF! | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #REF! | 0 | 26.9986 | #REF! | #REF! |  |  |  | 26.9986 | #REF! | #REF! |  |  |  | 26.9986 | #REF! | #REF! |  |  |  | 26.9986 | #REF! | #REF!
Archetype 5A-Gym and Fitness Centre (kWh/m2 floor area)
Exempler Building #58 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $
Base case | 0 | 0 | 0
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 121.7849 | 411.9754 | #REF! |  |  |  | 121.7849 | n/a | #REF! |  |  |  | 121.7849 | 205.429 | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | n/a | #REF! |  |  |  | 128.0565 | 137.953 | #REF! |  |  |  | 107.4626 | n/a | #REF! |  |  |  | 107.4626 | 34.2071 | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #VALUE! | 0 | 35.4164 | n/a | #REF! |  |  |  | 35.4164 | 826.0577 | #REF! |  |  |  | 35.4164 | n/a | #REF! |  |  |  | 35.4164 | 462.8505 | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 10.4947 | 10.8498 | #REF! |  |  |  | 11.4477 | n/a | #REF! |  |  |  | 11.4477 | 3.411 | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #VALUE! | 0 | 1.9468 | n/a | #REF! |  |  |  | 1.9468 | 3.586 | #REF! |  |  |  | 1.9468 | n/a | #REF! |  |  |  | 1.9468 | 2.1791 | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #VALUE! | 0 | 1.9468 | n/a | #REF! |  |  |  | 1.9468 | 4.9284 | #REF! |  |  |  | 1.9468 | n/a | #REF! |  |  |  | 1.9468 | 2.6377 | #REF!
Lighting: 30% reduction from MNECB | #REF! | #VALUE! | 0 | 24.8076 | n/a | #REF! |  |  |  | 24.8076 | 12.956 | #REF! |  |  |  | 24.8076 | n/a | #REF! |  |  |  | 24.8076 | 20.36 | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #VALUE! | 0 | 1.0569 | n/a | #REF! |  |  |  | 1.0569 | 1.5061 | #REF! |  |  |  | 1.0569 | n/a | #REF! |  |  |  | 1.0569 | 1.5061 | #REF!
HRV | #REF! | #VALUE! | 0 | 142.7667 | n/a | #REF! |  |  |  | 142.7667 | 666.9781 | #REF! |  |  |  | 142.7667 | n/a | #REF! |  |  |  | 142.7667 | 620.1261 | #REF!
DCV for all occupied zones | #REF! | #VALUE! | 0 | 3.3314 | n/a | #REF! |  |  |  | 3.3314 | 10.7215 | #REF! |  |  |  | 3.3314 | n/a | #REF! |  |  |  | 3.3314 | 4.7695 | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #VALUE! | 0 | 2.5797 | n/a | #REF! |  |  |  | 2.5797 | 8.6802 | #REF! |  |  |  | 2.5797 | n/a | #REF! |  |  |  | 2.5797 | 6.9601 | #REF!
VSD/VFD on large hp AHU | #REF! | #VALUE! | 0 | 1.6436 | n/a | #REF! |  |  |  | 1.6436 | 1.4267 | #REF! |  |  |  | 1.6436 | n/a | #REF! |  |  |  | 1.6436 | 0.53147 | #REF!
VSP on large hp heating/cooling pumps | #REF! | #VALUE! | 0 | 2.0228 | n/a | #REF! |  |  |  | 2.0228 | 6.9924 | #REF! |  |  |  | 2.0228 | n/a | #REF! |  |  |  | 2.0228 | 6.9924 | #REF!
Solar Wall for ventilation preheat | #REF! | #VALUE! | 0 | 4.409 | n/a | #REF! |  |  |  | 4.409 | 141.4179 | #REF! |  |  |  | 4.409 | n/a | #REF! |  |  |  | 4.409 | 141.7566 | #REF!
Solar DHW | #REF! | #VALUE! | 0 | 5.1842 | n/a | #REF! |  |  |  | 5.1842 | 179.6394 | #REF! |  |  |  | 5.1842 | n/a | #REF! |  |  |  | 5.1842 | 180.1043 | #REF!
Dry Bulb Economizer Control | #REF! | #VALUE! | 0 | 1.0325 | n/a | #REF! |  |  |  | 1.0325 | 2.8202 | #REF! |  |  |  | 1.0325 | n/a | #REF! |  |  |  | 1.0325 | 2.6107 | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #VALUE! | 0 | 8.3447 | n/a | #REF! |  |  |  | 8.3447 | 25.0329 | #REF! |  |  |  | 8.3447 | n/a | #REF! |  |  |  | 8.3447 | 20.4562 | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #VALUE! | 0 | 2.5917 | n/a | #REF! |  |  |  | 2.5917 | 5.1281 | #REF! |  |  |  | 2.5917 | n/a | #REF! |  |  |  | 2.5917 | 2.57 | #REF!
Archetype 5C-Sports Centre (kWh/m2 floor area)
Exempler Building #362 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $
Base case | 0 | 0 | 0
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 186.2082 | 1097.667 | #REF! |  |  |  | 186.2082 | n/a | #REF! |  |  |  | 186.2082 | n/a | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | n/a | #REF! |  |  |  | 142.0559 | 305.3718 | #REF! |  |  |  | 119.2107 | n/a | #REF! |  |  |  | 119.2107 | n/a | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #VALUE! | 0 | 44.6772 | n/a | #REF! |  |  |  | 44.6772 | 650.7016 | #REF! |  |  |  | 44.6772 | n/a | #REF! |  |  |  | 44.6772 | n/a | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 18.0331 | 28.2257 | #REF! |  |  |  | 19.7443 | n/a | #REF! |  |  |  | 19.7443 | n/a | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #VALUE! | 0 | 2.2507 | n/a | #REF! |  |  |  | 2.2507 | 3.99 | #REF! |  |  |  | 2.2507 | n/a | #REF! |  |  |  | 2.2507 | n/a | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #VALUE! | 0 | 2.2507 | n/a | #REF! |  |  |  | 2.2507 | 6.7586 | #REF! |  |  |  | 2.2507 | n/a | #REF! |  |  |  | 2.2507 | n/a | #REF!
Lighting: 30% reduction from MNECB | #REF! | #VALUE! | 0 | 25.1382 | n/a | #REF! |  |  |  | 25.1382 | 12.6211 | #REF! |  |  |  | 25.1382 | n/a | #REF! |  |  |  | 25.1382 | n/a | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #VALUE! | 0 | 1.2219 | n/a | #REF! |  |  |  | 1.2219 | 1.3416 | #REF! |  |  |  | 1.2219 | n/a | #REF! |  |  |  | 1.2219 | n/a | #REF!
HRV | #REF! | #VALUE! | 0 | 52.3135 | n/a | #REF! |  |  |  | 52.3135 | 54.1311 | #REF! |  |  |  | 52.3135 | n/a | #REF! |  |  |  | 52.3135 | n/a | #REF!
DCV for all occupied zones | #REF! | #VALUE! | 0 | 3.8514 | n/a | #REF! |  |  |  | 3.8514 | 1.7941 | #REF! |  |  |  | 3.8514 | n/a | #REF! |  |  |  | 3.8514 | n/a | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #VALUE! | 0 | 3.1017 | n/a | #REF! |  |  |  | 3.1017 | 10.0913 | #REF! |  |  |  | 3.1017 | n/a | #REF! |  |  |  | 3.1017 | n/a | #REF!
VSD/VFD on large hp AHU | #REF! | #VALUE! | 0 | 1.0635 | n/a | #REF! |  |  |  | 1.0635 | 1.9131 | #REF! |  |  |  | 1.0635 | n/a | #REF! |  |  |  | 1.0635 | n/a | #REF!
VSP on large hp heating/cooling pumps | #REF! | #VALUE! | 0 | 6.8543 | n/a | #REF! |  |  |  | 6.8543 | 106.4175 | #REF! |  |  |  | 6.8543 | n/a | #REF! |  |  |  | 6.8543 | n/a | #REF!
Solar Wall for ventilation preheat | #REF! | #VALUE! | 0 | 11.044 | n/a | #REF! |  |  |  | 11.044 | 241.1667 | #REF! |  |  |  | 11.044 | n/a | #REF! |  |  |  | 11.044 | n/a | #REF!
Solar DHW | #REF! | #VALUE! | 0 | 3.4629 | n/a | #REF! |  |  |  | 3.4629 | 182.5841 | #REF! |  |  |  | 3.4629 | n/a | #REF! |  |  |  | 3.4629 | n/a | #REF!
Dry Bulb Economizer Control | #REF! | #VALUE! | 0 | 1.5471 | n/a | #REF! |  |  |  | 1.5471 | 342.2752 | #REF! |  |  |  | 1.5471 | n/a | #REF! |  |  |  | 1.5471 | n/a | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #VALUE! | 0 | 6.8948 | n/a | #REF! |  |  |  | 6.8948 | n/a | #REF! |  |  |  | 6.8948 | n/a | #REF! |  |  |  | 6.8948 | n/a | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #VALUE! | 0 | 4.0469 | n/a | #REF! |  |  |  | 4.0469 | 6.1598 | #REF! |  |  |  | 4.0469 | n/a | #REF! |  |  |  | 4.0469 | n/a | #REF!
Archetype 5D-Sports and Arena (kWh/m2 floor area)
Exempler Building #405 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $
Base case | 0 | 0 | 0
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 454.1983 | n/a | #REF! |  |  |  | 454.1983 | n/a | #REF! |  |  |  | 454.1983 | n/a | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | n/a | #REF! |  |  |  | 159.31 | n/a | #REF! |  |  |  | 133.69 | n/a | #REF! |  |  |  | 133.69 | n/a | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #VALUE! | 0 | 45.7054 | n/a | #REF! |  |  |  | 45.7054 | n/a | #REF! |  |  |  | 45.7054 | n/a | #REF! |  |  |  | 45.7054 | n/a | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 51.5651 | n/a | #REF! |  |  |  | 56.4157 | n/a | #REF! |  |  |  | 56.4157 | n/a | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Lighting: 30% reduction from MNECB | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
HRV | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
DCV for all occupied zones | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
VSD/VFD on large hp AHU | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
VSP on large hp heating/cooling pumps | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Solar Wall for ventilation preheat | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Solar DHW | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Dry Bulb Economizer Control | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Archetype 6A-Office Building (kWh/m2 floor area)
Exempler Building #56 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $
Base case | 0 | 0 | 0
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | 0 | 0 | 0 | 0 | #REF! |  |  |  | 237.8235 | 916.9557 | #REF! |  |  |  | 237.8235 | 589.1036 | #REF! |  |  |  | 237.8235 | n/a | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | 0 | #REF! |  |  |  | 167.7265 | 620.3407 | #REF! |  |  |  | 140.7529 | 441.9356 | #REF! |  |  |  | 140.7529 | n/a | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #VALUE! | 0 | 109.8959 | n/a | #REF! |  |  |  | 109.8959 | n/a | #REF! |  |  |  | 109.8959 | n/a | #REF! |  |  |  | 109.8959 | n/a | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 22.8156 | 78.8522 | #REF! |  |  |  | 24.8255 | 29.0855 | #REF! |  |  |  | 24.8255 | 29.0855 | #REF!
Heating setpoint reduction (2 DegC) | #REF! | 156.8103 | 0 | 6.9111 | 151.2814 | #REF! |  |  |  | 6.9111 | 41.9752 | #REF! |  |  |  | 6.9111 | 302.7748 | #REF! |  |  |  | 6.9111 | 302.7748 | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #VALUE! | 0 | 6.9111 | n/a | #REF! |  |  |  | 6.9111 | n/a | #REF! |  |  |  | 6.9111 | n/a | #REF! |  |  |  | 6.9111 | n/a | #REF!
Lighting: 30% reduction from MNECB | #REF! | 53.3175 | 0 | 32.8859 | 27.0088 | #REF! |  |  |  | 32.8859 | 25.4952 | #REF! |  |  |  | 32.8859 | 25.3624 | #REF! |  |  |  | 32.8859 | 25.3624 | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | 6.6224 | 0 | 3.752 | 3.6209 | #REF! |  |  |  | 3.752 | 3.5512 | #REF! |  |  |  | 3.752 | 3.7817 | #REF! |  |  |  | 3.752 | n/a | #REF!
HRV | #REF! | 0 | 0 | 0 | 0 | #REF! |  |  |  | 0 | 0 | #REF! |  |  |  | 0 | 0 | #REF! |  |  |  | 0 | 0 | #REF!
DCV for all occupied zones | #REF! | 22.3901 | 0 | 11.8262 | 12.9291 | #REF! |  |  |  | 11.8262 | 18.8732 | #REF! |  |  |  | 11.8262 | n/a | #REF! |  |  |  | 11.8262 | 17.9585 | #REF!
Cold Deck Reset to eliminate reheat | #REF! | 1.4329 | 0 | 0.83544 | 0.76456 | #REF! |  |  |  | 0.83544 | 2.6311 | #REF! |  |  |  | 0.83544 | 1.3362 | #REF! |  |  |  | 0.83544 | 1.3362 | #REF!
VSD/VFD on large hp AHU | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | 0 | #REF! |  |  |  | 0 | 0 | #REF! |  |  |  | 0 | 0 | #REF!
VSP on large hp heating/cooling pumps | #REF! | #VALUE! | 0 | 0.81885 | n/a | #REF! |  |  |  | 0.81885 | 3.1801 | #REF! |  |  |  | 0.81885 | 7.0753 | #REF! |  |  |  | 0.81885 | 7.0753 | #REF!
Solar Wall for ventilation preheat | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Solar DHW | #REF! | 35.8705 | 0 | 11.1928 | 26.9162 | #REF! |  |  |  | 11.1928 | 26.9162 | #REF! |  |  |  | 11.1928 | 26.9162 | #REF! |  |  |  | 11.1928 | 26.9162 | #REF!
Dry Bulb Economizer Control | #REF! | #VALUE! | 0 | 0.33439 | n/a | #REF! |  |  |  | 0.33439 | n/a | #REF! |  |  |  | 0.33439 | n/a | #REF! |  |  |  | 0.33439 | n/a | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #VALUE! | 0 | 5.2867 | n/a | #REF! |  |  |  | 5.2867 | n/a | #REF! |  |  |  | 5.2867 | n/a | #REF! |  |  |  | 5.2867 | n/a | #REF!
Archetype 7A-Dining Hall (kWh/m2 floor area)
Exempler Building #120 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $
Base case | 0 | 0 | 0
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 82.3316 | n/a | #REF! |  |  |  | 82.3316 | n/a | #REF! |  |  |  | 82.3316 | 421.991 | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | n/a | #REF! |  |  |  | 140.836 | n/a | #REF! |  |  |  | 118.1869 | n/a | #REF! |  |  |  | 118.1869 | 53.7591 | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #VALUE! | 0 | 37.3852 | n/a | #REF! |  |  |  | 37.3852 | n/a | #REF! |  |  |  | 37.3852 | n/a | #REF! |  |  |  | 37.3852 | 832.6528 | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 20.2326 | n/a | #REF! |  |  |  | 22.4599 | n/a | #REF! |  |  |  | 22.4599 | 11.4241 | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #VALUE! | 0 | 2.138 | n/a | #REF! |  |  |  | 2.138 | n/a | #REF! |  |  |  | 2.138 | n/a | #REF! |  |  |  | 2.138 | 1.8731 | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #VALUE! | 0 | 2.138 | n/a | #REF! |  |  |  | 2.138 | n/a | #REF! |  |  |  | 2.138 | n/a | #REF! |  |  |  | 2.138 | n/a | #REF!
Lighting: 30% reduction from MNECB | #REF! | #VALUE! | 0 | 36.1831 | n/a | #REF! |  |  |  | 36.1831 | n/a | #REF! |  |  |  | 36.1831 | n/a | #REF! |  |  |  | 36.1831 | 13.0492 | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #VALUE! | 0 | 1.1607 | n/a | #REF! |  |  |  | 1.1607 | n/a | #REF! |  |  |  | 1.1607 | n/a | #REF! |  |  |  | 1.1607 | 0.95818 | #REF!
HRV | #REF! | #VALUE! | 0 | 24.3291 | n/a | #REF! |  |  |  | 24.3291 | n/a | #REF! |  |  |  | 24.3291 | n/a | #REF! |  |  |  | 24.3291 | 22.717 | #REF!
DCV for all occupied zones | #REF! | #VALUE! | 0 | 3.6584 | n/a | #REF! |  |  |  | 3.6584 | n/a | #REF! |  |  |  | 3.6584 | n/a | #REF! |  |  |  | 3.6584 | 2.1039 | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #VALUE! | 0 | 2.7621 | n/a | #REF! |  |  |  | 2.7621 | n/a | #REF! |  |  |  | 2.7621 | n/a | #REF! |  |  |  | 2.7621 | 4.665 | #REF!
VSD/VFD on large hp AHU | #REF! | #VALUE! | 0 | 0.3157 | n/a | #REF! |  |  |  | 0.3157 | n/a | #REF! |  |  |  | 0.3157 | n/a | #REF! |  |  |  | 0.3157 | 0.097161 | #REF!
VSP on large hp heating/cooling pumps | #REF! | #VALUE! | 0 | 3.9544 | n/a | #REF! |  |  |  | 3.9544 | n/a | #REF! |  |  |  | 3.9544 | n/a | #REF! |  |  |  | 3.9544 | n/a | #REF!
Solar Wall for ventilation preheat | #REF! | #VALUE! | 0 | 3.2455 | n/a | #REF! |  |  |  | 3.2455 | n/a | #REF! |  |  |  | 3.2455 | n/a | #REF! |  |  |  | 3.2455 | -20.6108 | #REF!
Solar DHW | #REF! | #VALUE! | 0 | 15.419 | n/a | #REF! |  |  |  | 15.419 | n/a | #REF! |  |  |  | 15.419 | n/a | #REF! |  |  |  | 15.419 | 27.5117 | #REF!
Dry Bulb Economizer Control | #REF! | #VALUE! | 0 | 0.96104 | n/a | #REF! |  |  |  | 0.96104 | n/a | #REF! |  |  |  | 0.96104 | n/a | #REF! |  |  |  | 0.96104 | 4.5895 | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #VALUE! | 0 | 4.7588 | n/a | #REF! |  |  |  | 4.7588 | n/a | #REF! |  |  |  | 4.7588 | n/a | #REF! |  |  |  | 4.7588 | 7.8426 | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #VALUE! | 0 | 3.4237 | n/a | #REF! |  |  |  | 3.4237 | n/a | #REF! |  |  |  | 3.4237 | n/a | #REF! |  |  |  | 3.4237 | 2.7663 | #REF!
Archetype 9A-Workshop Building (kWh/m2 floor area)
Exempler Building #152 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $
Base case | 374.29 | 299.432 | 374.29
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | 291.072 | 363.84 | 0 | 0 | #REF! |  |  |  | 236.4727 | 342.3063 | #REF! |  |  |  | 236.4727 | n/a | #REF! |  |  |  | 236.4727 | 173.3361 | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | 0 | #REF! |  |  |  | 162.067 | 244.1938 | #REF! |  |  |  | 136.0036 | n/a | #REF! |  |  |  | 136.0036 | 29.0266 | #REF!
Windows: Double Glazed to Triple LowE | #REF! | 2617.2126 | 373.47 | 35.5951 | 2289.9605 | #REF! |  |  |  | 35.5951 | 618.1 | #REF! |  |  |  | 35.5951 | n/a | #REF! |  |  |  | 35.5951 | 539.2223 | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #VALUE! | 374.29 | 0 | n/a | #REF! |  |  |  | 22.8663 | 12.0977 | #REF! |  |  |  | 24.7923 | n/a | #REF! |  |  |  | 24.7923 | 3.5708 | #REF!
Heating setpoint reduction (2 DegC) | #REF! | 259.2598 | 319.74 | 1.8735 | 1.969 | #REF! |  |  |  | 1.8735 | 1.7111 | #REF! |  |  |  | 1.8735 | n/a | #REF! |  |  |  | 1.8735 | 1.127 | #REF!
Temperature set back of 2 DegC afterhours | #REF! | 268.4989 | 330.78 | 1.8735 | 2.3761 | #REF! |  |  |  | 1.8735 | 2.0936 | #REF! |  |  |  | 1.8735 | n/a | #REF! |  |  |  | 1.8735 | 1.3827 | #REF!
Lighting: 30% reduction from MNECB | #REF! | 335.7547 | 388.2 | 19.4587 | 9.6278 | #REF! |  |  |  | 19.4587 | 11.2008 | #REF! |  |  |  | 19.4587 | n/a | #REF! |  |  |  | 19.4587 | 11.4096 | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | 301.375 | 374.29 | 1.0171 | 1.1293 | #REF! |  |  |  | 1.0171 | 1.1279 | #REF! |  |  |  | 1.0171 | n/a | #REF! |  |  |  | 1.0171 | 1.1279 | #REF!
HRV | #REF! | 1262.5522 | 369.27 | 88.1167 | 896.6429 | #REF! |  |  |  | 88.1167 | 614.902 | #REF! |  |  |  | 88.1167 | n/a | #REF! |  |  |  | 88.1167 | 436.6535 | #REF!
DCV for all occupied zones | #REF! | 307.2838 | 374.29 | 3.2059 | 5.2871 | #REF! |  |  |  | 3.2059 | 4.5947 | #REF! |  |  |  | 3.2059 | n/a | #REF! |  |  |  | 3.2059 | 3.1288 | #REF!
Cold Deck Reset to eliminate reheat | #REF! | 309.5296 | 374.29 | 3.2273 | 7.5158 | #REF! |  |  |  | 3.2273 | 6.8654 | #REF! |  |  |  | 3.2273 | n/a | #REF! |  |  |  | 3.2273 | 4.7759 | #REF!
VSD/VFD on large hp AHU | #REF! | 300.6485 | 374.29 | 1.1066 | 0.33121 | #REF! |  |  |  | 1.1066 | 0.26182 | #REF! |  |  |  | 1.1066 | n/a | #REF! |  |  |  | 1.1066 | 0.26182 | #REF!
VSP on large hp heating/cooling pumps | #REF! | #VALUE! | 374.29 | 3.1632 | n/a | #REF! |  |  |  | 3.1632 | 5.8562 | #REF! |  |  |  | 3.1632 | n/a | #REF! |  |  |  | 3.1632 | 5.8562 | #REF!
Solar Wall for ventilation preheat | #REF! | 393.7894 | 374.29 | 10.3421 | 86.0838 | #REF! |  |  |  | 10.3421 | 86.0838 | #REF! |  |  |  | 10.3421 | n/a | #REF! |  |  |  | 10.3421 | 86.0838 | #REF!
Solar DHW | #REF! | 500.1555 | 371.05 | 8.107 | 196.8298 | #REF! |  |  |  | 8.107 | 196.8298 | #REF! |  |  |  | 8.107 | n/a | #REF! |  |  |  | 8.107 | 196.8298 | #REF!
Dry Bulb Economizer Control | #REF! | 363.5662 | 374.86 | 1.1229 | 62.7799 | #REF! |  |  |  | 1.1229 | 77.5256 | #REF! |  |  |  | 1.1229 | n/a | #REF! |  |  |  | 1.1229 | n/a | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #VALUE! | 374.29 | 5.9195 | n/a | #REF! |  |  |  | 5.9195 | 11.8519 | #REF! |  |  |  | 5.9195 | n/a | #REF! |  |  |  | 5.9195 | 5.395 | #REF!
Retro-commissioning on thermostats and AHU | #REF! | 275.9808 | 337.42 | 3.5792 | 3.1815 | #REF! |  |  |  | 3.5792 | 2.6436 | #REF! |  |  |  | 3.5792 | n/a | #REF! |  |  |  | 3.5792 | 1.5115 | #REF!
Archetype 11A-Retail Building (kWh/m2 floor area)
Exempler Building #119 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $
Base case | 0 | 0 | 0
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 246.6607 | n/a | #REF! |  |  |  | 246.6607 | n/a | #REF! |  |  |  | 246.6607 | 246.6607 | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | n/a | #REF! |  |  |  | 159.31 | n/a | #REF! |  |  |  | 133.69 | n/a | #REF! |  |  |  | 133.69 | 133.69 | #REF!
Windows: Double Glazed to Triple LowE | #REF! | #VALUE! | 0 | 186.2711 | n/a | #REF! |  |  |  | 186.2711 | n/a | #REF! |  |  |  | 186.2711 | n/a | #REF! |  |  |  | 186.2711 | 186.2711 | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 58.3527 | n/a | #REF! |  |  |  | 63.9352 | n/a | #REF! |  |  |  | 63.9352 | 63.9352 | #REF!
Heating setpoint reduction (2 DegC) | #REF! | #VALUE! | 0 | 12.9767 | n/a | #REF! |  |  |  | 12.9767 | n/a | #REF! |  |  |  | 12.9767 | n/a | #REF! |  |  |  | 10.8257 | 12.9767 | #REF!
Temperature set back of 2 DegC afterhours | #REF! | #VALUE! | 0 | 12.9767 | n/a | #REF! |  |  |  | 12.9767 | n/a | #REF! |  |  |  | 12.9767 | n/a | #REF! |  |  |  | 10.8257 | 12.9767 | #REF!
Lighting: 30% reduction from MNECB | #REF! | #VALUE! | 0 | 45.3263 | n/a | #REF! |  |  |  | 45.3263 | n/a | #REF! |  |  |  | 45.3263 | n/a | #REF! |  |  |  | 45.3263 | 45.3263 | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | #VALUE! | 0 | 7.0449 | n/a | #REF! |  |  |  | 7.0449 | n/a | #REF! |  |  |  | 7.0449 | n/a | #REF! |  |  |  | 5.9412 | 7.0449 | #REF!
HRV | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | 0 | #REF!
DCV for all occupied zones | #REF! | #VALUE! | 0 | 22.2055 | n/a | #REF! |  |  |  | 22.2055 | n/a | #REF! |  |  |  | 22.2055 | n/a | #REF! |  |  |  | 18.5046 | 22.2055 | #REF!
Cold Deck Reset to eliminate reheat | #REF! | #VALUE! | 0 | 22.3535 | n/a | #REF! |  |  |  | 22.3535 | n/a | #REF! |  |  |  | 22.3535 | n/a | #REF! |  |  |  | 19.4651 | 22.3535 | #REF!
VSD/VFD on large hp AHU | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | 0 | #REF!
VSP on large hp heating/cooling pumps | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | 0 | #REF!
Solar Wall for ventilation preheat | #REF! | #VALUE! | 0 | 7.1634 | n/a | #REF! |  |  |  | 7.1634 | n/a | #REF! |  |  |  | 7.1634 | n/a | #REF! |  |  |  | 7.1634 | 7.1634 | #REF!
Solar DHW | #REF! | #VALUE! | 0 | 24.9568 | n/a | #REF! |  |  |  | 24.9568 | n/a | #REF! |  |  |  | 24.9568 | n/a | #REF! |  |  |  | 19.5179 | 24.9568 | #REF!
Dry Bulb Economizer Control | #REF! | #VALUE! | 0 | 8.947 | n/a | #REF! |  |  |  | 8.947 | n/a | #REF! |  |  |  | 8.947 | n/a | #REF! |  |  |  | 7.7776 | 8.947 | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #VALUE! | 0 | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | 0 | #REF!
Retro-commissioning on thermostats and AHU | #REF! | #VALUE! | 0 | 13.6107 | n/a | #REF! |  |  |  | 13.6107 | n/a | #REF! |  |  |  | 13.6107 | n/a | #REF! |  |  |  | 13.6107 | 13.6107 | #REF!
Archetype 13A-Firehall (kWh/m2 floor area)
Exempler Building #19 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $ | Material Cost ($/m^2) | Labour Cost ($/m^2) | Design Cost ($/m^2) | Total Cost ($/m2) | Current Payback (yrs) | Total m2 Principal Required $
Base case | 227.46 | 181.968 | 227.46
Wall Insulation: Additional RSI 1.32 on ext. | #REF! | 175.856 | 219.82 | 0 | 0 | #REF! |  |  |  | 212.3694 | n/a | #REF! |  |  |  | 212.3694 | 545.6112 | #REF! |  |  |  | 212.3694 | n/a | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | 0 | 0 | #REF! |  |  |  | 122.4298 | n/a | #REF! |  |  |  | 102.7408 | 37.7524 | #REF! |  |  |  | 102.7408 | n/a | #REF!
Windows: Double Glazed to Triple LowE | #REF! | 2713.6183 | 226.6 | 51.5949 | 2491.0624 | #REF! |  |  |  | 51.5949 | n/a | #REF! |  |  |  | 51.5949 | 793.2305 | #REF! |  |  |  | 51.5949 | n/a | #REF!
Air tightness: vintage ACH to 0.27 ACH | #REF! | #VALUE! | 227.46 | 0 | n/a | #REF! |  |  |  | 49.7388 | n/a | #REF! |  |  |  | 53.0997 | 10.0446 | #REF! |  |  |  | 53.0997 | n/a | #REF!
Heating setpoint reduction (2 DegC) | #REF! | 155.7647 | 180.98 | 5.5783 | 6.5181 | #REF! |  |  |  | 5.5783 | n/a | #REF! |  |  |  | 5.5783 | 3.3345 | #REF! |  |  |  | 5.5783 | n/a | #REF!
Temperature set back of 2 DegC afterhours | #REF! | 187.0729 | 209.01 | 5.5783 | 15.4023 | #REF! |  |  |  | 5.5783 | n/a | #REF! |  |  |  | 5.5783 | 7.3148 | #REF! |  |  |  | 5.5783 | n/a | #REF!
Lighting: 30% reduction from MNECB | #REF! | 218.7051 | 248.53 | 17.361 | 5.9923 | #REF! |  |  |  | 17.361 | n/a | #REF! |  |  |  | 17.361 | 6.1501 | #REF! |  |  |  | 17.361 | n/a | #REF!
Occupancy Sensors (Lights/Plug Loads) | #REF! | 186.29 | 227.46 | 3.0284 | 1.8993 | #REF! |  |  |  | 3.0284 | n/a | #REF! |  |  |  | 3.0284 | 1.8993 | #REF! |  |  |  | 3.0284 | n/a | #REF!
HRV | #REF! | 340.2406 | 179.44 | 80.2903 | 132.4564 | #REF! |  |  |  | 80.2903 | n/a | #REF! |  |  |  | 80.2903 | 111.9815 | #REF! |  |  |  | 80.2903 | n/a | #REF!
DCV for all occupied zones | #REF! | 202.5543 | 227.46 | 9.5454 | 12.95 | #REF! |  |  |  | 9.5454 | n/a | #REF! |  |  |  | 9.5454 | 5.2157 | #REF! |  |  |  | 9.5454 | n/a | #REF!
Cold Deck Reset to eliminate reheat | #REF! | 190.0031 | 227.46 | 3.0394 | 5.6036 | #REF! |  |  |  | 3.0394 | n/a | #REF! |  |  |  | 3.0394 | 4.8289 | #REF! |  |  |  | 3.0394 | n/a | #REF!
VSD/VFD on large hp AHU | #REF! | 184.3964 | 227.46 | 1.1981 | 1.4699 | #REF! |  |  |  | 1.1981 | n/a | #REF! |  |  |  | 1.1981 | 0.57274 | #REF! |  |  |  | 1.1981 | n/a | #REF!
VSP on large hp heating/cooling pumps | #REF! | 181.968 | 227.46 | 0 | 0 | #REF! |  |  |  | 0 | n/a | #REF! |  |  |  | 0 | 0 | #REF! |  |  |  | 0 | n/a | #REF!
Solar Wall for ventilation preheat | #REF! | 156.0755 | 227.46 | 8.958 | -33.0589 | #REF! |  |  |  | 8.958 | n/a | #REF! |  |  |  | 8.958 | -33.0589 | #REF! |  |  |  | 8.958 | n/a | #REF!
Solar DHW | #REF! | 397.9003 | 220.16 | 20.3537 | 205.4893 | #REF! |  |  |  | 20.3537 | n/a | #REF! |  |  |  | 20.3537 | 205.4893 | #REF! |  |  |  | 20.3537 | n/a | #REF!
Dry Bulb Economizer Control | #REF! | 190.2101 | 227.46 | 1.2158 | 7.2695 | #REF! |  |  |  | 1.2158 | n/a | #REF! |  |  |  | 1.2158 | 4.581 | #REF! |  |  |  | 1.2158 | n/a | #REF!
DX Cooling COP Upgrade to COP 4.0 | #REF! | #VALUE! | 227.46 | 11.1444 | n/a | #REF! |  |  |  | 11.1444 | n/a | #REF! |  |  |  | 11.1444 | 62.4196 | #REF! |  |  |  | 11.1444 | n/a | #REF!
Retro-commissioning on thermostats and AHU | #REF! | 183.4088 | 206.29 | 7.0666 | 12.7235 | #REF! |  |  |  | 7.0666 | n/a | #REF! |  |  |  | 7.0666 | 5.1298 | #REF! |  |  |  | 7.0666 | n/a | #REF!
|  |  |  | 2013 Capital Investment Thousand $ | [7 empty] | Payback (yrs) using 2013 energy rates | [10 empty] | Payback (yrs) using 2013 Present Value until 2018 |  |  |  |  | Payback (yrs) using 2013 Present Value until 2023 |  |  |  |  | Payback (yrs) using 2013 Present Value until 2028 |  |  |  |  | Payback (yrs) using 2013 Present Value until 2033
ECM |  |  |  | post-2004 | 1980-2004 | 1960-1979 |  |  |  | pre-1960 | All | post-2004 | 1980-2004 | 1960-1979 |  | 1980-2004 | 1960-1979 | pre-1960 | All |  |  | All | post-2004 | 1980-2004 | 1960-1979 | pre-1960 | All | post-2004 | 1980-2004 | 1960-1979 | pre-1960 | All | post-2004 | 1980-2004 | 1960-1979 | pre-1960 | All | post-2004 | 1980-2004 | 1960-1979 | pre-1960 | All
Base case
Wall Insulation: Additional RSI 1.32 on ext. |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Roof: Additional RSI 2.11 to 3.52 on interior |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Windows: Double Glazed to Triple LowE |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Air tightness: vintage ACH to 0.27 ACH |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! |  |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF!
Heating setpoint reduction (2 DegC) |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Temperature set back of 2 DegC afterhours |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting: 30% reduction from MNECB |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Occupancy Sensors (Lights/Plug Loads) |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
HRV |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DCV for all occupied zones |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cold Deck Reset to eliminate reheat |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSD/VFD on large hp AHU |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
VSP on large hp heating/cooling pumps |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar Wall for ventilation preheat |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Solar DHW |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Dry Bulb Economizer Control |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DX Cooling COP Upgrade to COP 4.0 |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! |  |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF!
Retro-commissioning on thermostats and AHU |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total (Highlighted Measures Only) |  |  |  | #REF! | #REF! | #REF! | 0 | 0 | 0 | #REF! | #REF! | #REF! |  |  |  | #REF! | #REF! | #REF! | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note on A12: khaddad: 10% reduction in lighting and plug loads
Note on A15: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A21: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A22: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A35: khaddad: 10% reduction in lighting and plug loads
Note on A38: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A44: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A45: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A58: khaddad: 10% reduction in lighting and plug loads
Note on A61: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A67: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A68: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A81: khaddad: 10% reduction in lighting and plug loads
Note on A84: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A90: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A91: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A104: khaddad: 10% reduction in lighting and plug loads
Note on A107: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A113: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A114: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A127: khaddad: 10% reduction in lighting and plug loads
Note on A130: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A136: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A137: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A150: khaddad: 10% reduction in lighting and plug loads
Note on A153: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A159: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A160: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A173: khaddad: 10% reduction in lighting and plug loads
Note on A176: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A182: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A183: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A196: khaddad: 10% reduction in lighting and plug loads
Note on A199: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A205: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A206: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A219: khaddad: 10% reduction in lighting and plug loads
Note on A222: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A228: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A229: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A242: khaddad: 10% reduction in lighting and plug loads
Note on A245: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A251: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A252: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A265: khaddad: 10% reduction in lighting and plug loads
Note on A268: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A274: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A275: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A288: khaddad: 10% reduction in lighting and plug loads
Note on A291: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A297: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A298: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A311: khaddad: 10% reduction in lighting and plug loads
Note on A314: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A320: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A321: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A334: khaddad: 10% reduction in lighting and plug loads
Note on A337: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A343: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A344: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A357: khaddad: 10% reduction in lighting and plug loads
Note on A360: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A366: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A367: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A379: khaddad: 10% reduction in lighting and plug loads
Note on A382: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A388: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A389: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw

## BldgEUI
Archetype 1A-Hanger (kWh/m2 floor area)
Exempler Building Hanger4 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Total EUI | Building Heating Load | Natural Gas Use | Building DES Gas Use | Heating Electricity Use | Non Heating Electricity Use | Total | Building Heating Load | Natural Gas Use | Building DES Gas Use | Heating Electricity Use | Non Heating Electricity Use | Total | Building Heating Load | Natural Gas Use | Building DES Gas Use | Heating Electricity Use | Non Heating Electricity Use | Total | Building Heating Load | Natural Gas Use | Building DES Gas Use | Heating Electricity Use | Non Heating Electricity Use | ECM Applic Index V1 | ECM Applic Index V2 | ECM Applic Index V3 | ECM Applic Index V4 | ECM Model Index
Base case | 210.6905 | 92.9384 | 116.173 | 0 | 0 | 94.5175 | 314.8132 | 130.6826 | 163.3532 | 0 | 0 | 151.46 | 424.7969 | 216.4267 | 270.5334 | 0 | 0 | 154.2636 | 437.6162 | 273.3923 | 341.7403 | 0 | 0 | 95.8759 | 1 | 1 | 1 | 1 | 1
Wall Insulation: Additional RSI 1.32 on ext. | 202.8732 | 90.0145 | 112.5181 | 0 | 0 | 90.3551 | 302.3967 | 124.1268 | 155.1585 | 0 | 0 | 147.2382 | 407.3876 | 205.8949 | 257.3687 | 0 | 0 | 150.0189 | 413.1991 | 257.2561 | 321.5701 | 0 | 0 | 91.629 | 0 | 1 | 1 | 1 | 1
Roof: Additional RSI 1.76 to 2.11 on exterior | 202.8732 | 90.0145 | 112.5181 | 0 | 0 | 90.3551 | 302.3967 | 124.1268 | 155.1585 | 0 | 0 | 147.2382 | 407.3876 | 205.8949 | 257.3687 | 0 | 0 | 150.0189 | 413.1991 | 257.2561 | 321.5701 | 0 | 0 | 91.629 | 0 | 1 | 1 | 1 | 1
Roof: Additional RSI 2.11 to 3.52 on interior | 202.8732 | 90.0145 | 112.5181 | 0 | 0 | 90.3551 | 302.3967 | 124.1268 | 155.1585 | 0 | 0 | 147.2382 | 407.3876 | 205.8949 | 257.3687 | 0 | 0 | 150.0189 | 413.1991 | 257.2561 | 321.5701 | 0 | 0 | 91.629 | 0 | 1 | 1 | 1 | 1
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 202.3033 | 89.5598 | 111.9497 | 0 | 0 | 90.3536 | 286.2705 | 111.3212 | 139.1515 | 0 | 0 | 147.119 | 376.2357 | 181.0002 | 226.2503 | 0 | 0 | 149.9854 | 388.8871 | 237.8254 | 297.2817 | 0 | 0 | 91.6054 | 0 | 1 | 1 | 1 | 1
Windows: Double Glazed to Triple LowE | 203.34 | 90.448 | 113.06 | 0 | 0 | 90.28 | 307.67 | 128.368 | 160.46 | 0 | 0 | 147.21 | 417.54 | 214.016 | 267.52 | 0 | 0 | 150.02 | 432.18 | 272.44 | 340.55 | 0 | 0 | 91.63 | 1 | 1 | 1 | 1 | 1
Air tightness: vintage ACH to 0.27 ACH | 210.6905 | 92.9384 | 116.173 | 0 | 0 | 94.5175 | 298.2887 | 121.6495 | 152.0619 | 0 | 0 | 146.2268 | 404.7613 | 203.7991 | 254.7488 | 0 | 0 | 150.0125 | 405.7243 | 251.3249 | 314.1561 | 0 | 0 | 91.5682 | 0 | 1 | 1 | 1 | 1
Heating setpoint reduction (2 DegC) | 194.8818 | 83.3246 | 104.1558 | 0 | 0 | 90.7261 | 293.8558 | 117.3823 | 146.7279 | 0 | 0 | 147.1279 | 395.9472 | 196.8114 | 246.0142 | 0 | 0 | 149.933 | 411.2096 | 255.7366 | 319.6707 | 0 | 0 | 91.5389 | 1 | 1 | 1 | 1 | 1
Temperature set back of 2 DegC afterhours | 198.15 | 86.336 | 107.92 | 0 | 0 | 90.23 | 299.78 | 122.08 | 152.6 | 0 | 0 | 147.18 | 405.21 | 204.184 | 255.23 | 0 | 0 | 149.98 | 422.11 | 264.416 | 330.52 | 0 | 0 | 91.59 | 1 | 1 | 1 | 1 | 1
Lighting: 30% reduction from MNECB | 198.4801 | 97.5199 | 121.8998 | 0 | 0 | 76.5802 | 304.6207 | 136.2389 | 170.2987 | 0 | 0 | 134.3221 | 416.2965 | 223.2151 | 279.0189 | 0 | 0 | 137.2776 | 426.3653 | 277.9758 | 347.4697 | 0 | 0 | 78.8956 | 1 | 1 | 1 | 1 | 1
Occupancy Sensors (Lights/Plug Loads) | 201.2387 | 92.9384 | 116.173 | 0 | 0 | 85.0658 | 299.6672 | 130.6826 | 163.3532 | 0 | 0 | 136.314 | 409.3706 | 216.4267 | 270.5334 | 0 | 0 | 138.8372 | 428.0286 | 273.3923 | 341.7403 | 0 | 0 | 86.2883 | 1 | 1 | 1 | 1 | 0
HRV | 167.0384 | 60.5907 | 75.7384 | 0 | 0 | 91.3 | 265.9793 | 95.0237 | 118.7796 | 0 | 0 | 147.1997 | 419.304 | 215.4332 | 269.2915 | 0 | 0 | 150.0125 | 432.5918 | 272.5559 | 340.6949 | 0 | 0 | 91.8969 | 1 | 1 | 1 | 1 | 1
DCV for all occupied zones | 166.7923 | 61.4605 | 76.8256 | 0 | 0 | 89.9667 | 265.5954 | 94.8727 | 118.5909 | 0 | 0 | 147.0045 | 420.4316 | 216.3826 | 270.4782 | 0 | 0 | 149.9534 | 433.2519 | 273.3168 | 341.646 | 0 | 0 | 91.6059 | 1 | 1 | 1 | 1 | 1
Cold Deck Reset to eliminate reheat | 203.5 | 90.152 | 112.69 | 0 | 0 | 90.81 | 309.33 | 129.928 | 162.41 | 0 | 0 | 146.92 | 420.5434 | 216.4267 | 270.5334 | 0 | 0 | 150.01 | 433.3603 | 273.3923 | 341.7403 | 0 | 0 | 91.62 | 1 | 1 | 1 | 1 | 1
VSD/VFD on large hp AHU | 210.6905 | 92.9384 | 116.173 | 0 | 0 | 94.5175 | 310.3809 | 130.7708 | 163.4635 | 0 | 0 | 146.9174 | 420.4619 | 216.3701 | 270.4626 | 0 | 0 | 149.9993 | 433.2544 | 273.3063 | 341.6328 | 0 | 0 | 91.6215 | 1 | 1 | 1 | 1 | 1
VSP on large hp heating/cooling pumps | 192.083 | 92.9384 | 116.173 | 0 | 0 | 75.91 | 279.4358 | 137.4837 | 171.8547 | 0 | 0 | 107.5812 | 387.3805 | 225.8454 | 282.3067 | 0 | 0 | 105.0738 | 433.3651 | 273.3923 | 341.7403 | 0 | 0 | 91.6248 | 1 | 1 | 1 | 1 | 1
Solar Wall for ventilation preheat | 202.32 | 85.984 | 107.48 | 0 | 0 | 94.84 | 306.44 | 123.728 | 154.66 | 0 | 0 | 151.78 | 416.42 | 209.472 | 261.84 | 0 | 0 | 154.58 | 429.25 | 266.44 | 333.05 | 0 | 0 | 96.2 | 1 | 1 | 1 | 1 | 1
Solar DHW | 208.57 | 91.2 | 114 | 0 | 0 | 94.57 | 312.69 | 128.944 | 161.18 | 0 | 0 | 151.51 | 422.67 | 214.688 | 268.36 | 0 | 0 | 154.31 | 435.5 | 271.656 | 339.57 | 0 | 0 | 95.93 | 1 | 1 | 1 | 1 | 1
Dry Bulb Economizer Control | 206.62 | 92.888 | 116.11 | 0 | 0 | 90.51 | 309.71 | 130.496 | 163.12 | 0 | 0 | 146.59 | 419.66 | 215.744 | 269.68 | 0 | 0 | 149.98 | 432.17 | 272.448 | 340.56 | 0 | 0 | 91.61 | 1 | 1 | 1 | 1 | 1
DX Cooling COP Upgrade to COP 4.0 | 210.6905 | 92.9384 | 116.173 | 0 | 0 | 94.5175 | 308.29 | 130.544 | 163.18 | 0 | 0 | 145.11 | 419.58 | 215.776 | 269.72 | 0 | 0 | 149.86 | 433.2203 | 273.3923 | 341.7403 | 0 | 0 | 91.48 | 1 | 1 | 1 | 1 | 1
Retro-commissioning on thermostats and AHU | 189.6214 | 83.6445 | 104.5557 | 0 | 0 | 85.0658 | 283.3319 | 117.6143 | 147.0179 | 0 | 0 | 136.314 | 382.3172 | 194.784 | 243.48 | 0 | 0 | 138.8372 | 393.8546 | 246.053 | 307.5663 | 0 | 0 | 86.2883 | 1 | 1 | 1 | 1 | 0
Archetype 2A-Training Building (kWh/m2 floor area)
Exempler Building Trenton #34 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | ECM Applicability Index V1 | ECM Applicability Index V2 | ECM Applicability Index V3 | ECM Applicability Index V4 | ECM Modelled Index
Base case | 224.6214 | 127.1932 | 7.9414 | 151.05 | 0 | 65.63 | 302.3314 | 185.9292 | 7.9414 | 224.47 | 0 | 69.92 | 419.9414 | 270.6092 | 7.9414 | 330.32 | 0 | 81.68 | 482.3214 | 316.3132 | 7.9414 | 387.45 | 0 | 86.93 | 1 | 1 | 1 | 1 | 1
Wall Insulation: Additional RSI 1.32 on ext. | 220.3814 | 123.8252 | 7.9414 | 146.84 | 0 | 65.6 | 291.3414 | 177.5852 | 7.9414 | 214.04 | 0 | 69.36 | 406.9714 | 261.3052 | 7.9414 | 318.69 | 0 | 80.34 | 463.5914 | 302.8812 | 7.9414 | 370.66 | 0 | 84.99 | 1 | 1 | 1 | 1 | 1
Roof: Additional RSI 1.76 to 2.11 on exterior | 220.3814 | 123.8252 | 7.9414 | 146.84 | 0 | 65.6 | 291.3414 | 177.5852 | 7.9414 | 214.04 | 0 | 69.36 | 406.9714 | 261.3052 | 7.9414 | 318.69 | 0 | 80.34 | 463.5914 | 302.8812 | 7.9414 | 370.66 | 0 | 84.99 | 1 | 1 | 1 | 1 | 1
Roof: Additional RSI 2.11 to 3.52 on interior | 220.3814 | 123.8252 | 7.9414 | 146.84 | 0 | 65.6 | 291.3414 | 177.5852 | 7.9414 | 214.04 | 0 | 69.36 | 406.9714 | 261.3052 | 7.9414 | 318.69 | 0 | 80.34 | 463.5914 | 302.8812 | 7.9414 | 370.66 | 0 | 84.99 | 1 | 1 | 1 | 1 | 1
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 212.6614 | 117.8092 | 7.9414 | 139.32 | 0 | 65.4 | 271.0614 | 162.8492 | 7.9414 | 195.62 | 0 | 67.5 | 317.5814 | 197.9532 | 7.9414 | 239.5 | 0 | 70.14 | 375.5014 | 240.3852 | 7.9414 | 292.54 | 0 | 75.02 | 1 | 1 | 1 | 1 | 1
Windows: Double Glazed to Triple LowE | 223.8314 | 126.5612 | 7.9414 | 150.26 | 0 | 65.63 | 300.1714 | 184.1932 | 7.9414 | 222.3 | 0 | 69.93 | 417.9414 | 269.1292 | 7.9414 | 328.47 | 0 | 81.53 | 479.0314 | 313.8812 | 7.9414 | 384.41 | 0 | 86.68 | 1 | 1 | 1 | 1 | 1
Air tightness: vintage ACH to 0.27 ACH | 224.6214 | 127.1932 | 7.9414 | 151.05 | 0 | 65.63 | 260.0114 | 152.4492 | 7.9414 | 182.62 | 0 | 69.45 | 340.1014 | 211.9692 | 7.9414 | 257.02 | 0 | 75.14 | 348.6214 | 218.1372 | 7.9414 | 264.73 | 0 | 75.95 | 0 | 1 | 1 | 1 | 1
Heating setpoint reduction (2 DegC) | 191.3014 | 101.0652 | 7.9414 | 118.39 | 0 | 64.97 | 259.4814 | 152.1452 | 7.9414 | 182.24 | 0 | 69.3 | 364.6214 | 226.7132 | 7.9414 | 275.45 | 0 | 81.23 | 419.6414 | 266.5452 | 7.9414 | 325.24 | 0 | 86.46 | 1 | 1 | 1 | 1 | 1
Temperature set back of 2 DegC afterhours | 195.0214 | 103.9612 | 7.9414 | 122.01 | 0 | 65.07 | 264.1814 | 155.8492 | 7.9414 | 186.87 | 0 | 69.37 | 372.4614 | 232.9452 | 7.9414 | 283.24 | 0 | 81.28 | 391.785 | 244.236 | 7.9414 | 297.3536 | 0 | 86.49 | 1 | 1 | 1 | 1 | 1
Lighting: 30% reduction from MNECB | 221.2014 | 136.5372 | 7.9414 | 162.73 | 0 | 50.53 | 291.8314 | 188.4012 | 7.9414 | 227.56 | 0 | 56.33 | 415.3314 | 277.1452 | 7.9414 | 338.49 | 0 | 68.9 | 478.0014 | 323.0332 | 7.9414 | 395.85 | 0 | 74.21 | 1 | 1 | 1 | 1 | 1
Occupancy Sensors (Lights/Plug Loads) | 219.8914 | 127.1932 | 7.9414 | 151.05 | 0 | 60.9 | 297.6214 | 185.9292 | 7.9414 | 224.47 | 0 | 65.21 | 415.2214 | 270.6092 | 7.9414 | 330.32 | 0 | 76.96 | 477.5914 | 316.3132 | 7.9414 | 387.45 | 0 | 82.2 | 1 | 1 | 1 | 1 | 1
HRV | 167.1114 | 80.8252 | 7.9414 | 93.09 | 0 | 66.08 | 242.3314 | 137.8092 | 7.9414 | 164.32 | 0 | 70.07 | 359.8314 | 222.5372 | 7.9414 | 270.23 | 0 | 81.66 | 421.8314 | 267.9292 | 7.9414 | 326.97 | 0 | 86.92 | 1 | 1 | 1 | 1 | 1
DCV for all occupied zones | 193.6114 | 102.3852 | 7.9414 | 120.04 | 0 | 65.63 | 257.4314 | 150.0092 | 7.9414 | 179.57 | 0 | 69.92 | 353.8714 | 217.7532 | 7.9414 | 264.25 | 0 | 81.68 | 404.3814 | 254.3132 | 7.9414 | 309.95 | 0 | 86.49 | 1 | 1 | 1 | 1 | 1
Cold Deck Reset to eliminate reheat | 222.6514 | 127.1932 | 7.9414 | 151.05 | 0 | 63.66 | 300.2314 | 185.9292 | 7.9414 | 224.47 | 0 | 67.82 | 417.4814 | 270.6092 | 7.9414 | 330.32 | 0 | 79.22 | 482.3214 | 316.3132 | 7.9414 | 387.45 | 0 | 86.93 | 1 | 1 | 1 | 1 | 0
VSD/VFD on large hp AHU | 224.0188 | 134.425 | 7.9414 | 160.0898 | 0 | 55.9875 | 301.5748 | 195.0085 | 7.9414 | 235.8192 | 0 | 57.8141 | 418.6516 | 286.0868 | 7.9414 | 349.667 | 0 | 61.0432 | 480.7946 | 334.6349 | 7.9414 | 410.3522 | 0 | 62.5009 | 1 | 1 | 1 | 1 | 1
VSP on large hp heating/cooling pumps | 202.7514 | 127.1932 | 7.9414 | 151.05 | 0 | 43.76 | 280.4514 | 185.9212 | 7.9414 | 224.46 | 0 | 48.05 | 398.0714 | 270.6092 | 7.9414 | 330.32 | 0 | 59.81 | 460.4514 | 316.3132 | 7.9414 | 387.45 | 0 | 65.06 | 1 | 1 | 1 | 1 | 0
Solar Wall for ventilation preheat | 223.1014 | 125.3692 | 7.9414 | 148.77 | 0 | 66.39 | 300.8114 | 184.1052 | 7.9414 | 222.19 | 0 | 70.68 | 418.4214 | 268.7852 | 7.9414 | 328.04 | 0 | 82.44 | 480.8014 | 314.4892 | 7.9414 | 385.17 | 0 | 87.69 | 1 | 1 | 1 | 1 | 0
Solar DHW | 220.6114 | 123.8972 | 7.9414 | 146.93 | 0 | 65.74 | 298.3214 | 182.6332 | 7.9414 | 220.35 | 0 | 70.03 | 415.9314 | 267.3132 | 7.9414 | 326.2 | 0 | 81.79 | 478.3114 | 313.0172 | 7.9414 | 383.33 | 0 | 87.04 | 1 | 1 | 1 | 1 | 1
Dry Bulb Economizer Control | 224.3214 | 127.1932 | 7.9414 | 151.05 | 0 | 65.33 | 302.0814 | 185.9292 | 7.9414 | 224.47 | 0 | 69.67 | 419.8414 | 270.6092 | 7.9414 | 330.32 | 0 | 81.58 | 482.2414 | 316.3132 | 7.9414 | 387.45 | 0 | 86.85 | 1 | 1 | 1 | 1 | 1
DX Cooling COP Upgrade to COP 4.0 | 224.6214 | 127.1932 | 7.9414 | 151.05 | 0 | 65.63 | 301.6014 | 185.9212 | 7.9414 | 224.46 | 0 | 69.2 | 418.4514 | 270.6092 | 7.9414 | 330.32 | 0 | 80.19 | 480.0814 | 316.3132 | 7.9414 | 387.45 | 0 | 84.69 | 1 | 1 | 1 | 1 | 1
Retro-commissioning on thermostats and AHU | 207.6614 | 115.1052 | 7.9414 | 135.94 | 0 | 63.78 | 277.6214 | 167.9692 | 7.9414 | 202.02 | 0 | 67.66 | 383.4614 | 244.1852 | 7.9414 | 297.29 | 0 | 78.23 | 439.6014 | 285.3212 | 7.9414 | 348.71 | 0 | 82.95 | 1 | 1 | 1 | 1 | 1
Archetype 3B-Storage Warehouse (kWh/m2 floor area)
Exempler Building #782 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | ECM Applicability Index V1 | ECM Applicability Index V2 | ECM Applicability Index V3 | ECM Applicability Index V4 | ECM Modelled Index
Base case | 98.2509 | 57.7146 | 0 | 72.1433 | 0 | 26.1076 | 126.5544 | 81.1374 | 0 | 101.4217 | 0 | 25.1327 | 181.2022 | 123.288 | 0 | 154.1099 | 0 | 27.0922 | 229.8109 | 159.9447 | 0 | 199.9309 | 0 | 29.88 | 1 | 1 | 1 | 1 | 1
Wall Insulation: Additional RSI 1.32 on ext. | 94.8973 | 55.1877 | 0 | 68.9847 | 0 | 25.9126 | 117.875 | 74.4435 | 0 | 93.0543 | 0 | 24.8207 | 170.6233 | 115.1758 | 0 | 143.9697 | 0 | 26.6535 | 210.7568 | 145.3334 | 0 | 181.6668 | 0 | 29.09 | 1 | 1 | 1 | 1 | 1
Roof: Additional RSI 1.76 to 2.11 on exterior | 94.8973 | 55.1877 | 0 | 68.9847 | 0 | 25.9126 | 117.875 | 74.4435 | 0 | 93.0543 | 0 | 24.8207 | 170.6233 | 115.1758 | 0 | 143.9697 | 0 | 26.6535 | 210.7568 | 145.3334 | 0 | 181.6668 | 0 | 29.09 | 1 | 1 | 1 | 1 | 1
Roof: Additional RSI 2.11 to 3.52 on interior | 94.8973 | 55.1877 | 0 | 68.9847 | 0 | 25.9126 | 117.875 | 74.4435 | 0 | 93.0543 | 0 | 24.8207 | 170.6233 | 115.1758 | 0 | 143.9697 | 0 | 26.6535 | 210.7568 | 145.3334 | 0 | 181.6668 | 0 | 29.09 | 1 | 1 | 1 | 1 | 1
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 93.9036 | 54.4708 | 0 | 68.0885 | 0 | 25.8151 | 114.8747 | 72.2381 | 0 | 90.2977 | 0 | 24.577 | 162.5575 | 109.0507 | 0 | 136.3134 | 0 | 26.2441 | 180.6969 | 122.4775 | 0 | 153.0969 | 0 | 27.6 | 1 | 1 | 1 | 1 | 1
Windows: Double Glazed to Triple LowE | 98.2509 | 57.7146 | 0 | 72.1433 | 0 | 26.1076 | 126.5544 | 81.1374 | 0 | 101.4217 | 0 | 25.1327 | 181.2022 | 123.288 | 0 | 154.1099 | 0 | 27.0922 | 229.8109 | 159.9447 | 0 | 199.9309 | 0 | 29.88 | 0 | 0 | 0 | 0 | 0
Air tightness: vintage ACH to 0.27 ACH | 98.2509 | 57.7146 | 0 | 72.1433 | 0 | 26.1076 | 126.5544 | 81.1374 | 0 | 101.4217 | 0 | 25.1327 | 181.2022 | 123.288 | 0 | 154.1099 | 0 | 27.0922 | 229.8109 | 159.9447 | 0 | 199.9309 | 0 | 29.88 | 0 | 0 | 0 | 0 | 0
Heating setpoint reduction (2 DegC) | 88.4449 | 50.9719 | 0 | 63.7149 | 0 | 24.73 | 114.8154 | 72.9473 | 0 | 91.1841 | 0 | 23.6314 | 167.7194 | 113.8978 | 0 | 142.3722 | 0 | 25.3472 | 215.2529 | 149.9623 | 0 | 187.4529 | 0 | 27.8 | 1 | 1 | 1 | 1 | 1
Temperature set back of 2 DegC afterhours | 98.2509 | 57.7146 | 0 | 72.1433 | 0 | 26.1076 | 126.5544 | 81.1374 | 0 | 101.4217 | 0 | 25.1327 | 181.2022 | 123.288 | 0 | 154.1099 | 0 | 27.0922 | 229.8109 | 159.9447 | 0 | 199.9309 | 0 | 29.88 | 1 | 1 | 1 | 1 | 0
Lighting: 30% reduction from MNECB | 96.9111 | 59.2867 | 0 | 74.1084 | 0 | 22.8027 | 125.2853 | 82.7816 | 0 | 103.477 | 0 | 21.8083 | 180.0013 | 125.0023 | 0 | 156.2529 | 0 | 23.7484 | 228.5244 | 161.6435 | 0 | 202.0544 | 0 | 26.47 | 1 | 1 | 1 | 1 | 1
Occupancy Sensors (Lights/Plug Loads) | 98.2509 | 57.7146 | 0 | 72.1433 | 0 | 26.1076 | 126.5544 | 81.1374 | 0 | 101.4217 | 0 | 25.1327 | 181.2022 | 123.288 | 0 | 154.1099 | 0 | 27.0922 | 229.8109 | 159.9447 | 0 | 199.9309 | 0 | 29.88 | 1 | 1 | 1 | 1 | 0
HRV | 98.2509 | 57.7146 | 0 | 72.1433 | 0 | 26.1076 | 126.5544 | 81.1374 | 0 | 101.4217 | 0 | 25.1327 | 181.2022 | 123.288 | 0 | 154.1099 | 0 | 27.0922 | 229.8109 | 159.9447 | 0 | 199.9309 | 0 | 29.88 | 0 | 0 | 0 | 0 | 0
DCV for all occupied zones | 91.0676 | 51.968 | 0 | 64.96 | 0 | 26.1076 | 116.4027 | 73.016 | 0 | 91.27 | 0 | 25.1327 | 165.7922 | 110.96 | 0 | 138.7 | 0 | 27.0922 | 209.82 | 143.952 | 0 | 179.94 | 0 | 29.88 | 1 | 1 | 1 | 1 | 0
Cold Deck Reset to eliminate reheat | 97.4633 | 57.7146 | 0 | 72.1433 | 0 | 25.32 | 125.7917 | 81.1374 | 0 | 101.4217 | 0 | 24.37 | 180.3899 | 123.288 | 0 | 154.1099 | 0 | 26.28 | 228.9109 | 159.9447 | 0 | 199.9309 | 0 | 28.98 | 1 | 1 | 1 | 1 | 0
VSD/VFD on large hp AHU | 98.2509 | 57.7146 | 0 | 72.1433 | 0 | 26.1076 | 126.5544 | 81.1374 | 0 | 101.4217 | 0 | 25.1327 | 181.2022 | 123.288 | 0 | 154.1099 | 0 | 27.0922 | 229.8109 | 159.9447 | 0 | 199.9309 | 0 | 29.88 | 1 | 1 | 1 | 1 | 0
VSP on large hp heating/cooling pumps | 98.2509 | 57.7146 | 0 | 72.1433 | 0 | 26.1076 | 126.5544 | 81.1374 | 0 | 101.4217 | 0 | 25.1327 | 181.2022 | 123.288 | 0 | 154.1099 | 0 | 27.0922 | 229.8109 | 159.9447 | 0 | 199.9309 | 0 | 29.88 | 1 | 1 | 1 | 1 | 0
Solar Wall for ventilation preheat | 92.51 | 52.72 | 0 | 65.9 | 0 | 26.61 | 120.81 | 76.144 | 0 | 95.18 | 0 | 25.63 | 175.45 | 118.288 | 0 | 147.86 | 0 | 27.59 | 224.07 | 154.952 | 0 | 193.69 | 0 | 30.38 | 1 | 1 | 1 | 1 | 0
Solar DHW | 98.2509 | 57.7146 | 0 | 72.1433 | 0 | 26.1076 | 126.5544 | 81.1374 | 0 | 101.4217 | 0 | 25.1327 | 181.2022 | 123.288 | 0 | 154.1099 | 0 | 27.0922 | 229.8109 | 159.9447 | 0 | 199.9309 | 0 | 29.88 | 0 | 0 | 0 | 0 | 0
Dry Bulb Economizer Control | 98.2509 | 57.7146 | 0 | 72.1433 | 0 | 26.1076 | 126.5544 | 81.1374 | 0 | 101.4217 | 0 | 25.1327 | 181.2022 | 123.288 | 0 | 154.1099 | 0 | 27.0922 | 229.8109 | 159.9447 | 0 | 199.9309 | 0 | 29.88 | 0 | 0 | 0 | 0 | 0
DX Cooling COP Upgrade to COP 4.0 | 98.2509 | 57.7146 | 0 | 72.1433 | 0 | 26.1076 | 126.5544 | 81.1374 | 0 | 101.4217 | 0 | 25.1327 | 181.2022 | 123.288 | 0 | 154.1099 | 0 | 27.0922 | 229.8109 | 159.9447 | 0 | 199.9309 | 0 | 29.88 | 0 | 0 | 0 | 0 | 0
Retro-commissioning on thermostats and AHU | 98.2509 | 57.7146 | 0 | 72.1433 | 0 | 26.1076 | 126.5544 | 81.1374 | 0 | 101.4217 | 0 | 25.1327 | 181.2022 | 123.288 | 0 | 154.1099 | 0 | 27.0922 | 229.8109 | 159.9447 | 0 | 199.9309 | 0 | 29.88 | 1 | 1 | 1 | 1 | 0
Archetype 4C-Barracks(kWh/m2 floor area)
Exempler Building # 45 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | ECM Applicability Index V1 | ECM Applicability Index V2 | ECM Applicability Index V3 | ECM Applicability Index V4 | ECM Modelled Index
Base case | 0 | 0 | 0 | 0 | 0 | 0 | 302.49 | 190.976 | 238.72 | 0 | 0 | 63.77 | 424.38 | 278.032 | 347.54 | 0 | 0 | 76.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
Wall Insulation: Additional RSI 1.32 on ext. | 0 | 0 | 0 | 0 | 0 | 0 | 288.76 | 181.248 | 226.56 | 0 | 0 | 62.2 | 406.47 | 265.392 | 331.74 | 0 | 0 | 74.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
Roof: Additional RSI 1.76 to 2.11 on exterior | 0 | 0 | 0 | 0 | 0 | 0 | 275.41 | 171.704 | 214.63 | 0 | 0 | 60.78 | 332.61 | 212.968 | 266.21 | 0 | 0 | 66.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
Roof: Additional RSI 2.11 to 3.52 on interior | 0 | 0 | 0 | 0 | 0 | 0 | 275.41 | 171.704 | 214.63 | 0 | 0 | 60.78 | 332.61 | 212.968 | 266.21 | 0 | 0 | 66.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 0 | 0 | 0 | 0 | 0 | 0 | 275.41 | 171.704 | 214.63 | 0 | 0 | 60.78 | 332.61 | 212.968 | 266.21 | 0 | 0 | 66.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
Windows: Double Glazed to Triple LowE | 0 | 0 | 0 | 0 | 0 | 0 | 299.91 | 189.12 | 236.4 | 0 | 0 | 63.51 | 422.04 | 276.352 | 345.44 | 0 | 0 | 76.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
Air tightness: vintage ACH to 0.27 ACH | 0 | 0 | 0 | 0 | 0 | 0 | 257.42 | 158.336 | 197.92 | 0 | 0 | 59.5 | 333.62 | 212.256 | 265.32 | 0 | 0 | 68.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
Heating setpoint reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 0 | 265.17 | 163.336 | 204.17 | 0 | 0 | 61 | 373.1 | 240.488 | 300.61 | 0 | 0 | 72.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
Temperature set back of 2 DegC afterhours | 0 | 0 | 0 | 0 | 0 | 0 | 273.38 | 170.184 | 212.73 | 0 | 0 | 60.65 | 384.88 | 250.16 | 312.7 | 0 | 0 | 72.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
Lighting: 30% reduction from MNECB | 0 | 0 | 0 | 0 | 0 | 0 | 298.68 | 196.2 | 245.25 | 0 | 0 | 53.43 | 420.87 | 283.496 | 354.37 | 0 | 0 | 66.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 0 | 298.31 | 190.976 | 238.72 | 0 | 0 | 59.59 | 420.19 | 278.032 | 347.54 | 0 | 0 | 72.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
HRV | 0 | 0 | 0 | 0 | 0 | 0 | 277.28 | 170.808 | 213.51 | 0 | 0 | 63.77 | 398.76 | 257.536 | 321.92 | 0 | 0 | 76.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
DCV for all occupied zones | 0 | 0 | 0 | 0 | 0 | 0 | 273.1 | 167.464 | 209.33 | 0 | 0 | 63.77 | 395.1 | 254.608 | 318.26 | 0 | 0 | 76.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
Cold Deck Reset to eliminate reheat | 0 | 0 | 0 | 0 | 0 | 0 | 302.49 | 190.976 | 238.72 | 0 | 0 | 63.77 | 424.38 | 278.032 | 347.54 | 0 | 0 | 76.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0
VSD/VFD on large hp AHU | 0 | 0 | 0 | 0 | 0 | 0 | 299.2948 | 201.6267 | 252.0334 | 0 | 0 | 47.2614 | 419.288 | 295.0055 | 368.7568 | 0 | 0 | 50.5311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
VSP on large hp heating/cooling pumps | 0 | 0 | 0 | 0 | 0 | 0 | 302.49 | 190.976 | 238.72 | 0 | 0 | 63.77 | 424.38 | 278.032 | 347.54 | 0 | 0 | 76.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0
Solar Wall for ventilation preheat | 0 | 0 | 0 | 0 | 0 | 0 | 298.4 | 185.104 | 231.38 | 0 | 0 | 67.02 | 420.29 | 272.16 | 340.2 | 0 | 0 | 80.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0
Solar DHW | 0 | 0 | 0 | 0 | 0 | 0 | 275.21 | 168.464 | 210.58 | 0 | 0 | 64.63 | 397.1 | 255.52 | 319.4 | 0 | 0 | 77.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
Dry Bulb Economizer Control | 0 | 0 | 0 | 0 | 0 | 0 | 302.49 | 190.976 | 238.72 | 0 | 0 | 63.77 | 424.38 | 278.032 | 347.54 | 0 | 0 | 76.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0
DX Cooling COP Upgrade to COP 4.0 | 0 | 0 | 0 | 0 | 0 | 0 | 302.49 | 190.976 | 238.72 | 0 | 0 | 63.77 | 424.38 | 278.032 | 347.54 | 0 | 0 | 76.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0
Retro-commissioning on thermostats and AHU | 0 | 0 | 0 | 0 | 0 | 0 | 282.11 | 176.44 | 220.55 | 0 | 0 | 61.56 | 391.81 | 254.792 | 318.49 | 0 | 0 | 73.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1
Archetype 5E-Recreation Centre (kWh/m2 floor area)
Exempler Building # 720 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | ECM Applicability Index V1 | ECM Applicability Index V2 | ECM Applicability Index V3 | ECM Applicability Index V4 | ECM Modelled Index
Base case | 0 | 0 | 0 | 0 | 0 | 0 | 225.82 | 110.568 | 95.9002 | 42.3098 | 0 | 87.61 | 0 | 0 | 0 | 0 | 0 | 0 | 407.21 | 238.448 | 215.5656 | 82.4944 | 0 | 109.15 | 0 | 1 | 0 | 1 | 1
Wall Insulation: Additional RSI 1.32 on ext. | 0 | 0 | 0 | 0 | 0 | 0 | 215.4 | 103.28 | 90.1553 | 38.9447 | 0 | 86.3 | 0 | 0 | 0 | 0 | 0 | 0 | 386.45 | 223.96 | 204.2489 | 75.7011 | 0 | 106.5 | 0 | 1 | 0 | 1 | 1
Roof: Additional RSI 1.76 to 2.11 on exterior | 0 | 0 | 0 | 0 | 0 | 0 | 195.11 | 89.56 | 75.9455 | 36.0045 | 0 | 83.16 | 0 | 0 | 0 | 0 | 0 | 0 | 302.44 | 166.568 | 145.014 | 63.196 | 0 | 94.23 | 0 | 1 | 0 | 1 | 1
Roof: Additional RSI 2.11 to 3.52 on interior | 0 | 0 | 0 | 0 | 0 | 0 | 195.11 | 89.56 | 75.9455 | 36.0045 | 0 | 83.16 | 0 | 0 | 0 | 0 | 0 | 0 | 302.44 | 166.568 | 145.014 | 63.196 | 0 | 94.23 | 0 | 1 | 0 | 1 | 1
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 0 | 0 | 0 | 0 | 0 | 0 | 195.11 | 89.56 | 75.9455 | 36.0045 | 0 | 83.16 | 0 | 0 | 0 | 0 | 0 | 0 | 302.44 | 166.568 | 145.014 | 63.196 | 0 | 94.23 | 0 | 1 | 0 | 1 | 1
Windows: Double Glazed to Triple LowE | 0 | 0 | 0 | 0 | 0 | 0 | 224.01 | 109.232 | 94.864 | 41.676 | 0 | 87.47 | 0 | 0 | 0 | 0 | 0 | 0 | 404.1 | 236.176 | 213.6221 | 81.5979 | 0 | 108.88 | 0 | 1 | 0 | 1 | 1
Air tightness: vintage ACH to 0.27 ACH | 0 | 0 | 0 | 0 | 0 | 0 | 188.28 | 83.504 | 71.6881 | 32.6919 | 0 | 83.9 | 0 | 0 | 0 | 0 | 0 | 0 | 278.2 | 145.704 | 130.8005 | 51.3295 | 0 | 96.07 | 0 | 1 | 0 | 1 | 1
Heating setpoint reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 0 | 196.73 | 87.888 | 74.3742 | 35.4858 | 0 | 86.87 | 0 | 0 | 0 | 0 | 0 | 0 | 357.26 | 199.184 | 178.0196 | 70.9604 | 0 | 108.28 | 0 | 1 | 0 | 1 | 1
Temperature set back of 2 DegC afterhours | 0 | 0 | 0 | 0 | 0 | 0 | 205.26 | 94.632 | 93.6703 | 24.6197 | 0 | 86.97 | 0 | 0 | 0 | 0 | 0 | 0 | 366.25 | 206.296 | 202.7889 | 55.0811 | 0 | 108.38 | 0 | 1 | 0 | 1 | 1
Lighting: 30% reduction from MNECB | 0 | 0 | 0 | 0 | 0 | 0 | 220.32 | 121.256 | 108.44 | 43.13 | 0 | 68.75 | 0 | 0 | 0 | 0 | 0 | 0 | 408.78 | 249.984 | 229.14 | 83.34 | 0 | 96.3 | 0 | 1 | 0 | 1 | 1
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 0 | 219.61 | 110.568 | 95.9002 | 42.3098 | 0 | 81.4 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 238.448 | 215.5656 | 82.4944 | 0 | 102.94 | 0 | 1 | 0 | 1 | 1
HRV | 0 | 0 | 0 | 0 | 0 | 0 | 211.89 | 99.328 | 82.0794 | 42.0806 | 0 | 87.73 | 0 | 0 | 0 | 0 | 0 | 0 | 392.7 | 226.8 | 201.0617 | 82.4383 | 0 | 109.2 | 0 | 1 | 0 | 1 | 1
DCV for all occupied zones | 0 | 0 | 0 | 0 | 0 | 0 | 206.6398 | 95.2239 | 76.72 | 42.3098 | 0 | 87.61 | 0 | 0 | 0 | 0 | 0 | 0 | 364.0944 | 203.9555 | 172.45 | 82.4944 | 0 | 109.15 | 0 | 1 | 0 | 1 | 1
Cold Deck Reset to eliminate reheat | 0 | 0 | 0 | 0 | 0 | 0 | 223.19 | 110.568 | 95.9002 | 42.3098 | 0 | 84.98 | 0 | 0 | 0 | 0 | 0 | 0 | 403.93 | 238.448 | 215.5656 | 82.4944 | 0 | 105.87 | 0 | 1 | 0 | 1 | 0
VSD/VFD on large hp AHU | 0 | 0 | 0 | 0 | 0 | 0 | 225.0826 | 119.4 | 106.9402 | 42.3098 | 0 | 75.8326 | 0 | 0 | 0 | 0 | 0 | 0 | 360.4691 | 220.3555 | 192.95 | 82.4944 | 0 | 85.0247 | 0 | 1 | 0 | 1 | 0
VSP on large hp heating/cooling pumps | 0 | 0 | 0 | 0 | 0 | 0 | 223.26 | 110.568 | 95.9002 | 42.3098 | 0 | 85.05 | 0 | 0 | 0 | 0 | 0 | 0 | 404.65 | 238.448 | 215.5656 | 82.4944 | 0 | 106.59 | 0 | 1 | 0 | 1 | 0
Solar Wall for ventilation preheat | 0 | 0 | 0 | 0 | 0 | 0 | 220.4298 | 105.7919 | 89.93 | 42.3098 | 0 | 88.19 | 0 | 0 | 0 | 0 | 0 | 0 | 401.8244 | 233.6755 | 209.6 | 82.4944 | 0 | 109.73 | 0 | 1 | 0 | 1 | 0
Solar DHW | 0 | 0 | 0 | 0 | 0 | 0 | 223.7398 | 108.8639 | 93.77 | 42.3098 | 0 | 87.66 | 0 | 0 | 0 | 0 | 0 | 0 | 405.1344 | 236.7475 | 213.44 | 82.4944 | 0 | 109.2 | 0 | 1 | 0 | 1 | 1
Dry Bulb Economizer Control | 0 | 0 | 0 | 0 | 0 | 0 | 222.58 | 110.568 | 95.9 | 42.31 | 0 | 84.37 | 0 | 0 | 0 | 0 | 0 | 0 | 403.71 | 238.448 | 215.57 | 82.49 | 0 | 105.65 | 0 | 1 | 0 | 1 | 1
DX Cooling COP Upgrade to COP 4.0 | 0 | 0 | 0 | 0 | 0 | 0 | 222.87 | 110.568 | 95.9002 | 42.3098 | 0 | 84.66 | 0 | 0 | 0 | 0 | 0 | 0 | 403.6 | 238.448 | 215.5656 | 82.4944 | 0 | 105.54 | 0 | 1 | 0 | 1 | 1
Retro-commissioning on thermostats and AHU | 0 | 0 | 0 | 0 | 0 | 0 | 209.8598 | 99.8399 | 82.49 | 42.3098 | 0 | 85.06 | 0 | 0 | 0 | 0 | 0 | 0 | 373.1044 | 214.9315 | 186.17 | 82.4944 | 0 | 104.44 | 0 | 1 | 0 | 1 | 1
Archetype 6A-Office (kWh/m2 floor area)
Exempler Building # 007 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | ECM Applicability Index V1 | ECM Applicability Index V2 | ECM Applicability Index V3 | ECM Applicability Index V4 | ECM Modelled Index
Base case | 0 | 0 | 0 | 0 | 0 | 0 | 436.19 | 276.456 | 345.57 | 0 | 0 | 90.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
Wall Insulation: Additional RSI 1.32 on ext. | 0 | 0 | 0 | 0 | 0 | 0 | 427.75 | 269.976 | 337.47 | 0 | 0 | 90.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
Roof: Additional RSI 1.76 to 2.11 on exterior | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 256.776 | 320.97 | 0 | 0 | 90.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
Roof: Additional RSI 2.11 to 3.52 on interior | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 256.776 | 320.97 | 0 | 0 | 90.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 256.776 | 320.97 | 0 | 0 | 90.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
Windows: Double Glazed to Triple LowE | 0 | 0 | 0 | 0 | 0 | 0 | 432.37 | 273.456 | 341.82 | 0 | 0 | 90.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
Air tightness: vintage ACH to 0.27 ACH | 0 | 0 | 0 | 0 | 0 | 0 | 399.74 | 247.696 | 309.62 | 0 | 0 | 90.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
Heating setpoint reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 0 | 403.7 | 250.776 | 313.47 | 0 | 0 | 90.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
Temperature set back of 2 DegC afterhours | 0 | 0 | 0 | 0 | 0 | 0 | 416.41 | 260.736 | 325.92 | 0 | 0 | 90.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
Lighting: 30% reduction from MNECB | 0 | 0 | 0 | 0 | 0 | 0 | 427.43 | 284.736 | 355.92 | 0 | 0 | 71.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 0 | 428.13 | 276.456 | 345.57 | 0 | 0 | 82.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
HRV | 0 | 0 | 0 | 0 | 0 | 0 | 375.16 | 227.448 | 284.31 | 0 | 0 | 90.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
DCV for all occupied zones | 0 | 0 | 0 | 0 | 0 | 0 | 301.11 | 168.048 | 210.06 | 0 | 0 | 91.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
Cold Deck Reset to eliminate reheat | 0 | 0 | 0 | 0 | 0 | 0 | 433.47 | 276.456 | 345.57 | 0 | 0 | 87.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
VSD/VFD on large hp AHU | 0 | 0 | 0 | 0 | 0 | 0 | 433.8159 | 278.8333 | 348.5417 | 0 | 0 | 85.2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
VSP on large hp heating/cooling pumps | 0 | 0 | 0 | 0 | 0 | 0 | 435.62 | 276.456 | 345.57 | 0 | 0 | 90.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
Solar Wall for ventilation preheat | 0 | 0 | 0 | 0 | 0 | 0 | 419.62 | 261.36 | 326.7 | 0 | 0 | 92.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
Solar DHW | 0 | 0 | 0 | 0 | 0 | 0 | 434.84 | 275.352 | 344.19 | 0 | 0 | 90.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
Dry Bulb Economizer Control | 0 | 0 | 0 | 0 | 0 | 0 | 436.15 | 276.456 | 345.57 | 0 | 0 | 90.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
DX Cooling COP Upgrade to COP 4.0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.19 | 276.456 | 345.57 | 0 | 0 | 90.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
Retro-commissioning on thermostats and AHU | 0 | 0 | 0 | 0 | 0 | 0 | 401.73 | 249.704 | 312.13 | 0 | 0 | 89.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
Archetype 6B-Small Office (kWh/m2 floor area)
Exempler Building # 96 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | ECM Applicability Index V1 | ECM Applicability Index V2 | ECM Applicability Index V3 | ECM Applicability Index V4 | ECM Modelled Index
Base case | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wall Insulation: Additional RSI 1.32 on ext. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roof: Additional RSI 1.76 to 2.11 on exterior | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roof: Additional RSI 2.11 to 3.52 on interior | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Windows: Double Glazed to Triple LowE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air tightness: vintage ACH to 0.27 ACH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating setpoint reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Temperature set back of 2 DegC afterhours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting: 30% reduction from MNECB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HRV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DCV for all occupied zones | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cold Deck Reset to eliminate reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VSD/VFD on large hp AHU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VSP on large hp heating/cooling pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Wall for ventilation preheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar DHW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dry Bulb Economizer Control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DX Cooling COP Upgrade to COP 4.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retro-commissioning on thermostats and AHU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Archetype 7A- Dining Hall (kWh/m2 floor area)
Exempler Building # 40 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | ECM Applicability Index V1 | ECM Applicability Index V2 | ECM Applicability Index V3 | ECM Applicability Index V4 | ECM Modelled Index
Base case | 437.95 | 277.056 | 0 | 346.32 | 0 | 91.63 | 480.29 | 309.44 | 0 | 386.8 | 0 | 93.49 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 1 | 1 | 1 | 0 | 1
Wall Insulation: Additional RSI 1.32 on ext. | 429.81 | 270.544 | 0 | 338.18 | 0 | 91.63 | 464.28 | 296.632 | 0 | 370.79 | 0 | 93.49 | 466.43 | 302.936 | 0 | 378.67 | 0 | 87.76 | 491.36 | 322.88 | 0 | 403.6 | 0 | 87.76 | 0 | 1 | 1 | 0 | 0
Roof: Additional RSI 1.76 to 2.11 on exterior | 427.85 | 268.976 | 0 | 336.22 | 0 | 91.63 | 463.6 | 296.088 | 0 | 370.11 | 0 | 93.49 | 471.69 | 307.144 | 0 | 383.93 | 0 | 87.76 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 0 | 1 | 1 | 0 | 0
Roof: Additional RSI 2.11 to 3.52 on interior | 427.85 | 268.976 | 0 | 336.22 | 0 | 91.63 | 463.6 | 296.088 | 0 | 370.11 | 0 | 93.49 | 471.69 | 307.144 | 0 | 383.93 | 0 | 87.76 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 0 | 1 | 1 | 0 | 0
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 427.85 | 268.976 | 0 | 336.22 | 0 | 91.63 | 463.6 | 296.088 | 0 | 370.11 | 0 | 93.49 | 471.69 | 307.144 | 0 | 383.93 | 0 | 87.76 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 0 | 1 | 1 | 0 | 0
Windows: Double Glazed to Triple LowE | 437.95 | 277.056 | 0 | 346.32 | 0 | 91.63 | 480.29 | 309.44 | 0 | 386.8 | 0 | 93.49 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 0 | 0 | 0 | 0 | 0
Air tightness: vintage ACH to 0.27 ACH | 437.95 | 277.056 | 0 | 346.32 | 0 | 91.63 | 464.64 | 297.216 | 0 | 371.52 | 0 | 93.12 | 446.55 | 288.088 | 0 | 360.11 | 0 | 86.44 | 446.55 | 288.088 | 0 | 360.11 | 0 | 86.44 | 0 | 0 | 0 | 0 | 0
Heating setpoint reduction (2 DegC) | 435.13 | 274.8 | 0 | 343.5 | 0 | 91.63 | 469.29 | 300.528 | 0 | 375.66 | 0 | 93.63 | 490.18 | 321.968 | 0 | 402.46 | 0 | 87.72 | 490.18 | 321.968 | 0 | 402.46 | 0 | 87.72 | 1 | 1 | 1 | 0 | 0
Temperature set back of 2 DegC afterhours | 437.95 | 277.056 | 0 | 346.32 | 0 | 91.63 | 480.29 | 309.44 | 0 | 386.8 | 0 | 93.49 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 0 | 0 | 0 | 0 | 0
Lighting: 30% reduction from MNECB | 432.88 | 282.384 | 0 | 352.98 | 0 | 79.9 | 475.06 | 315.216 | 0 | 394.02 | 0 | 81.04 | 486.48 | 329.04 | 0 | 411.3 | 0 | 75.18 | 486.48 | 329.04 | 0 | 411.3 | 0 | 75.18 | 1 | 1 | 1 | 0 | 0
Occupancy Sensors (Lights/Plug Loads) | 428.78 | 277.056 | 0 | 346.32 | 0 | 82.46 | 470.94 | 309.44 | 0 | 386.8 | 0 | 84.14 | 482.57 | 322.872 | 0 | 403.59 | 0 | 78.98 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 1 | 1 | 1 | 0 | 0
HRV | 376.21 | 234.584 | 0 | 293.23 | 0 | 82.98 | 380.13 | 223.632 | 0 | 279.54 | 0 | 100.59 | 379.98 | 233.998 | 0 | 291.06 | 1.15 | 87.77 | 379.98 | 233.998 | 0 | 291.06 | 1.15 | 87.77 | 1 | 1 | 1 | 0 | 0
DCV for all occupied zones | 400.19 | 249.352 | 0 | 311.69 | 0 | 88.5 | 441.61 | 278.496 | 0 | 348.12 | 0 | 93.49 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 450.7 | 290.352 | 0 | 362.94 | 0 | 87.76 | 1 | 1 | 1 | 0 | 0
Cold Deck Reset to eliminate reheat | 428.28 | 277.056 | 0 | 346.32 | 0 | 81.96 | 477.48 | 309.44 | 0 | 386.8 | 0 | 90.68 | 468.53 | 306.728 | 0 | 383.41 | 0 | 85.12 | 468.53 | 306.728 | 0 | 383.41 | 0 | 85.12 | 1 | 1 | 1 | 0 | 0
VSD/VFD on large hp AHU | 437.95 | 277.056 | 0 | 346.32 | 0 | 91.63 | 479.67 | 310.864 | 0 | 388.58 | 0 | 91.09 | 493.22 | 312.4 | 0 | 390.5 | 0 | 102.72 | 493.22 | 312.4 | 0 | 390.5 | 0 | 102.72 | 0 | 0 | 0 | 0 | 0
VSP on large hp heating/cooling pumps | 437.95 | 277.056 | 0 | 346.32 | 0 | 91.63 | 480.17 | 311.456 | 0 | 389.32 | 0 | 90.85 | 490.48 | 323.016 | 0 | 403.77 | 0 | 86.71 | 490.48 | 323.016 | 0 | 403.77 | 0 | 86.71 | 0 | 1 | 1 | 0 | 0
Solar Wall for ventilation preheat | 437.95 | 277.056 | 0 | 346.32 | 0 | 91.63 | 480.29 | 309.44 | 0 | 386.8 | 0 | 93.49 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 0 | 0 | 0 | 0 | 0
Solar DHW | 434.27 | 277.056 | 0 | 346.32 | 0 | 87.95 | 476.61 | 309.44 | 0 | 386.8 | 0 | 89.81 | 487.67 | 322.872 | 0 | 403.59 | 0 | 84.08 | 487.67 | 322.872 | 0 | 403.59 | 0 | 84.08 | 1 | 1 | 1 | 0 | 1
Dry Bulb Economizer Control | 437.95 | 277.056 | 0 | 346.32 | 0 | 91.63 | 480.29 | 309.44 | 0 | 386.8 | 0 | 93.49 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 0 | 0 | 0 | 0 | 0
DX Cooling COP Upgrade to COP 4.0 | 437.95 | 277.056 | 0 | 346.32 | 0 | 91.63 | 480.29 | 309.44 | 0 | 386.8 | 0 | 93.49 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 0 | 0 | 0 | 0 | 0
Retro-commissioning on thermostats and AHU | 437.95 | 277.056 | 0 | 346.32 | 0 | 91.63 | 480.29 | 309.44 | 0 | 386.8 | 0 | 93.49 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 491.35 | 322.872 | 0 | 403.59 | 0 | 87.76 | 0 | 0 | 0 | 0 | 0
Archetype 8A- Vehicle Garage (kWh/m2 floor area)
Exempler Building # 624 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | ECM Applicability Index V1 | ECM Applicability Index V2 | ECM Applicability Index V3 | ECM Applicability Index V4 | ECM Modelled Index
Base case | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539.06 | 291.4322 | 330.58 | 33.7103 | 0 | 174.7697 | 0 | 0 | 0 | 1 | 1
Wall Insulation: Additional RSI 1.32 on ext. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 528.89 | 283.547 | 324 | 30.4338 | 0 | 174.4562 | 0 | 0 | 0 | 1 | 1
Roof: Additional RSI 1.76 to 2.11 on exterior | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 428.26 | 206.1269 | 227.49 | 30.1686 | 0 | 170.6014 | 0 | 0 | 0 | 1 | 1
Roof: Additional RSI 2.11 to 3.52 on interior | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 428.26 | 206.1269 | 227.49 | 30.1686 | 0 | 170.6014 | 0 | 0 | 0 | 1 | 1
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 428.26 | 206.1269 | 227.49 | 30.1686 | 0 | 170.6014 | 0 | 0 | 0 | 1 | 1
Windows: Double Glazed to Triple LowE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.46 | 289.3752 | 328.61 | 33.109 | 0 | 174.741 | 0 | 0 | 0 | 1 | 1
Air tightness: vintage ACH to 0.27 ACH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425.19 | 201.3388 | 229.84 | 21.8335 | 0 | 173.5165 | 0 | 0 | 0 | 1 | 1
Heating setpoint reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475.74 | 241.7319 | 276.09 | 26.0748 | 0 | 173.5752 | 0 | 0 | 0 | 1 | 1
Temperature set back of 2 DegC afterhours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539.06 | 291.4322 | 330.58 | 33.7103 | 0 | 174.7697 | 0 | 0 | 0 | 0 | 0
Lighting: 30% reduction from MNECB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.96 | 306.7837 | 350.66 | 32.8196 | 0 | 147.4804 | 0 | 0 | 0 | 1 | 1
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 528.3403 | 291.4322 | 330.58 | 33.7103 | 0 | 164.05 | 0 | 0 | 0 | 1 | 1
HRV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465.52 | 231.6053 | 265.97 | 23.5367 | 0 | 176.0133 | 0 | 0 | 0 | 1 | 1
DCV for all occupied zones | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 435.84 | 209.4075 | 240.64 | 21.1194 | 0 | 174.0806 | 0 | 0 | 0 | 1 | 1
Cold Deck Reset to eliminate reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 533.8203 | 291.4322 | 330.58 | 33.7103 | 0 | 169.53 | 0 | 0 | 0 | 1 | 0
VSD/VFD on large hp AHU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 531.0053 | 310.7636 | 354.7442 | 33.7103 | 0 | 142.5508 | 0 | 0 | 0 | 1 | 0
VSP on large hp heating/cooling pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539.06 | 291.4322 | 330.58 | 33.7103 | 0 | 174.7697 | 0 | 0 | 0 | 1 | 0
Solar Wall for ventilation preheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.2903 | 287.5442 | 325.72 | 33.7103 | 0 | 176.86 | 0 | 0 | 0 | 1 | 0
Solar DHW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 534.1003 | 291.4322 | 330.58 | 33.7103 | 0 | 169.81 | 0 | 0 | 0 | 1 | 1
Dry Bulb Economizer Control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 538.26 | 292.4157 | 331.15 | 34.3696 | 0 | 172.7404 | 0 | 0 | 0 | 1 | 0
DX Cooling COP Upgrade to COP 4.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 533.6903 | 291.4322 | 330.58 | 33.7103 | 0 | 169.4 | 0 | 0 | 0 | 1 | 1
Retro-commissioning on thermostats and AHU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496.9003 | 262.2882 | 294.15 | 33.7103 | 0 | 169.04 | 0 | 0 | 0 | 1 | 1
Archetype 9A- Workshop (kWh/m2 floor area)
Exempler Building # 581 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | ECM Applicability Index V1 | ECM Applicability Index V2 | ECM Applicability Index V3 | ECM Applicability Index V4 | ECM Modelled Index
Base case | 500.63 | 299.432 | 374.29 | 0 | 0 | 126.34 | 569.18 | 344.52 | 430.65 | 0 | 0 | 138.53 | 0 | 0 | 0 | 0 | 0 | 0 | 831.76 | 505.992 | 632.49 | 0 | 0 | 199.27 | 1 | 1 | 0 | 1 | 1
Wall Insulation: Additional RSI 1.32 on ext. | 488.36 | 291.072 | 363.84 | 0 | 0 | 124.52 | 552.35 | 334.512 | 418.14 | 0 | 0 | 134.21 | 0 | 0 | 0 | 0 | 0 | 0 | 797.74 | 485.496 | 606.87 | 0 | 0 | 190.87 | 1 | 1 | 0 | 1 | 1
Roof: Additional RSI 1.76 to 2.11 on exterior | 491.75 | 293.904 | 367.38 | 0 | 0 | 124.37 | 552.89 | 334.792 | 418.49 | 0 | 0 | 134.4 | 0 | 0 | 0 | 0 | 0 | 0 | 714.98 | 435.656 | 544.57 | 0 | 0 | 170.41 | 1 | 1 | 0 | 1 | 1
Roof: Additional RSI 2.11 to 3.52 on interior | 491.75 | 293.904 | 367.38 | 0 | 0 | 124.37 | 552.89 | 334.792 | 418.49 | 0 | 0 | 134.4 | 0 | 0 | 0 | 0 | 0 | 0 | 714.98 | 435.656 | 544.57 | 0 | 0 | 170.41 | 1 | 1 | 0 | 1 | 1
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 491.75 | 293.904 | 367.38 | 0 | 0 | 124.37 | 552.89 | 334.792 | 418.49 | 0 | 0 | 134.4 | 0 | 0 | 0 | 0 | 0 | 0 | 714.98 | 435.656 | 544.57 | 0 | 0 | 170.41 | 1 | 1 | 0 | 1 | 1
Windows: Double Glazed to Triple LowE | 499.79 | 298.776 | 373.47 | 0 | 0 | 126.32 | 566.88 | 342.848 | 428.56 | 0 | 0 | 138.32 | 0 | 0 | 0 | 0 | 0 | 0 | 828.94 | 503.904 | 629.88 | 0 | 0 | 199.06 | 1 | 1 | 0 | 1 | 1
Air tightness: vintage ACH to 0.27 ACH | 500.63 | 299.432 | 374.29 | 0 | 0 | 126.34 | 514.23 | 308.824 | 386.03 | 0 | 0 | 128.2 | 0 | 0 | 0 | 0 | 0 | 0 | 643.56 | 387.616 | 484.52 | 0 | 0 | 159.04 | 0 | 1 | 0 | 1 | 1
Heating setpoint reduction (2 DegC) | 445.48 | 255.792 | 319.74 | 0 | 0 | 125.74 | 506.79 | 295.304 | 369.13 | 0 | 0 | 137.66 | 0 | 0 | 0 | 0 | 0 | 0 | 744.08 | 437.848 | 547.31 | 0 | 0 | 196.77 | 1 | 1 | 0 | 1 | 1
Temperature set back of 2 DegC afterhours | 456.38 | 264.624 | 330.78 | 0 | 0 | 125.6 | 519.32 | 305.352 | 381.69 | 0 | 0 | 137.63 | 0 | 0 | 0 | 0 | 0 | 0 | 760.67 | 450.8 | 563.5 | 0 | 0 | 197.17 | 1 | 1 | 0 | 1 | 1
Lighting: 30% reduction from MNECB | 494.66 | 310.56 | 388.2 | 0 | 0 | 106.46 | 564.06 | 354.096 | 442.62 | 0 | 0 | 121.44 | 0 | 0 | 0 | 0 | 0 | 0 | 826.81 | 515.464 | 644.33 | 0 | 0 | 182.48 | 1 | 1 | 0 | 1 | 1
Occupancy Sensors (Lights/Plug Loads) | 492.66 | 299.432 | 374.29 | 0 | 0 | 118.37 | 561.2 | 344.52 | 430.65 | 0 | 0 | 130.55 | 0 | 0 | 0 | 0 | 0 | 0 | 823.78 | 505.992 | 632.49 | 0 | 0 | 191.29 | 1 | 1 | 0 | 1 | 1
HRV | 495.46 | 295.416 | 369.27 | 0 | 0 | 126.19 | 561.35 | 338.392 | 422.99 | 0 | 0 | 138.36 | 0 | 0 | 0 | 0 | 0 | 0 | 820.08 | 496.752 | 620.94 | 0 | 0 | 199.14 | 1 | 1 | 0 | 1 | 1
DCV for all occupied zones | 463.2 | 269.488 | 336.86 | 0 | 0 | 126.34 | 526.11 | 310.064 | 387.58 | 0 | 0 | 138.53 | 0 | 0 | 0 | 0 | 0 | 0 | 768.51 | 455.392 | 569.24 | 0 | 0 | 199.27 | 1 | 1 | 0 | 1 | 1
Cold Deck Reset to eliminate reheat | 496.83 | 299.432 | 374.29 | 0 | 0 | 122.54 | 565.02 | 344.52 | 430.65 | 0 | 0 | 134.37 | 0 | 0 | 0 | 0 | 0 | 0 | 825.78 | 505.992 | 632.49 | 0 | 0 | 193.29 | 1 | 1 | 0 | 0 | 0
VSD/VFD on large hp AHU | 498.4951 | 325.0503 | 406.3129 | 0 | 0 | 92.1822 | 566.4793 | 376.928 | 471.16 | 0 | 0 | 95.3194 | 0 | 0 | 0 | 0 | 0 | 0 | 829.0593 | 538.4 | 673 | 0 | 0 | 156.0594 | 1 | 1 | 0 | 1 | 0
VSP on large hp heating/cooling pumps | 500.63 | 299.432 | 374.29 | 0 | 0 | 126.34 | 564.4 | 344.52 | 430.65 | 0 | 0 | 133.75 | 0 | 0 | 0 | 0 | 0 | 0 | 826.98 | 505.992 | 632.49 | 0 | 0 | 194.49 | 1 | 1 | 0 | 0 | 0
Solar Wall for ventilation preheat | 484.49 | 285.352 | 356.69 | 0 | 0 | 127.8 | 553.04 | 330.44 | 413.05 | 0 | 0 | 139.99 | 0 | 0 | 0 | 0 | 0 | 0 | 815.62 | 491.912 | 614.89 | 0 | 0 | 200.73 | 1 | 1 | 0 | 1 | 0
Solar DHW | 497.49 | 296.84 | 371.05 | 0 | 0 | 126.44 | 566.04 | 341.928 | 427.41 | 0 | 0 | 138.63 | 0 | 0 | 0 | 0 | 0 | 0 | 828.62 | 503.4 | 629.25 | 0 | 0 | 199.37 | 1 | 1 | 0 | 1 | 1
Dry Bulb Economizer Control | 500.96 | 299.888 | 374.86 | 0 | 0 | 126.1 | 569.72 | 345.144 | 431.43 | 0 | 0 | 138.29 | 0 | 0 | 0 | 0 | 0 | 0 | 833.29 | 507.456 | 634.32 | 0 | 0 | 198.97 | 1 | 1 | 0 | 1 | 1
DX Cooling COP Upgrade to COP 4.0 | 500.63 | 299.432 | 374.29 | 0 | 0 | 126.34 | 564.76 | 344.52 | 430.65 | 0 | 0 | 134.11 | 0 | 0 | 0 | 0 | 0 | 0 | 822.05 | 505.992 | 632.49 | 0 | 0 | 189.56 | 1 | 1 | 0 | 1 | 1
Retro-commissioning on thermostats and AHU | 459.09 | 269.936 | 337.42 | 0 | 0 | 121.67 | 520.8 | 310.528 | 388.16 | 0 | 0 | 132.64 | 0 | 0 | 0 | 0 | 0 | 0 | 757.11 | 455.848 | 569.81 | 0 | 0 | 187.3 | 1 | 1 | 0 | 1 | 1
Archetype 9B- Small Workshop (kWh/m2 floor area)
Exempler Building # 688 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | ECM Applicability Index V1 | ECM Applicability Index V2 | ECM Applicability Index V3 | ECM Applicability Index V4 | ECM Modelled Index
Base case | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 704.3644 | 466.842 | 0 | 491.6019 | 73.5605 | 139.202 | 0 | 0 | 0 | 1 | 1
Wall Insulation: Additional RSI 1.32 on ext. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 674.0191 | 443.9852 | 0 | 463.5201 | 73.1691 | 137.3299 | 0 | 0 | 0 | 1 | 1
Roof: Additional RSI 1.76 to 2.11 on exterior | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 591.7161 | 377.9262 | 0 | 381.8433 | 72.4516 | 137.4212 | 0 | 0 | 0 | 1 | 1
Roof: Additional RSI 2.11 to 3.52 on interior | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 591.7161 | 377.9262 | 0 | 381.8433 | 72.4516 | 137.4212 | 0 | 0 | 0 | 1 | 1
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 591.7161 | 377.9262 | 0 | 381.8433 | 72.4516 | 137.4212 | 0 | 0 | 0 | 1 | 1
Windows: Double Glazed to Triple LowE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690.8682 | 456.366 | 0 | 478.6862 | 73.417 | 138.765 | 0 | 0 | 0 | 1 | 1
Air tightness: vintage ACH to 0.27 ACH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 522.2342 | 321.7432 | 0 | 314.4683 | 70.1685 | 137.5973 | 0 | 0 | 0 | 1 | 1
Heating setpoint reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637.384 | 413.0007 | 0 | 427.4069 | 71.0752 | 138.9019 | 0 | 0 | 0 | 1 | 1
Temperature set back of 2 DegC afterhours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621.6145 | 403.3205 | 0 | 416.1057 | 70.4359 | 135.0729 | 0 | 0 | 0 | 1 | 1
Lighting: 30% reduction from MNECB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 698.3713 | 479.3076 | 0 | 506.2217 | 74.3302 | 117.8194 | 0 | 0 | 0 | 1 | 1
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 696.4924 | 466.842 | 0 | 491.6019 | 73.5605 | 131.33 | 0 | 0 | 0 | 1 | 1
HRV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621.3928 | 399.3414 | 0 | 410.4632 | 70.9708 | 139.9587 | 0 | 0 | 0 | 1 | 1
DCV for all occupied zones | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555.5262 | 347.0004 | 0 | 344.8902 | 71.0883 | 139.5477 | 0 | 0 | 0 | 1 | 1
Cold Deck Reset to eliminate reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700.1824 | 466.842 | 0 | 491.6019 | 73.5605 | 135.02 | 0 | 0 | 0 | 1 | 0
VSD/VFD on large hp AHU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 697.0605 | 503.2679 | 0 | 491.6019 | 109.9864 | 95.4722 | 0 | 0 | 0 | 1 | 0
VSP on large hp heating/cooling pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 704.3644 | 466.842 | 0 | 491.6019 | 73.5605 | 139.202 | 0 | 0 | 0 | 0 | 0
Solar Wall for ventilation preheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 695.9805 | 458.8005 | 0 | 481.55 | 73.5605 | 140.87 | 0 | 0 | 0 | 1 | 0
Solar DHW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 697.7819 | 460.0315 | 0 | 491.6019 | 66.75 | 139.43 | 0 | 0 | 0 | 1 | 1
Dry Bulb Economizer Control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 703.2669 | 467.253 | 0 | 491.9851 | 73.6649 | 137.6169 | 0 | 0 | 0 | 1 | 1
DX Cooling COP Upgrade to COP 4.0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700.0224 | 466.842 | 0 | 491.6019 | 73.5605 | 134.86 | 0 | 0 | 0 | 1 | 1
Retro-commissioning on thermostats and AHU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 642.78 | 420.152 | 0 | 442.44 | 66.2 | 134.14 | 0 | 0 | 0 | 1 | 1
Archetype 13B- Firehall (kWh/m2 floor area)
Exempler Building # 004 | V1: Post-2004 | [5 empty] | V2: 1980-2004 | [5 empty] | V3: 1960-1979 | [5 empty] | V4: Pre-1960
ECM | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | Total | Building Heating Load | Natural Gas Consumption | Building DES Gas Consumption | Heating Electricity Consumption | Non Heating Electricity Consumption | ECM Applicability Index V1 | ECM Applicability Index V2 | ECM Applicability Index V3 | ECM Applicability Index V4 | ECM Modelled Index
Base case | 387.23 | 181.968 | 227.46 | 0 | 0 | 159.77 | 0 | 0 | 0 | 0 | 0 | 0 | 749.09 | 451.88 | 564.85 | 0 | 0 | 184.24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
Wall Insulation: Additional RSI 1.32 on ext. | 379 | 175.856 | 219.82 | 0 | 0 | 159.18 | 0 | 0 | 0 | 0 | 0 | 0 | 733.13 | 440.192 | 550.24 | 0 | 0 | 182.89 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
Roof: Additional RSI 1.76 to 2.11 on exterior | 373.78 | 172.032 | 215.04 | 0 | 0 | 158.74 | 0 | 0 | 0 | 0 | 0 | 0 | 639.18 | 371.728 | 464.66 | 0 | 0 | 174.52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
Roof: Additional RSI 2.11 to 3.52 on interior | 373.78 | 172.032 | 215.04 | 0 | 0 | 158.74 | 0 | 0 | 0 | 0 | 0 | 0 | 639.18 | 371.728 | 464.66 | 0 | 0 | 174.52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
Roof: Additional RSI 1.76 on ext, 2.11 on int. | 373.78 | 172.032 | 215.04 | 0 | 0 | 158.74 | 0 | 0 | 0 | 0 | 0 | 0 | 639.18 | 371.728 | 464.66 | 0 | 0 | 174.52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
Windows: Double Glazed to Triple LowE | 386.31 | 181.28 | 226.6 | 0 | 0 | 159.71 | 0 | 0 | 0 | 0 | 0 | 0 | 746.27 | 449.784 | 562.23 | 0 | 0 | 184.04 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
Air tightness: vintage ACH to 0.27 ACH | 387.23 | 181.968 | 227.46 | 0 | 0 | 159.77 | 0 | 0 | 0 | 0 | 0 | 0 | 507.62 | 270.064 | 337.58 | 0 | 0 | 170.04 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
Heating setpoint reduction (2 DegC) | 339.84 | 144.784 | 180.98 | 0 | 0 | 158.86 | 0 | 0 | 0 | 0 | 0 | 0 | 657 | 379.704 | 474.63 | 0 | 0 | 182.37 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
Temperature set back of 2 DegC afterhours | 368.22 | 167.208 | 209.01 | 0 | 0 | 159.21 | 0 | 0 | 0 | 0 | 0 | 0 | 708.29 | 420.08 | 525.1 | 0 | 0 | 183.19 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
Lighting: 30% reduction from MNECB | 379.64 | 198.824 | 248.53 | 0 | 0 | 131.11 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 470.456 | 588.07 | 0 | 0 | 155.93 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
Occupancy Sensors (Lights/Plug Loads) | 373.12 | 181.968 | 227.46 | 0 | 0 | 145.66 | 0 | 0 | 0 | 0 | 0 | 0 | 734.98 | 451.88 | 564.85 | 0 | 0 | 170.13 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
HRV | 340.73 | 143.552 | 179.44 | 0 | 0 | 161.29 | 0 | 0 | 0 | 0 | 0 | 0 | 700.23 | 412.176 | 515.22 | 0 | 0 | 185.01 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
DCV for all occupied zones | 341.73 | 145.568 | 181.96 | 0 | 0 | 159.77 | 0 | 0 | 0 | 0 | 0 | 0 | 636.12 | 361.504 | 451.88 | 0 | 0 | 184.24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
Cold Deck Reset to eliminate reheat | 382.43 | 181.968 | 227.46 | 0 | 0 | 154.97 | 0 | 0 | 0 | 0 | 0 | 0 | 743.52 | 451.88 | 564.85 | 0 | 0 | 178.67 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0
VSD/VFD on large hp AHU | 386.7092 | 188.218 | 235.2725 | 0 | 0 | 151.4367 | 0 | 0 | 0 | 0 | 0 | 0 | 747.7533 | 467.9205 | 584.9006 | 0 | 0 | 162.8527 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0
VSP on large hp heating/cooling pumps | 381.3 | 181.968 | 227.46 | 0 | 0 | 153.84 | 0 | 0 | 0 | 0 | 0 | 0 | 743.16 | 451.88 | 564.85 | 0 | 0 | 178.31 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0
Solar Wall for ventilation preheat | 374.08 | 167.448 | 209.31 | 0 | 0 | 164.77 | 0 | 0 | 0 | 0 | 0 | 0 | 735.94 | 437.36 | 546.7 | 0 | 0 | 189.24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0
Solar DHW | 380.1 | 176.128 | 220.16 | 0 | 0 | 159.94 | 0 | 0 | 0 | 0 | 0 | 0 | 741.96 | 446.04 | 557.55 | 0 | 0 | 184.41 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
Dry Bulb Economizer Control | 385.75 | 181.968 | 227.46 | 0 | 0 | 158.29 | 0 | 0 | 0 | 0 | 0 | 0 | 746.75 | 451.888 | 564.86 | 0 | 0 | 181.89 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
DX Cooling COP Upgrade to COP 4.0 | 387.23 | 181.968 | 227.46 | 0 | 0 | 159.77 | 0 | 0 | 0 | 0 | 0 | 0 | 747.51 | 451.88 | 564.85 | 0 | 0 | 182.66 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
Retro-commissioning on thermostats and AHU | 364.18 | 165.032 | 206.29 | 0 | 0 | 157.89 | 0 | 0 | 0 | 0 | 0 | 0 | 689.87 | 407.96 | 509.95 | 0 | 0 | 179.92 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1
Note on A14: khaddad: 10% reduction in lighting and plug loads
Note on A17: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A23: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A24: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A39: khaddad: 10% reduction in lighting and plug loads
Note on A42: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A48: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A49: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A64: khaddad: 10% reduction in lighting and plug loads
Note on A67: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A73: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A74: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A89: khaddad: 10% reduction in lighting and plug loads
Note on A92: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A98: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A99: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A114: khaddad: 10% reduction in lighting and plug loads
Note on A117: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A123: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A124: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A139: khaddad: 10% reduction in lighting and plug loads
Note on A142: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A148: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A149: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A164: khaddad: 10% reduction in lighting and plug loads
Note on A167: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A173: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A174: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A189: khaddad: 10% reduction in lighting and plug loads
Note on A192: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A198: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A199: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A214: khaddad: 10% reduction in lighting and plug loads
Note on A217: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A223: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A224: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A239: khaddad: 10% reduction in lighting and plug loads
Note on A242: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A248: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A249: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A264: khaddad: 10% reduction in lighting and plug loads
Note on A267: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A273: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A274: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw
Note on A289: khaddad: 10% reduction in lighting and plug loads
Note on A292: Lubun, Mike: used SAT reset costing but applied to ahus with cooling
Note on A298: khaddad: =4 for V1 =3.5 for V2 =3 for V3 =2.5 for V4
Note on A299: khaddad: 10% redution in fuel and electricity except for lighting, plug loads, and dhw

## BaseBldgEnergy
Base wide fuel and electricity consumption for each archetype and vintage
1A: Hanger (GWh)
| V1 (GWh) |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 3.4059 | 0 | 2.771 | 0 | 6.1769 | 0 | 0 | 0 | 0 | 0 | 7.3529 | 0 | 4.1928 | 0 | 11.5457 | 4.1921 | 0 | 1.1761 | 0 | 5.3682 | 14.9509 | 0 | 14.9509 | 8.1399
Wall | 3.2988 | 0 | 2.649 | 0 | 5.9478 | 0 | 0 | 0 | 0 | 0 | 6.9951 | 0 | 4.0774 | 0 | 11.0725 | 3.9447 | 0 | 1.124 | 0 | 5.0687 | 14.2386 | 0 | 14.2386 | 7.8504
Roof | 3.2821 | 0 | 2.649 | 0 | 5.9311 | 0 | 0 | 0 | 0 | 0 | 6.1493 | 0 | 4.0765 | 0 | 10.2258 | 3.6468 | 0 | 1.1237 | 0 | 4.7705 | 13.0782 | 0 | 13.0782 | 7.8492
Windows | 3.3146 | 0 | 2.6468 | 0 | 5.9614 | 0 | 0 | 0 | 0 | 0 | 7.271 | 0 | 4.0774 | 0 | 11.3484 | 4.1775 | 0 | 1.124 | 0 | 5.3016 | 14.7632 | 0 | 14.7632 | 7.8483
Air tightness | 3.4059 | 0 | 2.771 | 0 | 6.1769 | 0 | 0 | 0 | 0 | 0 | 6.9239 | 0 | 4.0772 | 0 | 11.0011 | 3.8538 | 0 | 1.1233 | 0 | 4.977 | 14.1836 | 0 | 14.1836 | 7.9715
T Reduction (2 DegC) | 3.0536 | 0 | 2.6599 | 0 | 5.7135 | 0 | 0 | 0 | 0 | 0 | 6.6865 | 0 | 4.0751 | 0 | 10.7616 | 3.9214 | 0 | 1.1229 | 0 | 5.0443 | 13.6615 | 0 | 13.6615 | 7.8579
T set back | 3.164 | 0 | 2.6453 | 0 | 5.8093 | 0 | 0 | 0 | 0 | 0 | 6.937 | 0 | 4.0763 | 0 | 11.0133 | 4.0545 | 0 | 1.1235 | 0 | 5.178 | 14.1554 | 0 | 14.1554 | 7.8452
Lighting (30%) | 3.5738 | 0 | 2.2452 | 0 | 5.819 | 0 | 0 | 0 | 0 | 0 | 7.5835 | 0 | 3.7311 | 0 | 11.3146 | 4.2624 | 0 | 0.96781 | 0 | 5.2302 | 15.4198 | 0 | 15.4198 | 6.9441
Occupancy Sensors (Lights/Plug Loads) | 3.4059 | 0 | 2.4939 | 0 | 5.8998 | 0 | 0 | 0 | 0 | 0 | 7.3529 | 0 | 3.7735 | 0 | 11.1264 | 4.1921 | 0 | 1.0585 | 0 | 5.2506 | 14.9509 | 0 | 14.9509 | 7.3259
HRV | 2.2205 | 0 | 2.6767 | 0 | 4.8972 | 0 | 0 | 0 | 0 | 0 | 7.3191 | 0 | 4.0772 | 0 | 11.3964 | 4.1793 | 0 | 1.1273 | 0 | 5.3066 | 13.7189 | 0 | 13.7189 | 7.8812
DCV | 2.2523 | 0 | 2.6376 | 0 | 4.89 | 0 | 0 | 0 | 0 | 0 | 7.3514 | 0 | 4.0756 | 0 | 11.427 | 4.191 | 0 | 1.1237 | 0 | 5.3147 | 13.7947 | 0 | 13.7947 | 7.837
Cold Deck Reset | 3.3038 | 0 | 2.6623 | 0 | 5.9661 | 0 | 0 | 0 | 0 | 0 | 7.3529 | 0 | 4.0772 | 0 | 11.4301 | 4.1921 | 0 | 1.1239 | 0 | 5.316 | 14.8488 | 0 | 14.8488 | 7.8634
VSD | 3.4059 | 0 | 2.771 | 0 | 6.1769 | 0 | 0 | 0 | 0 | 0 | 7.351 | 0 | 4.0769 | 0 | 11.4279 | 4.1908 | 0 | 1.1239 | 0 | 5.3147 | 14.9477 | 0 | 14.9477 | 7.9718
VSP | 3.4059 | 0 | 2.2255 | 0 | 5.6314 | 0 | 0 | 0 | 0 | 0 | 7.6729 | 0 | 2.8558 | 0 | 10.5287 | 4.1921 | 0 | 1.124 | 0 | 5.3161 | 15.2709 | 0 | 15.2709 | 6.2053
Solar Wall | 3.1511 | 0 | 2.7805 | 0 | 5.9315 | 0 | 0 | 0 | 0 | 0 | 7.1166 | 0 | 4.2014 | 0 | 11.318 | 4.0855 | 0 | 1.1801 | 0 | 5.2656 | 14.3532 | 0 | 14.3532 | 8.1619
Solar DHW | 3.3422 | 0 | 2.7726 | 0 | 6.1148 | 0 | 0 | 0 | 0 | 0 | 7.2938 | 0 | 4.194 | 0 | 11.4879 | 4.1655 | 0 | 1.1768 | 0 | 5.3423 | 14.8015 | 0 | 14.8015 | 8.1434
DB Economizer | 3.4041 | 0 | 2.6535 | 0 | 6.0576 | 0 | 0 | 0 | 0 | 0 | 7.3297 | 0 | 4.0763 | 0 | 11.4061 | 4.1776 | 0 | 1.1238 | 0 | 5.3014 | 14.9114 | 0 | 14.9114 | 7.8537
COP | 3.4059 | 0 | 2.771 | 0 | 6.1769 | 0 | 0 | 0 | 0 | 0 | 7.3308 | 0 | 4.0731 | 0 | 11.4039 | 4.1921 | 0 | 1.1222 | 0 | 5.3143 | 14.9288 | 0 | 14.9288 | 7.9663
Retro-commissioning | 3.0653 | 0 | 2.4939 | 0 | 5.5592 | 0 | 0 | 0 | 0 | 0 | 6.6176 | 0 | 3.7735 | 0 | 10.3911 | 3.7729 | 0 | 1.0585 | 0 | 4.8314 | 13.4559 | 0 | 13.4559 | 7.3259
2A-Training Building (GWh)
| V1 |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 3.0503 | 0 | 1.2591 | 0 | 4.3094 | 0.59372 | 0 | 0.17862 | 0 | 0.77234 | 0 | 0.36126 | 0.10904 | 0 | 0.47031 | 1.3724 | 3.3985 | 1.2357 | 0 | 6.0066 | 5.0164 | 6.8359 | 11.8522 | 2.7825
Wall | 2.9695 | 0 | 1.2585 | 0 | 4.228 | 0.56707 | 0 | 0.17719 | 0 | 0.74426 | 0 | 0.34884 | 0.10725 | 0 | 0.4561 | 1.3141 | 3.2542 | 1.2081 | 0 | 5.7764 | 4.8507 | 6.5509 | 11.4016 | 2.7511
Roof | 2.8252 | 0 | 1.2547 | 0 | 4.0799 | 0.52002 | 0 | 0.17244 | 0 | 0.69245 | 0 | 0.26427 | 0.093637 | 0 | 0.3579 | 1.043 | 2.5827 | 1.0664 | 0 | 4.6921 | 4.3882 | 5.1763 | 9.5645 | 2.5872
Windows | 3.0351 | 0 | 1.2591 | 0 | 4.2942 | 0.58817 | 0 | 0.17864 | 0 | 0.76682 | 0 | 0.35929 | 0.10884 | 0 | 0.46813 | 1.3619 | 3.3723 | 1.2322 | 0 | 5.9663 | 4.9851 | 6.7848 | 11.7699 | 2.7788
Air tightness | 3.0503 | 0 | 1.2591 | 0 | 4.3094 | 0.48681 | 0 | 0.17742 | 0 | 0.66423 | 0 | 0.28298 | 0.10031 | 0 | 0.38329 | 0.94644 | 2.3437 | 1.0796 | 0 | 4.3697 | 4.4835 | 4.7757 | 9.2592 | 2.6165
T Reduction (2 DegC) | 2.4237 | 0 | 1.2464 | 0 | 3.6701 | 0.48584 | 0 | 0.17703 | 0 | 0.66287 | 0 | 0.30266 | 0.10844 | 0 | 0.4111 | 1.1565 | 2.8638 | 1.229 | 0 | 5.2493 | 4.066 | 5.7571 | 9.8231 | 2.761
T set back | 2.4931 | 0 | 1.2484 | 0 | 3.7415 | 0.49767 | 0 | 0.17721 | 0 | 0.67488 | 0 | 0.31098 | 0.10851 | 0 | 0.41949 | 1.0597 | 2.6241 | 1.2295 | 0 | 4.9132 | 4.0505 | 5.3365 | 9.3869 | 2.7635
Lighting (30%) | 3.2743 | 0 | 1.2484 | 0 | 4.5227 | 0.60161 | 0 | 0.1439 | 0 | 0.74551 | 0 | 0.36999 | 0.091982 | 0 | 0.46197 | 1.4016 | 3.4707 | 1.0549 | 0 | 5.9271 | 5.2775 | 6.983 | 12.2605 | 2.5391
Occupancy Sensors (Lights/Plug Loads) | 3.0503 | 0 | 1.1684 | 0 | 4.2186 | 0.59372 | 0 | 0.16659 | 0 | 0.7603 | 0 | 0.36126 | 0.10274 | 0 | 0.464 | 1.3724 | 3.3985 | 1.1685 | 0 | 5.9393 | 5.0164 | 6.8359 | 11.8522 | 2.6062
HRV | 1.9383 | 0 | 1.2677 | 0 | 3.206 | 0.44006 | 0 | 0.179 | 0 | 0.61906 | 0 | 0.29709 | 0.10902 | 0 | 0.4061 | 1.1625 | 2.8786 | 1.2356 | 0 | 5.2767 | 3.5408 | 5.774 | 9.3149 | 2.7913
DCV | 2.4553 | 0 | 1.2591 | 0 | 3.7144 | 0.47902 | 0 | 0.17864 | 0 | 0.65766 | 0 | 0.2907 | 0.10904 | 0 | 0.39974 | 1.1034 | 2.7323 | 1.2295 | 0 | 5.0652 | 4.0377 | 5.4964 | 9.5342 | 2.7763
Cold Deck Reset | 3.0503 | 0 | 1.2213 | 0 | 4.2716 | 0.59372 | 0 | 0.17325 | 0 | 0.76697 | 0 | 0.36126 | 0.10576 | 0 | 0.46702 | 1.3724 | 3.3985 | 1.2357 | 0 | 6.0066 | 5.0164 | 6.8359 | 11.8522 | 2.736
VSD | 3.2237 | 0 | 1.0741 | 0 | 4.2978 | 0.62271 | 0 | 0.14769 | 0 | 0.7704 | 0 | 0.38193 | 0.081493 | 0 | 0.46342 | 1.4519 | 3.5953 | 0.88845 | 0 | 5.9357 | 5.2983 | 7.2314 | 12.5296 | 2.1918
VSP | 3.0503 | 0 | 0.83954 | 0 | 3.8898 | 0.59369 | 0 | 0.12275 | 0 | 0.71644 | 0 | 0.36126 | 0.079846 | 0 | 0.44111 | 1.3724 | 3.3985 | 0.92483 | 0 | 5.6957 | 5.0163 | 6.8359 | 11.8522 | 1.967
Solar Wall | 3.0065 | 0 | 1.2737 | 0 | 4.2802 | 0.58789 | 0 | 0.18056 | 0 | 0.76845 | 0 | 0.35883 | 0.11006 | 0 | 0.46889 | 1.3645 | 3.3789 | 1.2465 | 0 | 5.9899 | 4.9589 | 6.7958 | 11.7547 | 2.8108
Solar DHW | 2.9712 | 0 | 1.2612 | 0 | 4.2324 | 0.58319 | 0 | 0.1789 | 0 | 0.76209 | 0 | 0.35686 | 0.10919 | 0 | 0.46605 | 1.3581 | 3.3631 | 1.2373 | 0 | 5.9584 | 4.9125 | 6.7635 | 11.676 | 2.7866
DB Economizer | 3.0503 | 0 | 1.2534 | 0 | 4.3036 | 0.59372 | 0 | 0.17798 | 0 | 0.7717 | 0 | 0.36126 | 0.10891 | 0 | 0.47017 | 1.3724 | 3.3985 | 1.2346 | 0 | 6.0054 | 5.0164 | 6.8359 | 11.8522 | 2.7748
COP | 3.0503 | 0 | 1.2591 | 0 | 4.3094 | 0.59369 | 0 | 0.17678 | 0 | 0.77047 | 0 | 0.36126 | 0.10705 | 0 | 0.46832 | 1.3724 | 3.3985 | 1.2039 | 0 | 5.9747 | 5.0163 | 6.8359 | 11.8522 | 2.7468
Retro-commissioning | 2.7604 | 0 | 1.2236 | 0 | 3.984 | 0.53637 | 0 | 0.17284 | 0 | 0.70921 | 0 | 0.32599 | 0.10444 | 0 | 0.43042 | 1.2379 | 3.0655 | 1.1791 | 0 | 5.4826 | 4.5347 | 6.1663 | 10.701 | 2.68
3A-Active Warehouse (GWh)
| V1 |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 0.025149 | 0 | 0.05953 | 0 | 0.084679 | 0.28216 | 0 | 0.22543 | 0 | 0.50758 | 0 | 0 | 0 | 0 | 0 | 0.25821 | 0.26408 | 0.26104 | 0 | 0.78332 | 0.56551 | 0.48014 | 1.0456 | 0.546
Wall | 0.022684 | 0 | 0.058249 | 0 | 0.080933 | 0.25727 | 0 | 0.22501 | 0 | 0.48228 | 0 | 0 | 0 | 0 | 0 | 0.24069 | 0.24616 | 0.26063 | 0 | 0.74748 | 0.52065 | 0.44756 | 0.96821 | 0.54389
Roof | 0.023125 | 0 | 0.058484 | 0 | 0.081608 | 0.25628 | 0 | 0.22509 | 0 | 0.48137 | 0 | 0 | 0 | 0 | 0 | 0.20446 | 0.20911 | 0.25825 | 0 | 0.67183 | 0.48387 | 0.3802 | 0.86407 | 0.54183
Windows | 0.024889 | 0 | 0.059275 | 0 | 0.084164 | 0.27768 | 0 | 0.22484 | 0 | 0.50252 | 0 | 0 | 0 | 0 | 0 | 0.2558 | 0.26161 | 0.26047 | 0 | 0.77787 | 0.55836 | 0.47566 | 1.034 | 0.54459
Air tightness | 0.025149 | 0 | 0.05953 | 0 | 0.084679 | 0.20088 | 0 | 0.22435 | 0 | 0.42522 | 0 | 0 | 0 | 0 | 0 | 0.15173 | 0.15518 | 0.25842 | 0 | 0.56533 | 0.37775 | 0.28214 | 0.6599 | 0.54229
T Reduction (2 DegC) | 0.018172 | 0 | 0.055874 | 0 | 0.074046 | 0.21133 | 0 | 0.22402 | 0 | 0.43534 | 0 | 0 | 0 | 0 | 0 | 0.20673 | 0.21143 | 0.25874 | 0 | 0.67691 | 0.43623 | 0.38442 | 0.82065 | 0.53863
T set back | 0.025149 | 0 | 0.05953 | 0 | 0.084679 | 0.28216 | 0 | 0.22543 | 0 | 0.50758 | 0 | 0 | 0 | 0 | 0 | 0.25821 | 0.26408 | 0.26104 | 0 | 0.78332 | 0.56551 | 0.48014 | 1.0456 | 0.546
Lighting (30%) | 0.02723 | 0 | 0.0526 | 0 | 0.079829 | 0.29899 | 0 | 0.18935 | 0 | 0.48834 | 0 | 0 | 0 | 0 | 0 | 0.26587 | 0.27191 | 0.22547 | 0 | 0.76325 | 0.59209 | 0.49439 | 1.0865 | 0.46742
Occupancy Sensors (Lights/Plug Loads) | 0.025149 | 0 | 0.05593 | 0 | 0.081079 | 0.28216 | 0 | 0.20909 | 0 | 0.49124 | 0 | 0 | 0 | 0 | 0 | 0.25821 | 0.26408 | 0.24491 | 0 | 0.7672 | 0.56551 | 0.48014 | 1.0456 | 0.50993
HRV | 0.022526 | 0 | 0.058299 | 0 | 0.080825 | 0.2615 | 0 | 0.22551 | 0 | 0.48701 | 0 | 0 | 0 | 0 | 0 | 0.24875 | 0.2544 | 0.26096 | 0 | 0.7641 | 0.53278 | 0.46255 | 0.99532 | 0.54477
DCV | 0.021904 | 0 | 0.057903 | 0 | 0.079807 | 0.2562 | 0 | 0.22509 | 0 | 0.48129 | 0 | 0 | 0 | 0 | 0 | 0.24601 | 0.2516 | 0.26055 | 0 | 0.75816 | 0.52411 | 0.45746 | 0.98157 | 0.54354
Cold Deck Reset | 0.025149 | 0 | 0.058108 | 0 | 0.083257 | 0.28216 | 0 | 0.21862 | 0 | 0.50078 | 0 | 0 | 0 | 0 | 0 | 0.25821 | 0.26408 | 0.25317 | 0 | 0.77545 | 0.56551 | 0.48014 | 1.0456 | 0.5299
VSD | 0.028699 | 0 | 0.055163 | 0 | 0.083863 | 0.31586 | 0 | 0.18947 | 0 | 0.50533 | 0 | 0 | 0 | 0 | 0 | 0.28418 | 0.29064 | 0.19792 | 0 | 0.77274 | 0.62874 | 0.52843 | 1.1572 | 0.44255
VSP | 0.025149 | 0 | 0.05953 | 0 | 0.084679 | 0.28216 | 0 | 0.22543 | 0 | 0.50758 | 0 | 0 | 0 | 0 | 0 | 0.25821 | 0.26408 | 0.26104 | 0 | 0.78332 | 0.56551 | 0.48014 | 1.0456 | 0.546
Solar Wall | 0.023034 | 0 | 0.058695 | 0 | 0.081729 | 0.26665 | 0 | 0.22634 | 0 | 0.49298 | 0 | 0 | 0 | 0 | 0 | 0.25148 | 0.2572 | 0.26194 | 0 | 0.77062 | 0.54116 | 0.46763 | 1.0088 | 0.54697
Solar DHW | 0.025149 | 0 | 0.058199 | 0 | 0.083348 | 0.28216 | 0 | 0.21937 | 0 | 0.50153 | 0 | 0 | 0 | 0 | 0 | 0.25821 | 0.26408 | 0.25506 | 0 | 0.77734 | 0.56551 | 0.48014 | 1.0456 | 0.53263
DB Economizer | 0.025239 | 0 | 0.059228 | 0 | 0.084467 | 0.28274 | 0 | 0.22393 | 0 | 0.50667 | 0 | 0 | 0 | 0 | 0 | 0.25839 | 0.26426 | 0.25915 | 0 | 0.7818 | 0.56636 | 0.48047 | 1.0468 | 0.54231
COP | 0.025149 | 0 | 0.05953 | 0 | 0.084679 | 0.28216 | 0 | 0.22476 | 0 | 0.50692 | 0 | 0 | 0 | 0 | 0 | 0.25821 | 0.26408 | 0.25866 | 0 | 0.78095 | 0.56551 | 0.48014 | 1.0456 | 0.54295
Retro-commissioning | 0.022695 | 0 | 0.05738 | 0 | 0.080075 | 0.25437 | 0 | 0.22012 | 0 | 0.47449 | 0 | 0 | 0 | 0 | 0 | 0.23256 | 0.23784 | 0.25202 | 0 | 0.72243 | 0.50962 | 0.43245 | 0.94207 | 0.52952
3B-Storage Type Warehouse (GWh)
| V1 |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 0 | 0.05353 | 0.024933 | 0 | 0.078463 | 0 | 0.063011 | 0.030569 | 0 | 0.093581 | 0 | 0.048797 | 0.047265 | 0 | 0.096063 | 0 | 0.045184 | 0.060966 | 0 | 0.10615 | 0 | 0.38277 | 0.38277 | 0.16373
Wall | 0 | 0.051187 | 0.023841 | 0 | 0.075028 | 0 | 0.057813 | 0.029914 | 0 | 0.087727 | 0 | 0.045587 | 0.045014 | 0 | 0.090601 | 0 | 0.041057 | 0.056481 | 0 | 0.097538 | 0 | 0.35571 | 0.35571 | 0.15525
Roof | 0 | 0.050522 | 0.023531 | 0 | 0.074053 | 0 | 0.0561 | 0.029549 | 0 | 0.085649 | 0 | 0.043162 | 0.043264 | 0 | 0.086426 | 0 | 0.0346 | 0.049323 | 0 | 0.083923 | 0 | 0.33524 | 0.33524 | 0.14567
Windows | 0 | 0.05353 | 0.024933 | 0 | 0.078463 | 0 | 0.063011 | 0.030569 | 0 | 0.093581 | 0 | 0.048797 | 0.047265 | 0 | 0.096063 | 0 | 0.045184 | 0.060966 | 0 | 0.10615 | 0 | 0.38277 | 0.38277 | 0.16373
Air tightness | 0 | 0.05353 | 0.024933 | 0 | 0.078463 | 0 | 0.063011 | 0.030569 | 0 | 0.093581 | 0 | 0.048797 | 0.047265 | 0 | 0.096063 | 0 | 0.045184 | 0.060966 | 0 | 0.10615 | 0 | 0.38277 | 0.38277 | 0.16373
T Reduction (2 DegC) | 0 | 0.047276 | 0.02202 | 0 | 0.069296 | 0 | 0.056651 | 0.028581 | 0 | 0.085232 | 0 | 0.045081 | 0.043869 | 0 | 0.08895 | 0 | 0.042364 | 0.05704 | 0 | 0.099405 | 0 | 0.34795 | 0.34795 | 0.15151
T set back | 0 | 0.05353 | 0.024933 | 0 | 0.078463 | 0 | 0.063011 | 0.030569 | 0 | 0.093581 | 0 | 0.048797 | 0.047265 | 0 | 0.096063 | 0 | 0.045184 | 0.060966 | 0 | 0.10615 | 0 | 0.38277 | 0.38277 | 0.16373
Lighting (30%) | 0 | 0.054988 | 0.025612 | 0 | 0.0806 | 0 | 0.064288 | 0.027126 | 0 | 0.091414 | 0 | 0.049476 | 0.045546 | 0 | 0.095022 | 0 | 0.045664 | 0.059529 | 0 | 0.10519 | 0 | 0.38985 | 0.38985 | 0.15781
Occupancy Sensors (Lights/Plug Loads) | 0 | 0.05353 | 0.024933 | 0 | 0.078463 | 0 | 0.063011 | 0.030569 | 0 | 0.093581 | 0 | 0.048797 | 0.047265 | 0 | 0.096063 | 0 | 0.045184 | 0.060966 | 0 | 0.10615 | 0 | 0.38277 | 0.38277 | 0.16373
HRV | 0 | 0.05353 | 0.024933 | 0 | 0.078463 | 0 | 0.063011 | 0.030569 | 0 | 0.093581 | 0 | 0.048797 | 0.047265 | 0 | 0.096063 | 0 | 0.045184 | 0.060966 | 0 | 0.10615 | 0 | 0.38277 | 0.38277 | 0.16373
DCV | 0 | 0.0482 | 0.02245 | 0 | 0.07065 | 0 | 0.056704 | 0.030175 | 0 | 0.08688 | 0 | 0.048797 | 0.047265 | 0 | 0.096063 | 0 | 0.040666 | 0.05654 | 0 | 0.097207 | 0 | 0.3534 | 0.3534 | 0.15643
Cold Deck Reset | 0 | 0.05353 | 0.024933 | 0 | 0.078463 | 0 | 0.063011 | 0.029761 | 0 | 0.092772 | 0 | 0.048797 | 0.046747 | 0 | 0.095544 | 0 | 0.045184 | 0.060462 | 0 | 0.10565 | 0 | 0.38277 | 0.38277 | 0.1619
VSD | 0 | 0.05353 | 0.024933 | 0 | 0.078463 | 0 | 0.063011 | 0.030569 | 0 | 0.093581 | 0 | 0.048797 | 0.047265 | 0 | 0.096063 | 0 | 0.045184 | 0.060966 | 0 | 0.10615 | 0 | 0.38277 | 0.38277 | 0.16373
VSP | 0 | 0.05353 | 0.024933 | 0 | 0.078463 | 0 | 0.063011 | 0.030569 | 0 | 0.093581 | 0 | 0.048797 | 0.047265 | 0 | 0.096063 | 0 | 0.045184 | 0.060966 | 0 | 0.10615 | 0 | 0.38277 | 0.38277 | 0.16373
Solar Wall | 0 | 0.048898 | 0.022775 | 0 | 0.071673 | 0 | 0.059133 | 0.030854 | 0 | 0.089988 | 0 | 0.046818 | 0.046368 | 0 | 0.093187 | 0 | 0.043774 | 0.059864 | 0 | 0.10364 | 0 | 0.36113 | 0.36113 | 0.15986
Solar DHW | 0 | 0.05353 | 0.024933 | 0 | 0.078463 | 0 | 0.063011 | 0.030569 | 0 | 0.093581 | 0 | 0.048797 | 0.047265 | 0 | 0.096063 | 0 | 0.045184 | 0.060966 | 0 | 0.10615 | 0 | 0.38277 | 0.38277 | 0.16373
DB Economizer | 0 | 0.05353 | 0.024933 | 0 | 0.078463 | 0 | 0.063011 | 0.030569 | 0 | 0.093581 | 0 | 0.048797 | 0.047265 | 0 | 0.096063 | 0 | 0.045184 | 0.060966 | 0 | 0.10615 | 0 | 0.38277 | 0.38277 | 0.16373
COP | 0 | 0.05353 | 0.024933 | 0 | 0.078463 | 0 | 0.063011 | 0.030569 | 0 | 0.093581 | 0 | 0.048797 | 0.047265 | 0 | 0.096063 | 0 | 0.045184 | 0.060966 | 0 | 0.10615 | 0 | 0.38277 | 0.38277 | 0.16373
Retro-commissioning | 0 | 0.05353 | 0.024933 | 0 | 0.078463 | 0 | 0.063011 | 0.030569 | 0 | 0.093581 | 0 | 0.048797 | 0.047265 | 0 | 0.096063 | 0 | 0.045184 | 0.060966 | 0 | 0.10615 | 0 | 0.38277 | 0.38277 | 0.16373
4A-Hotel Type Accomodation (GWh)
| V1 |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 0 | 0 | 0 | 0 | 0 | 2.2134 | 0 | 0.73905 | 0 | 2.9524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2134 | 0 | 2.2134 | 0.73905
Wall | 0 | 0 | 0 | 0 | 0 | 2.1494 | 0 | 0.72174 | 0 | 2.8712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1494 | 0 | 2.1494 | 0.72174
Roof | 0 | 0 | 0 | 0 | 0 | 2.0481 | 0 | 0.69223 | 0 | 2.7404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0481 | 0 | 2.0481 | 0.69223
Windows | 0 | 0 | 0 | 0 | 0 | 2.1441 | 0 | 0.72419 | 0 | 2.8683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1441 | 0 | 2.1441 | 0.72419
Air tightness | 0 | 0 | 0 | 0 | 0 | 1.7894 | 0 | 0.62956 | 0 | 2.4189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7894 | 0 | 1.7894 | 0.62956
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 1.7355 | 0 | 0.66567 | 0 | 2.4012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7355 | 0 | 1.7355 | 0.66567
T set back | 0 | 0 | 0 | 0 | 0 | 1.7355 | 0 | 0.66563 | 0 | 2.4011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7355 | 0 | 1.7355 | 0.66563
Lighting (30%) | 0 | 0 | 0 | 0 | 0 | 2.2979 | 0 | 0.65222 | 0 | 2.9501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2979 | 0 | 2.2979 | 0.65222
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 2.2134 | 0 | 0.70575 | 0 | 2.9191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2134 | 0 | 2.2134 | 0.70575
HRV | 0 | 0 | 0 | 0 | 0 | 2.1829 | 0 | 0.83107 | 0 | 3.0139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1829 | 0 | 2.1829 | 0.83107
DCV | 0 | 0 | 0 | 0 | 0 | 2.1842 | 0 | 0.80931 | 0 | 2.9935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1842 | 0 | 2.1842 | 0.80931
Cold Deck Reset | 0 | 0 | 0 | 0 | 0 | 2.2134 | 0 | 0.71681 | 0 | 2.9302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2134 | 0 | 2.2134 | 0.71681
VSD | 0 | 0 | 0 | 0 | 0 | 2.2877 | 0 | 0.65982 | 0 | 2.9475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2877 | 0 | 2.2877 | 0.65982
VSP | 0 | 0 | 0 | 0 | 0 | 2.2134 | 0 | 0.72698 | 0 | 2.9404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2134 | 0 | 2.2134 | 0.72698
Solar Wall | 0 | 0 | 0 | 0 | 0 | 2.1242 | 0 | 0.78265 | 0 | 2.9068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1242 | 0 | 2.1242 | 0.78265
Solar DHW | 0 | 0 | 0 | 0 | 0 | 1.9355 | 0 | 0.74596 | 0 | 2.6815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9355 | 0 | 1.9355 | 0.74596
DB Economizer | 0 | 0 | 0 | 0 | 0 | 2.2146 | 0 | 0.57717 | 0 | 2.7918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2146 | 0 | 2.2146 | 0.57717
COP | 0 | 0 | 0 | 0 | 0 | 2.2134 | 0 | 0.70215 | 0 | 2.9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2134 | 0 | 2.2134 | 0.70215
Retro-commissioning | 0 | 0 | 0 | 0 | 0 | 2.0501 | 0 | 0.69837 | 0 | 2.7484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0501 | 0 | 2.0501 | 0.69837
4B-Dormitory (GWh)
| V1 |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 0 | 0 | 0 | 0 | 0 | 0 | 0.28851 | 0.097434 | 0 | 0.38594 | 2.3895 | 0 | 0.57473 | 0 | 2.9643 | 0 | 2.1541 | 0.58503 | 0 | 2.7391 | 2.3895 | 4.441 | 6.8306 | 1.2572
Wall | 0 | 0 | 0 | 0 | 0 | 0 | 0.28422 | 0.097412 | 0 | 0.38163 | 2.3449 | 0 | 0.57455 | 0 | 2.9195 | 0 | 2.0863 | 0.58478 | 0 | 2.6711 | 2.3449 | 4.3101 | 6.655 | 1.2567
Roof | 0 | 0 | 0 | 0 | 0 | 0 | 0.27899 | 0.097429 | 0 | 0.37642 | 2.2656 | 0 | 0.57472 | 0 | 2.8403 | 0 | 2.0499 | 0.58504 | 0 | 2.635 | 2.2656 | 4.2344 | 6.4999 | 1.2572
Windows | 0 | 0 | 0 | 0 | 0 | 0 | 0.28717 | 0.097429 | 0 | 0.3846 | 2.3615 | 0 | 0.57467 | 0 | 2.9361 | 0 | 2.1097 | 0.58491 | 0 | 2.6946 | 2.3615 | 4.358 | 6.7195 | 1.257
Air tightness | 0 | 0 | 0 | 0 | 0 | 0 | 0.26881 | 0.097391 | 0 | 0.3662 | 2.0976 | 0 | 0.57423 | 0 | 2.6718 | 0 | 1.7567 | 0.58422 | 0 | 2.3409 | 2.0976 | 3.6827 | 5.7803 | 1.2558
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 0 | 0.27058 | 0.097408 | 0 | 0.36799 | 2.2482 | 0 | 0.57457 | 0 | 2.8227 | 0 | 2.0315 | 0.58486 | 0 | 2.6164 | 2.2482 | 4.1857 | 6.4338 | 1.2568
T set back | 0 | 0 | 0 | 0 | 0 | 0 | 0.28851 | 0.097434 | 0 | 0.38594 | 2.3895 | 0 | 0.57473 | 0 | 2.9643 | 0 | 2.1541 | 0.58503 | 0 | 2.7391 | 2.3895 | 4.441 | 6.8306 | 1.2572
Lighting (30%) | 0 | 0 | 0 | 0 | 0 | 0 | 0.29433 | 0.086311 | 0 | 0.38064 | 2.4332 | 0 | 0.50919 | 0 | 2.9423 | 0 | 2.1901 | 0.51837 | 0 | 2.7084 | 2.4332 | 4.5171 | 6.9502 | 1.1139
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 0 | 0.28851 | 0.093035 | 0 | 0.38155 | 2.3895 | 0 | 0.54881 | 0 | 2.9384 | 0 | 2.1541 | 0.55871 | 0 | 2.7128 | 2.3895 | 4.441 | 6.8306 | 1.2006
HRV | 0 | 0 | 0 | 0 | 0 | 0 | 0.28851 | 0.097434 | 0 | 0.38594 | 2.3895 | 0 | 0.57473 | 0 | 2.9643 | 0 | 2.1541 | 0.58503 | 0 | 2.7391 | 2.3895 | 4.441 | 6.8306 | 1.2572
DCV | 0 | 0 | 0 | 0 | 0 | 0 | 0.25965 | 0.097434 | 0 | 0.35709 | 2.3895 | 0 | 0.57473 | 0 | 2.9643 | 0 | 2.1541 | 0.58503 | 0 | 2.7391 | 2.3895 | 4.3886 | 6.7781 | 1.2572
Cold Deck Reset | 0 | 0 | 0 | 0 | 0 | 0 | 0.28851 | 0.097434 | 0 | 0.38594 | 2.3895 | 0 | 0.57473 | 0 | 2.9643 | 0 | 2.1541 | 0.58503 | 0 | 2.7391 | 2.3895 | 4.441 | 6.8306 | 1.2572
VSD | 0 | 0 | 0 | 0 | 0 | 0 | 0.28902 | 0.096748 | 0 | 0.38577 | 2.3936 | 0 | 0.57043 | 0 | 2.964 | 0 | 2.1576 | 0.58032 | 0 | 2.7379 | 2.3936 | 4.4484 | 6.842 | 1.2475
VSP | 0 | 0 | 0 | 0 | 0 | 0 | 0.28851 | 0.097434 | 0 | 0.38594 | 2.3895 | 0 | 0.57473 | 0 | 2.9643 | 0 | 2.1541 | 0.58503 | 0 | 2.7391 | 2.3895 | 4.441 | 6.8306 | 1.2572
Solar Wall | 0 | 0 | 0 | 0 | 0 | 0 | 0.28851 | 0.097434 | 0 | 0.38594 | 2.3895 | 0 | 0.57473 | 0 | 2.9643 | 0 | 2.1541 | 0.58503 | 0 | 2.7391 | 2.3895 | 4.441 | 6.8306 | 1.2572
Solar DHW | 0 | 0 | 0 | 0 | 0 | 0 | 0.28851 | 0.077799 | 0 | 0.36631 | 2.3895 | 0 | 0.459 | 0 | 2.8485 | 0 | 2.1541 | 0.46731 | 0 | 2.6214 | 2.3895 | 4.441 | 6.8306 | 1.0041
DB Economizer | 0 | 0 | 0 | 0 | 0 | 0 | 0.28851 | 0.097434 | 0 | 0.38594 | 2.3895 | 0 | 0.57473 | 0 | 2.9643 | 0 | 2.1541 | 0.58503 | 0 | 2.7391 | 2.3895 | 4.441 | 6.8306 | 1.2572
COP | 0 | 0 | 0 | 0 | 0 | 0 | 0.28851 | 0.097307 | 0 | 0.38582 | 2.3895 | 0 | 0.57448 | 0 | 2.964 | 0 | 2.1541 | 0.58468 | 0 | 2.7387 | 2.3895 | 4.441 | 6.8306 | 1.2565
Retro-commissioning | 0 | 0 | 0 | 0 | 0 | 0 | 0.25945 | 0.097248 | 0 | 0.35669 | 2.1489 | 0 | 0.57358 | 0 | 2.7224 | 0 | 1.9371 | 0.58383 | 0 | 2.5209 | 2.1489 | 3.9937 | 6.1425 | 1.2547
4C-Barracks (GWh)
| V1 |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 0 | 0 | 0 | 0 | 0 | 0.44717 | 0 | 0.11945 | 0 | 0.56662 | 0.49601 | 0 | 0.21854 | 0 | 0.71455 | 0 | 0 | 0 | 0 | 0 | 0.94318 | 0 | 0.94318 | 0.33799
Wall | 0 | 0 | 0 | 0 | 0 | 0.42439 | 0 | 0.11651 | 0 | 0.54091 | 0.47346 | 0 | 0.21254 | 0 | 0.686 | 0 | 0 | 0 | 0 | 0 | 0.89785 | 0 | 0.89785 | 0.32905
Roof | 0 | 0 | 0 | 0 | 0 | 0.40204 | 0 | 0.11385 | 0 | 0.5159 | 0.37993 | 0 | 0.18885 | 0 | 0.56878 | 0 | 0 | 0 | 0 | 0 | 0.78198 | 0 | 0.78198 | 0.3027
Windows | 0 | 0 | 0 | 0 | 0 | 0.44282 | 0 | 0.11897 | 0 | 0.56179 | 0.49301 | 0 | 0.21786 | 0 | 0.71087 | 0 | 0 | 0 | 0 | 0 | 0.93584 | 0 | 0.93584 | 0.33682
Air tightness | 0 | 0 | 0 | 0 | 0 | 0.37074 | 0 | 0.11146 | 0 | 0.4822 | 0.37866 | 0 | 0.19425 | 0 | 0.57292 | 0 | 0 | 0 | 0 | 0 | 0.74941 | 0 | 0.74941 | 0.30571
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 0.38245 | 0 | 0.11427 | 0 | 0.49672 | 0.42903 | 0 | 0.20617 | 0 | 0.6352 | 0 | 0 | 0 | 0 | 0 | 0.81148 | 0 | 0.81148 | 0.32043
T set back | 0 | 0 | 0 | 0 | 0 | 0.39849 | 0 | 0.11361 | 0 | 0.5121 | 0.44629 | 0 | 0.20529 | 0 | 0.65157 | 0 | 0 | 0 | 0 | 0 | 0.84477 | 0 | 0.84477 | 0.3189
Lighting (30%) | 0 | 0 | 0 | 0 | 0 | 0.4594 | 0 | 0.10009 | 0 | 0.55949 | 0.50576 | 0 | 0.18913 | 0 | 0.69489 | 0 | 0 | 0 | 0 | 0 | 0.96516 | 0 | 0.96516 | 0.28922
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 0.44717 | 0 | 0.11162 | 0 | 0.55879 | 0.49601 | 0 | 0.20662 | 0 | 0.70263 | 0 | 0 | 0 | 0 | 0 | 0.94318 | 0 | 0.94318 | 0.31825
HRV | 0 | 0 | 0 | 0 | 0 | 0.39995 | 0 | 0.11945 | 0 | 0.5194 | 0.45944 | 0 | 0.21854 | 0 | 0.67798 | 0 | 0 | 0 | 0 | 0 | 0.85939 | 0 | 0.85939 | 0.33799
DCV | 0 | 0 | 0 | 0 | 0 | 0.39212 | 0 | 0.11945 | 0 | 0.51157 | 0.45422 | 0 | 0.21854 | 0 | 0.67276 | 0 | 0 | 0 | 0 | 0 | 0.84634 | 0 | 0.84634 | 0.33799
Cold Deck Reset | 0 | 0 | 0 | 0 | 0 | 0.44717 | 0 | 0.11945 | 0 | 0.56662 | 0.49601 | 0 | 0.21854 | 0 | 0.71455 | 0 | 0 | 0 | 0 | 0 | 0.94318 | 0 | 0.94318 | 0.33799
VSD | 0 | 0 | 0 | 0 | 0 | 0.47211 | 0 | 0.08853 | 0 | 0.56064 | 0.52629 | 0 | 0.14372 | 0 | 0.67001 | 0 | 0 | 0 | 0 | 0 | 0.9984 | 0 | 0.9984 | 0.23225
VSP | 0 | 0 | 0 | 0 | 0 | 0.44717 | 0 | 0.11945 | 0 | 0.56662 | 0.49601 | 0 | 0.21854 | 0 | 0.71455 | 0 | 0 | 0 | 0 | 0 | 0.94318 | 0 | 0.94318 | 0.33799
Solar Wall | 0 | 0 | 0 | 0 | 0 | 0.43342 | 0 | 0.12554 | 0 | 0.55896 | 0.48553 | 0 | 0.22778 | 0 | 0.71332 | 0 | 0 | 0 | 0 | 0 | 0.91895 | 0 | 0.91895 | 0.35333
Solar DHW | 0 | 0 | 0 | 0 | 0 | 0.39446 | 0 | 0.12106 | 0 | 0.51552 | 0.45585 | 0 | 0.22099 | 0 | 0.67683 | 0 | 0 | 0 | 0 | 0 | 0.85031 | 0 | 0.85031 | 0.34205
DB Economizer | 0 | 0 | 0 | 0 | 0 | 0.44717 | 0 | 0.11945 | 0 | 0.56662 | 0.49601 | 0 | 0.21854 | 0 | 0.71455 | 0 | 0 | 0 | 0 | 0 | 0.94318 | 0 | 0.94318 | 0.33799
COP | 0 | 0 | 0 | 0 | 0 | 0.44717 | 0 | 0.11945 | 0 | 0.56662 | 0.49601 | 0 | 0.21854 | 0 | 0.71455 | 0 | 0 | 0 | 0 | 0 | 0.94318 | 0 | 0.94318 | 0.33799
Retro-commissioning | 0 | 0 | 0 | 0 | 0 | 0.41313 | 0 | 0.11531 | 0 | 0.52845 | 0.45455 | 0 | 0.20853 | 0 | 0.66308 | 0 | 0 | 0 | 0 | 0 | 0.86768 | 0 | 0.86768 | 0.32384
4D-Accomodation Building (GWh)
| V1 |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 0 | 0 | 0 | 0 | 0 | 0.051792 | 0 | 0.10469 | 0 | 0.15648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051792 | 0 | 0.051792 | 0.10469
Wall | 0 | 0 | 0 | 0 | 0 | 0.048865 | 0 | 0.099159 | 0 | 0.14802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048865 | 0 | 0.048865 | 0.099159
Roof | 0 | 0 | 0 | 0 | 0 | 0.05027 | 0 | 0.1018 | 0 | 0.15207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05027 | 0 | 0.05027 | 0.1018
Windows | 0 | 0 | 0 | 0 | 0 | 0.051196 | 0 | 0.10364 | 0 | 0.15484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051196 | 0 | 0.051196 | 0.10364
Air tightness | 0 | 0 | 0 | 0 | 0 | 0.044633 | 0 | 0.093269 | 0 | 0.1379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044633 | 0 | 0.044633 | 0.093269
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 0.044646 | 0 | 0.096069 | 0 | 0.14072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044646 | 0 | 0.044646 | 0.096069
T set back | 0 | 0 | 0 | 0 | 0 | 0.039235 | 0 | 0.087922 | 0 | 0.12716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.039235 | 0 | 0.039235 | 0.087922
Lighting (30%) | 0 | 0 | 0 | 0 | 0 | 0.052573 | 0 | 0.10193 | 0 | 0.15451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052573 | 0 | 0.052573 | 0.10193
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 0.051792 | 0 | 0.10326 | 0 | 0.15506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051792 | 0 | 0.051792 | 0.10326
HRV | 0 | 0 | 0 | 0 | 0 | 0.046737 | 0 | 0.097483 | 0 | 0.14422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046737 | 0 | 0.046737 | 0.097483
DCV | 0 | 0 | 0 | 0 | 0 | 0.046193 | 0 | 0.09629 | 0 | 0.14248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046193 | 0 | 0.046193 | 0.09629
Cold Deck Reset | 0 | 0 | 0 | 0 | 0 | 0.051792 | 0 | 0.10389 | 0 | 0.15568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051792 | 0 | 0.051792 | 0.10389
VSD | 0 | 0 | 0 | 0 | 0 | 0.053791 | 0 | 0.10056 | 0 | 0.15435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053791 | 0 | 0.053791 | 0.10056
VSP | 0 | 0 | 0 | 0 | 0 | 0.051792 | 0 | 0.10469 | 0 | 0.15648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051792 | 0 | 0.051792 | 0.10469
Solar Wall | 0 | 0 | 0 | 0 | 0 | 0.045107 | 0 | 0.097241 | 0 | 0.14235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045107 | 0 | 0.045107 | 0.097241
Solar DHW | 0 | 0 | 0 | 0 | 0 | 0.045953 | 0 | 0.096497 | 0 | 0.14245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045953 | 0 | 0.045953 | 0.096497
DB Economizer | 0 | 0 | 0 | 0 | 0 | 0.05186 | 0 | 0.10403 | 0 | 0.15589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05186 | 0 | 0.05186 | 0.10403
COP | 0 | 0 | 0 | 0 | 0 | 0.051792 | 0 | 0.10432 | 0 | 0.15611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.051792 | 0 | 0.051792 | 0.10432
Retro-commissioning | 0 | 0 | 0 | 0 | 0 | 0.047667 | 0 | 0.097227 | 0 | 0.14489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047667 | 0 | 0.047667 | 0.097227
5A-Gym and Fitness Centre (GWh)
| V1 |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 0 | 0 | 0 | 0 | 0 | 0.24886 | 0 | 0.15775 | 0 | 0.40661 | 0 | 0 | 0 | 0 | 0 | 0.6614 | 0.52912 | 0.48441 | 0 | 1.6749 | 0.91026 | 0.96203 | 1.8723 | 0.64216
Wall | 0 | 0 | 0 | 0 | 0 | 0.23246 | 0 | 0.15539 | 0 | 0.38785 | 0 | 0 | 0 | 0 | 0 | 0.62121 | 0.49697 | 0.47265 | 0 | 1.5908 | 0.85367 | 0.90358 | 1.7572 | 0.62804
Roof | 0 | 0 | 0 | 0 | 0 | 0.20158 | 0 | 0.14974 | 0 | 0.35132 | 0 | 0 | 0 | 0 | 0 | 0.46202 | 0.36961 | 0.41819 | 0 | 1.2498 | 0.6636 | 0.67203 | 1.3356 | 0.56793
Windows | 0 | 0 | 0 | 0 | 0 | 0.24585 | 0 | 0.1575 | 0 | 0.40335 | 0 | 0 | 0 | 0 | 0 | 0.65509 | 0.52407 | 0.48321 | 0 | 1.6624 | 0.90095 | 0.95286 | 1.8538 | 0.64071
Air tightness | 0 | 0 | 0 | 0 | 0 | 0.18795 | 0 | 0.15107 | 0 | 0.33902 | 0 | 0 | 0 | 0 | 0 | 0.40415 | 0.32332 | 0.42636 | 0 | 1.1538 | 0.59209 | 0.58785 | 1.1799 | 0.57743
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 0.19781 | 0 | 0.15642 | 0 | 0.35423 | 0 | 0 | 0 | 0 | 0 | 0.55249 | 0.44199 | 0.48055 | 0 | 1.475 | 0.7503 | 0.80362 | 1.5539 | 0.63696
T set back | 0 | 0 | 0 | 0 | 0 | 0.21299 | 0 | 0.1566 | 0 | 0.36959 | 0 | 0 | 0 | 0 | 0 | 0.57221 | 0.45777 | 0.48099 | 0 | 1.511 | 0.78521 | 0.83231 | 1.6175 | 0.63759
Lighting (30%) | 0 | 0 | 0 | 0 | 0 | 0.27292 | 0 | 0.12379 | 0 | 0.39671 | 0 | 0 | 0 | 0 | 0 | 0.69339 | 0.55471 | 0.42738 | 0 | 1.6755 | 0.96631 | 1.0086 | 1.9749 | 0.55117
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 0.24886 | 0 | 0.14657 | 0 | 0.39543 | 0 | 0 | 0 | 0 | 0 | 0.6614 | 0.52912 | 0.45685 | 0 | 1.6474 | 0.91026 | 0.96203 | 1.8723 | 0.60342
HRV | 0 | 0 | 0 | 0 | 0 | 0.22356 | 0 | 0.15797 | 0 | 0.38153 | 0 | 0 | 0 | 0 | 0 | 0.62909 | 0.50327 | 0.48463 | 0 | 1.617 | 0.85265 | 0.91503 | 1.7677 | 0.6426
DCV | 0 | 0 | 0 | 0 | 0 | 0.21433 | 0 | 0.15775 | 0 | 0.37208 | 0 | 0 | 0 | 0 | 0 | 0.56572 | 0.45258 | 0.48441 | 0 | 1.5027 | 0.78005 | 0.82287 | 1.6029 | 0.64216
Cold Deck Reset | 0 | 0 | 0 | 0 | 0 | 0.24886 | 0 | 0.15301 | 0 | 0.40188 | 0 | 0 | 0 | 0 | 0 | 0.6614 | 0.52912 | 0.46985 | 0 | 1.6604 | 0.91026 | 0.96203 | 1.8723 | 0.62287
VSD | 0 | 0 | 0 | 0 | 0 | 0.26874 | 0 | 0.13654 | 0 | 0.40528 | 0 | 0 | 0 | 0 | 0 | 0.61121 | 0.48897 | 0.37734 | 0 | 1.4775 | 0.87995 | 0.88903 | 1.769 | 0.51388
VSP | 0 | 0 | 0 | 0 | 0 | 0.24886 | 0 | 0.15314 | 0 | 0.402 | 0 | 0 | 0 | 0 | 0 | 0.6614 | 0.52912 | 0.47305 | 0 | 1.6636 | 0.91026 | 0.96203 | 1.8723 | 0.62619
Solar Wall | 0 | 0 | 0 | 0 | 0 | 0.23811 | 0 | 0.15879 | 0 | 0.39691 | 0 | 0 | 0 | 0 | 0 | 0.64816 | 0.51853 | 0.48698 | 0 | 1.6537 | 0.88627 | 0.94277 | 1.829 | 0.64578
Solar DHW | 0 | 0 | 0 | 0 | 0 | 0.24503 | 0 | 0.15784 | 0 | 0.40287 | 0 | 0 | 0 | 0 | 0 | 0.65668 | 0.52534 | 0.48463 | 0 | 1.6667 | 0.9017 | 0.95517 | 1.8569 | 0.64247
DB Economizer | 0 | 0 | 0 | 0 | 0 | 0.24886 | 0 | 0.15192 | 0 | 0.40078 | 0 | 0 | 0 | 0 | 0 | 0.6614 | 0.52912 | 0.46887 | 0 | 1.6594 | 0.91026 | 0.96203 | 1.8723 | 0.62079
COP | 0 | 0 | 0 | 0 | 0 | 0.24886 | 0 | 0.15611 | 0 | 0.40497 | 0 | 0 | 0 | 0 | 0 | 0.6614 | 0.52912 | 0.46839 | 0 | 1.6589 | 0.91026 | 0.96203 | 1.8723 | 0.6245
Retro-commissioning | 0 | 0 | 0 | 0 | 0 | 0.22471 | 0 | 0.15316 | 0 | 0.37787 | 0 | 0 | 0 | 0 | 0 | 0.59617 | 0.47693 | 0.4635 | 0 | 1.5366 | 0.82088 | 0.86715 | 1.688 | 0.61666
5C-Sports Centre (GWh)
| V1 |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 0 | 0 | 0 | 0 | 0 | 1.0512 | 0 | 0.27567 | 0 | 1.3269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0512 | 0 | 1.0512 | 0.27567
Wall | 0 | 0 | 0 | 0 | 0 | 1.0266 | 0 | 0.27463 | 0 | 1.3012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0266 | 0 | 1.0266 | 0.27463
Roof | 0 | 0 | 0 | 0 | 0 | 0.97639 | 0 | 0.27387 | 0 | 1.2503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97639 | 0 | 0.97639 | 0.27387
Windows | 0 | 0 | 0 | 0 | 0 | 1.0398 | 0 | 0.27545 | 0 | 1.3153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0398 | 0 | 1.0398 | 0.27545
Air tightness | 0 | 0 | 0 | 0 | 0 | 0.94186 | 0 | 0.27415 | 0 | 1.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94186 | 0 | 0.94186 | 0.27415
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 0.95358 | 0 | 0.27448 | 0 | 1.2281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95358 | 0 | 0.95358 | 0.27448
T set back | 0 | 0 | 0 | 0 | 0 | 0.99145 | 0 | 0.27527 | 0 | 1.2667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99145 | 0 | 0.99145 | 0.27527
Lighting (30%) | 0 | 0 | 0 | 0 | 0 | 1.0827 | 0 | 0.21753 | 0 | 1.3002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0827 | 0 | 1.0827 | 0.21753
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 1.0512 | 0 | 0.25115 | 0 | 1.3024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0512 | 0 | 1.0512 | 0.25115
HRV | 0 | 0 | 0 | 0 | 0 | 0.86487 | 0 | 0.27637 | 0 | 1.1412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86487 | 0 | 0.86487 | 0.27637
DCV | 0 | 0 | 0 | 0 | 0 | 0.639 | 0 | 0.27697 | 0 | 0.91598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.639 | 0 | 0.639 | 0.27697
Cold Deck Reset | 0 | 0 | 0 | 0 | 0 | 1.0512 | 0 | 0.26739 | 0 | 1.3186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0512 | 0 | 1.0512 | 0.26739
VSD | 0 | 0 | 0 | 0 | 0 | 1.0603 | 0 | 0.2594 | 0 | 1.3197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0603 | 0 | 1.0603 | 0.2594
VSP | 0 | 0 | 0 | 0 | 0 | 1.0512 | 0 | 0.27393 | 0 | 1.3252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0512 | 0 | 1.0512 | 0.27393
Solar Wall | 0 | 0 | 0 | 0 | 0 | 0.99382 | 0 | 0.28266 | 0 | 1.2765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99382 | 0 | 0.99382 | 0.28266
Solar DHW | 0 | 0 | 0 | 0 | 0 | 1.047 | 0 | 0.27576 | 0 | 1.3228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.047 | 0 | 1.047 | 0.27576
DB Economizer | 0 | 0 | 0 | 0 | 0 | 1.0512 | 0 | 0.27554 | 0 | 1.3268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0512 | 0 | 1.0512 | 0.27554
COP | 0 | 0 | 0 | 0 | 0 | 1.0512 | 0 | 0.27567 | 0 | 1.3269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0512 | 0 | 1.0512 | 0.27567
Retro-commissioning | 0 | 0 | 0 | 0 | 0 | 0.9495 | 0 | 0.27256 | 0 | 1.2221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9495 | 0 | 0.9495 | 0.27256
5D-Sports and Arena (GWh)
| V1 |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Windows | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air tightness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
T set back | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting (30%) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HRV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DCV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cold Deck Reset | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VSD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Wall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar DHW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DB Economizer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Retro-commissioning | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6A-Office Building (GWh)
| V1 |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 4.3424 | 0 | 1.1489 | 0 | 5.4914 | 0.12562 | 0 | 0.055425 | 0 | 0.18104 | 0 | 0 | 0 | 0 | 0 | 3.1042 | 8.022 | 2.8555 | 0 | 13.9817 | 7.5723 | 14.5855 | 22.1577 | 4.0598
Wall | 4.3407 | 0 | 1.1489 | 0 | 5.4896 | 0.12562 | 0 | 0.055424 | 0 | 0.18104 | 0 | 0 | 0 | 0 | 0 | 3.1043 | 8.0222 | 2.8555 | 0 | 13.982 | 7.5706 | 14.5858 | 22.1564 | 4.0598
Roof | 4.3437 | 0 | 1.1489 | 0 | 5.4926 | 0.12562 | 0 | 0.055425 | 0 | 0.18104 | 0 | 0 | 0 | 0 | 0 | 3.1042 | 8.022 | 2.8555 | 0 | 13.9817 | 7.5735 | 14.5855 | 22.159 | 4.0598
Windows | 4.3424 | 0 | 1.1489 | 0 | 5.4914 | 0.12562 | 0 | 0.055425 | 0 | 0.18104 | 0 | 0 | 0 | 0 | 0 | 3.1042 | 8.022 | 2.8555 | 0 | 13.9817 | 7.5723 | 14.5855 | 22.1577 | 4.0598
Air tightness | 4.3424 | 0 | 1.1489 | 0 | 5.4914 | 0.12066 | 0 | 0.054521 | 0 | 0.17518 | 0 | 0 | 0 | 0 | 0 | 2.7698 | 7.1578 | 2.8125 | 0 | 12.7401 | 7.2329 | 13.0141 | 20.247 | 4.016
T Reduction (2 DegC) | 4.3071 | 0 | 1.1489 | 0 | 5.456 | 0.122 | 0 | 0.054925 | 0 | 0.17693 | 0 | 0 | 0 | 0 | 0 | 3.0955 | 7.9996 | 2.8542 | 0 | 13.9492 | 7.5246 | 14.5446 | 22.0692 | 4.058
T set back | 4.3424 | 0 | 1.1489 | 0 | 5.4914 | 0.12562 | 0 | 0.055425 | 0 | 0.18104 | 0 | 0 | 0 | 0 | 0 | 3.1042 | 8.022 | 2.8555 | 0 | 13.9817 | 7.5723 | 14.5855 | 22.1577 | 4.0598
Lighting (30%) | 4.4259 | 0 | 1.0019 | 0 | 5.4278 | 0.12796 | 0 | 0.050966 | 0 | 0.17893 | 0 | 0 | 0 | 0 | 0 | 3.1635 | 8.1753 | 2.4462 | 0 | 13.7849 | 7.7174 | 14.8641 | 22.5815 | 3.499
Occupancy Sensors (Lights/Plug Loads) | 4.3424 | 0 | 1.1489 | 0 | 5.4914 | 0.12562 | 0 | 0.055425 | 0 | 0.18104 | 0 | 0 | 0 | 0 | 0 | 3.1042 | 8.022 | 2.8555 | 0 | 13.9817 | 7.5723 | 14.5855 | 22.1577 | 4.0598
HRV | 3.6768 | 0 | 1.0405 | 0 | 4.7172 | 0.090786 | 0 | 0.052835 | 0 | 0.14362 | 0 | 0 | 0 | 0 | 0 | 2.2497 | 5.8139 | 2.8558 | 0 | 10.9194 | 6.0173 | 10.5707 | 16.588 | 3.9491
DCV | 3.9082 | 0 | 1.1097 | 0 | 5.0179 | 0.11306 | 0 | 0.0535 | 0 | 0.16656 | 0 | 0 | 0 | 0 | 0 | 2.7916 | 7.214 | 2.8555 | 0 | 12.8611 | 6.8128 | 13.1164 | 19.9292 | 4.0187
Cold Deck Reset | 4.3424 | 0 | 1.0277 | 0 | 5.3701 | 0.12562 | 0 | 0.054337 | 0 | 0.17996 | 0 | 0 | 0 | 0 | 0 | 2.949 | 7.6209 | 2.7696 | 0 | 13.3395 | 7.4171 | 13.8562 | 21.2732 | 3.8516
VSD | 4.3424 | 0 | 1.1489 | 0 | 5.4914 | 0.1262 | 0 | 0.054585 | 0 | 0.18078 | 0 | 0 | 0 | 0 | 0 | 3.0035 | 7.7618 | 3.3422 | 0 | 14.1076 | 7.4722 | 14.1124 | 21.5846 | 4.5457
VSP | 4.3424 | 0 | 1.1489 | 0 | 5.4914 | 0.12644 | 0 | 0.054529 | 0 | 0.18097 | 0 | 0 | 0 | 0 | 0 | 3.1056 | 8.0256 | 2.8213 | 0 | 13.9525 | 7.5745 | 14.592 | 22.1665 | 4.0248
Solar Wall | 4.3424 | 0 | 1.1489 | 0 | 5.4914 | 0.12562 | 0 | 0.055425 | 0 | 0.18104 | 0 | 0 | 0 | 0 | 0 | 3.1042 | 8.022 | 2.8555 | 0 | 13.9817 | 7.5723 | 14.5855 | 22.1577 | 4.0598
Solar DHW | 4.3424 | 0 | 1.1028 | 0 | 5.4452 | 0.12562 | 0 | 0.054001 | 0 | 0.17962 | 0 | 0 | 0 | 0 | 0 | 3.1042 | 8.022 | 2.7357 | 0 | 13.862 | 7.5723 | 14.5855 | 22.1577 | 3.8925
DB Economizer | 4.3424 | 0 | 1.1489 | 0 | 5.4914 | 0.12562 | 0 | 0.055425 | 0 | 0.18104 | 0 | 0 | 0 | 0 | 0 | 3.1042 | 8.022 | 2.8555 | 0 | 13.9817 | 7.5723 | 14.5855 | 22.1577 | 4.0598
COP | 4.3424 | 0 | 1.1489 | 0 | 5.4914 | 0.12562 | 0 | 0.055425 | 0 | 0.18104 | 0 | 0 | 0 | 0 | 0 | 3.1042 | 8.022 | 2.8555 | 0 | 13.9817 | 7.5723 | 14.5855 | 22.1577 | 4.0598
Retro-commissioning | 4.3424 | 0 | 1.1489 | 0 | 5.4914 | 0.12562 | 0 | 0.055425 | 0 | 0.18104 | 0 | 0 | 0 | 0 | 0 | 3.1042 | 8.022 | 2.8555 | 0 | 13.9817 | 7.5723 | 14.5855 | 22.1577 | 4.0598
7A-Dining Hall (GWh)
| V1 |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1387 | 0 | 2.4653 | 0 | 7.604 | 5.1387 | 0 | 5.1387 | 2.4653
Wall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9996 | 0 | 2.4609 | 0 | 7.4605 | 4.9996 | 0 | 4.9996 | 2.4609
Roof | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6345 | 0 | 2.4065 | 0 | 6.041 | 3.6345 | 0 | 3.6345 | 2.4065
Windows | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1024 | 0 | 2.4649 | 0 | 7.5673 | 5.1024 | 0 | 5.1024 | 2.4649
Air tightness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5501 | 0 | 2.4476 | 0 | 5.9977 | 3.5501 | 0 | 3.5501 | 2.4476
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2623 | 0 | 2.4485 | 0 | 6.7108 | 4.2623 | 0 | 4.2623 | 2.4485
T set back | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1387 | 0 | 2.4653 | 0 | 7.604 | 5.1387 | 0 | 5.1387 | 2.4653
Lighting (30%) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4094 | 0 | 2.0804 | 0 | 7.4897 | 5.4094 | 0 | 5.4094 | 2.0804
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1387 | 0 | 2.3141 | 0 | 7.4528 | 5.1387 | 0 | 5.1387 | 2.3141
HRV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0838 | 0 | 2.4828 | 0 | 6.5666 | 4.0838 | 0 | 4.0838 | 2.4828
DCV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6924 | 0 | 2.4556 | 0 | 6.148 | 3.6924 | 0 | 3.6924 | 2.4556
Cold Deck Reset | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1387 | 0 | 2.3914 | 0 | 7.5301 | 5.1387 | 0 | 5.1387 | 2.3914
VSD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4795 | 0 | 2.0108 | 0 | 7.4904 | 5.4795 | 0 | 5.4795 | 2.0108
VSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1387 | 0 | 2.4653 | 0 | 7.604 | 5.1387 | 0 | 5.1387 | 2.4653
Solar Wall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0701 | 0 | 2.4948 | 0 | 7.5649 | 5.0701 | 0 | 5.0701 | 2.4948
Solar DHW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1387 | 0 | 2.3953 | 0 | 7.534 | 5.1387 | 0 | 5.1387 | 2.3953
DB Economizer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.156 | 0 | 2.4367 | 0 | 7.5927 | 5.156 | 0 | 5.156 | 2.4367
COP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1387 | 0 | 2.3896 | 0 | 7.5282 | 5.1387 | 0 | 5.1387 | 2.3896
Retro-commissioning | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6248 | 0 | 2.3845 | 0 | 7.0093 | 4.6248 | 0 | 4.6248 | 2.3845
9A-Workshop Building (GWh)
| V1 |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 2.8154 | 0 | 0.95033 | 0 | 3.7657 | 6.6651 | 0 | 2.144 | 0 | 8.8091 | 0 | 0 | 0 | 0 | 0 | 18.7464 | 8.5791 | 9.2848 | 0 | 36.6103 | 28.2269 | 15.5984 | 43.8253 | 12.3791
Wall | 2.7368 | 0 | 0.93664 | 0 | 3.6734 | 6.4715 | 0 | 2.0772 | 0 | 8.5487 | 0 | 0 | 0 | 0 | 0 | 17.987 | 8.2316 | 8.8934 | 0 | 35.112 | 27.1953 | 14.9665 | 42.1619 | 11.9072
Roof | 2.7634 | 0 | 0.93551 | 0 | 3.6989 | 6.4769 | 0 | 2.0801 | 0 | 8.557 | 0 | 0 | 0 | 0 | 0 | 16.1405 | 7.3865 | 7.9401 | 0 | 31.4671 | 25.3809 | 13.4301 | 38.811 | 10.9557
Windows | 2.8092 | 0 | 0.95018 | 0 | 3.7594 | 6.6328 | 0 | 2.1408 | 0 | 8.7735 | 0 | 0 | 0 | 0 | 0 | 18.669 | 8.5437 | 9.275 | 0 | 36.4877 | 28.111 | 15.534 | 43.645 | 12.3659
Air tightness | 2.8154 | 0 | 0.95033 | 0 | 3.7657 | 5.9745 | 0 | 1.9841 | 0 | 7.9587 | 0 | 0 | 0 | 0 | 0 | 14.3607 | 6.572 | 7.4103 | 0 | 28.343 | 23.1506 | 11.9491 | 35.0998 | 10.3448
T Reduction (2 DegC) | 2.4051 | 0 | 0.94582 | 0 | 3.3509 | 5.713 | 0 | 2.1306 | 0 | 7.8435 | 0 | 0 | 0 | 0 | 0 | 16.2217 | 7.4237 | 9.1683 | 0 | 32.8137 | 24.3398 | 13.4977 | 37.8375 | 12.2447
T set back | 2.4881 | 0 | 0.94476 | 0 | 3.4329 | 5.9074 | 0 | 2.1301 | 0 | 8.0375 | 0 | 0 | 0 | 0 | 0 | 16.7016 | 7.6433 | 9.1869 | 0 | 33.5318 | 25.0971 | 13.8969 | 38.994 | 12.2618
Lighting (30%) | 2.92 | 0 | 0.80079 | 0 | 3.7208 | 6.8504 | 0 | 1.8795 | 0 | 8.7299 | 0 | 0 | 0 | 0 | 0 | 19.0973 | 8.7397 | 8.5025 | 0.046594 | 36.3861 | 28.8677 | 15.8903 | 44.7581 | 11.1828
Occupancy Sensors (Lights/Plug Loads) | 2.8154 | 0 | 0.89038 | 0 | 3.7058 | 6.6651 | 0 | 2.0205 | 0 | 8.6856 | 0 | 0 | 0 | 0 | 0 | 18.7464 | 8.5791 | 8.913 | 0 | 36.2384 | 28.2269 | 15.5984 | 43.8253 | 11.8239
HRV | 2.7776 | 0 | 0.9492 | 0 | 3.7269 | 6.5466 | 0 | 2.1414 | 0 | 8.688 | 0 | 0 | 0 | 0 | 0 | 18.404 | 8.4224 | 9.2787 | 0 | 36.1052 | 27.7283 | 15.3135 | 43.0418 | 12.3693
DCV | 2.5339 | 0 | 0.95033 | 0 | 3.4842 | 5.9985 | 0 | 2.144 | 0 | 8.1426 | 0 | 0 | 0 | 0 | 0 | 16.8717 | 7.7212 | 9.2848 | 0 | 33.8777 | 25.4041 | 14.0385 | 39.4426 | 12.3791
Cold Deck Reset | 2.8154 | 0 | 0.92175 | 0 | 3.7372 | 6.6651 | 0 | 2.0796 | 0 | 8.7448 | 0 | 0 | 0 | 0 | 0 | 18.7464 | 8.5791 | 9.0062 | 0 | 36.3316 | 28.2269 | 15.5984 | 43.8253 | 12.0075
VSD | 3.0563 | 0 | 0.69339 | 0 | 3.7497 | 7.2921 | 0 | 1.4752 | 0 | 8.7673 | 0 | 0 | 0 | 0 | 0 | 19.947 | 9.1286 | 7.2714 | 0 | 36.347 | 30.2954 | 16.5974 | 46.8928 | 9.4401
VSP | 2.8154 | 0 | 0.95033 | 0 | 3.7657 | 6.6651 | 0 | 2.07 | 0 | 8.7352 | 0 | 0 | 0 | 0 | 0 | 18.7464 | 8.5791 | 9.0621 | 0 | 36.3875 | 28.2269 | 15.5984 | 43.8253 | 12.0824
Solar Wall | 2.683 | 0 | 0.96131 | 0 | 3.6443 | 6.3927 | 0 | 2.1666 | 0 | 8.5593 | 0 | 0 | 0 | 0 | 0 | 18.2247 | 8.3404 | 9.3528 | 0 | 35.9179 | 27.3005 | 15.1643 | 42.4648 | 12.4807
Solar DHW | 2.791 | 0 | 0.95108 | 0 | 3.7421 | 6.615 | 0 | 2.1456 | 0 | 8.7605 | 0 | 0 | 0 | 0 | 0 | 18.6503 | 8.5351 | 9.2894 | 0 | 36.4749 | 28.0564 | 15.5184 | 43.5748 | 12.3861
DB Economizer | 2.8197 | 0 | 0.94852 | 0 | 3.7682 | 6.6772 | 0 | 2.1403 | 0 | 8.8175 | 0 | 0 | 0 | 0 | 0 | 18.8006 | 8.6039 | 9.2708 | 0 | 36.6753 | 28.2975 | 15.6435 | 43.941 | 12.3596
COP | 2.8154 | 0 | 0.95033 | 0 | 3.7657 | 6.6651 | 0 | 2.1418 | 0 | 8.807 | 0 | 0 | 0 | 0 | 0 | 18.7464 | 8.5791 | 9.2517 | 0 | 36.5772 | 28.2269 | 15.5984 | 43.8253 | 12.3439
Retro-commissioning | 2.5381 | 0 | 0.9152 | 0 | 3.4533 | 6.0075 | 0 | 2.0529 | 0 | 8.0604 | 0 | 0 | 0 | 0 | 0 | 16.8886 | 7.7289 | 8.7271 | 0 | 33.3446 | 25.4342 | 14.0526 | 39.4867 | 11.6951
11B-Retail Building (GWh)
| V1 |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0.056655 | 0 | 0.24666 | 0 | 0.34546 | 0.34546 | 0.056655
Wall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1807 | 0.055893 | 0 | 0.2366 | 0 | 0.32855 | 0.32855 | 0.055893
Roof | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15382 | 0.05593 | 0 | 0.20975 | 0 | 0.27967 | 0.27967 | 0.05593
Windows | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18574 | 0.056477 | 0 | 0.24222 | 0 | 0.33771 | 0.33771 | 0.056477
Air tightness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13095 | 0.056002 | 0 | 0.18695 | 0 | 0.23809 | 0.23809 | 0.056002
T Reduction (2 DegC) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16809 | 0.056533 | 0 | 0.22462 | 0 | 0.30562 | 0.30562 | 0.056533
T set back | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16415 | 0.054975 | 0 | 0.21913 | 0 | 0.29846 | 0.29846 | 0.054975
Lighting (30%) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19508 | 0.047953 | 0 | 0.24303 | 0 | 0.35469 | 0.35469 | 0.047953
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0.053451 | 0 | 0.24346 | 0 | 0.34546 | 0.34546 | 0.053451
HRV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16253 | 0.056963 | 0 | 0.2195 | 0 | 0.29551 | 0.29551 | 0.056963
DCV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14123 | 0.056796 | 0 | 0.19803 | 0 | 0.25678 | 0.25678 | 0.056796
Cold Deck Reset | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0.054953 | 0 | 0.24496 | 0 | 0.34546 | 0.34546 | 0.054953
VSD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20483 | 0.038857 | 0 | 0.24369 | 0 | 0.37242 | 0.37242 | 0.038857
VSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0.056655 | 0 | 0.24666 | 0 | 0.34546 | 0.34546 | 0.056655
Solar Wall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18673 | 0.057334 | 0 | 0.24407 | 0 | 0.33951 | 0.33951 | 0.057334
Solar DHW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18723 | 0.056748 | 0 | 0.24398 | 0 | 0.34042 | 0.34042 | 0.056748
DB Economizer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19017 | 0.05601 | 0 | 0.24618 | 0 | 0.34577 | 0.34577 | 0.05601
COP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0.054888 | 0 | 0.24489 | 0 | 0.34546 | 0.34546 | 0.054888
Retro-commissioning | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.171 | 0.054595 | 0 | 0.2256 | 0 | 0.31091 | 0.31091 | 0.054595
13B-Firehall (GWh)
| V1 |  |  |  |  | V2 |  |  |  |  | V3 |  |  |  |  | V4 |  |  |  |  | Base Wide
ECM | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Natural Gas | DES | Electricity | Unheated | Total | Bldg Natural Gas | DES Fuel | Total Fuel | Electricity
Base case | 0.60231 | 0 | 0.42307 | 0 | 1.0254 | 0 | 0 | 0 | 0 | 0 | 0.64788 | 0 | 0.21132 | 0 | 0.85921 | 0 | 0 | 0 | 0 | 0 | 1.2502 | 0 | 1.2502 | 0.63439
Wall | 0.58208 | 0 | 0.42151 | 0 | 1.0036 | 0 | 0 | 0 | 0 | 0 | 0.63113 | 0 | 0.20977 | 0 | 0.8409 | 0 | 0 | 0 | 0 | 0 | 1.2132 | 0 | 1.2132 | 0.63128
Roof | 0.56943 | 0 | 0.42034 | 0 | 0.98977 | 0 | 0 | 0 | 0 | 0 | 0.53297 | 0 | 0.20017 | 0 | 0.73314 | 0 | 0 | 0 | 0 | 0 | 1.1024 | 0 | 1.1024 | 0.62052
Windows | 0.60004 | 0 | 0.42291 | 0 | 1.0229 | 0 | 0 | 0 | 0 | 0 | 0.64488 | 0 | 0.21109 | 0 | 0.85597 | 0 | 0 | 0 | 0 | 0 | 1.2449 | 0 | 1.2449 | 0.63401
Air tightness | 0.60231 | 0 | 0.42307 | 0 | 1.0254 | 0 | 0 | 0 | 0 | 0 | 0.3872 | 0 | 0.19504 | 0 | 0.58224 | 0 | 0 | 0 | 0 | 0 | 0.98952 | 0 | 0.98952 | 0.61811
T Reduction (2 DegC) | 0.47924 | 0 | 0.42066 | 0 | 0.8999 | 0 | 0 | 0 | 0 | 0 | 0.5444 | 0 | 0.20918 | 0 | 0.75358 | 0 | 0 | 0 | 0 | 0 | 1.0236 | 0 | 1.0236 | 0.62984
T set back | 0.55346 | 0 | 0.42159 | 0 | 0.97505 | 0 | 0 | 0 | 0 | 0 | 0.60229 | 0 | 0.21012 | 0 | 0.81241 | 0 | 0 | 0 | 0 | 0 | 1.1557 | 0 | 1.1557 | 0.63171
Lighting (30%) | 0.65811 | 0 | 0.34718 | 0 | 1.0053 | 0 | 0 | 0 | 0 | 0 | 0.67452 | 0 | 0.17885 | 0 | 0.85337 | 0 | 0 | 0 | 0 | 0 | 1.3326 | 0 | 1.3326 | 0.52603
Occupancy Sensors (Lights/Plug Loads) | 0.60231 | 0 | 0.38571 | 0 | 0.98802 | 0 | 0 | 0 | 0 | 0 | 0.64788 | 0 | 0.19514 | 0 | 0.84302 | 0 | 0 | 0 | 0 | 0 | 1.2502 | 0 | 1.2502 | 0.58085
HRV | 0.47516 | 0 | 0.4271 | 0 | 0.90225 | 0 | 0 | 0 | 0 | 0 | 0.59096 | 0 | 0.21221 | 0 | 0.80316 | 0 | 0 | 0 | 0 | 0 | 1.0661 | 0 | 1.0661 | 0.6393
DCV | 0.48183 | 0 | 0.42307 | 0 | 0.9049 | 0 | 0 | 0 | 0 | 0 | 0.51831 | 0 | 0.21132 | 0 | 0.72963 | 0 | 0 | 0 | 0 | 0 | 1.0001 | 0 | 1.0001 | 0.63439
Cold Deck Reset | 0.60231 | 0 | 0.41036 | 0 | 1.0127 | 0 | 0 | 0 | 0 | 0 | 0.64788 | 0 | 0.20493 | 0 | 0.85282 | 0 | 0 | 0 | 0 | 0 | 1.2502 | 0 | 1.2502 | 0.6153
VSD | 0.623 | 0 | 0.401 | 0 | 1.024 | 0 | 0 | 0 | 0 | 0 | 0.67088 | 0 | 0.18679 | 0 | 0.85767 | 0 | 0 | 0 | 0 | 0 | 1.2939 | 0 | 1.2939 | 0.5878
VSP | 0.60231 | 0 | 0.40737 | 0 | 1.0097 | 0 | 0 | 0 | 0 | 0 | 0.64788 | 0 | 0.20452 | 0 | 0.8524 | 0 | 0 | 0 | 0 | 0 | 1.2502 | 0 | 1.2502 | 0.61189
Solar Wall | 0.55425 | 0 | 0.43631 | 0 | 0.99056 | 0 | 0 | 0 | 0 | 0 | 0.62706 | 0 | 0.21706 | 0 | 0.84412 | 0 | 0 | 0 | 0 | 0 | 1.1813 | 0 | 1.1813 | 0.65337
Solar DHW | 0.58298 | 0 | 0.42352 | 0 | 1.0065 | 0 | 0 | 0 | 0 | 0 | 0.63951 | 0 | 0.21152 | 0 | 0.85103 | 0 | 0 | 0 | 0 | 0 | 1.2225 | 0 | 1.2225 | 0.63504
DB Economizer | 0.60231 | 0 | 0.41915 | 0 | 1.0215 | 0 | 0 | 0 | 0 | 0 | 0.64789 | 0 | 0.20863 | 0 | 0.85652 | 0 | 0 | 0 | 0 | 0 | 1.2502 | 0 | 1.2502 | 0.62778
COP | 0.60231 | 0 | 0.42307 | 0 | 1.0254 | 0 | 0 | 0 | 0 | 0 | 0.64788 | 0 | 0.20951 | 0 | 0.85739 | 0 | 0 | 0 | 0 | 0 | 1.2502 | 0 | 1.2502 | 0.63258
Retro-commissioning | 0.54626 | 0 | 0.41809 | 0 | 0.96435 | 0 | 0 | 0 | 0 | 0 | 0.58491 | 0 | 0.20637 | 0 | 0.79128 | 0 | 0 | 0 | 0 | 0 | 1.1312 | 0 | 1.1312 | 0.62446

## ECMSuccessScores
ECM | Criteria | Min. Score | Max. Score | Score
Wall | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 5
| Customer Acceptance | 0 | 5 | 5
| Total score |  |  | 5
| Risk is too high flag |  |  | 1
Roof | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 5
| Customer Acceptance | 0 | 5 | 5
| Total score |  |  | 5
| Risk is too high flag |  |  | 1
Window | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 5
| Customer Acceptance | 0 | 5 | 5
| Total score |  |  | 5
| Risk is too high flag |  |  | 1
Air Tightness | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 3
| Implementation Difficulty / Risk | 0 | 5 | 4
| Customer Acceptance | 0 | 5 | 4
| Total score |  |  | 4
| Risk is too high flag |  |  | 1
T Reduction | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 5
| Customer Acceptance | 0 | 5 | 2.5
| Total score |  |  | 4.375
| Risk is too high flag |  |  | 1
T set back | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 5
| Customer Acceptance | 0 | 5 | 4
| Total score |  |  | 4.75
| Risk is too high flag |  |  | 1
Lighting | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 4
| Customer Acceptance | 0 | 5 | 5
| Total score |  |  | 4.75
| Risk is too high flag |  |  | 1
Occupancy Sensors (Lights/Plug Loads) | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 5
| Customer Acceptance | 0 | 5 | 5
| Total score |  |  | 5
| Risk is too high flag |  |  | 1
HRV | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 5
| Customer Acceptance | 0 | 5 | 4
| Total score |  |  | 4.75
| Risk is too high flag |  |  | 1
DCV | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 2.5
| Customer Acceptance | 0 | 5 | 5
| Total score |  |  | 4.375
| Risk is too high flag |  |  | 1
Cold Deck Reset | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 5
| Customer Acceptance | 0 | 5 | 5
| Total score |  |  | 5
| Risk is too high flag |  |  | 1
VSD | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 5
| Customer Acceptance | 0 | 5 | 5
| Total score |  |  | 5
| Risk is too high flag |  |  | 1
VSP | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 5
| Customer Acceptance | 0 | 5 | 5
| Total score |  |  | 5
| Risk is too high flag |  |  | 1
Solar Wall | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 4
| Implementation Difficulty / Risk | 0 | 5 | 4
| Customer Acceptance | 0 | 5 | 5
| Total score |  |  | 4.5
| Risk is too high flag |  |  | 1
Solar DHW | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 5
| Customer Acceptance | 0 | 5 | 5
| Total score |  |  | 5
| Risk is too high flag |  |  | 1
DB Economizer | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 5
| Customer Acceptance | 0 | 5 | 5
| Total score |  |  | 5
| Risk is too high flag |  |  | 1
COP | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 5
| Customer Acceptance | 0 | 5 | 5
| Total score |  |  | 5
| Risk is too high flag |  |  | 1
Retro-commissioning | Supply chain strength | 0 | 5 | 5
| Knowledge base | 0 | 5 | 5
| Implementation Difficulty / Risk | 0 | 5 | 5
| Customer Acceptance | 0 | 5 | 5
| Total score |  |  | 5
| Risk is too high flag |  |  | 1

## BaseECMScores
Tables listing scores assigned to various base wide ECM for energy reduction, GHG reduction, cost, and probability of success
All vintages across the base (V1+V2+V3+V4)
ECM | Fuel Reduction | Electricity Reduction | Total Energy Reduction | GHG Reduction | Payback Years | Energy Reduction Rank | Energy Reduction Score | GHG Reduction Rank | GHG Reduction Score | Payback Rank | Payback Score | Possibility of Success Score | Total Score
| % | % | % | % | [8 empty] | %
Base case | 0 | 0 | 0 | 0
Air tightness | 16.5181 | 7.7253 | 14.4703 | 15.1611 | 14.9375 | 1 | 5 | 1 | 5 | 8 | 2.0588 | 4 | 88.1765
DCV | 11.2628 | 0.88628 | 8.8462 | 9.6614 | 7.5314 | 3 | 4.4118 | 3 | 4.4118 | 10 | 2.6471 | 4.375 | 82.8309
Roof | 10.8773 | 6.2634 | 9.8028 | 10.1653 | 78.3701 | 2 | 4.7059 | 2 | 4.7059 | 3 | 0.58824 | 5 | 82.6471
T reduction (2 DegC) | 10.7338 | 1.6981 | 8.6294 | 9.3393 | 4.1987 | 4 | 4.1176 | 4 | 4.1176 | 14 | 3.8235 | 4.375 | 82.2426
Retro-commissioning | 7.8771 | 5.2139 | 7.2568 | 7.4661 | 3.7661 | 6 | 3.5294 | 6 | 3.5294 | 15 | 4.1176 | 5 | 76.7647
HRV | 10.4224 | 0.76018 | 8.1721 | 8.9312 | 71.0506 | 5 | 3.8235 | 5 | 3.8235 | 4 | 0.88235 | 4.75 | 70.4265
T set back | 2.0666 | 1.5892 | 1.9554 | 1.9929 | 5.4893 | 8 | 2.9412 | 8 | 2.9412 | 13 | 3.5294 | 4.75 | 66.0147
VSP | -0.28853 | 9.0625 | 1.8893 | 1.1546 | 2.1889 | 9 | 2.6471 | 11 | 2.0588 | 17 | 4.7059 | 5 | 62.0588
Wall | 3.1188 | 2.4841 | 2.971 | 3.0209 | 299.6576 | 7 | 3.2353 | 7 | 3.2353 | 2 | 0.29412 | 5 | 61.1765
Cold Deck Reset | 0.86613 | 3.0824 | 1.3823 | 1.2082 | 7.0485 | 11 | 2.0588 | 10 | 2.3529 | 11 | 2.9412 | 5 | 54.7059
Solar Wall | 2.1757 | -0.75271 | 1.4937 | 1.7238 | 52.9837 | 10 | 2.3529 | 9 | 2.6471 | 6 | 1.4706 | 4.5 | 52.9118
Occupancy Sensors (Lights/Plug Loads) | 0 | 5.6789 | 1.3226 | 0.87642 | 3.1037 | 12 | 1.7647 | 13 | 1.4706 | 16 | 4.4118 | 5 | 50.8824
Solar DHW | 0.88228 | 1.4032 | 1.0036 | 0.96268 | 64.5562 | 13 | 1.4706 | 12 | 1.7647 | 5 | 1.1765 | 5 | 41.1765
DB Economizer | -0.084602 | 1.5527 | 0.29673 | 0.16809 | 6.3954 | 16 | 0.58824 | 16 | 0.58824 | 12 | 3.2353 | 5 | 32.9412
VSD | -3.2834 | 12.0796 | 0.29457 | -0.91244 | 0.83511 | 17 | 0.29412 | 18 | 0 | 18 | 5 | 5 | 32.0588
Lighting (30%) | -2.6379 | 12.1839 | 0.81405 | -0.35045 | 18.4532 | 14 | 1.1765 | 17 | 0.29412 | 7 | 1.7647 | 4.75 | 29.8382
Windows | 0.64041 | 0.9539 | 0.71342 | 0.68879 | 427.6644 | 15 | 0.88235 | 14 | 1.1765 | 1 | 0 | 5 | 29.4118
COP | 0.019429 | 1.1062 | 0.27253 | 0.18715 | 9.7859 | 18 | 0 | 15 | 0.88235 | 9 | 2.3529 | 5 | 28.2353
Minimum | [5 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 18 |  | 18 |  | 18
Vintage 1 buildings across the base
ECM | Fuel Reduction | Electricity Reduction | Total Energy Reduction | GHG Reduction | Payback Years | Energy Reduction Rank | Energy Reduction Score | GHG Reduction Rank | GHG Reduction Score | Payback Rank | Payback Score | Possibility of Success Score | Total Score
| % | % | % | %
Base case | 0 | 0 | 0 | 0
HRV | 21.8333 | 2.9003 | 15.8427 | 17.7122 | 51.8226 | 1 | 5 | 1 | 5 | 8 | 2.0588 | 4.75 | 90.4265
DCV | 18.1165 | 2.6635 | 13.227 | 14.7529 | 6.5101 | 2 | 4.6875 | 2 | 4.7059 | 13 | 3.5294 | 4.375 | 89.4669
T reduction (2 DegC) | 10.9215 | 2.0689 | 8.1204 | 8.9946 | 5.6591 | 3 | 4.375 | 3 | 4.4118 | 15 | 4.1176 | 4.375 | 86.9853
Retro-commissioning | 6.7392 | 5.3466 | 6.2986 | 6.4361 | 5.8882 | 4 | 4.0625 | 5 | 3.8235 | 14 | 3.8235 | 5 | 81.6728
T set back | 8.1961 | 2.162 | 6.2869 | 6.8827 | 7.0961 | 5 | 3.75 | 4 | 4.1176 | 12 | 3.2353 | 4.75 | 79.0294
VSP | 0 | 14.778 | 4.6759 | 3.2167 | 1.6881 | 6 | 3.4375 | 6 | 3.5294 | 18 | 5 | 5 | 78.7684
Occupancy Sensors (Lights/Plug Loads) | 0 | 7.0629 | 2.2348 | 1.5374 | 2.5061 | 8 | 2.8125 | 11 | 2.0588 | 17 | 4.7059 | 5 | 63.2169
Roof | 3.0683 | 2.2071 | 2.7958 | 2.8809 | 10000 | 7 | 3.125 | 7 | 3.2353 | 1 | 0 | 5 | 59.5221
Solar Wall | 3.4144 | -0.682 | 2.1183 | 2.5228 | 84.234 | 9 | 2.5 | 8 | 2.9412 | 6 | 1.4706 | 4.5 | 56
Cold Deck Reset | 0.71214 | 4.6777 | 1.9669 | 1.5753 | 8.5485 | 11 | 1.875 | 10 | 2.3529 | 11 | 2.9412 | 5 | 53.4191
Wall | 2.059 | 2.1129 | 2.0761 | 2.0707 | 10000 | 10 | 2.1875 | 9 | 2.6471 | 1 | 0 | 5 | 48.8419
Solar DHW | 1.3003 | 0.6422 | 1.0921 | 1.1571 | 76.4904 | 14 | 0.9375 | 12 | 1.7647 | 7 | 1.7647 | 5 | 39.2096
Windows | 0.8029 | 1.8804 | 1.1438 | 1.0374 | 358.0889 | 13 | 1.25 | 13 | 1.4706 | 5 | 1.1765 | 5 | 37.5735
DB Economizer | -0.01766 | 1.9478 | 0.60422 | 0.41015 | 8.9086 | 15 | 0.625 | 14 | 1.1765 | 10 | 2.6471 | 5 | 35.5515
Lighting (30%) | -4.4679 | 13.7922 | 1.3098 | -0.4933 | 18.4039 | 12 | 1.5625 | 17 | 0.29412 | 9 | 2.3529 | 4.75 | 34.3051
VSD | -3.0584 | 7.0569 | 0.14215 | -0.85669 | 2.8744 | 16 | 0.3125 | 18 | 0 | 16 | 4.4118 | 5 | 30.4228
COP | 0 | 0 | 0 | 0 | 10000 | 17 | 0 | 15 | 0.88235 | 1 | 0 | 5 | 21.1765
Air tightness | 0 | 0 | 0 | 0 | 10000 | 17 | 0 | 15 | 0.88235 | 1 | 0 | 4 | 18.1765
Minimum | [5 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 17 |  | 18 |  | 18
Vintage 2 buildings across the base
ECM | Fuel Reduction | Electricity Reduction | Total Energy Reduction | GHG Reduction | Payback Years | Energy Reduction Rank | Energy Reduction Score | GHG Reduction Rank | GHG Reduction Score | Payback Rank | Payback Score | Possibility of Success Score | Total Score
| % | % | % | %
Base case | 0 | 0 | 0 | 0
T reduction (2 DegC) | 15.2384 | 2.633 | 12.0743 | 13.1249 | 4.2497 | 1 | 5 | 1 | 5 | 16 | 4.4118 | 4.375 | 96.3603
T set back | 12.0844 | 2.7354 | 9.7378 | 10.5169 | 5.1224 | 3 | 4.4118 | 3 | 4.4118 | 14 | 3.8235 | 4.75 | 87.4853
Air tightness | 12.9681 | 7.2725 | 11.5385 | 12.0131 | 32.4275 | 2 | 4.7059 | 2 | 4.7059 | 7 | 1.7647 | 4 | 83.1765
Retro-commissioning | 9.1163 | 3.9342 | 7.8156 | 8.2475 | 6.3769 | 5 | 3.8235 | 5 | 3.8235 | 13 | 3.5294 | 5 | 79.1176
DCV | 11.5304 | -1.4666 | 8.2681 | 9.3513 | 16.1841 | 4 | 4.1176 | 4 | 4.1176 | 9 | 2.3529 | 4.375 | 77.8309
Roof | 5.2903 | 3.3086 | 4.7929 | 4.958 | 312.5822 | 6 | 3.5294 | 6 | 3.5294 | 4 | 0.88235 | 5 | 67.0588
HRV | 5.0506 | -1.9614 | 3.2906 | 3.875 | 802.3829 | 7 | 3.2353 | 7 | 3.2353 | 1 | 0 | 4.75 | 59.5441
Wall | 3.1913 | 2.3877 | 2.9896 | 3.0565 | 467.5645 | 8 | 2.9412 | 8 | 2.9412 | 2 | 0.29412 | 5 | 57.0588
Solar DHW | 3.2886 | 0.60044 | 2.6139 | 2.8379 | 140.5965 | 9 | 2.6471 | 10 | 2.3529 | 6 | 1.4706 | 5 | 54.4118
Occupancy Sensors (Lights/Plug Loads) | 0 | 5.6815 | 1.4261 | 0.95259 | 4.6047 | 11 | 2.0588 | 12 | 1.7647 | 15 | 4.1176 | 5 | 54.1176
Solar Wall | 3.8852 | -1.8414 | 2.4478 | 2.9251 | 252.6155 | 10 | 2.3529 | 9 | 2.6471 | 5 | 1.1765 | 4.5 | 52.0294
DB Economizer | -0.11342 | 4.2234 | 0.97515 | 0.61371 | 2.9944 | 13 | 1.4706 | 13 | 1.4706 | 17 | 4.7059 | 5 | 49.7059
Windows | 1.0831 | 0.50096 | 0.93698 | 0.98549 | 428.5462 | 14 | 1.1765 | 11 | 2.0588 | 3 | 0.58824 | 5 | 39.4118
VSP | -0.0064366 | 3.6134 | 0.90217 | 0.60049 | 7.168 | 15 | 0.88235 | 14 | 1.1765 | 12 | 3.2353 | 5 | 39.1176
Lighting (30%) | -3.0707 | 13.4535 | 1.0769 | -0.30019 | 18.0738 | 12 | 1.7647 | 17 | 0.29412 | 8 | 2.0588 | 4.75 | 34.8382
Cold Deck Reset | 0 | 2.7737 | 0.69621 | 0.46505 | 11.5887 | 16 | 0.58824 | 15 | 0.88235 | 11 | 2.9412 | 5 | 34.1176
VSD | -6.6674 | 21.5338 | 0.41121 | -1.9391 | 0.59892 | 17 | 0.29412 | 18 | 0 | 18 | 5 | 5 | 32.0588
COP | 0.00020738 | 1.0588 | 0.26593 | 0.1777 | 15.7325 | 18 | 0 | 16 | 0.58824 | 10 | 2.6471 | 5 | 27.0588
Minimum | [5 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 18 |  | 18 |  | 18
Vintage 3 buildings across the base
ECM | Fuel Reduction | Electricity Reduction | Total Energy Reduction | GHG Reduction | Payback Years | Energy Reduction Rank | Energy Reduction Score | GHG Reduction Rank | GHG Reduction Score | Payback Rank | Payback Score | Possibility of Success Score | Total Score
| % | % | % | %
Base case | 0 | 0 | 0 | 0
Retro-commissioning | 9.8397 | 8.2187 | 9.3288 | 9.4884 | 2.1846 | 2 | 4.7059 | 2 | 4.7059 | 15 | 4.1176 | 5 | 93.2353
Roof | 15.0031 | 3.2974 | 11.3136 | 12.4664 | 144.438 | 1 | 5 | 1 | 5 | 3 | 0.58824 | 5 | 86.7647
T reduction (2 DegC) | 9.3842 | 2.5474 | 7.2293 | 7.9026 | 4.3664 | 4 | 4.1176 | 4 | 4.1176 | 12 | 3.2353 | 4.375 | 80.4779
VSP | -2.751 | 25.6448 | 6.1991 | 3.4025 | 0.67654 | 5 | 3.8235 | 7 | 3.2353 | 18 | 5 | 5 | 79.4118
Air tightness | 10.6718 | 3.0885 | 8.2816 | 9.0284 | 32.1128 | 3 | 4.4118 | 3 | 4.4118 | 7 | 1.7647 | 4 | 79.0588
T set back | 5.1812 | 2.4547 | 4.3218 | 4.5903 | 6.1283 | 6 | 3.5294 | 5 | 3.8235 | 11 | 2.9412 | 4.75 | 74.5441
Occupancy Sensors (Lights/Plug Loads) | 0 | 8.9583 | 2.8236 | 1.9413 | 1.782 | 8 | 2.9412 | 10 | 2.3529 | 16 | 4.4118 | 5 | 65.2941
Wall | 4.042 | 2.3748 | 3.5165 | 3.6807 | 406.2305 | 7 | 3.2353 | 6 | 3.5294 | 1 | 0 | 5 | 62.3529
DCV | 2.5891 | 2.1882 | 2.4627 | 2.5022 | 11.8099 | 9 | 2.6471 | 8 | 2.9412 | 9 | 2.3529 | 4.375 | 59.3015
HRV | 2.0971 | 2.1422 | 2.1113 | 2.1068 | 132.1392 | 10 | 2.3529 | 9 | 2.6471 | 4 | 0.88235 | 4.75 | 51.8971
Solar Wall | 2.3693 | -0.44262 | 1.483 | 1.76 | 79.338 | 12 | 1.7647 | 11 | 2.0588 | 5 | 1.1765 | 4.5 | 43.7941
Windows | 1.028 | 2.1764 | 1.39 | 1.2769 | 259.089 | 13 | 1.4706 | 12 | 1.7647 | 2 | 0.29412 | 5 | 38.5294
Solar DHW | 0.99386 | 2.086 | 1.3381 | 1.2305 | 54.5789 | 14 | 1.1765 | 13 | 1.4706 | 6 | 1.4706 | 5 | 37.9412
COP | 0.19005 | 2.3112 | 0.85862 | 0.64972 | 3.6841 | 16 | 0.58824 | 14 | 1.1765 | 13 | 3.5294 | 5 | 37.9412
VSD | -0.79915 | 4.6157 | 0.90754 | 0.37426 | 1.4307 | 15 | 0.88235 | 17 | 0.29412 | 17 | 4.7059 | 5 | 37.3529
Lighting (30%) | -2.8175 | 11.3543 | 1.6493 | 0.25359 | 14.2568 | 11 | 2.0588 | 18 | 0 | 8 | 2.0588 | 4.75 | 34.8382
DB Economizer | 0.1993 | 2.2275 | 0.83856 | 0.63882 | 3.0447 | 17 | 0.29412 | 15 | 0.88235 | 14 | 3.8235 | 5 | 34.7059
Cold Deck Reset | 0 | 2.3498 | 0.74063 | 0.50921 | 7.493 | 18 | 0 | 16 | 0.58824 | 10 | 2.6471 | 5 | 27.0588
Minimum | [5 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 18 |  | 18 |  | 18
Vintage 4 buildings across the base
ECM | Fuel Reduction | Electricity Reduction | Total Energy Reduction | GHG Reduction | Payback Years | Energy Reduction Rank | Energy Reduction Score | GHG Reduction Rank | GHG Reduction Score | Payback Rank | Payback Score | Possibility of Success Score | Total Score
| % | % | % | %
Base case | 0 | 0 | 0 | 0
Air tightness | 21.1276 | 11.9475 | 19.3259 | 19.9526 | 11.2404 | 1 | 5 | 1 | 5 | 9 | 2.3529 | 4 | 89.0588
DCV | 11.2539 | 0.39604 | 9.1229 | 9.8642 | 6.18 | 3 | 4.4118 | 3 | 4.4118 | 11 | 2.9412 | 4.375 | 83.7132
Roof | 12.6335 | 9.2418 | 11.9679 | 12.1994 | 61.3099 | 2 | 4.7059 | 2 | 4.7059 | 4 | 0.88235 | 5 | 83.5294
T reduction (2 DegC) | 10.172 | 1.1096 | 8.3934 | 9.0121 | 3.686 | 5 | 3.8235 | 5 | 3.8235 | 16 | 4.4118 | 4.375 | 79.8897
Retro-commissioning | 7.5891 | 4.5811 | 6.9987 | 7.2041 | 3.171 | 6 | 3.5294 | 6 | 3.5294 | 17 | 4.7059 | 5 | 78.5294
HRV | 10.4143 | 0.19871 | 8.4094 | 9.1068 | 55.6231 | 4 | 4.1176 | 4 | 4.1176 | 5 | 1.1765 | 4.75 | 75.4265
T set back | 7.7629 | 0.87609 | 6.4113 | 6.8814 | 4.9352 | 7 | 3.2353 | 7 | 3.2353 | 13 | 3.5294 | 4.75 | 70.1324
Cold Deck Reset | 1.1696 | 2.7905 | 1.4877 | 1.3771 | 5.373 | 9 | 2.6471 | 9 | 2.6471 | 12 | 3.2353 | 5 | 61.7647
Wall | 3.166 | 2.6707 | 3.0688 | 3.1026 | 315.7596 | 8 | 2.9412 | 8 | 2.9412 | 2 | 0.29412 | 5 | 57.0588
Occupancy Sensors (Lights/Plug Loads) | 0 | 4.23 | 0.83017 | 0.54139 | 3.9043 | 11 | 2.0588 | 12 | 1.7647 | 15 | 4.1176 | 5 | 54.1176
Solar Wall | 1.6326 | -0.62465 | 1.1896 | 1.3437 | 73.1036 | 10 | 2.3529 | 10 | 2.3529 | 3 | 0.58824 | 4.5 | 48.2059
VSP | -0.010433 | 3.4187 | 0.66256 | 0.42846 | 4.9312 | 12 | 1.7647 | 14 | 1.1765 | 14 | 3.8235 | 5 | 47.0588
Solar DHW | 0.39388 | 1.6583 | 0.64203 | 0.55571 | 44.7111 | 13 | 1.4706 | 11 | 2.0588 | 6 | 1.4706 | 5 | 44.1176
COP | 0 | 1.1649 | 0.22863 | 0.1491 | 6.7677 | 16 | 0.58824 | 15 | 0.88235 | 10 | 2.6471 | 5 | 33.2353
VSD | -3.157 | 13.9353 | 0.19751 | -0.96936 | 0.48888 | 17 | 0.29412 | 18 | 0 | 18 | 5 | 5 | 32.0588
Windows | 0.47787 | 0.36774 | 0.45626 | 0.46377 | 695.0666 | 15 | 0.88235 | 13 | 1.4706 | 1 | 0 | 5 | 31.4706
Lighting (30%) | -2.1928 | 11.5626 | 0.5068 | -0.43226 | 19.806 | 14 | 1.1765 | 17 | 0.29412 | 7 | 1.7647 | 4.75 | 29.8382
DB Economizer | -0.13627 | 0.61809 | 0.011779 | -0.03972 | 13.4093 | 18 | 0 | 16 | 0.58824 | 8 | 2.0588 | 5 | 25.2941
Minimum | [5 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 18 |  | 18 |  | 18

## BldgECMScores
Energy and GHG Savings Scale
| Low | < 0%
| Med | ≥ 0 and < 5%
| High | ≥ 5 and < 10%
| Very High | ≥ 10%
| 1A:Hanger | [12 empty] | 1A:Hanger | [12 empty] | 1A:Hanger | [12 empty] | 1A:Hanger
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity Reduction (%) | Energy Reduction (%) | GHG Reduction (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0
Wall | 3.146 | 4.4039 | 3.7103 | 3.5591 | 10000 | 11 | 1.6667 | 9 | 2.3333 | 1 | 0 | 5 | 43 | 5.0166 | 2.7874 | 3.9441 | 4.2188 | 407.7729 | 10 | 2.3529 | 9 | 2.6471 | 1 | 0 | 5 | 50 | 4.8662 | 2.7515 | 4.0983 | 4.3264 | 347.3014 | 7 | 3.2353 | 7 | 3.2353 | 1 | 0 | 5 | 60.2941 | 5.9022 | 4.4295 | 5.5796 | 5.6897 | 288.2923 | 5 | 3.8235 | 5 | 3.8235 | 1 | 0 | 5 | 68.5294
Roof | 3.6353 | 4.4054 | 3.9808 | 3.8883 | 10000 | 9 | 2.3333 | 8 | 2.6667 | 1 | 0 | 5 | 50 | 14.8156 | 2.8661 | 9.0666 | 10.5392 | 260.5776 | 5 | 3.8235 | 3 | 4.4118 | 2 | 0.29412 | 5 | 73.5294 | 16.3688 | 2.7733 | 11.4316 | 12.8984 | 186.2436 | 1 | 5 | 1 | 5 | 2 | 0.29412 | 5 | 85.8824 | 13.0095 | 4.4541 | 11.1351 | 11.7749 | 154.5994 | 1 | 5 | 1 | 5 | 4 | 0.88235 | 5 | 87.6471
Windows | 2.6796 | 4.4833 | 3.4888 | 3.272 | 183.3571 | 12 | 1.3333 | 12 | 1.3333 | 4 | 0.9375 | 5 | 36.4792 | 1.7712 | 2.806 | 2.269 | 2.1415 | 184.5609 | 13 | 1.4706 | 12 | 1.7647 | 3 | 0.58824 | 5 | 39.4118 | 1.1139 | 2.7508 | 1.7083 | 1.5317 | 183.8859 | 11 | 2.0588 | 10 | 2.3529 | 3 | 0.58824 | 5 | 47.6471 | 0.34832 | 4.4285 | 1.2422 | 0.9371 | 198.8161 | 11 | 2.0588 | 11 | 2.0588 | 2 | 0.29412 | 5 | 44.7059
Air tightness | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0 | 17 | 5 | 4 | 27 | 6.9122 | 3.4552 | 5.249 | 5.675 | 23.9935 | 7 | 3.2353 | 7 | 3.2353 | 7 | 1.7647 | 4 | 62.5882 | 5.8346 | 2.7557 | 4.7165 | 5.0487 | 26.5495 | 5 | 3.8235 | 4 | 4.1176 | 7 | 1.7647 | 4 | 72.8824 | 8.0717 | 4.493 | 7.2876 | 7.5553 | 20.0053 | 3 | 4.4118 | 3 | 4.4118 | 7 | 1.7647 | 4 | 79.0588
T reduction (2 DegC) | 10.3442 | 4.0113 | 7.5032 | 8.2643 | 1.9611 | 5 | 3.6667 | 4 | 4 | 12 | 3.4375 | 4.375 | 77.1042 | 10.1776 | 2.8602 | 6.6571 | 7.5589 | 1.5862 | 6 | 3.5294 | 5 | 3.8235 | 13 | 3.5294 | 4.375 | 75.1838 | 9.0633 | 2.8072 | 6.7914 | 7.4663 | 1.3146 | 4 | 4.1176 | 3 | 4.4118 | 15 | 4.1176 | 4.375 | 85.1838 | 6.458 | 4.5236 | 6.0342 | 6.1789 | 1.3874 | 4 | 4.1176 | 4 | 4.1176 | 16 | 4.4118 | 4.375 | 84.0074
T set back | 7.104 | 4.5362 | 5.9521 | 6.2607 | 2.047 | 6 | 3.3333 | 6 | 3.3333 | 10 | 2.8125 | 4.75 | 69.3542 | 6.5828 | 2.8258 | 4.7753 | 5.2383 | 1.8897 | 9 | 2.6471 | 8 | 2.9412 | 11 | 2.9412 | 4.75 | 62.1912 | 5.6567 | 2.7768 | 4.6109 | 4.9216 | 1.6539 | 6 | 3.5294 | 5 | 3.8235 | 14 | 3.8235 | 4.75 | 77.1912 | 3.2833 | 4.4702 | 3.5433 | 3.4546 | 1.8609 | 6 | 3.5294 | 6 | 3.5294 | 14 | 3.8235 | 4.75 | 75.1324
Lighting (30%) | -4.9296 | 18.9777 | 5.7954 | 2.9222 | 11.232 | 7 | 3 | 13 | 1 | 8 | 2.1875 | 4.75 | 48.8125 | -4.2518 | 11.3151 | 3.2376 | 1.3192 | 11.9772 | 11 | 2.0588 | 14 | 1.1765 | 8 | 2.0588 | 4.75 | 43.0735 | -3.1366 | 11.011 | 2.0011 | 0.47476 | 12.339 | 9 | 2.6471 | 18 | 0 | 8 | 2.0588 | 4.75 | 38.9559 | -1.6765 | 17.7106 | 2.5709 | 1.1211 | 11.9115 | 7 | 3.2353 | 9 | 2.6471 | 8 | 2.0588 | 4.75 | 61.6029
Occupancy Sensors (Lights/Plug Loads) | 0 | 10 | 4.4861 | 3.2843 | 0.69916 | 8 | 2.6667 | 11 | 1.6667 | 16 | 4.6875 | 4.75 | 58.6458 | 0 | 10 | 4.8111 | 3.5787 | 0.43631 | 8 | 2.9412 | 10 | 2.3529 | 18 | 5 | 4.75 | 66.3088 | 0 | 10 | 3.6315 | 2.5526 | 0.42838 | 8 | 2.9412 | 8 | 2.9412 | 18 | 5 | 4.75 | 70.4265 | 0 | 10 | 2.1909 | 1.443 | 0.68926 | 8 | 2.9412 | 8 | 2.9412 | 18 | 5 | 4.75 | 70.4265
HRV | 34.8055 | 3.4042 | 20.7186 | 24.4924 | 64.34 | 2 | 4.6667 | 1 | 5 | 6 | 1.5625 | 4.75 | 86.6042 | 27.2866 | 2.8128 | 15.512 | 18.5281 | 55.2161 | 2 | 4.7059 | 2 | 4.7059 | 6 | 1.4706 | 4.75 | 84.5441 | 0.45905 | 2.7557 | 1.2931 | 1.0453 | 162.1926 | 12 | 1.7647 | 11 | 2.0588 | 4 | 0.88235 | 4.75 | 43.6618 | 0.30592 | 4.1501 | 1.1481 | 0.86064 | 174.2591 | 12 | 1.7647 | 12 | 1.7647 | 3 | 0.58824 | 4.75 | 40.7206
DCV | 33.8696 | 4.8148 | 20.8354 | 24.3272 | 1.6716 | 1 | 5 | 2 | 4.6667 | 14 | 4.0625 | 4.375 | 92.9792 | 27.4022 | 2.9417 | 15.634 | 18.6484 | 1.5482 | 1 | 5 | 1 | 5 | 15 | 4.1176 | 4.375 | 95.4779 | 0.020378 | 2.794 | 1.0276 | 0.72839 | 4.8202 | 15 | 0.88235 | 14 | 1.1765 | 9 | 2.3529 | 4.375 | 34.5956 | 0.027613 | 4.4536 | 0.99729 | 0.6663 | 4.8566 | 14 | 1.1765 | 14 | 1.1765 | 10 | 2.6471 | 4.375 | 37.5368
Cold Deck Reset | 2.9981 | 3.9226 | 3.4128 | 3.3017 | 4.5932 | 13 | 1 | 10 | 2 | 9 | 2.5 | 5 | 43.5 | 0.57743 | 2.9975 | 1.7417 | 1.4435 | 4.2806 | 14 | 1.1765 | 13 | 1.4706 | 9 | 2.3529 | 5 | 40.5882 | 0 | 2.7573 | 1.0013 | 0.70384 | 4.7596 | 17 | 0.29412 | 16 | 0.58824 | 10 | 2.6471 | 5 | 29.1176 | 0 | 4.4389 | 0.97251 | 0.64055 | 4.757 | 16 | 0.58824 | 16 | 0.58824 | 11 | 2.9412 | 5 | 32.0588
VSD | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0 | 17 | 5 | 5 | 30 | -0.067496 | 2.9992 | 1.4079 | 1.03 | 2.1301 | 17 | 0.29412 | 17 | 0.29412 | 10 | 2.6471 | 5 | 27.0588 | 0.02616 | 2.7643 | 1.0205 | 0.72509 | 2.2506 | 16 | 0.58824 | 15 | 0.88235 | 11 | 2.9412 | 5 | 34.1176 | 0.031464 | 4.4373 | 0.99673 | 0.66724 | 2.2519 | 15 | 0.88235 | 13 | 1.4706 | 13 | 3.5294 | 5 | 42.0588
VSP | 0 | 19.6868 | 8.8317 | 6.4657 | 1.698 | 4 | 4 | 5 | 3.6667 | 13 | 3.75 | 5 | 79.9167 | -5.2043 | 28.9706 | 11.2376 | 7.026 | 0.74926 | 3 | 4.4118 | 6 | 3.5294 | 17 | 4.7059 | 5 | 84.7059 | -4.3519 | 31.8868 | 8.8081 | 4.8985 | 0.6748 | 3 | 4.4118 | 6 | 3.5294 | 17 | 4.7059 | 5 | 84.7059 | 0 | 4.4339 | 0.97142 | 0.63983 | 7.4325 | 17 | 0.29412 | 17 | 0.29412 | 9 | 2.3529 | 5 | 26.1765
Solar Wall | 7.4828 | -0.34119 | 3.9729 | 4.9132 | 56.8028 | 10 | 2 | 7 | 3 | 7 | 1.875 | 4.5 | 54.125 | 5.3217 | -0.2113 | 2.6597 | 3.3416 | 56.7031 | 12 | 1.7647 | 11 | 2.0588 | 5 | 1.1765 | 4.5 | 43.7941 | 3.2134 | -0.20513 | 1.972 | 2.3408 | 56.56 | 10 | 2.3529 | 9 | 2.6471 | 6 | 1.4706 | 4.5 | 52.9118 | 2.543 | -0.33809 | 1.9118 | 2.1272 | 56.89 | 9 | 2.6471 | 7 | 3.2353 | 6 | 1.4706 | 4.5 | 59.0882
Solar DHW | 1.8705 | -0.055528 | 1.0064 | 1.2379 | 138.6284 | 15 | 0.33333 | 15 | 0.33333 | 5 | 1.25 | 5 | 23.4167 | 1.3304 | -0.033037 | 0.67443 | 0.84246 | 137.7312 | 18 | 0 | 18 | 0 | 4 | 0.88235 | 5 | 17.6471 | 0.80336 | -0.030109 | 0.50069 | 0.59061 | 136.4565 | 18 | 0 | 17 | 0.29412 | 5 | 1.1765 | 5 | 20.5882 | 0.63509 | -0.056474 | 0.48357 | 0.53529 | 139.4217 | 18 | 0 | 18 | 0 | 5 | 1.1765 | 5 | 18.5294
DB Economizer | 0.054195 | 4.24 | 1.932 | 1.4289 | 2.0156 | 14 | 0.66667 | 14 | 0.66667 | 11 | 3.125 | 5 | 33.7083 | 0.14279 | 3.2153 | 1.621 | 1.2424 | 1.648 | 15 | 0.88235 | 15 | 0.88235 | 12 | 3.2353 | 5 | 37.0588 | 0.31544 | 2.7768 | 1.2093 | 0.94372 | 1.8189 | 14 | 1.1765 | 13 | 1.4706 | 13 | 3.5294 | 5 | 44.1176 | 0.34539 | 4.4494 | 1.2445 | 0.93761 | 1.7995 | 10 | 2.3529 | 10 | 2.3529 | 15 | 4.1176 | 5 | 60.2941
COP | 0 | 0 | 0 | 0 | 10000 | 16 | 0 | 16 | 0 | 1 | 0 | 5 | 15 | 0.10606 | 3.0437 | 1.5194 | 1.1574 | 1.5761 | 16 | 0.58824 | 16 | 0.58824 | 14 | 3.8235 | 5 | 34.7059 | 0.30065 | 2.8546 | 1.2281 | 0.95257 | 2.2034 | 13 | 1.4706 | 12 | 1.7647 | 12 | 3.2353 | 5 | 47.3529 | 0 | 4.5849 | 1.0045 | 0.66162 | 2.2892 | 13 | 1.4706 | 15 | 0.88235 | 12 | 3.2353 | 5 | 41.1765
Retro-commissioning | 10 | 10 | 10 | 10 | 1.4247 | 3 | 4.3333 | 3 | 4.3333 | 15 | 4.375 | 5 | 88.7917 | 10 | 10 | 10 | 10 | 0.91116 | 4 | 4.1176 | 4 | 4.1176 | 16 | 4.4118 | 5 | 85.8824 | 10 | 10 | 10 | 10 | 0.80483 | 2 | 4.7059 | 2 | 4.7059 | 16 | 4.4118 | 5 | 94.1176 | 10 | 10 | 10 | 10 | 1.0204 | 2 | 4.7059 | 2 | 4.7059 | 17 | 4.7059 | 5 | 95
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 16 |  | 16 |  | 17 | [8 empty] | 18 |  | 18 |  | 18 | [8 empty] | 18 |  | 18 |  | 18 | [8 empty] | 18 |  | 18 |  | 18
| 2A-Training Building | [12 empty] | 2A-Training Building | [12 empty] | 2A-Training Building | [12 empty] | 2A-Training Building
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0
Wall | 2.6479 | 0.045711 | 1.8876 | 2.1306 | 10000 | 9 | 2.6471 | 8 | 2.9412 | 1 | 0 | 5 | 54.1176 | 4.4877 | 0.80092 | 3.6351 | 3.9231 | 472.8365 | 9 | 2.6471 | 9 | 2.6471 | 2 | 0.29412 | 5 | 52.9412 | 3.4382 | 1.6405 | 3.0885 | 3.2103 | 341.5452 | 9 | 2.6471 | 9 | 2.6471 | 2 | 0.29412 | 5 | 52.9412 | 4.2464 | 2.2317 | 3.8833 | 4.0112 | 236.3361 | 9 | 2.6471 | 8 | 2.9412 | 3 | 5 | 5 | 69.1176
Roof | 7.3778 | 0.35045 | 5.3245 | 5.9807 | 10000 | 7 | 3.2353 | 7 | 3.2353 | 1 | 0 | 5 | 60.2941 | 12.4133 | 3.4611 | 10.343 | 11.0424 | 408.3918 | 6 | 3.5294 | 6 | 3.5294 | 3 | 0.58824 | 5 | 66.1765 | 26.8491 | 14.1283 | 24.3748 | 25.2367 | 247.554 | 1 | 5 | 1 | 5 | 3 | 0.58824 | 5 | 86.7647 | 24.0041 | 13.7007 | 22.1471 | 22.8014 | 171.2979 | 2 | 4.7059 | 2 | 4.7059 | 4 | 5 | 5 | 95.8824
Windows | 0.49688 | 0 | 0.3517 | 0.3981 | 2774.8453 | 13 | 1.4706 | 13 | 1.4706 | 5 | 1.1765 | 5 | 39.1176 | 0.93369 | -0.014302 | 0.71445 | 0.78851 | 1033.8988 | 13 | 1.4706 | 13 | 1.4706 | 1 | 0 | 5 | 35.5882 | 0.54691 | 0.18364 | 0.47626 | 0.50087 | 844.3625 | 14 | 1.1765 | 12 | 1.7647 | 1 | 0 | 5 | 35.5882 | 0.76886 | 0.28759 | 0.68212 | 0.71268 | 511.7424 | 13 | 1.4706 | 11 | 2.0588 | 2 | 5 | 5 | 54.7059
Air tightness | 0 | 0 | 0 | 0 | 10000 | 16 | 0.58824 | 15 | 0.88235 | 1 | 0 | 4 | 22.2941 | 18.0069 | 0.6722 | 13.9979 | 15.3522 | 65.125 | 4 | 4.1176 | 4 | 4.1176 | 6 | 1.4706 | 4 | 74.0588 | 21.6696 | 8.0069 | 19.0122 | 19.9379 | 30.3012 | 2 | 4.7059 | 2 | 4.7059 | 9 | 2.3529 | 4 | 84.9412 | 31.0376 | 12.6309 | 27.7201 | 28.889 | 18.0832 | 1 | 5 | 1 | 5 | 10 | 5 | 4 | 97
T reduction (2 DegC) | 20.542 | 1.0056 | 14.8338 | 16.6582 | 7.0206 | 2 | 4.7059 | 2 | 4.7059 | 14 | 3.8235 | 4.375 | 90.4779 | 18.1704 | 0.88673 | 14.1732 | 15.5235 | 5.5687 | 3 | 4.4118 | 3 | 4.4118 | 15 | 4.1176 | 4.375 | 87.2426 | 16.2212 | 0.55093 | 13.1733 | 14.235 | 4.4187 | 5 | 3.8235 | 5 | 3.8235 | 14 | 3.8235 | 4.375 | 78.125 | 15.7338 | 0.54066 | 12.9955 | 13.9603 | 3.9094 | 5 | 3.8235 | 5 | 3.8235 | 13 | 5 | 4.375 | 81.6544
T set back | 18.2651 | 0.85327 | 13.1777 | 14.8037 | 7.9289 | 4 | 4.1176 | 4 | 4.1176 | 13 | 3.5294 | 4.75 | 82.4853 | 16.1782 | 0.78661 | 12.6186 | 13.8211 | 6.256 | 5 | 3.8235 | 5 | 3.8235 | 12 | 3.2353 | 4.75 | 77.4853 | 13.9182 | 0.48972 | 11.3063 | 12.2162 | 5.1425 | 6 | 3.5294 | 6 | 3.5294 | 13 | 3.5294 | 4.75 | 74.25 | 22.7866 | 0.50615 | 18.771 | 20.1859 | 2.7344 | 3 | 4.4118 | 3 | 4.4118 | 15 | 5 | 4.75 | 91.0147
Lighting (30%) | -7.3463 | 0.85327 | -4.9506 | -5.7162 | 30.5882 | 18 | 0 | 18 | 0 | 9 | 2.3529 | 4.75 | 21.3088 | -1.3295 | 19.4365 | 3.473 | 1.8506 | 30.077 | 10 | 2.3529 | 10 | 2.3529 | 9 | 2.3529 | 4.75 | 54.25 | -2.4153 | 15.6464 | 1.0978 | -0.12599 | 35.022 | 11 | 2.0588 | 17 | 0.29412 | 7 | 1.7647 | 4.75 | 36.0147 | -2.1245 | 14.6325 | 0.89567 | -0.16846 | 35.3593 | 11 | 2.0588 | 17 | 0.29412 | 8 | 5 | 4.75 | 45.7206
Occupancy Sensors (Lights/Plug Loads) | 0 | 7.2071 | 2.1058 | 1.4328 | 5.8221 | 8 | 2.9412 | 10 | 2.3529 | 15 | 4.1176 | 4.75 | 63.6618 | 0 | 6.7363 | 1.5579 | 1.0316 | 5.917 | 11 | 2.0588 | 12 | 1.7647 | 14 | 3.8235 | 4.75 | 52.4853 | 0 | 5.7786 | 1.124 | 0.73244 | 5.9045 | 10 | 2.3529 | 11 | 2.0588 | 12 | 3.2353 | 4.75 | 54.8382 | 0 | 5.4412 | 0.98067 | 0.63514 | 5.892 | 10 | 2.3529 | 12 | 1.7647 | 11 | 5 | 4.75 | 58.0735
HRV | 36.4548 | -0.68566 | 25.6031 | 29.0713 | 56.7927 | 1 | 5 | 1 | 5 | 7 | 1.7647 | 4.75 | 89.5441 | 25.8808 | -0.21453 | 19.8458 | 21.8845 | 53.2722 | 1 | 5 | 1 | 5 | 8 | 2.0588 | 4.75 | 90.4265 | 17.7644 | 0.024486 | 14.3139 | 15.5159 | 52.5768 | 4 | 4.1176 | 4 | 4.1176 | 6 | 1.4706 | 4.75 | 76.3088 | 15.2962 | 0.011504 | 12.5414 | 13.5121 | 52.2812 | 6 | 3.5294 | 6 | 3.5294 | 7 | 5 | 4.75 | 78.6618
DCV | 19.5042 | 0 | 13.8054 | 15.6268 | 13.9247 | 3 | 4.4118 | 3 | 4.4118 | 11 | 2.9412 | 4.375 | 83.7132 | 19.3192 | -0.014302 | 14.8479 | 16.3584 | 9.6171 | 2 | 4.7059 | 2 | 4.7059 | 11 | 2.9412 | 4.375 | 87.8309 | 19.5322 | 0 | 15.7331 | 17.0565 | 6.5356 | 3 | 4.4118 | 3 | 4.4118 | 11 | 2.9412 | 4.375 | 83.7132 | 19.6008 | 0.50615 | 16.1593 | 17.3719 | 5.4187 | 4 | 4.1176 | 4 | 4.1176 | 12 | 5 | 4.375 | 85.7721
Cold Deck Reset | 0 | 3.0017 | 0.87703 | 0.59673 | 17.3094 | 11 | 2.0588 | 12 | 1.7647 | 10 | 2.6471 | 5 | 49.7059 | 0 | 3.0034 | 0.6946 | 0.45995 | 16.2379 | 14 | 1.1765 | 15 | 0.88235 | 10 | 2.6471 | 5 | 37.3529 | 0 | 3.0118 | 0.5858 | 0.38174 | 13.8616 | 13 | 1.4706 | 14 | 1.1765 | 10 | 2.6471 | 5 | 41.4706 | 0 | 0 | 0 | 0 | 10000 | 18 | 0 | 16 | 0.58824 | 1 | 5 | 5 | 34.1176
VSD | -5.6857 | 14.6921 | 0.2683 | -1.6346 | 2.3622 | 14 | 1.1765 | 17 | 0.29412 | 16 | 4.4118 | 5 | 38.5294 | -4.8833 | 17.3139 | 0.25026 | -1.4839 | 1.8815 | 16 | 0.58824 | 18 | 0 | 16 | 4.4118 | 5 | 32.3529 | -5.7195 | 25.2655 | 0.30714 | -1.7922 | 1.1037 | 17 | 0.29412 | 18 | 0 | 16 | 4.4118 | 5 | 30.2941 | -5.7923 | 28.102 | 0.31656 | -1.8359 | 0.93237 | 15 | 0.88235 | 18 | 0 | 16 | 5 | 5 | 36.1765
VSP | 0 | 33.3232 | 9.7364 | 6.6246 | 0.91006 | 5 | 3.8235 | 6 | 3.5294 | 17 | 4.7059 | 5 | 80.5882 | 0.0043027 | 31.2786 | 7.2371 | 4.7937 | 0.90998 | 8 | 2.9412 | 8 | 2.9412 | 17 | 4.7059 | 5 | 70.2941 | 0 | 26.7752 | 5.2079 | 3.3937 | 0.91006 | 8 | 2.9412 | 8 | 2.9412 | 17 | 4.7059 | 5 | 70.2941 | 0 | 25.1582 | 4.5343 | 2.9367 | 0.91006 | 8 | 2.9412 | 9 | 2.6471 | 17 | 5 | 5 | 69.1176
Solar Wall | 1.434 | -1.158 | 0.67669 | 0.91875 | -90.5578 | 12 | 1.7647 | 11 | 2.0588 | 18 | 5 | 4.5 | 55.2647 | 0.98102 | -1.087 | 0.50276 | 0.66432 | -90.5578 | 15 | 0.88235 | 14 | 1.1765 | 18 | 5 | 4.5 | 42.9118 | 0.67403 | -0.93046 | 0.36196 | 0.47067 | -90.5578 | 15 | 0.88235 | 13 | 1.4706 | 18 | 5 | 4.5 | 44.9706 | 0.57664 | -0.87427 | 0.31514 | 0.40728 | -90.5578 | 16 | 0.58824 | 13 | 1.4706 | 18 | 5 | 4.5 | 42.9118
Solar DHW | 2.5913 | -0.16761 | 1.7852 | 2.0429 | 139.1473 | 10 | 2.3529 | 9 | 2.6471 | 6 | 1.4706 | 5 | 54.4118 | 1.7727 | -0.15732 | 1.3264 | 1.4771 | 139.1473 | 12 | 1.7647 | 11 | 2.0588 | 4 | 0.88235 | 5 | 44.4118 | 1.218 | -0.13467 | 0.9549 | 1.0465 | 139.1473 | 12 | 1.7647 | 10 | 2.3529 | 4 | 0.88235 | 5 | 46.4706 | 1.042 | -0.12654 | 0.8314 | 0.9056 | 139.1473 | 12 | 1.7647 | 10 | 2.3529 | 6 | 5 | 5 | 58.8235
DB Economizer | 0 | 0.45711 | 0.13356 | 0.090872 | 45.4948 | 15 | 0.88235 | 14 | 1.1765 | 8 | 2.0588 | 5 | 35.5882 | 0 | 0.35755 | 0.082691 | 0.054756 | 54.5937 | 18 | 0 | 17 | 0.29412 | 7 | 1.7647 | 5 | 22.3529 | 0 | 0.12243 | 0.023813 | 0.015518 | 136.4843 | 18 | 0 | 16 | 0.58824 | 5 | 1.1765 | 5 | 22.6471 | 0 | 0.092028 | 0.016586 | 0.010742 | 170.6054 | 17 | 0.29412 | 15 | 0.88235 | 5 | 5 | 5 | 38.2353
COP | 0 | 0 | 0 | 0 | 10000 | 16 | 0.58824 | 15 | 0.88235 | 1 | 0 | 5 | 25.2941 | 0.0043027 | 1.0297 | 0.24146 | 0.16134 | 70.8504 | 17 | 0.29412 | 16 | 0.58824 | 5 | 1.1765 | 5 | 24.7059 | 0 | 1.8242 | 0.35481 | 0.23121 | 34.332 | 16 | 0.58824 | 15 | 0.88235 | 8 | 2.0588 | 5 | 31.4706 | 0 | 2.5768 | 0.46442 | 0.30079 | 22.8369 | 14 | 1.1765 | 14 | 1.1765 | 9 | 5 | 5 | 46.4706
Retro-commissioning | 9.5037 | 2.8188 | 7.5505 | 8.1747 | 8.5344 | 6 | 3.5294 | 5 | 3.8235 | 12 | 3.2353 | 5 | 76.1765 | 9.6596 | 3.2323 | 8.1731 | 8.6753 | 6.1585 | 7 | 3.2353 | 7 | 3.2353 | 13 | 3.5294 | 5 | 70.8824 | 9.7646 | 4.2238 | 8.6869 | 9.0623 | 4.134 | 7 | 3.2353 | 7 | 3.2353 | 15 | 4.1176 | 5 | 72.6471 | 9.7979 | 4.5784 | 8.8572 | 9.1886 | 3.5446 | 7 | 3.2353 | 7 | 3.2353 | 14 | 5 | 5 | 75.2941
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 18 |  | 18 |  | 18 | [8 empty] | 18 |  | 18 |  | 18 | [8 empty] | 18 |  | 18 |  | 18 | [8 empty] | 18 |  | 18 |  | 18
| 3A-Active Warehouse | [12 empty] | 3A-Active Warehouse | [12 empty] | 3A-Active Warehouse | [12 empty] | 3A-Active Warehouse
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 6.4896e-15 | 0 | 0 | 3.818e-15 | [9 empty] | 1.0117e-14 | 0 | 0 | 6.8345e-15 | [9 empty] | 5.2018e-15 | 0 | 0 | 3.9886e-15 | [9 empty] | 0 | 0 | 0 | 0
Wall | 9.8022 | 0.1545 | 4.6125 | 5.8304 | 10000 | 6 | 3.2143 | 5 | 3.8235 | 1 | 0 | 5 | 64.2647 | 9.6712 | 0.18396 | 4.9837 | 6.5932 | 2413.8971 | 6 | 3.4375 | 6 | 3.5294 | 3 | 0.625 | 5 | 65.6434 | 5.338 | 0.33069 | 3.6556 | 4.1702 |  | 6 | 3.4375 | 6 | 3.5294 |  | 5 | 5 | 78.7684 | 6.7846 | 0.15699 | 4.7477 | 5.3891 | 1532.0403 | 5 | 3.75 | 5 | 3.8235 | 3 | 0.625 | 5 | 69.8897
Roof | 8.0486 | 0.11587 | 3.7814 | 4.7829 | 10000 | 8 | 2.5 | 6 | 3.5294 | 1 | 0 | 5 | 57.2059 | 10.058 | 0.14717 | 5.1634 | 6.8426 | 2390.8962 | 5 | 3.75 | 5 | 3.8235 | 4 | 0.9375 | 5 | 70.8272 | 15.0268 | 0.69444 | 10.2111 | 11.6841 |  | 3 | 4.375 | 3 | 4.4118 |  | 5 | 5 | 91.5074 | 20.8136 | 1.0675 | 14.7448 | 16.6559 | 1273.4094 | 2 | 4.6875 | 2 | 4.7059 | 4 | 0.9375 | 5 | 83.5662
Windows | 1.0342 | 0.27037 | 0.62331 | 0.71974 | 743.7916 | 12 | 1.0714 | 12 | 1.7647 | 7 | 1.875 | 5 | 40.4779 | 1.7408 | 0.25754 | 0.99673 | 1.2596 | 484.1999 | 13 | 1.25 | 10 | 2.3529 | 5 | 1.25 | 5 | 43.9706 | 0.70281 | 0.23148 | 0.54444 | 0.59288 |  | 13 | 1.25 | 12 | 1.7647 |  | 5 | 5 | 51.1029 | 0.93341 | 0.21978 | 0.71408 | 0.78315 | 422.3805 | 12 | 1.5625 | 10 | 2.3529 | 5 | 1.25 | 5 | 46.1581
Air tightness | 6.4896e-15 | 0 | 0 | 3.818e-15 | 10000 | 15 | 0 | 14 | 1.1765 | 1 | 0 | 4 | 20.2353 | 31.5925 | 0.47829 | 16.2255 | 21.498 | 143.8491 | 1 | 5 | 1 | 5 | 6 | 1.5625 | 4 | 86.6875 | 46.2684 | 1.0251 | 31.0667 | 35.7164 |  | 1 | 5 | 1 | 5 |  | 5 | 4 | 97 | 41.2371 | 1.0047 | 28.8719 | 32.7659 | 52.3096 | 1 | 5 | 1 | 5 | 7 | 1.875 | 4 | 87.625
T reduction (2 DegC) | 27.7428 | 0.50212 | 13.0895 | 16.5285 | 6.0732 | 1 | 5 | 1 | 5 | 15 | 4.375 | 4.375 | 96.25 | 27.5306 | 0.62546 | 14.232 | 18.8017 | 4.4109 | 2 | 4.6875 | 2 | 4.7059 | 15 | 4.375 | 4.375 | 92.0037 | 21.3353 | 0.85979 | 14.4556 | 16.5599 |  | 2 | 4.6875 | 2 | 4.7059 |  | 5 | 4.375 | 93.8787 | 19.9359 | 0.87912 | 14.0789 | 15.9234 | 2.6364 | 3 | 4.375 | 3 | 4.4118 | 15 | 4.375 | 4.375 | 87.7574
T set back | 6.4896e-15 | 0 | 0 | 3.818e-15 | 10000 | 15 | 0 | 14 | 1.1765 | 1 | 0 | 4.75 | 22.4853 | 1.1095e-14 | 0 | 0 | 7.4955e-15 | 10000 | 17 | 0 | 16 | 0.58824 | 1 | 0 | 4.75 | 18.3676 | 5.2018e-15 | 0 | 0 | 3.9886e-15 |  | 17 | 0 | 16 | 0.58824 |  | 5 | 4.75 | 33.3676 | 0 | 0 | 0 | 0 | 10000 | 17 | 0 | 16 | 0.58824 | 1 | 0 | 4.75 | 18.3676
Lighting (30%) | -8.2734 | 16.8405 | 5.2358 | 2.0654 | 25.4579 | 4 | 3.9286 | 9 | 2.6471 | 12 | 3.4375 | 4.75 | 70.5919 | -6.5442 | 16.0044 | 3.7908 | 0.77134 | 25.7692 | 8 | 2.8125 | 13 | 1.4706 | 12 | 3.4375 | 4.75 | 54.5441 | -3.581 | 14.3519 | 2.4444 | 0.60144 |  | 8 | 2.8125 | 11 | 2.0588 |  | 5 | 4.75 | 63.3493 | -2.9674 | 13.6264 | 2.1326 | 0.52653 | 25.9675 | 8 | 2.8125 | 12 | 1.7647 | 10 | 2.8125 | 4.75 | 54.7279
Occupancy Sensors (Lights/Plug Loads) | 6.4896e-15 | 7.6254 | 4.1019 | 3.1392 | 2.2885 | 7 | 2.8571 | 8 | 2.9412 | 16 | 4.6875 | 4.75 | 68.9007 | 1.1095e-14 | 7.2468 | 3.2184 | 2.3511 | 2.2938 | 9 | 2.5 | 9 | 2.6471 | 16 | 4.6875 | 4.75 | 64.3419 | 5.2018e-15 | 6.5182 | 2.1901 | 1.5202 |  | 9 | 2.5 | 9 | 2.6471 |  | 5 | 4.75 | 65.2794 | 0 | 6.1774 | 1.8986 | 1.3007 | 2.2963 | 9 | 2.5 | 9 | 2.6471 | 16 | 4.6875 | 4.75 | 64.3419
HRV | 10.4317 | -0.11587 | 4.7579 | 6.0895 | 0 | 5 | 3.5714 | 4 | 4.1176 | 17 | 5 | 4.75 | 83.0735 | 8.0271 | -0.036792 | 4.0523 | 5.4109 | 0 | 7 | 3.125 | 7 | 3.2353 | 17 | 5 | 4.75 | 73.7721 | 4.3507 | 0.033069 | 2.9 | 3.3437 |  | 7 | 3.125 | 7 | 3.2353 |  | 5 | 4.75 | 73.7721 | 3.664 | 0.031397 | 2.5475 | 2.8991 | 0 | 7 | 3.125 | 7 | 3.2353 | 17 | 5 | 4.75 | 73.7721
DCV | 12.9047 | 0.07725 | 6.0046 | 7.6239 | 23.8565 | 2 | 4.6429 | 2 | 4.7059 | 13 | 3.75 | 4.375 | 89.8162 | 10.0903 | 0.14717 | 5.1797 | 6.8644 | 21.2803 | 4 | 4.0625 | 4 | 4.1176 | 13 | 3.75 | 4.375 | 81.636 | 5.6225 | 0.19841 | 3.8 | 4.3574 |  | 5 | 3.75 | 5 | 3.8235 |  | 5 | 4.375 | 81.1397 | 4.7228 | 0.18838 | 3.3292 | 3.768 | 19.2062 | 6 | 3.4375 | 6 | 3.5294 | 12 | 3.4375 | 4.375 | 72.2059
Cold Deck Reset | 6.4896e-15 | 3.0127 | 1.6206 | 1.2403 | 27.4057 | 10 | 1.7857 | 10 | 2.3529 | 11 | 3.125 | 5 | 53.3456 | 1.1095e-14 | 3.0169 | 1.3399 | 0.97879 | 26.0688 | 11 | 1.875 | 11 | 2.0588 | 11 | 3.125 | 5 | 51.9118 | 5.2018e-15 | 3.0093 | 1.0111 | 0.70184 |  | 11 | 1.875 | 10 | 2.3529 |  | 5 | 5 | 59.5956 | 0 | 3.0141 | 0.92637 | 0.63464 | 22.2671 | 11 | 1.875 | 11 | 2.0588 | 11 | 3.125 | 5 | 51.9118
VSD | -14.1175 | 12.9357 | 0.4349 | -2.9804 | 0 | 13 | 0.71429 | 18 | 0 | 17 | 5 | 5 | 35 | -13.1025 | 15.9505 | 0.44274 | -3.6767 | 0 | 14 | 0.9375 | 18 | 0 | 17 | 5 | 5 | 36.5625 | -10.2514 | 21.6093 | 0.4538 | -2.8206 |  | 14 | 0.9375 | 18 | 0 |  | 5 | 5 | 36.5625 | -10.0584 | 24.1798 | 0.46447 | -2.8493 | 0 | 14 | 0.9375 | 18 | 0 | 17 | 5 | 5 | 36.5625
VSP | 6.4896e-15 | 0 | 0 | 3.818e-15 | 10000 | 15 | 0 | 14 | 1.1765 | 1 | 0 | 5 | 23.2353 | 1.1095e-14 | 0 | 0 | 7.4955e-15 | 10000 | 17 | 0 | 16 | 0.58824 | 1 | 0 | 5 | 19.1176 | 5.2018e-15 | 0 | 0 | 3.9886e-15 |  | 17 | 0 | 16 | 0.58824 |  | 5 | 5 | 34.1176 | 0 | 0 | 0 | 0 | 10000 | 17 | 0 | 16 | 0.58824 | 1 | 0 | 5 | 19.1176
Solar Wall | 8.4083 | -0.42487 | 3.6568 | 4.7719 | 118.4674 | 9 | 2.1429 | 7 | 3.2353 | 8 | 2.1875 | 4.5 | 57.7096 | 6.0284 | -0.40471 | 2.8758 | 3.9413 | 118.4674 | 10 | 2.1875 | 8 | 2.9412 | 7 | 1.875 | 4.5 | 55.0257 | 3.1292 | -0.36376 | 1.9556 | 2.3145 |  | 10 | 2.1875 | 8 | 2.9412 |  | 5 | 4.5 | 64.4007 | 2.6052 | -0.34537 | 1.6983 | 1.9839 | 118.4674 | 10 | 2.1875 | 8 | 2.9412 | 6 | 1.5625 | 4.5 | 54.0882
Solar DHW | 6.4896e-15 | 2.8196 | 1.5167 | 1.1608 | 32.6829 | 11 | 1.4286 | 11 | 2.0588 | 10 | 2.8125 | 5 | 47.8493 | 1.1095e-14 | 2.6858 | 1.1928 | 0.87136 | 32.6829 | 12 | 1.5625 | 12 | 1.7647 | 10 | 2.8125 | 5 | 46.7279 | 5.2018e-15 | 2.414 | 0.81111 | 0.56302 |  | 12 | 1.5625 | 13 | 1.4706 |  | 5 | 5 | 51.2316 | 0 | 2.292 | 0.70443 | 0.48259 | 32.6829 | 13 | 1.25 | 13 | 1.4706 | 9 | 2.5 | 5 | 41.5441
DB Economizer | -0.35971 | 0.73387 | 0.22855 | 0.090491 | 49.1643 | 14 | 0.35714 | 13 | 1.4706 | 9 | 2.5 | 5 | 35.2941 | -0.22566 | 0.66225 | 0.17974 | 0.062407 | 51.5317 | 15 | 0.625 | 15 | 0.88235 | 9 | 2.5 | 5 | 33.0515 | -0.1506 | 0.69444 | 0.13333 | 0.046486 |  | 16 | 0.3125 | 15 | 0.88235 |  | 5 | 5 | 38.364 | -0.069657 | 0.72214 | 0.17369 | 0.09706 | 38.8753 | 16 | 0.3125 | 15 | 0.88235 | 8 | 2.1875 | 5 | 29.9265
COP | 6.4896e-15 | 0 | 0 | 3.818e-15 | 10000 | 15 | 0 | 14 | 1.1765 | 1 | 0 | 5 | 23.2353 | 1.1095e-14 | 0.29433 | 0.13072 | 0.095492 | 62.8719 | 16 | 0.3125 | 14 | 1.1765 | 8 | 2.1875 | 5 | 31.9853 | 5.2018e-15 | 0.89286 | 0.3 | 0.20824 |  | 15 | 0.625 | 14 | 1.1765 |  | 5 | 5 | 42.6103 | 0 | 0.91052 | 0.27984 | 0.19172 | 13.5294 | 15 | 0.625 | 14 | 1.1765 | 13 | 3.75 | 5 | 38.8603
Retro-commissioning | 9.7572 | 2.0085 | 5.589 | 6.5672 | 15.0898 | 3 | 4.2857 | 3 | 4.4118 | 14 | 4.0625 | 5 | 88.0699 | 10.7995 | 2.3547 | 6.5196 | 8.0597 | 10.9859 | 3 | 4.375 | 3 | 4.4118 | 14 | 4.0625 | 5 | 88.6949 | 9.9063 | 3.1415 | 7.6333 | 8.3286 |  | 4 | 4.0625 | 4 | 4.1176 |  | 5 | 5 | 87.261 | 9.9331 | 3.4537 | 7.9417 | 8.5688 | 5.6958 | 4 | 4.0625 | 4 | 4.1176 | 14 | 4.0625 | 5 | 84.4485
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 | [10 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 15 |  | 18 |  | 17 | [8 empty] | 17 |  | 18 |  | 17 | [8 empty] | 17 |  | 18 | [10 empty] | 17 |  | 18 |  | 17
| 3B-Storage Type Warehouse | [12 empty] | 3B-Storage Type Warehouse | [12 empty] | 3B-Storage Type Warehouse | [12 empty] | 3B-Storage Type Warehouse
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0
Wall | 4.3783 | 0.74683 | 3.4133 | 3.7295 | 0 | 5 | 2.1429 | 5 | 2.1429 | 17 | 5 | 5 | 60 | 8.2501 | 1.2413 | 6.8582 | 7.3415 | 1542.5128 | 4 | 2.8571 | 4 | 4.1176 | 12 | 3.2353 | 5 | 73.5294 | 6.5799 | 1.6193 | 5.8382 | 6.1058 | 1241.6738 | 3 | 3.3333 | 3 | 4.4118 | 12 | 3.2353 | 5 | 78.9216 | 9.1352 | 2.6439 | 8.2912 | 8.6001 | 689.4032 | 3 | 3.5714 | 3 | 4.4118 | 12 | 3.2353 | 5 | 80.5882
Roof | 5.6205 | 1.1202 | 4.4246 | 4.8164 | 0 | 4 | 2.8571 | 4 | 2.8571 | 17 | 5 | 5 | 70 | 10.9681 | 2.211 | 9.229 | 9.8328 | 861.2031 | 2 | 4.2857 | 1 | 5 | 13 | 3.5294 | 5 | 90.5882 | 11.5479 | 3.1306 | 10.2894 | 10.7435 | 581.7551 | 1 | 5 | 1 | 5 | 13 | 3.5294 | 5 | 95.5882 | 23.4251 | 7.6305 | 21.3715 | 22.1232 | 323.0026 | 1 | 5 | 1 | 5 | 13 | 3.5294 | 5 | 95.5882
Windows | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 8 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471 | 0 | 0 | 0 | 0 | 10000 | 7 | 0 | 6 | 3.5294 | 1 | 0 | 5 | 39.7059 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471
Air tightness | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 8 | 0 | 1 | 0 | 4 | 12 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 4 | 34.6471 | 0 | 0 | 0 | 0 | 10000 | 7 | 0 | 6 | 3.5294 | 1 | 0 | 4 | 36.7059 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 4 | 34.6471
T reduction (2 DegC) | 11.6829 | 5.2766 | 9.9806 | 10.5383 | 5.3643 | 1 | 5 | 1 | 5 | 16 | 4.6875 | 4.375 | 97.1875 | 10.0941 | 5.9736 | 9.2758 | 9.5599 | 4.6297 | 1 | 5 | 2 | 4.7059 | 18 | 5 | 4.375 | 96.0662 | 7.6165 | 6.4412 | 7.4407 | 7.5041 | 4.0146 | 2 | 4.1667 | 2 | 4.7059 | 18 | 5 | 4.375 | 90.2328 | 6.2412 | 6.9612 | 6.3348 | 6.3005 | 3.5914 | 4 | 2.8571 | 4 | 4.1176 | 18 | 5 | 4.375 | 76.9485
T set back | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 8 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 4.75 | 36.8971 | 0 | 0 | 0 | 0 | 10000 | 7 | 0 | 6 | 3.5294 | 1 | 0 | 4.75 | 38.9559 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 4.75 | 36.8971
Lighting (30%) | -2.7238 | 12.6587 | 1.3637 | 0.024462 | 27.7 | 6 | 1.4286 | 7 | 0.71429 | 14 | 4.0625 | 4.75 | 41.4375 | -2.0265 | 13.2273 | 1.0028 | -0.048965 | 27.6871 | 6 | 1.4286 | 18 | 0 | 16 | 4.4118 | 4.75 | 37.4853 | -1.3906 | 12.3426 | 0.66274 | -0.078057 | 27.6693 | 5 | 1.6667 | 18 | 0 | 16 | 4.4118 | 4.75 | 39.152 | -1.0621 | 11.4123 | 0.55981 | -0.03386 | 27.0196 | 6 | 1.4286 | 18 | 0 | 16 | 4.4118 | 4.75 | 37.4853
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 8 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 4.75 | 36.8971 | 0 | 0 | 0 | 0 | 10000 | 7 | 0 | 6 | 3.5294 | 1 | 0 | 4.75 | 38.9559 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 4.75 | 36.8971
HRV | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 8 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 4.75 | 36.8971 | 0 | 0 | 0 | 0 | 10000 | 7 | 0 | 6 | 3.5294 | 1 | 0 | 4.75 | 38.9559 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 4.75 | 36.8971
DCV | 9.957 | 0 | 7.3112 | 8.1781 | 19.5275 | 2 | 4.2857 | 2 | 4.2857 | 15 | 4.375 | 4.375 | 86.25 | 10.0094 | 0 | 8.0216 | 8.7118 | 13.8176 | 3 | 3.5714 | 3 | 4.4118 | 17 | 4.7059 | 4.375 | 83.125 | 0 | 0 | 0 | 0 | 9.1027 | 7 | 0 | 6 | 3.5294 | 17 | 4.7059 | 4.375 | 51.9485 | 9.9989 | 0 | 8.6988 | 9.1747 | 7.0168 | 2 | 4.2857 | 2 | 4.7059 | 17 | 4.7059 | 4.375 | 90.1838
Cold Deck Reset | 0 | 3.0167 | 0.80161 | 0.53897 | 144.1637 | 7 | 0.71429 | 6 | 1.4286 | 12 | 3.4375 | 5 | 40.3125 | 0 | 3.0347 | 0.60266 | 0.39342 | 148.8686 | 7 | 0.71429 | 6 | 3.5294 | 14 | 3.8235 | 5 | 56.1765 | 0 | 2.998 | 0.44824 | 0.28653 | 139.7903 | 6 | 0.83333 | 5 | 3.8235 | 14 | 3.8235 | 5 | 59.0686 | 0 | 3.012 | 0.39163 | 0.24828 | 126.1574 | 7 | 0.71429 | 6 | 3.5294 | 14 | 3.8235 | 5 | 56.1765
VSD | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 8 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471 | 0 | 0 | 0 | 0 | 10000 | 7 | 0 | 6 | 3.5294 | 1 | 0 | 5 | 39.7059 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471
VSP | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 8 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471 | 0 | 0 | 0 | 0 | 10000 | 7 | 0 | 6 | 3.5294 | 1 | 0 | 5 | 39.7059 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471
Solar Wall | 8.654 | -1.9244 | 5.8431 | 6.7641 | 96.6902 | 3 | 3.5714 | 3 | 3.5714 | 13 | 3.75 | 4.5 | 74.75 | 6.1542 | -1.9787 | 4.5391 | 5.0998 | 96.0794 | 5 | 2.1429 | 5 | 3.8235 | 15 | 4.1176 | 4.5 | 67.6176 | 4.0555 | -1.8373 | 3.1745 | 3.4923 | 95.9289 | 4 | 2.5 | 4 | 4.1176 | 15 | 4.1176 | 4.5 | 72.1765 | 3.1215 | -1.6734 | 2.4981 | 2.7263 | 96.4436 | 5 | 2.1429 | 5 | 3.8235 | 15 | 4.1176 | 4.5 | 67.6176
Solar DHW | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 8 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471 | 0 | 0 | 0 | 0 | 10000 | 7 | 0 | 6 | 3.5294 | 1 | 0 | 5 | 39.7059 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471
DB Economizer | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 8 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471 | 0 | 0 | 0 | 0 | 10000 | 7 | 0 | 6 | 3.5294 | 1 | 0 | 5 | 39.7059 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471
COP | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 8 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471 | 0 | 0 | 0 | 0 | 10000 | 7 | 0 | 6 | 3.5294 | 1 | 0 | 5 | 39.7059 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471
Retro-commissioning | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 8 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471 | 0 | 0 | 0 | 0 | 10000 | 7 | 0 | 6 | 3.5294 | 1 | 0 | 5 | 39.7059 | 0 | 0 | 0 | 0 | 10000 | 8 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 8 |  | 8 |  | 17 | [8 empty] | 8 |  | 18 |  | 18 | [8 empty] | 7 |  | 18 |  | 18 | [8 empty] | 8 |  | 18 |  | 18
| 4A-Hotel Type Accomodation | [12 empty] | 4A-Hotel Type Accomodation | [12 empty] | 4A-Hotel Type Accomodation | [12 empty] | 4A-Hotel Type Accomodation
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 2.8896 | 2.343 | 2.7528 | 2.7983 | 252.9338 | 9 | 2.6471 | 9 | 2.6471 | 1 | 0 | 5 | 52.0588 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Roof | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 7.4658 | 6.3356 | 7.1829 | 7.2769 | 242.3487 | 5 | 3.8235 | 5 | 3.8235 | 2 | 0.29412 | 5 | 69.4118 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Windows | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 3.1288 | 2.0116 | 2.8492 | 2.9421 | 236.2226 | 8 | 2.9412 | 8 | 2.9412 | 3 | 0.58824 | 5 | 57.9412 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Air tightness | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 19.1569 | 14.8155 | 18.0701 | 18.4312 | 35.9517 | 3 | 4.4118 | 3 | 4.4118 | 5 | 1.1765 | 4 | 77.2941 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12
T reduction (2 DegC) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 21.591 | 9.9301 | 18.6721 | 19.6418 | 6.0296 | 2 | 4.7059 | 2 | 4.7059 | 11 | 2.9412 | 4.375 | 87.8309 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125
T set back | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 21.5911 | 9.9349 | 18.6734 | 19.6427 | 6.0284 | 1 | 5 | 1 | 5 | 12 | 3.2353 | 4.75 | 93.9559 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
Lighting (30%) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | -3.8164 | 11.7496 | 0.080061 | -1.2145 | 24.2077 | 16 | 0.58824 | 18 | 0 | 6 | 1.4706 | 4.75 | 22.7794 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 4.5067 | 1.1281 | 0.75332 | 16.6543 | 12 | 1.7647 | 12 | 1.7647 | 8 | 2.0588 | 4.75 | 45.1324 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
HRV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 1.3788 | -12.4503 | -2.0829 | -0.93284 | -69.515 | 18 | 0 | 16 | 0.58824 | 18 | 5 | 4.75 | 33.3676 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
DCV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 1.3185 | -9.5068 | -1.3913 | -0.491 | -27.1519 | 17 | 0.29412 | 15 | 0.88235 | 17 | 4.7059 | 4.375 | 35.4779 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125
Cold Deck Reset | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 3.0096 | 0.75337 | 0.50308 | 3.5968 | 13 | 1.4706 | 13 | 1.4706 | 13 | 3.5294 | 5 | 46.1765 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
VSD | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -3.3554 | 10.7212 | 0.16827 | -1.0024 | 0.97551 | 15 | 0.88235 | 17 | 0.29412 | 14 | 3.8235 | 5 | 34.7059 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
VSP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 1.6343 | 0.4091 | 0.27319 | 21.9562 | 14 | 1.1765 | 14 | 1.1765 | 7 | 1.7647 | 5 | 36.7647 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Solar Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 4.031 | -5.8995 | 1.5452 | 2.3711 | -16.3159 | 10 | 2.3529 | 10 | 2.3529 | 16 | 4.4118 | 4.5 | 59.6765 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5
Solar DHW | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 12.553 | -0.93376 | 9.177 | 10.2986 | 191.5874 | 4 | 4.1176 | 4 | 4.1176 | 4 | 0.88235 | 5 | 75.2941 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
DB Economizer | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -0.056498 | 21.9047 | 5.4408 | 3.6145 | 0.19811 | 7 | 3.2353 | 7 | 3.2353 | 15 | 4.1176 | 5 | 72.6471 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
COP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 4.9935 | 1.25 | 0.83469 | 7.5426 | 11 | 2.0588 | 11 | 2.0588 | 10 | 2.6471 | 5 | 51.7647 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Retro-commissioning | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 7.3797 | 5.5047 | 6.9103 | 7.0663 | 14.3405 | 6 | 3.5294 | 6 | 3.5294 | 9 | 2.3529 | 5 | 71.4706 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 18 |  | 18 |  | 18 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
| 4B-Dormitory | [12 empty] | 4B-Dormitory | [12 empty] | 4B-Dormitory | [12 empty] | 4B-Dormitory
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 10000 | 9 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471 | 1.4874 | 0.021825 | 1.1757 | 1.2827 | 1922.1821 | 7 | 2.5 | 7 | 3.2353 | 8 | 2.1875 | 5 | 61.7096 | 1.8674 | 0.031987 | 1.5115 | 1.6356 | 1361.0512 | 6 | 2.7273 | 6 | 3.5294 | 8 | 2.1875 | 5 | 65.3593 | 3.1445 | 0.043579 | 2.591 | 2.7863 | 733.4646 | 6 | 2.7273 | 5 | 3.8235 | 8 | 2.1875 | 5 | 67.4181
Roof | 1.6648 | -0.0014558 | 1.2791 | 1.4094 | 10000 | 5 | 2.5 | 5 | 3.8235 | 1 | 0 | 5 | 59.2647 | 3.3008 | 0.0043649 | 2.5996 | 2.8402 | 581.5929 | 6 | 2.9167 | 5 | 3.8235 | 9 | 2.5 | 5 | 69.6814 | 5.1878 | 0.0014539 | 4.1822 | 4.5327 | 345.585 | 4 | 3.6364 | 4 | 4.1176 | 9 | 2.5 | 5 | 76.7781 | 4.8353 | -0.0014526 | 3.972 | 4.2766 | 186.2343 | 4 | 3.6364 | 4 | 4.1176 | 9 | 2.5 | 5 | 76.7781
Windows | 0 | 0 | 0 | 0 | 10000 | 9 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471 | 0.46502 | 0.0043649 | 0.36704 | 0.40067 | 4545.3818 | 10 | 1.25 | 9 | 2.6471 | 7 | 1.875 | 5 | 47.9044 | 1.1753 | 0.011631 | 0.94971 | 1.0283 | 1601.1016 | 7 | 2.2727 | 7 | 3.2353 | 7 | 1.875 | 5 | 59.1812 | 2.0582 | 0.021789 | 1.6947 | 1.8229 | 825.5512 | 7 | 2.2727 | 7 | 3.2353 | 7 | 1.875 | 5 | 59.1812
Air tightness | 0 | 0 | 0 | 0 | 10000 | 9 | 0 | 7 | 3.2353 | 1 | 0 | 4 | 34.6471 | 6.8299 | 0.043649 | 5.3864 | 5.8818 | 121.0611 | 3 | 4.1667 | 3 | 4.4118 | 10 | 2.8125 | 4 | 80.4865 | 12.2181 | 0.087236 | 9.8661 | 10.6859 | 66.2702 | 1 | 5 | 1 | 5 | 10 | 2.8125 | 4 | 90.4375 | 18.4487 | 0.13945 | 15.1806 | 16.3336 | 39.6269 | 1 | 5 | 1 | 5 | 10 | 2.8125 | 4 | 90.4375
T reduction (2 DegC) | 6.5199 | 0.020382 | 5.0155 | 5.5236 | 40.5239 | 3 | 3.75 | 3 | 4.4118 | 13 | 3.5294 | 4.375 | 80.8456 | 6.2155 | 0.026189 | 4.899 | 5.3508 | 38.0725 | 4 | 3.75 | 4 | 4.1176 | 12 | 3.4375 | 4.375 | 78.511 | 5.9166 | 0.029079 | 4.7751 | 5.1729 | 35.5738 | 3 | 4.0909 | 3 | 4.4118 | 12 | 3.4375 | 4.375 | 82.9562 | 5.6881 | 0.029052 | 4.678 | 5.0344 | 33.4085 | 3 | 4.0909 | 3 | 4.4118 | 11 | 3.125 | 4.375 | 82.0187
T set back | 0 | 0 | 0 | 0 | 10000 | 9 | 0 | 7 | 3.2353 | 1 | 0 | 4.75 | 36.8971 | 0 | 0 | 0 | 0 | 10000 | 13 | 0 | 11 | 2.0588 | 1 | 0 | 4.75 | 28.6618 | 0 | 0 | 0 | 0 | 10000 | 12 | 0 | 10 | 2.3529 | 1 | 0 | 4.75 | 30.7206 | 0 | 0 | 0 | 0 | 10000 | 12 | 0 | 10 | 2.3529 | 1 | 0 | 4.75 | 30.7206
Lighting (30%) | -2.2011 | 11.4196 | 0.95161 | -0.11324 | 22.4748 | 7 | 1.25 | 18 | 0 | 15 | 4.1176 | 4.75 | 35.3529 | -2.0165 | 11.4157 | 0.84054 | -0.13994 | 22.5411 | 9 | 1.6667 | 18 | 0 | 14 | 4.0625 | 4.75 | 38.1042 | -1.8254 | 11.4046 | 0.7397 | -0.1543 | 22.6078 | 9 | 1.3636 | 18 | 0 | 14 | 4.0625 | 4.75 | 35.983 | -1.6712 | 11.3944 | 0.66092 | -0.16192 | 22.6581 | 9 | 1.3636 | 18 | 0 | 14 | 4.0625 | 4.75 | 35.983
Occupancy Sensors (Lights/Plug Loads) | 0 | 4.5178 | 1.0457 | 0.6925 | 21.2906 | 6 | 1.875 | 6 | 3.5294 | 16 | 4.4118 | 4.75 | 65.3162 | 0 | 4.5142 | 0.96018 | 0.63067 | 21.2949 | 8 | 2.0833 | 8 | 2.9412 | 15 | 4.375 | 4.75 | 62.5466 | 0 | 4.5096 | 0.87435 | 0.56962 | 21.3014 | 8 | 1.8182 | 8 | 2.9412 | 15 | 4.375 | 4.75 | 60.6905 | 0 | 4.4989 | 0.80302 | 0.51969 | 21.333 | 8 | 1.8182 | 8 | 2.9412 | 15 | 4.375 | 4.75 | 60.6905
HRV | 0 | 0 | 0 | 0 | 10000 | 9 | 0 | 7 | 3.2353 | 1 | 0 | 4.75 | 36.8971 | 0 | 0 | 0 | 0 | 10000 | 13 | 0 | 11 | 2.0588 | 1 | 0 | 4.75 | 28.6618 | 0 | 0 | 0 | 0 | 10000 | 12 | 0 | 10 | 2.3529 | 1 | 0 | 4.75 | 30.7206 | 0 | 0 | 0 | 0 | 10000 | 12 | 0 | 10 | 2.3529 | 1 | 0 | 4.75 | 30.7206
DCV | 9.9996 | 0 | 7.6851 | 8.4669 | 45.4247 | 2 | 4.375 | 2 | 4.7059 | 12 | 3.2353 | 4.375 | 86.3971 | 10.0022 | 0 | 7.8747 | 8.6048 | 40.7138 | 2 | 4.5833 | 2 | 4.7059 | 11 | 3.125 | 4.375 | 87.5245 | 0 | 0 | 0 | 0 | 36.2286 | 12 | 0 | 10 | 2.3529 | 11 | 3.125 | 4.375 | 38.9706 | 0 | 0 | 0 | 0 | 32.6991 | 12 | 0 | 10 | 2.3529 | 12 | 3.4375 | 4.375 | 39.9081
Cold Deck Reset | 0 | 0 | 0 | 0 | 10000 | 9 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471 | 0 | 0 | 0 | 0 | 10000 | 13 | 0 | 11 | 2.0588 | 1 | 0 | 5 | 29.4118 | 0 | 0 | 0 | 0 | 10000 | 12 | 0 | 10 | 2.3529 | 1 | 0 | 5 | 31.4706 | 0 | 0 | 0 | 0 | 10000 | 12 | 0 | 10 | 2.3529 | 1 | 0 | 5 | 31.4706
VSD | -0.1876 | 0.66442 | 0.0096118 | -0.056998 | 0 | 8 | 0.625 | 17 | 0.29412 | 18 | 5 | 5 | 36.4338 | -0.17813 | 0.70328 | 0.0093494 | -0.054989 | 0 | 12 | 0.41667 | 17 | 0.29412 | 17 | 5 | 5 | 34.9755 | -0.16879 | 0.74854 | 0.0090707 | -0.052916 | 0 | 10 | 0.90909 | 17 | 0.29412 | 17 | 5 | 5 | 38.4225 | -0.16431 | 0.80665 | 0.0089989 | -0.05215 | 0 | 11 | 0.45455 | 17 | 0.29412 | 17 | 5 | 5 | 35.2406
VSP | 0 | 0 | 0 | 0 | 10000 | 9 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471 | 0 | 0 | 0 | 0 | 10000 | 13 | 0 | 11 | 2.0588 | 1 | 0 | 5 | 29.4118 | 0 | 0 | 0 | 0 | 10000 | 12 | 0 | 10 | 2.3529 | 1 | 0 | 5 | 31.4706 | 0 | 0 | 0 | 0 | 10000 | 12 | 0 | 10 | 2.3529 | 1 | 0 | 5 | 31.4706
Solar Wall | 0 | 0 | 0 | 0 | 10000 | 9 | 0 | 7 | 3.2353 | 1 | 0 | 4.5 | 36.1471 | 0 | 0 | 0 | 0 | 10000 | 13 | 0 | 11 | 2.0588 | 1 | 0 | 4.5 | 27.9118 | 0 | 0 | 0 | 0 | 10000 | 12 | 0 | 10 | 2.3529 | 1 | 0 | 4.5 | 29.9706 | 0 | 0 | 0 | 0 | 10000 | 12 | 0 | 10 | 2.3529 | 1 | 0 | 4.5 | 29.9706
Solar DHW | 0 | 20.1649 | 4.6674 | 3.0909 | 30.9795 | 4 | 3.125 | 4 | 4.1176 | 14 | 3.8235 | 5 | 77.1691 | 0 | 20.1519 | 4.2864 | 2.8154 | 30.9809 | 5 | 3.3333 | 6 | 3.5294 | 13 | 3.75 | 5 | 74.2892 | 0 | 20.1362 | 3.9041 | 2.5435 | 30.9831 | 5 | 3.1818 | 5 | 3.8235 | 13 | 3.75 | 5 | 75.2874 | 0 | 20.1235 | 3.5919 | 2.3246 | 30.9747 | 5 | 3.1818 | 6 | 3.5294 | 13 | 3.75 | 5 | 73.2286
DB Economizer | 0 | 0 | 0 | 0 | 10000 | 9 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471 | 0 | 0 | 0 | 0 | 10000 | 13 | 0 | 11 | 2.0588 | 1 | 0 | 5 | 29.4118 | 0 | 0 | 0 | 0 | 10000 | 12 | 0 | 10 | 2.3529 | 1 | 0 | 5 | 31.4706 | 0 | 0 | 0 | 0 | 10000 | 12 | 0 | 10 | 2.3529 | 1 | 0 | 5 | 31.4706
COP | 0 | 0 | 0 | 0 | 10000 | 9 | 0 | 7 | 3.2353 | 1 | 0 | 5 | 37.6471 | 0 | 0.12934 | 0.02751 | 0.018069 | 0 | 11 | 0.83333 | 10 | 2.3529 | 17 | 5 | 5 | 52.3039 | 0 | 0.043131 | 0.0083624 | 0.0054479 | 0 | 11 | 0.45455 | 9 | 2.6471 | 17 | 5 | 5 | 51.7112 | 0 | 0.060594 | 0.010816 | 0.0069996 | 0 | 10 | 0.90909 | 9 | 2.6471 | 17 | 5 | 5 | 54.893
Retro-commissioning | 10.0726 | 0.19092 | 7.7854 | 8.5579 | 17.9185 | 1 | 5 | 1 | 5 | 17 | 4.7059 | 5 | 99.1177 | 10.0742 | 0.1899 | 7.9718 | 8.6933 | 16.1098 | 1 | 5 | 1 | 5 | 16 | 4.6875 | 5 | 99.0625 | 10.0726 | 0.20049 | 8.1585 | 8.8256 | 14.3552 | 2 | 4.5455 | 2 | 4.7059 | 16 | 4.6875 | 5 | 93.8219 | 10.073 | 0.20571 | 8.3118 | 8.9332 | 12.9778 | 2 | 4.5455 | 2 | 4.7059 | 16 | 4.6875 | 5 | 93.8219
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 |  |  |  | 1.8128 | 1.9581 | 1.841 | 1.8312 |  | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 9 |  | 18 |  | 18 | [8 empty] | 13 |  | 18 |  | 17 |  |  |  | 0 | 0.011631 | 0.0090707 | 0 |  | 12 |  | 18 |  | 17 | [8 empty] | 12 |  | 18 |  | 17
| 4C-Barracks | [12 empty] | 4C-Barracks | [12 empty] | 4C-Barracks | [12 empty] | 4C-Barracks
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 5.0938 | 2.462 | 4.539 | 4.7297 | 605.3574 | 9 | 2.1429 | 9 | 2.6471 | 6 | 1.4706 | 5 | 52.9412 | 4.5462 | 2.746 | 4.2203 | 4.3351 | 459.7229 | 9 | 2.1429 | 9 | 2.6471 | 6 | 1.4706 | 5 | 52.9412 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Roof | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 10.0913 | 4.6887 | 8.9524 | 9.3438 | 207.5449 | 6 | 3.2143 | 6 | 3.5294 | 7 | 1.7647 | 5 | 67.5 | 23.4016 | 13.5867 | 21.6245 | 22.2502 | 50.9233 | 1 | 5 | 1 | 5 | 8 | 2.0588 | 5 | 91.1765 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Windows | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0.97185 | 0.40772 | 0.85292 | 0.8938 | 937.9654 | 14 | 0.35714 | 12 | 1.7647 | 5 | 1.1765 | 5 | 33.3824 | 0.60425 | 0.31234 | 0.55139 | 0.57 | 1028.9432 | 14 | 0.35714 | 12 | 1.7647 | 5 | 1.1765 | 5 | 33.3824 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Air tightness | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 17.0912 | 6.6959 | 14.8997 | 15.6529 | 57.5611 | 1 | 5 | 1 | 5 | 9 | 2.3529 | 4 | 89.0588 | 23.6577 | 11.114 | 21.3865 | 22.1862 | 31.8365 | 2 | 4.6429 | 2 | 4.7059 | 9 | 2.3529 | 4 | 84.5 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12
T reduction (2 DegC) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 14.473 | 4.3437 | 12.3376 | 13.0716 | 2.9712 | 2 | 4.6429 | 2 | 4.7059 | 15 | 4.1176 | 4.375 | 90.9191 | 13.5035 | 5.6611 | 12.0835 | 12.5835 | 2.0942 | 3 | 4.2857 | 3 | 4.4118 | 15 | 4.1176 | 4.375 | 86.3603 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125
T set back | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 10.8872 | 4.8926 | 9.6235 | 10.0578 | 3.4592 | 4 | 3.9286 | 4 | 4.1176 | 14 | 3.8235 | 4.75 | 82.0441 | 10.0247 | 6.0645 | 9.3077 | 9.5602 | 2.4749 | 4 | 3.9286 | 4 | 4.1176 | 14 | 3.8235 | 4.75 | 82.0441 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
Lighting (30%) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | -2.7354 | 16.2145 | 1.2595 | -0.11359 | 20.8633 | 12 | 1.0714 | 17 | 0.29412 | 10 | 2.6471 | 4.75 | 31.75 | -1.9652 | 13.4565 | 0.82709 | -0.15612 | 21.0036 | 13 | 0.71429 | 17 | 0.29412 | 10 | 2.6471 | 4.75 | 29.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 6.5548 | 1.3819 | 0.9069 | 3.749 | 10 | 1.7857 | 11 | 2.0588 | 13 | 3.5294 | 4.75 | 51.75 | 0 | 5.4529 | 0.98732 | 0.63967 | 3.7401 | 11 | 1.4286 | 11 | 2.0588 | 13 | 3.5294 | 4.75 | 49.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
HRV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 10.5605 | 0 | 8.3342 | 9.0994 | 0 | 7 | 2.8571 | 7 | 3.2353 | 16 | 4.4118 | 4.75 | 70.1324 | 7.3718 | 0 | 6.037 | 6.507 | 0 | 8 | 2.5 | 8 | 2.9412 | 16 | 4.4118 | 4.75 | 65.5735 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
DCV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 12.3115 | 0 | 9.716 | 10.6081 | 8.3606 | 3 | 4.2857 | 3 | 4.4118 | 11 | 2.9412 | 4.375 | 82.8309 | 8.4249 | 0 | 6.8995 | 7.4366 | 8.392 | 6 | 3.2143 | 6 | 3.5294 | 11 | 2.9412 | 4.375 | 69.1544 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125
Cold Deck Reset | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 15 | 0 | 13 | 1.4706 | 1 | 0 | 5 | 25.2941 | 0 | 0 | 0 | 0 | 10000 | 15 | 0 | 13 | 1.4706 | 1 | 0 | 5 | 25.2941 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
VSD | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -5.577 | 25.8878 | 1.0563 | -1.2237 | 0 | 13 | 0.71429 | 18 | 0 | 16 | 4.4118 | 5 | 33.2353 | -6.1049 | 34.2385 | 1.1999 | -1.3722 | 0 | 10 | 1.7857 | 18 | 0 | 16 | 4.4118 | 5 | 40.7353 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
VSP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 15 | 0 | 13 | 1.4706 | 1 | 0 | 5 | 25.2941 | 0 | 0 | 0 | 0 | 10000 | 15 | 0 | 13 | 1.4706 | 1 | 0 | 5 | 25.2941 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Solar Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 3.0747 | -5.0964 | 1.3521 | 1.9442 | -35.9185 | 11 | 1.4286 | 10 | 2.3529 | 18 | 5 | 4.5 | 54.9706 | 2.112 | -4.2296 | 0.96376 | 1.3681 | -35.9185 | 12 | 1.0714 | 10 | 2.3529 | 18 | 5 | 4.5 | 52.4706 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5
Solar DHW | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 11.7879 | -1.3486 | 9.0185 | 9.9704 | 173.602 | 5 | 3.5714 | 5 | 3.8235 | 8 | 2.0588 | 5 | 72.9412 | 8.0969 | -1.1192 | 6.4282 | 7.0158 | 173.602 | 7 | 2.8571 | 7 | 3.2353 | 7 | 1.7647 | 5 | 62.9412 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
DB Economizer | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 15 | 0 | 13 | 1.4706 | 1 | 0 | 5 | 25.2941 | 0 | 0 | 0 | 0 | 10000 | 15 | 0 | 13 | 1.4706 | 1 | 0 | 5 | 25.2941 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
COP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 15 | 0 | 13 | 1.4706 | 1 | 0 | 5 | 25.2941 | 0 | 0 | 0 | 0 | 10000 | 15 | 0 | 13 | 1.4706 | 1 | 0 | 5 | 25.2941 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Retro-commissioning | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 7.6114 | 3.4656 | 6.7374 | 7.0378 | 7.1932 | 8 | 2.5 | 8 | 2.9412 | 12 | 3.2353 | 5 | 62.7941 | 8.3588 | 4.5809 | 7.6747 | 7.9156 | 4.5055 | 5 | 3.5714 | 5 | 3.8235 | 12 | 3.2353 | 5 | 76.4706 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 15 |  | 18 |  | 18 | [8 empty] | 15 |  | 18 |  | 18 | [8 empty] | 1 |  | 1 |  | 1
| 4D-Accomodation Building | [12 empty] | 4D-Accomodation Building | [12 empty] | 4D-Accomodation Building | [12 empty] | 4D-Accomodation Building
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 5.6507 | 4.2184 | 5.4332 | 5.5115 | 529.4675 | 9 | 2.6471 | 9 | 2.6471 | 4 | 0.88235 | 5 | 54.7059 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Roof | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 2.9378 | 2.2537 | 2.834 | 2.8714 | 466.9044 | 10 | 2.3529 | 10 | 2.3529 | 5 | 1.1765 | 5 | 51.4706 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Windows | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 1.1508 | 0.57787 | 1.0638 | 1.0952 | 877.0944 | 11 | 2.0588 | 11 | 2.0588 | 2 | 0.29412 | 5 | 44.7059 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Air tightness | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 13.8228 | 2.4126 | 12.0904 | 12.7143 | 67.3468 | 2 | 4.7059 | 1 | 5 | 11 | 2.9412 | 4 | 88.7647 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12
T reduction (2 DegC) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 13.7969 | -7.989 | 10.4891 | 11.6805 | 62.464 | 3 | 4.4118 | 2 | 4.7059 | 13 | 3.5294 | 4.375 | 87.5368 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125
T set back | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 11.0686 | -7.989 | 21.2305 | 9.2172 | 105.5627 | 1 | 5 | 6 | 3.5294 | 9 | 2.3529 | 4.75 | 81.0147 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
Lighting (30%) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | -1.5077 | 14.7212 | 0.95635 | 0.068911 | 21.0308 | 12 | 1.7647 | 16 | 0.58824 | 17 | 4.7059 | 4.75 | 44.8382 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 5.3453 | 0.81158 | 0.51929 | 47.6077 | 13 | 1.4706 | 12 | 1.7647 | 15 | 4.1176 | 4.75 | 49.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
HRV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 9.76 | -1.5025 | 8.05 | 8.6659 | 730.6806 | 7 | 3.2353 | 7 | 3.2353 | 3 | 0.58824 | 4.75 | 61.3088 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
DCV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 10.81 | -0.10113 | 9.1533 | 9.75 | 66.6318 | 6 | 3.5294 | 5 | 3.8235 | 12 | 3.2353 | 4.375 | 74.3015 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125
Cold Deck Reset | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 3.0049 | 0.45624 | 0.29192 | 119.4271 | 15 | 0.88235 | 13 | 1.4706 | 8 | 2.0588 | 5 | 37.6471 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
VSD | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -3.8603 | 26.7403 | 0.78581 | -0.88751 | 8.6824 | 14 | 1.1765 | 18 | 0 | 18 | 5 | 5 | 38.2353 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
VSP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 18 | 0 | 17 | 0.29412 | 1 | 0 | 5 | 17.0588 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Solar Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 12.9073 | -9.7804 | 9.4626 | 10.7032 | 87.8285 | 4 | 4.1176 | 3 | 4.4118 | 10 | 2.6471 | 4.5 | 81.1471 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5
Solar DHW | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 11.2729 | -2.2248 | 9.2235 | 9.9616 | 172.7972 | 5 | 3.8235 | 4 | 4.1176 | 7 | 1.7647 | 5 | 75.8824 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
DB Economizer | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -0.13189 | 2.846 | 0.32025 | 0.15741 | 53.2407 | 16 | 0.58824 | 14 | 1.1765 | 14 | 3.8235 | 5 | 38.8235 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
COP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 1.3869 | 0.21057 | 0.13473 | 351.5583 | 17 | 0.29412 | 15 | 0.88235 | 6 | 1.4706 | 5 | 27.6471 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Retro-commissioning | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 7.9652 | 4.6952 | 7.4687 | 7.6476 | 29.1795 | 8 | 2.9412 | 8 | 2.9412 | 16 | 4.4118 | 5 | 69.4118 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
`
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 18 |  | 18 |  | 18 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
| 5A-Gym and Fitness Centre | [12 empty] | 5A-Gym and Fitness Centre | [12 empty] | 5A-Gym and Fitness Centre | [12 empty] | 5A-Gym and Fitness Centre
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 6.5914 | 1.4953 | 4.6143 | 5.1854 | 395.6019 | 8 | 2.9412 | 8 | 2.9412 | 3 | 0.58824 | 5 | 57.9412 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 6.076 | 2.4279 | 5.0981 | 5.4178 | 197.5529 | 8 | 2.9412 | 8 | 2.9412 | 3 | 0.58824 | 5 | 57.9412
Roof | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 19.0001 | 5.0793 | 13.5993 | 15.1593 | 134.3125 | 2 | 4.7059 | 2 | 4.7059 | 5 | 1.1765 | 5 | 84.4118 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 30.1449 | 13.6693 | 25.7287 | 27.1726 | 33.2475 | 2 | 4.7059 | 2 | 4.7059 | 6 | 1.4706 | 5 | 85.2941
Windows | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 1.2083 | 0.1598 | 0.80152 | 0.91902 | 759.6988 | 16 | 0.58824 | 13 | 1.4706 | 1 | 0 | 5 | 29.4118 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0.95283 | 0.24737 | 0.76373 | 0.82556 | 429.7689 | 15 | 0.88235 | 12 | 1.7647 | 2 | 0.29412 | 5 | 34.4118
Air tightness | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 24.4772 | 4.2347 | 16.6239 | 18.8923 | 23.4144 | 1 | 5 | 1 | 5 | 8 | 2.0588 | 4 | 88.1765 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 38.8949 | 11.9835 | 31.6814 | 34.0398 | 7.3781 | 1 | 5 | 1 | 5 | 11 | 2.9412 | 4 | 90.8235
T reduction (2 DegC) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 20.5123 | 0.84465 | 12.8819 | 15.0859 | 3.0852 | 3 | 4.4118 | 3 | 4.4118 | 16 | 4.4118 | 4.375 | 88.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 16.4665 | 0.79707 | 12.2664 | 13.6396 | 1.8504 | 3 | 4.4118 | 3 | 4.4118 | 16 | 4.4118 | 4.375 | 88.125
T set back | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 14.4129 | 0.73051 | 9.1046 | 10.6379 | 4.2774 | 4 | 4.1176 | 4 | 4.1176 | 14 | 3.8235 | 4.75 | 83.3676 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 13.4839 | 0.70545 | 10.0587 | 11.1785 | 2.245 | 6 | 3.5294 | 5 | 3.8235 | 15 | 4.1176 | 4.75 | 78.0735
Lighting (30%) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | -9.6664 | 21.5272 | 2.4356 | -1.0601 | 15.6506 | 10 | 2.3529 | 17 | 0.29412 | 9 | 2.3529 | 4.75 | 39.8382 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | -4.838 | 11.7728 | -0.38555 | -1.8412 | 25.4378 | 18 | 0 | 18 | 0 | 7 | 1.7647 | 4.75 | 19.5441
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 7.0882 | 2.75 | 1.9557 | 1.7367 | 9 | 2.6471 | 10 | 2.3529 | 18 | 5 | 4.75 | 64.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 5.6894 | 1.525 | 1.0264 | 1.7367 | 10 | 2.3529 | 11 | 2.0588 | 17 | 4.7059 | 4.75 | 59.25
HRV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 10.1657 | -0.13697 | 6.1686 | 7.3232 | 538.6913 | 7 | 3.2353 | 7 | 3.2353 | 2 | 0.29412 | 4.75 | 60.4265 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 4.8849 | -0.045809 | 3.5633 | 3.9954 | 506.3869 | 9 | 2.6471 | 9 | 2.6471 | 1 | 0 | 4.75 | 51.3088
DCV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 13.8776 | 0 | 8.4936 | 10.0487 | 8.8167 | 5 | 3.8235 | 5 | 3.8235 | 11 | 2.9412 | 4.375 | 75.4779 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 14.4654 | 0 | 10.588 | 11.8557 | 3.9221 | 5 | 3.8235 | 4 | 4.1176 | 12 | 3.2353 | 4.375 | 78.4191
Cold Deck Reset | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 3.0019 | 1.1646 | 0.82824 | 10.0088 | 13 | 1.4706 | 14 | 1.1765 | 10 | 2.6471 | 5 | 41.4706 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 3.005 | 0.80548 | 0.54214 | 8.0254 | 14 | 1.1765 | 16 | 0.58824 | 10 | 2.6471 | 5 | 35.2941
VSD | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -7.9878 | 13.443 | 0.32656 | -2.075 | 1.7546 | 18 | 0 | 18 | 0 | 17 | 4.7059 | 5 | 29.1176 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 7.5876 | 22.1029 | 11.4783 | 10.2063 | 0.58494 | 4 | 4.1176 | 6 | 3.5294 | 18 | 5 | 5 | 83.5294
VSP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 2.922 | 1.1336 | 0.80619 | 8.0627 | 14 | 1.1765 | 15 | 0.88235 | 12 | 3.2353 | 5 | 39.1176 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 2.3454 | 0.62867 | 0.42313 | 8.0627 | 16 | 0.58824 | 17 | 0.29412 | 9 | 2.3529 | 5 | 28.2353
Solar Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 4.3196 | -0.66202 | 2.3869 | 2.9452 | 72.5488 | 11 | 2.0588 | 9 | 2.6471 | 6 | 1.4706 | 4.5 | 50.8529 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 2.0015 | -0.53138 | 1.3226 | 1.5445 | 72.6571 | 11 | 2.0588 | 10 | 2.3529 | 5 | 1.1765 | 4.5 | 47.9118
Solar DHW | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 1.5413 | -0.057071 | 0.92117 | 1.1003 | 139.8695 | 15 | 0.88235 | 11 | 2.0588 | 4 | 0.88235 | 5 | 38.2353 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0.71314 | -0.045809 | 0.50971 | 0.57622 | 140.2121 | 17 | 0.29412 | 15 | 0.88235 | 4 | 0.88235 | 5 | 25.8824
DB Economizer | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 3.6982 | 1.4348 | 1.0203 | 3.2518 | 12 | 1.7647 | 12 | 1.7647 | 15 | 4.1176 | 5 | 52.0588 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 4.7678e-15 | 3.2066 | 0.85951 | 0.5785 | 3.0103 | 13 | 1.4706 | 14 | 1.1765 | 13 | 3.5294 | 5 | 44.1176
COP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 1.0387 | 0.40298 | 0.28658 | 23.9825 | 17 | 0.29412 | 16 | 0.58824 | 7 | 1.7647 | 5 | 26.4706 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 3.3074 | 0.88652 | 0.59668 | 19.5979 | 12 | 1.7647 | 13 | 1.4706 | 8 | 2.0588 | 5 | 43.8235
Retro-commissioning | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 9.7028 | 2.9106 | 7.0677 | 7.8288 | 5.0414 | 6 | 3.5294 | 6 | 3.5294 | 13 | 3.5294 | 5 | 75 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 9.8623 | 4.3152 | 8.3754 | 8.8615 | 2.4904 | 7 | 3.2353 | 7 | 3.2353 | 14 | 3.8235 | 5 | 71.7647
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 18 |  | 18 |  | 18 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 18 |  | 18 |  | 18
| 5C-Sports Centre | [12 empty] | 5C-Sports Centre | [12 empty] | 5C-Sports Centre | [12 empty] | 5C-Sports Centre
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 2.344 | 0.37519 | 1.9349 | 2.0759 | 965.3597 | 10 | 2.3529 | 9 | 2.6471 | 2 | 0.29412 | 5 | 50.8824 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Roof | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 7.1187 | 0.65107 | 5.775 | 6.238 | 261.8832 | 6 | 3.5294 | 6 | 3.5294 | 5 | 1.1765 | 5 | 67.9412 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Windows | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 1.0852 | 0.077246 | 0.87577 | 0.94792 | 553.3805 | 12 | 1.7647 | 11 | 2.0588 | 3 | 0.58824 | 5 | 43.5294 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Air tightness | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 10.4031 | 0.55175 | 8.3565 | 9.0617 | 35.7939 | 3 | 4.4118 | 3 | 4.4118 | 10 | 2.6471 | 4 | 81.7059 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12
T reduction (2 DegC) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 9.289 | 0.43037 | 7.4486 | 8.0828 | 3.3563 | 5 | 3.8235 | 5 | 3.8235 | 15 | 4.1176 | 4.375 | 79.0074 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125
T set back | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 5.6863 | 0.14346 | 4.5347 | 4.9315 | 5.629 | 7 | 3.2353 | 7 | 3.2353 | 13 | 3.5294 | 4.75 | 70.1324 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
Lighting (30%) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | -2.9951 | 21.0881 | 2.0083 | 0.28419 | 15.0629 | 9 | 2.6471 | 14 | 1.1765 | 11 | 2.9412 | 4.75 | 49.8382 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 8.8943 | 1.8478 | 1.2111 | 1.5469 | 11 | 2.0588 | 10 | 2.3529 | 17 | 4.7059 | 4.75 | 59.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
HRV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 17.7272 | -0.25381 | 13.9916 | 15.2789 | 44.1731 | 2 | 4.7059 | 2 | 4.7059 | 9 | 2.3529 | 4.75 | 87.1912 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
DCV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 39.2135 | -0.47451 | 30.9682 | 33.8094 | 1.4659 | 1 | 5 | 1 | 5 | 18 | 5 | 4.375 | 98.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125
Cold Deck Reset | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 3.0015 | 0.62358 | 0.4087 | 11.6359 | 13 | 1.4706 | 12 | 1.7647 | 12 | 3.2353 | 5 | 47.3529 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
VSD | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -0.85994 | 5.8991 | 0.54428 | 0.060403 | 2.2855 | 14 | 1.1765 | 16 | 0.58824 | 16 | 4.4118 | 5 | 40.5882 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
VSP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0.629 | 0.13068 | 0.085647 | 122.7059 | 16 | 0.58824 | 15 | 0.88235 | 7 | 1.7647 | 5 | 30.5882 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Solar Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 5.4605 | -2.5381 | 3.7988 | 4.3714 | 75.4685 | 8 | 2.9412 | 8 | 2.9412 | 8 | 2.0588 | 4.5 | 60.8529 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5
Solar DHW | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0.39934 | -0.033105 | 0.3095 | 0.34046 | 142.8232 | 15 | 0.88235 | 13 | 1.4706 | 6 | 1.4706 | 5 | 35.8824 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
DB Economizer | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0.04414 | 0.0091703 | 0.0060103 | 394.6642 | 17 | 0.29412 | 17 | 0.29412 | 4 | 0.88235 | 5 | 21.7647 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
COP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 18 | 0 | 18 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Retro-commissioning | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 9.6768 | 1.1256 | 7.9002 | 8.5124 | 5.3338 | 4 | 4.1176 | 4 | 4.1176 | 14 | 3.8235 | 5 | 84.1176 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 18 |  | 18 |  | 18 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
| 5D-Sports and Arena | [12 empty] | 5D-Sports and Arena | [12 empty] | 5D-Sports and Arena | [12 empty] | 5D-Sports and Arena
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Roof | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Windows | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Air tightness | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12
T reduction (2 DegC) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125
T set back | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
Lighting (30%) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
HRV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
DCV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125
Cold Deck Reset | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
VSD | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
VSP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Solar Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5
Solar DHW | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
DB Economizer | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
COP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Retro-commissioning | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
| 6A-Office Building | [12 empty] | 6A-Office Building | [12 empty] | 6A-Office Building | [12 empty] | 6A-Office Building
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0
Wall | 0.040425 | 0 | 0.031967 | 0.034878 | 0 | 7 | 3.2353 | 7 | 3.2353 | 16 | 0 | 5 | 60.2941 | 0.0025853 | 0 | 0.0020821 | 0.0022574 | 754.0448 | 10 | 0.5 | 8 | 2.9412 | 7 | 1.875 | 5 | 44.7132 | -0.0024778 | 0 | -0.0020352 | -0.0021913 | 484.4405 | 17 | 0.29412 | 17 | 0.29412 | 8 | 2.1875 | 5 | 25.6801 | -0.0024778 | 0 | -0.0020352 | -0.0021913 | 10000 | 17 | 0.29412 | 17 | 0.29412 | 1 | 0 | 5 | 19.1176
Roof | -0.028875 | 0 | -0.022834 | -0.024913 | 0 | 18 | 0 | 18 | 0 | 16 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 510.1278 | 11 | 0 | 9 | 2.6471 | 8 | 2.1875 | 5 | 40.0919 | 0 | 0 | 0 | 0 | 363.4191 | 8 | 2.9412 | 8 | 2.9412 | 9 | 2.5 | 5 | 63.6765 | 0 | 0 | 0 | 0 | 10000 | 9 | 2.6471 | 9 | 2.6471 | 1 | 0 | 5 | 52.0588
Windows | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 5 | 5 | 71.1765 | 0 | 0 | 0 | 0 | 10000 | 11 | 0 | 9 | 2.6471 | 1 | 0 | 5 | 33.5294 | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 0 | 5 | 56.1765 | 0 | 0 | 0 | 0 | 10000 | 9 | 2.6471 | 9 | 2.6471 | 1 | 0 | 5 | 52.0588
Air tightness | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 5 | 4 | 68.1765 | 3.9504 | 0.39576 | 3.2584 | 3.4994 | 79.6063 | 3 | 4 | 3 | 4.4118 | 9 | 2.5 | 4 | 78.3824 | 10.7733 | 1.5041 | 9.1177 | 9.7018 | 29.6319 | 2 | 4.7059 | 2 | 4.7059 | 13 | 3.75 | 4 | 89.1324 | 10.7733 | 1.5041 | 9.1177 | 9.7018 | 29.6319 | 2 | 4.7059 | 2 | 4.7059 | 13 | 3.75 | 4 | 89.1324
T reduction (2 DegC) | 0.81428 | 0 | 0.64391 | 0.70254 | 124.404 | 6 | 3.5294 | 4 | 4.1176 | 10 | 2 | 4.375 | 72.6544 | 2.88 | -0.14975 | 2.2903 | 2.4957 | 33.5919 | 4 | 3.5 | 4 | 4.1176 | 10 | 2.8125 | 4.375 | 74.886 | 0.27999 | 0.045579 | 0.23812 | 0.25289 | 263.9753 | 6 | 3.5294 | 6 | 3.5294 | 10 | 2.8125 | 4.375 | 70.9743 | 0.27999 | 0.045579 | 0.23812 | 0.25289 | 263.9753 | 7 | 3.2353 | 7 | 3.2353 | 10 | 2.8125 | 4.375 | 66.8566
T set back | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 5 | 4.75 | 70.4265 | 0 | 0 | 0 | 0 | 10000 | 11 | 0 | 9 | 2.6471 | 1 | 0 | 4.75 | 32.7794 | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 0 | 4.75 | 55.4265 | 0 | 0 | 0 | 0 | 10000 | 9 | 2.6471 | 9 | 2.6471 | 1 | 0 | 4.75 | 51.3088
Lighting (30%) | -1.9231 | 12.8015 | 1.1577 | 0.097365 | 32.2937 | 4 | 4.1176 | 6 | 3.5294 | 11 | 1.6667 | 4.75 | 72.7794 | -1.8666 | 13.3169 | 1.0889 | 0.059505 | 30.5102 | 5 | 3 | 7 | 3.2353 | 12 | 3.4375 | 4.75 | 68.2096 | -1.9104 | 14.3345 | 0.99115 | -0.032487 | 30.423 | 4 | 4.1176 | 18 | 0 | 12 | 3.4375 | 4.75 | 53.386 | -1.9104 | 14.3345 | 0.99115 | -0.032487 | 30.423 | 5 | 3.8235 | 18 | 0 | 12 | 3.4375 | 4.75 | 51.3272
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 4.1751 | 8 | 2.9412 | 8 | 2.9412 | 14 | 0.66667 | 4.75 | 57.4265 | 0 | 0 | 0 | 0 | 4.0947 | 11 | 0 | 9 | 2.6471 | 14 | 4.0625 | 4.75 | 44.9669 | 0 | 0 | 0 | 0 | 4.3605 | 8 | 2.9412 | 8 | 2.9412 | 15 | 4.375 | 4.75 | 68.5515 | 0 | 0 | 0 | 0 | 10000 | 9 | 2.6471 | 9 | 2.6471 | 1 | 0 | 4.75 | 51.3088
HRV | 15.3298 | 9.4401 | 14.0975 | 14.5216 | 0 | 1 | 5 | 1 | 5 | 16 | 0 | 4.75 | 84.25 | 27.7301 | -7.5944 | 20.8541 | 23.249 | 0 | 1 | 5 | 1 | 5 | 17 | 5 | 4.75 | 99.25 | 27.8823 | -1.3218 | 22.6661 | 24.5063 | 0 | 1 | 5 | 1 | 5 | 17 | 5 | 4.75 | 99.25 | 27.8823 | -1.3218 | 22.6661 | 24.5063 | 0 | 1 | 5 | 1 | 5 | 17 | 5 | 4.75 | 99.25
DCV | 9.9994 | 3.4159 | 8.622 | 9.0961 | 11.9584 | 2 | 4.7059 | 2 | 4.7059 | 13 | 1 | 4.375 | 82.0074 | 10 | 0 | 8.0535 | 8.7315 | 15.5201 | 2 | 4.5 | 2 | 4.7059 | 13 | 3.75 | 4.375 | 88.8162 | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 0 | 4.375 | 54.3015 | 10.0721 | 0 | 8.2731 | 8.9078 | 14.7679 | 3 | 4.4118 | 3 | 4.4118 | 14 | 4.0625 | 4.375 | 87.0772
Cold Deck Reset | 0 | 10.5533 | 2.208 | 1.4481 | 0.88158 | 3 | 4.4118 | 3 | 4.4118 | 15 | 0.33333 | 5 | 77.7647 | 0 | 3.0057 | 0.58506 | 0.38128 | 3.0338 | 7 | 2 | 6 | 3.5294 | 16 | 4.6875 | 5 | 67.7684 | 5.0001 | 3.0082 | 4.6443 | 4.7699 | 1.273 | 3 | 4.4118 | 3 | 4.4118 | 16 | 4.6875 | 5 | 90.8272 | 5.0001 | 3.0082 | 4.6443 | 4.7699 | 1.273 | 4 | 4.1176 | 4 | 4.1176 | 16 | 4.6875 | 5 | 86.7096
VSD | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 5 | 5 | 71.1765 | -0.46019 | 2.5671 | 0.12909 | -0.076158 | 0 | 8 | 1.5 | 17 | 0.29412 | 17 | 5 | 5 | 42.5588 | 3.2434 | -17.0465 | -0.38058 | 0.89793 | 0 | 18 | 0 | 4 | 4.1176 | 17 | 5 | 5 | 58.8235 | 3.2434 | -17.0465 | -0.38058 | 0.89793 | 0 | 18 | 0 | 5 | 3.8235 | 17 | 5 | 5 | 56.7647
VSP | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 5 | 5 | 71.1765 | -0.6515 | 2.8238 | 0.024985 | -0.21064 | 3.9165 | 9 | 1 | 18 | 0 | 15 | 4.375 | 5 | 35.125 | -0.0446 | 1.1964 | 0.17706 | 0.098862 | 8.2418 | 7 | 3.2353 | 7 | 3.2353 | 14 | 4.0625 | 5 | 72.4816 | -0.0446 | 1.1964 | 0.17706 | 0.098862 | 8.2418 | 8 | 2.9412 | 8 | 2.9412 | 15 | 4.375 | 5 | 69.3015
Solar Wall | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 5 | 4.5 | 69.6765 | 0 | 0 | 0 | 0 | 10000 | 11 | 0 | 9 | 2.6471 | 1 | 0 | 4.5 | 32.0294 | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 0 | 4.5 | 54.6765 | 0 | 0 | 0 | 0 | 10000 | 9 | 2.6471 | 9 | 2.6471 | 1 | 0 | 4.5 | 50.5588
Solar DHW | 0 | 4.0162 | 0.84028 | 0.55108 | 31.0361 | 5 | 3.8235 | 5 | 3.8235 | 12 | 1.3333 | 5 | 72.5294 | 0 | 3.9362 | 0.7662 | 0.49933 | 31.0361 | 6 | 2.5 | 5 | 3.8235 | 11 | 3.125 | 5 | 68.6397 | 0 | 4.1933 | 0.74896 | 0.48473 | 31.0361 | 5 | 3.8235 | 5 | 3.8235 | 11 | 3.125 | 5 | 77.9044 | 0 | 4.1933 | 0.74896 | 0.48473 | 31.0361 | 6 | 3.5294 | 6 | 3.5294 | 11 | 3.125 | 5 | 73.7868
DB Economizer | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 5 | 5 | 71.1765 | 0 | 0 | 0 | 0 | 10000 | 11 | 0 | 9 | 2.6471 | 1 | 0 | 5 | 33.5294 | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 0 | 5 | 56.1765 | 0 | 0 | 0 | 0 | 10000 | 9 | 2.6471 | 9 | 2.6471 | 1 | 0 | 5 | 52.0588
COP | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 5 | 5 | 71.1765 | 0 | 0 | 0 | 0 | 10000 | 11 | 0 | 9 | 2.6471 | 1 | 0 | 5 | 33.5294 | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 0 | 5 | 56.1765 | 0 | 0 | 0 | 0 | 10000 | 9 | 2.6471 | 9 | 2.6471 | 1 | 0 | 5 | 52.0588
Retro-commissioning | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 5 | 5 | 71.1765 | 0 | 0 | 0 | 0 | 10000 | 11 | 0 | 9 | 2.6471 | 1 | 0 | 5 | 33.5294 | 0 | 0 | 0 | 0 | 10000 | 8 | 2.9412 | 8 | 2.9412 | 1 | 0 | 5 | 56.1765 | 0 | 0 | 0 | 0 | 10000 | 9 | 2.6471 | 9 | 2.6471 | 1 | 0 | 5 | 52.0588
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 18 |  | 18 |  | 16 | [8 empty] | 11 |  | 18 |  | 17 | [8 empty] | 18 |  | 18 |  | 17 | [8 empty] | 18 |  | 18 |  | 17
| 7A-Dining Hall | [12 empty] | 7A-Dining Hall | [12 empty] | 7A-Dining Hall | [12 empty] | 7A-Dining Hall
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | -7.8019e-15 | 0 | 0 | -6.0556e-15
Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 2.7057 | 0.17939 | 1.8866 | 2.1402 | 366.0848 | 8 | 2.8125 | 7 | 3.2353 | 4 | 0.88235 | 5 | 59.9816
Roof | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 29.2711 | 2.385 | 20.5543 | 23.2532 | 47.1026 | 2 | 4.6875 | 2 | 4.7059 | 5 | 1.1765 | 5 | 84.2831
Windows | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0.70584 | 0.016426 | 0.48232 | 0.55153 | 699.2094 | 15 | 0.625 | 13 | 1.4706 | 3 | 0.58824 | 5 | 31.4338
Air tightness | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 30.914 | 0.71709 | 21.1238 | 24.1551 | 32.6082 | 1 | 5 | 1 | 5 | 6 | 1.4706 | 4 | 86.4118
T reduction (2 DegC) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 17.0538 | 0.6835 | 11.7464 | 13.3897 | 1.5944 | 5 | 3.75 | 5 | 3.8235 | 15 | 4.1176 | 4.375 | 78.4926
T set back | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | -7.8019e-15 | 0 | 0 | -6.0556e-15 | 10000 | 17 | 0 | 14 | 1.1765 | 1 | 0 | 4.75 | 22.4853
Lighting (30%) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | -5.2676 | 15.6145 | 1.5026 | -0.59358 | 15.757 | 9 | 2.5 | 17 | 0.29412 | 9 | 2.3529 | 4.75 | 40.8676
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | -7.8019e-15 | 6.1336 | 1.9886 | 1.3729 | 1.1048 | 7 | 3.125 | 8 | 2.9412 | 16 | 4.4118 | 4.75 | 69.9485
HRV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 20.5286 | -0.71157 | 13.6423 | 15.7744 | 18.0034 | 4 | 4.0625 | 4 | 4.1176 | 8 | 2.0588 | 4.75 | 77.6875
DCV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 28.1454 | 0.39431 | 19.1481 | 21.9339 | 1.7526 | 3 | 4.375 | 3 | 4.4118 | 14 | 3.8235 | 4.375 | 86.1029
Cold Deck Reset | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -7.8019e-15 | 2.9981 | 0.97201 | 0.67106 | 5.379 | 12 | 1.5625 | 11 | 2.0588 | 11 | 2.9412 | 5 | 49.1728
VSD | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -6.6332 | 18.4351 | 1.4942 | -1.0222 | 0.11774 | 10 | 2.1875 | 18 | 0 | 17 | 4.7059 | 5 | 44.4301
VSP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -7.8019e-15 | 0 | 0 | -6.0556e-15 | 10000 | 17 | 0 | 14 | 1.1765 | 1 | 0 | 5 | 23.2353
Solar Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 1.3341 | -1.196 | 0.51381 | 0.76779 | -29.7473 | 14 | 0.9375 | 9 | 2.6471 | 18 | 5 | 4.5 | 53.5919
Solar DHW | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -7.8019e-15 | 2.8379 | 0.92007 | 0.6352 | 31.7227 | 13 | 1.25 | 12 | 1.7647 | 7 | 1.7647 | 5 | 41.3971
DB Economizer | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -0.33746 | 1.1611 | 0.14841 | -0.0020268 | 5.5024 | 16 | 0.3125 | 16 | 0.58824 | 10 | 2.6471 | 5 | 29.2463
COP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -7.8019e-15 | 3.0725 | 0.99613 | 0.68771 | 5.2494 | 11 | 1.875 | 10 | 2.3529 | 12 | 3.2353 | 5 | 54.3015
Retro-commissioning | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 10.0003 | 3.2784 | 7.821 | 8.4957 | 2.6765 | 6 | 3.4375 | 6 | 3.5294 | 13 | 3.5294 | 5 | 74.3566
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 17 |  | 18 |  | 18
| 9A-Workshop Building | [12 empty] | 9A-Workshop Building | [12 empty] | 9A-Workshop Building | [12 empty] | 9A-Workshop Building
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0
Wall | 2.792 | 1.4406 | 2.4509 | 2.564 | 0 | 6 | 3.5294 | 6 | 3.5294 | 17 | 0 | 5 | 64.4118 | 2.9049 | 3.1185 | 2.9569 | 2.9395 | 353.046 | 6 | 3.5294 | 7 | 3.2353 | 3 | 0.58824 | 5 | 64.1176 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 4.0507 | 4.2154 | 4.0901 | 4.0769 | 178.0783 | 7 | 3.2353 | 7 | 3.2353 | 4 | 0.88235 | 5 | 62.9412
Roof | 1.8462 | 1.5593 | 1.7738 | 1.7978 | 0 | 7 | 3.2353 | 7 | 3.2353 | 17 | 0 | 5 | 60.2941 | 2.8236 | 2.9813 | 2.862 | 2.8492 | 251.5428 | 7 | 3.2353 | 8 | 2.9412 | 4 | 0.88235 | 5 | 60.8824 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 13.9006 | 14.4829 | 14.0401 | 13.9933 | 29.8234 | 2 | 4.7059 | 2 | 4.7059 | 7 | 1.7647 | 5 | 86.1765
Windows | 0.21908 | 0.01583 | 0.16779 | 0.1848 | 1965.0627 | 14 | 1.1765 | 12 | 1.7647 | 4 | 4.0625 | 5 | 47.7757 | 0.48531 | 0.15159 | 0.40409 | 0.43124 | 576.4116 | 16 | 0.58824 | 14 | 1.1765 | 1 | 0 | 5 | 27.3529 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0.41265 | 0.10538 | 0.33904 | 0.36373 | 494.3976 | 15 | 0.88235 | 14 | 1.1765 | 2 | 0.29412 | 5 | 30.2941
Air tightness | 0 | 0 | 0 | 0 | 10000 | 15 | 0.88235 | 13 | 1.4706 | 1 | 5 | 4 | 43.4706 | 10.3611 | 7.4569 | 9.6542 | 9.8905 | 14.3086 | 2 | 4.7059 | 2 | 4.7059 | 8 | 2.0588 | 4 | 84.0588 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 23.3948 | 20.1887 | 22.6267 | 22.8843 | 4.2788 | 1 | 5 | 1 | 5 | 12 | 3.2353 | 4 | 91.7059
T reduction (2 DegC) | 14.5743 | 0.47491 | 11.0161 | 12.1961 | 1.6529 | 1 | 5 | 1 | 5 | 14 | 0.9375 | 4.375 | 85.9375 | 14.2854 | 0.62802 | 10.9614 | 12.0725 | 1.4443 | 1 | 5 | 1 | 5 | 16 | 4.4118 | 4.375 | 96.3603 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 13.4674 | 1.2546 | 10.5415 | 11.5228 | 0.97424 | 3 | 4.4118 | 3 | 4.4118 | 17 | 4.7059 | 4.375 | 89.0074
T set back | 11.6247 | 0.58572 | 8.8389 | 9.7627 | 2.0152 | 2 | 4.7059 | 2 | 4.7059 | 13 | 1.25 | 4.75 | 83.8824 | 11.3689 | 0.64968 | 8.76 | 9.6321 | 1.7797 | 3 | 4.4118 | 3 | 4.4118 | 15 | 4.1176 | 4.75 | 88.3676 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 10.9077 | 1.0538 | 8.5469 | 9.3387 | 1.1972 | 5 | 3.8235 | 4 | 4.1176 | 16 | 4.4118 | 4.75 | 83.0735
Lighting (30%) | -3.7164 | 15.7353 | 1.1925 | -0.43539 | 11.6226 | 9 | 2.6471 | 17 | 0.29412 | 9 | 2.5 | 4.75 | 42.3382 | -2.7795 | 12.3367 | 0.89954 | -0.33027 | 13.5223 | 11 | 2.0588 | 17 | 0.29412 | 9 | 2.3529 | 4.75 | 37.7794 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | -1.872 | 8.4258 | 0.59512 | -0.23232 | 13.7793 | 12 | 1.7647 | 17 | 0.29412 | 8 | 2.0588 | 4.75 | 34.8382
Occupancy Sensors (Lights/Plug Loads) | 0 | 6.3084 | 1.592 | 1.0641 | 1.3022 | 8 | 2.9412 | 9 | 2.6471 | 15 | 0.625 | 4.75 | 55.2426 | 0 | 5.7605 | 1.402 | 0.93336 | 1.3006 | 9 | 2.6471 | 10 | 2.3529 | 17 | 4.7059 | 4.75 | 63.3676 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 4.0046 | 0.95941 | 0.63763 | 1.3006 | 10 | 2.3529 | 10 | 2.3529 | 15 | 4.1176 | 4.75 | 59.5441
HRV | 1.3412 | 0.11873 | 1.0327 | 1.135 | 775.716 | 10 | 2.3529 | 8 | 2.9412 | 5 | 3.75 | 4.75 | 62.5588 | 1.7787 | 0.12272 | 1.3757 | 1.5104 | 525.8751 | 10 | 2.3529 | 9 | 2.6471 | 2 | 0.29412 | 4.75 | 50.1324 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 1.8261 | 0.065238 | 1.4043 | 1.5457 | 366.7326 | 9 | 2.6471 | 9 | 2.6471 | 3 | 0.58824 | 4.75 | 53.0735
DCV | 10.0003 | 0 | 7.4766 | 8.3135 | 4.3478 | 4 | 4.1176 | 4 | 4.1176 | 11 | 1.875 | 4.375 | 76.3971 | 10.0012 | 0 | 7.567 | 8.3807 | 3.7784 | 5 | 3.8235 | 5 | 3.8235 | 13 | 3.5294 | 4.375 | 77.2426 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 10.0002 | 0 | 7.6044 | 8.4079 | 2.5729 | 6 | 3.5294 | 6 | 3.5294 | 13 | 3.5294 | 4.375 | 73.125
Cold Deck Reset | 0 | 3.0078 | 0.75904 | 0.50733 | 8.6661 | 11 | 2.0588 | 11 | 2.0588 | 10 | 2.1875 | 5 | 50.386 | 0 | 3.003 | 0.73088 | 0.48656 | 7.9162 | 13 | 1.4706 | 13 | 1.4706 | 11 | 2.9412 | 5 | 44.4118 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 3.001 | 0.71896 | 0.47783 | 5.5069 | 11 | 2.0588 | 11 | 2.0588 | 11 | 2.9412 | 5 | 52.6471
VSD | -8.5556 | 27.0364 | 0.42643 | -2.5522 | 0.40735 | 13 | 1.4706 | 18 | 0 | 16 | 0.3125 | 5 | 26.2316 | -9.4067 | 31.1922 | 0.47448 | -2.8285 | 0.32201 | 15 | 0.88235 | 18 | 0 | 18 | 5 | 5 | 36.1765 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -6.4048 | 21.6845 | 0.32469 | -1.9323 | 0.32201 | 16 | 0.58824 | 18 | 0 | 18 | 5 | 5 | 34.1176
VSP | 0 | 0 | 0 | 0 | 10000 | 15 | 0.88235 | 13 | 1.4706 | 1 | 5 | 5 | 46.4706 | 0 | 3.4505 | 0.8398 | 0.55908 | 6.7526 | 12 | 1.7647 | 12 | 1.7647 | 12 | 3.2353 | 5 | 49.4118 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 2.3988 | 0.57469 | 0.38194 | 6.7526 | 13 | 1.4706 | 13 | 1.4706 | 9 | 2.3529 | 5 | 42.6471
Solar Wall | 4.7022 | -1.1556 | 3.2239 | 3.7142 | 50.7862 | 5 | 3.8235 | 5 | 3.8235 | 8 | 2.8125 | 4.5 | 75.4669 | 4.0868 | -1.0539 | 2.8357 | 3.2539 | 50.7862 | 8 | 2.9412 | 6 | 3.5294 | 7 | 1.7647 | 4.5 | 64.0882 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 2.7827 | -0.73267 | 1.9405 | 2.2229 | 50.7862 | 8 | 2.9412 | 8 | 2.9412 | 6 | 1.4706 | 4.5 | 59.0882
Solar DHW | 0.86564 | -0.079151 | 0.62721 | 0.70628 | 150.0523 | 12 | 1.7647 | 10 | 2.3529 | 6 | 3.4375 | 5 | 54.136 | 0.75235 | -0.072187 | 0.55167 | 0.61875 | 150.0523 | 14 | 1.1765 | 11 | 2.0588 | 5 | 1.1765 | 5 | 41.1765 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0.51226 | -0.050183 | 0.37751 | 0.42271 | 150.0523 | 14 | 1.1765 | 12 | 1.7647 | 5 | 1.1765 | 5 | 39.1176
DB Economizer | -0.15229 | 0.18996 | -0.065917 | -0.09456 | 91.358 | 18 | 0 | 16 | 0.58824 | 7 | 3.125 | 5 | 28.4926 | -0.18112 | 0.17325 | -0.094873 | -0.1237 | 137.7093 | 18 | 0 | 16 | 0.58824 | 6 | 1.4706 | 5 | 23.5294 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -0.28933 | 0.15055 | -0.18395 | -0.21929 | 10000 | 18 | 0 | 16 | 0.58824 | 1 | 0 | 5 | 19.1176
COP | 0 | 0 | 0 | 0 | 10000 | 15 | 0.88235 | 13 | 1.4706 | 1 | 5 | 5 | 46.4706 | 0 | 0.10106 | 0.024597 | 0.016375 | 12.9615 | 17 | 0.29412 | 15 | 0.88235 | 10 | 2.6471 | 5 | 31.1765 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0.3563 | 0.085361 | 0.056732 | 5.9001 | 17 | 0.29412 | 15 | 0.88235 | 10 | 2.6471 | 5 | 31.1765
Retro-commissioning | 9.8507 | 3.6964 | 8.2975 | 8.8126 | 3.023 | 3 | 4.4118 | 3 | 4.4118 | 12 | 1.5625 | 5 | 81.4522 | 9.8665 | 4.2518 | 8.4999 | 8.9567 | 2.5308 | 4 | 4.1176 | 4 | 4.1176 | 14 | 3.8235 | 5 | 84.1176 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 9.91 | 6.0069 | 8.9749 | 9.2886 | 1.4865 | 4 | 4.1176 | 5 | 3.8235 | 14 | 3.8235 | 5 | 82.0588
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 18 |  | 18 |  | 17 | [8 empty] | 18 |  | 18 |  | 18 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 18 |  | 18 |  | 18
| 11B-Retail Building | [12 empty] | 11B-Retail Building | [12 empty] | 11B-Retail Building | [12 empty] | 11B-Retail Building
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0
Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 5.7123 | 1.0639 | 4.3082 | 4.7527 | 246.6607 | 8 | 2.9412 | 8 | 2.9412 | 1 | 0 | 5 | 56.1765
Roof | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 22.3267 | 1.3582 | 15.9929 | 17.9979 | 133.69 | 3 | 4.4118 | 3 | 4.4118 | 3 | 0.71429 | 5 | 78.9076
Windows | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 2.6273 | 0.27286 | 1.9161 | 2.1412 | 186.2711 | 9 | 2.6471 | 9 | 2.6471 | 2 | 0.35714 | 5 | 53.1303
Air tightness | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 36.0319 | 2.3485 | 25.8574 | 29.0782 | 72.5432 | 1 | 5 | 1 | 5 | 4 | 1.0714 | 4 | 85.2143
T reduction (2 DegC) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 13.0583 | 1.3091 | 9.5093 | 10.6328 | 12.9767 | 6 | 3.5294 | 6 | 3.5294 | 10 | 3.2143 | 4.375 | 72.1796
T set back | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 15.3572 | 3.4093 | 11.7482 | 12.8906 | 12.9767 | 5 | 3.8235 | 5 | 3.8235 | 10 | 3.2143 | 4.75 | 77.4223
Lighting (30%) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | -2.9739 | 9.6882 | 0.85085 | -0.3599 | 45.3263 | 14 | 1.1765 | 18 | 0 | 5 | 1.4286 | 4.75 | 26.771
Occupancy Sensors (Lights/Plug Loads) | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 3.6999 | 1.1176 | 0.76382 | 7.0449 | 11 | 2.0588 | 11 | 2.0588 | 14 | 4.6429 | 4.75 | 57.0021
HRV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 16.505 | 0.86151 | 11.7796 | 13.2755 | 0 | 4 | 4.1176 | 4 | 4.1176 | 15 | 5 | 4.75 | 86.8971
DCV | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 29.8436 | 0.99948 | 21.1308 | 23.8889 | 22.2055 | 2 | 4.7059 | 2 | 4.7059 | 8 | 2.5 | 4.375 | 86.5074
Cold Deck Reset | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 1.9656 | 0.59373 | 0.40578 | 22.3535 | 16 | 0.58824 | 15 | 0.88235 | 7 | 2.1429 | 5 | 31.7227
VSD | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 3.4329 | 1.0369 | 0.7087 | 0 | 12 | 1.7647 | 12 | 1.7647 | 15 | 5 | 5 | 54.7059
VSP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 0.29412 | 15 | 5 | 5 | 32.0588
Solar Wall | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 2.0447 | -0.78397 | 1.1903 | 1.4608 | 7.1634 | 10 | 2.3529 | 10 | 2.3529 | 13 | 4.2857 | 4.5 | 59.2983
Solar DHW | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 3.0938 | 0.93453 | 0.6387 | 24.9568 | 13 | 1.4706 | 13 | 1.4706 | 6 | 1.7857 | 5 | 40.9454
DB Economizer | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -0.077955 | 0.69596 | 0.15581 | 0.081814 | 8.947 | 17 | 0.29412 | 16 | 0.58824 | 12 | 3.9286 | 5 | 32.9622
COP | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 2.0408 | 0.61644 | 0.4213 | 0 | 15 | 0.88235 | 14 | 1.1765 | 15 | 5 | 5 | 44.4118
Retro-commissioning | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 10.0003 | 5.8387 | 8.7433 | 9.1412 | 13.6107 | 7 | 3.2353 | 7 | 3.2353 | 9 | 2.8571 | 5 | 68.8655
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 18 |  | 18 |  | 15
| 13B-Firehall | [12 empty] | 13B-Firehall | [12 empty] | 13B-Firehall | [12 empty] | 13B-Firehall
| V1 | [12 empty] | V2 | [12 empty] | V3 | [12 empty] | V4
ECM | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score | Fuel PR (%) | Electricity PR (%) | Energy PR (%) | GHG PR (%) | Payback Years | Energy Reduction Rank | Energy Score | GHG Reduction Rank | GHG Score | Payback Rank | Payback Score | Success Score | Total Score
Base case | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0
Wall | 3.3588 | 0.36928 | 2.1254 | 2.4713 | 0 | 9 | 2.5 | 9 | 2.6471 | 15 | 4.1176 | 5 | 63.3824 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 2.5865 | 0.73274 | 2.1306 | 2.2826 | 505.5005 | 8 | 2.9412 | 8 | 2.9412 | 2 | 4.7059 | 5 | 70.2941 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Roof | 5.4603 | 0.64468 | 3.4734 | 4.0307 | 0 | 7 | 3.125 | 7 | 3.2353 | 15 | 4.1176 | 5 | 71.875 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 17.7375 | 5.2757 | 14.6725 | 15.6947 | 35.1094 | 3 | 4.4118 | 3 | 4.4118 | 6 | 3.5294 | 5 | 87.3529 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Windows | 0.37809 | 0.037554 | 0.23758 | 0.27699 | 2260.7521 | 15 | 0.625 | 13 | 1.4706 | 3 | 0.58824 | 5 | 31.4338 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0.46384 | 0.10855 | 0.37646 | 0.4056 | 724.5048 | 15 | 0.88235 | 14 | 1.1765 | 1 | 5 | 5 | 44.4118 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Air tightness | 0 | 0 | 0 | 0 | 10000 | 17 | 0 | 15 | 0.88235 | 1 | 0 | 4 | 18.1765 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12 | 40.2355 | 7.7073 | 32.2351 | 34.9034 | 11.9236 | 1 | 5 | 1 | 5 | 7 | 3.2353 | 4 | 91.7059 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4 | 12
T reduction (2 DegC) | 20.4344 | 0.56957 | 12.2382 | 14.5371 | 5.5514 | 1 | 5 | 2 | 4.7059 | 12 | 3.2353 | 4.375 | 90.7721 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 15.9724 | 1.015 | 12.2936 | 13.5205 | 2.8452 | 4 | 4.1176 | 4 | 4.1176 | 14 | 1.1765 | 4.375 | 74.3015 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125
T set back | 8.1113 | 0.3505 | 4.9092 | 5.8074 | 13.3341 | 5 | 3.75 | 5 | 3.8235 | 6 | 1.4706 | 4.75 | 71.6765 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 7.0373 | 0.56991 | 5.4466 | 5.9771 | 6.2962 | 7 | 3.2353 | 7 | 3.2353 | 9 | 2.6471 | 4.75 | 67.4853 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
Lighting (30%) | -9.2632 | 17.9383 | 1.9601 | -1.1879 | 7.2531 | 10 | 2.1875 | 18 | 0 | 10 | 2.6471 | 4.75 | 37.5037 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | -4.1108 | 15.3658 | 0.67949 | -0.91816 | 7.4931 | 14 | 1.1765 | 17 | 0.29412 | 8 | 2.9412 | 4.75 | 33.3676 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
Occupancy Sensors (Lights/Plug Loads) | 0 | 8.8314 | 3.6438 | 2.6218 | 2.1901 | 6 | 3.4375 | 8 | 2.9412 | 13 | 3.5294 | 5 | 70.239 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 7.6585 | 1.8836 | 1.2554 | 2.1901 | 9 | 2.6471 | 10 | 2.3529 | 15 | 0.88235 | 5 | 52.6471 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
HRV | 21.1114 | -0.95137 | 12.0084 | 14.5616 | 100.7363 | 2 | 4.6875 | 1 | 5 | 5 | 1.1765 | 4.75 | 85.5919 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25 | 8.7864 | -0.41793 | 6.5226 | 7.2776 | 88.9889 | 6 | 3.5294 | 6 | 3.5294 | 4 | 4.1176 | 4.75 | 76.0147 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.75 | 14.25
DCV | 20.0035 | 0 | 11.7501 | 14.0651 | 10.6492 | 3 | 4.375 | 3 | 4.4118 | 8 | 2.0588 | 4.375 | 80.8088 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125 | 20 | 0 | 15.081 | 16.7215 | 4.2891 | 2 | 4.7059 | 2 | 4.7059 | 13 | 1.4706 | 4.375 | 83.4191 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.375 | 13.125
Cold Deck Reset | 0 | 3.0043 | 1.2396 | 0.89189 | 6.4613 | 13 | 1.25 | 12 | 1.7647 | 11 | 2.9412 | 5 | 44.9265 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 3.0232 | 0.74357 | 0.49558 | 5.5681 | 13 | 1.4706 | 13 | 1.4706 | 10 | 2.3529 | 5 | 42.6471 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
VSD | -3.4347 | 5.2158 | 0.1345 | -0.86659 | 1.8078 | 16 | 0.3125 | 17 | 0.29412 | 14 | 3.8235 | 5 | 30.7169 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -3.5497 | 11.6084 | 0.17844 | -1.065 | 0.70439 | 18 | 0 | 18 | 0 | 16 | 0.58824 | 5 | 16.7647 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
VSP | 0 | 3.7116 | 1.5314 | 1.1019 | 0 | 12 | 1.5625 | 11 | 2.0588 | 15 | 4.1176 | 5 | 52.7022 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 3.2186 | 0.79163 | 0.52761 | 0 | 12 | 1.7647 | 12 | 1.7647 | 17 | 0.29412 | 5 | 40.5882 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Solar Wall | 7.9794 | -3.1295 | 3.3959 | 4.6815 | -67.6355 | 8 | 2.8125 | 6 | 3.5294 | 18 | 5 | 4.5 | 72.8934 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5 | 3.2132 | -2.7139 | 1.7555 | 2.2417 | -67.6355 | 10 | 2.3529 | 9 | 2.6471 | 18 | 0 | 4.5 | 48.5 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 4.5 | 13.5
Solar DHW | 3.2094 | -0.1064 | 1.8413 | 2.225 | 160.0764 | 11 | 1.875 | 10 | 2.3529 | 4 | 0.88235 | 5 | 47.2426 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 1.2924 | -0.092271 | 0.95182 | 1.0654 | 160.0764 | 11 | 2.0588 | 11 | 2.0588 | 3 | 4.4118 | 5 | 57.0588 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
DB Economizer | 0 | 0.92633 | 0.3822 | 0.275 | 8.3822 | 14 | 0.9375 | 14 | 1.1765 | 9 | 2.3529 | 5 | 36.8566 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | -0.0017704 | 1.2755 | 0.31238 | 0.2076 | 5.2835 | 16 | 0.58824 | 15 | 0.88235 | 11 | 2.0588 | 5 | 31.4706 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
COP | 0 | 0 | 0 | 0 | 10000 | 17 | 0 | 15 | 0.88235 | 1 | 0 | 5 | 21.1765 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 0 | 0.85758 | 0.21092 | 0.14058 | 71.9736 | 17 | 0.29412 | 16 | 0.58824 | 5 | 3.8235 | 5 | 32.6471 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Retro-commissioning | 9.3071 | 1.1767 | 5.9525 | 6.8934 | 11.7523 | 4 | 4.0625 | 4 | 4.1176 | 7 | 1.7647 | 5 | 77.5552 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15 | 9.7194 | 2.3448 | 7.9056 | 8.5105 | 4.6957 | 5 | 3.8235 | 5 | 3.8235 | 12 | 1.7647 | 5 | 73.8235 | 0 | 0 | 0 | 0 | 10000 | 1 | 0 | 1 | 0 | 1 | 0 | 5 | 15
Minimum | [5 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 1 |  | 1 |  | 1
Maximum | [5 empty] | 17 |  | 18 |  | 18 | [8 empty] | 1 |  | 1 |  | 1 | [8 empty] | 18 |  | 18 |  | 18 | [8 empty] | 1 |  | 1 |  | 1

## clcost
Retrofit Costs | Escalation
| 1 | 1.2 | 1.15
| Materials $ | Labour $ | Design $ | Total $ | Incentive $
Wall RSI Upgrade: $/m2
Interior Metal or Concrete: blown, extra RSI 1.4 | 32.28 | 25.824 | 9.89 | 67.994
Exterior Concrete: 50 mm RSI 2, new finish | 98.99 | 178.176 | 44.5395 | 321.7055
Exterior Concrete: 38 mm RSI 1.32, EIFS | 107.6 | 188.52 | 42.067 | 338.187
Exterior Concrete: 38 mm RSI 1.32, foam EIFS | 83.93 | 229.824 | 49.496 | 363.25
Exterior Concrete: 55 mm RSI 2.0, EIFS | 98.99 | 178.176 | 44.5395 | 321.7055
Exterior Metal: 50 mm RSI 2, new finish | 77.47 | 170.436 | 39.5945 | 287.5005
Roof RSI Upgrade: $/m2
Deck Roof Interior: 108 mm RSI 3.87 foam old finish | 69.73 | 55.776 | 20.0445 | 145.5505
Deck Roof Interior: 108 mm RSI 3.87 foam, new finish | 95.98 | 71.532 | 27.715 | 195.227
Deck Roof Interior: 50 mm foam, Exterior: 78 mm RSI 4.58 | 156.02 | 124.728 | 45.0455 | 325.7935
Deck Roof Exterior: 78 mm RSI 2.64 new finish | 101.36 | 81.276 | 29.1985 | 211.8345
Deck Roof Exterior: 78 mm RSI 2.64, new deck finished | 171.73 | 137.388 | 49.496 | 358.614
Deck Roof Exterior: 78 mm RSI 2.64, new membrane | 97.05 | 77.988 | 27.968 | 203.006
Deck Roof Exterior: 50 mm RSI 1.76 new membrane | 109.75 | 87.804 | 31.6825 | 229.2365
Deck Roof Exterior: 50 mm RSI 1.76, Interior: 50 mm RSI 1.76 | 163.98 | 131.184 | 47.265 | 342.429
Metal Roof Exterior: 37 mm RSI 1.4, new finish | 77.9 | 62.496 | 22.517 | 162.913
Metal Roof Exterior: 50 mm RSI 1.76, old finish | 70.16 | 56.292 | 20.2975 | 146.7495
Metal Roof Exterior: 78 mm RSI 2.64, new finish | 123.74 | 98.904 | 35.6385 | 258.2825
Metal Roof Exterior: 78 mm RSI 2.64, old finish | 81.13 | 64.824 | 23.2645 | 169.2185
Metal Roof Interior: 152 mm RSI 3.7, new finish | 55.31 | 44.16 | 16.0885 | 115.5585
Metal Roof Interior: 108 mm RSI 3.87, foam new finish | 69.94 | 55.776 | 20.0445 | 145.7605
Metal Roof Exterior: 50 mm RSI 1.76, Interior: 37 mm foam RSI 1.4 old finish | 197.34 | 158.04 | 49.496 | 404.876
Window Upgrade $/m2
| 941.7 | 107.628 | 180.4925 | 1229.8205
Air Sealing $/unit
Overhead door gasket (2.75 m x 2.75 m door) | 75 | 210 | 46 | 331
Overhead door sweep (2.75 m x 2.75 m door) | 65 | 210 | 46 | 321
Overhead door thermal blind (2.75 m x 2.75 m door) | 1500 | 600 | 345 | 2445
Overhead door (2.75 m x 2.75 m door) dock bay seals | 2300 | 960 | 529 | 3789
Older Window (pre-1980) perimeter ($/m per) | 10.93 | 32.784 | 7.8545 | 51.5685
Newer Window (post-1980) perimeter ($/m per) | 9.56 | 32.784 | 7.8545 | 50.1985
Wall/Roof/Sill junction sealing (pre-1980 $/m lineal) | 19.67 | 43.272 | 18.8485 | 81.7905
Wall/Roof/Sill junction sealing (post-1980 $/m lineal) | 16.39 | 43.272 | 11.316 | 70.978
Sealing envelope penetrations (pre-1980 $/unit) | 110 | 96 | 34.5 | 240.5
Sealing envelope penetrations (post-1980 $/unit) | 100 | 96 | 34.5 | 230.5
Note on C2: Lubun, Mike: increase from base of 60/hr to 72/hr
Note on D2: Lubun, Mike: increase from base of 100/hr to 115/hr

## 13b B19T
Archetype 13 - Firehall
Exemplar Building | B004 |  | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 912 | Corresponding
A/Grade Wall Area (m2) | 870.36 | Building
Roof Area (m2) | 881.47 | Numbers
Window Area (m2) | 49.8
Air Sealing | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | Door Gasket $ | Door Sweep $ | Dock Seal $ | Door Blind $ | Window $/m perimeter |  | N/A | 50.1985 | 51.5685 | 51.5685
| 331 | 321 | 3789 | 2445 | Junctions $ /m length |  | N/A | 70.978 | 81.7905 | 81.7905
[5 empty] | $/Penetration Sealing |  | N/A | 230.5 | 240.5 | 240.5
| No. of Storeys | Perimeter Length (m) | Total Perimeter Area (m2) | Vertical Junction length (m) | Total Window and Curtainwall Area (m2) | Total Window and Curtainwall Perimeter Length (m) | Total Man-Door Area (m2) | Total Overhead Door Area (m2) | Total Overhead Door Perimeter Length (m) | Number of Man-Doors | Number of Overhead Doors | No. of Envelope Penetrations (excluding doors and windows)
West Orientation | 1 | 60 | 120 | 6.1 | 15.17 | 33.5022 | 7.84 | 118.32 | 58.53 | 2 | 5 | 5
East Orientation | 1 | 60 | 120 | 6.1 | 18.89 | 41.7176 | 7.84 | 110.71 | 53.22 | 2 | 4 | 5
North Orientation | 1 | 30.2 | 60.4 | 6.1 | 13.27 | 29.3061 | 3.92 | 0 | 0 | 1 | 0 | 2
South Orientation | 1 | 31.8 | 63.6 | 6.1 | 1.46 | 3.2243 | 7.84 | 0 | 0 | 2 | 0 | 2
Roof | [11 empty] | 10
Sum |  |  | 364 | 24.4 | 48.79 | 107.7502 | 27.44 | 229.03 | 111.75 | 7 | 9 | 24
| Air Sealing Cost of Perimeter (# storeys) $ | Air Sealing Cost of Wall Junctions $ | Air Sealing Cost of Windows & Curtainwalls $ | Air Sealing Cost of Man-Doors $ | Air Sealing Cost of Overhead Doors $ | Air Sealing Cost of Envelope Penetrations $ | Total Air Sealing Retrofit Cost $ | Total Air Sealing Retrofit Cost $/m2
1980-2000 Built Bldgs | 25835.992 | 1731.8632 | 5408.8976 | 2317 | 22005 | 5532 | 62830.7528 | 68.8934
1960-1979 Built Bldgs | 29771.742 | 1995.6882 | 5556.5153 | 2317 | 22005 | 5772 | 67417.9455 | 73.9232
pre-1960 Built Bldgs | 29771.742 | 1995.6882 | 5556.5153 | 2317 | 22005 | 5772 | 67417.9455 | 73.9232
Wall & Roof Insulation | Cost/m2 of Wall and Roof Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Wall: RSI 0.88 to 2.88 |  |  |  | 321.7055 |  |  |  | 279999.599 |  |  |  | 307.0171
Wall: RSI 1.4 to 2.72 |  |  | 321.7055 |  |  |  | 279999.599 |  |  |  | 307.0171
Wall: RSI 2.11 to 4.43 |  | 321.7055 |  |  |  | 279999.599 |  |  |  | 307.0171
Roof: RSI 1.76 to 3.52 (Ext) |  | 229.2365 |  |  |  | 202065.0977 |  |  |  | 221.5626
Roof: RSI 1.76 to 5.63 (Int) |  | 195.227 |  |  |  | 172086.7437 |  |  |  | 188.6916
Roof: RSI 1.76 to 3.87 (Int+Ext) |  | 342.429 |  |  |  | 301840.8906 |  |  |  | 330.9659
Roof: RSI 1.05 to 3.69 (Ext) |  |  | 203.006 |  |  |  | 178943.6988 |  |  |  | 196.2102
Roof: RSI 1.05 to 4.75 (Int) |  |  | 325.7935 |  |  |  | 287177.1964 |  |  |  | 314.8873
Roof: RSI 1.05 to 4.92 (Int+Ext) |  |  | 342.429 |  |  |  | 301840.8906 |  |  |  | 330.9659
Roof: RSI 0.7 to 3.34 (Ext) |  |  |  | 203.006 |  |  |  | 178943.6988 |  |  |  | 196.2102
Roof: RSI 0.7 to 4.4 (Int) |  |  |  | 195.227 |  |  |  | 172086.7437 |  |  |  | 188.6916
Roof: RSI 0.7 to 4.57 (Int+Ext) |  |  |  | 342.429 |  |  |  | 301840.8906 |  |  |  | 330.9659
Window Replacement | Cost/m2 of Window Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Upgrade to Triple LowE | 1229.8205 | 1229.8205 | 1229.8205 | 1229.8205 | 61245.0609 | 61245.0609 | 61245.0609 | 61245.0609 | 67.1547 | 67.1547 | 67.1547 | 67.1547
Note on D12: Lubun, Mike: number of storeys+1 x perimeter area
Note on M13: Lubun, Mike: estimate based upon 50 rooms, plus 10 extra
Note on F16: Lubun, Mike: same curtainwall as north plus 8 windows in office = 16 panels x 2.968 per panel x 3.806 total height + 8 windows at .9 x 1.19

## 8a B624
Archetype 3A - Vehicle Garage
Exemplar Building | B624 |  | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 2270 | Corresponding
A/Grade Wall Area (m2) | 1182.04 | Building
Roof Area (m2) | 1758.55 | Numbers
Window Area (m2) | 3.63
Air Sealing | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | Door Gasket $ | Door Sweep $ | Dock Seal $ | Door Blind $ | Window $/m perimeter |  | N/A | 50.1985 | 51.5685 | 51.5685
| 331 | 321 | 3789 | 2445 | Junctions $ /m length |  | N/A | 70.978 | 81.7905 | 81.7905
[5 empty] | $/Penetration Sealing |  | N/A | 230.5 | 240.5 | 240.5
| No. of Storeys | Perimeter Length (m) | Total Perimeter Area (m2) | Vertical Junction length (m) | Total Window and Curtainwall Area (m2) | Total Window and Curtainwall Perimeter Length (m) | Total Man-Door Area (m2) | Total Overhead Door Area (m2) | Total Overhead Door Perimeter Length (m) | Number of Man-Doors | Number of Overhead Doors | No. of Envelope Penetrations (excluding doors and windows)
West Orientation | 1.5 | 31.5 | 78.75 | 6.25 | 0 | 0 | 7.84 | 0 | 0 | 2 | 0 | 2
East Orientation | 1.5 | 31.5 | 78.75 | 6.25 | 0 | 0 | 7.84 | 0 | 0 | 2 | 0 | 2
North Orientation | 1.5 | 53.34 | 133.35 | 6.25 | 0 | 0 | 7.84 | 67.2 | 65.6 | 2 | 4 | 6
South Orientation | 1.5 | 53.34 | 133.35 | 6.25 | 3.63 | 8.0167 | 3.92 | 84 | 82 | 1 | 5 | 6
Roof | [11 empty] | 8
Sum |  |  | 424.2 | 25 | 3.63 | 8.0167 | 27.44 | 151.2 | 147.6 | 7 | 9 | 24
| Air Sealing Cost of Perimeter (# storeys) $ | Air Sealing Cost of Wall Junctions $ | Air Sealing Cost of Windows & Curtainwalls $ | Air Sealing Cost of Man-Doors $ | Air Sealing Cost of Overhead Doors $ | Air Sealing Cost of Envelope Penetrations $ | Total Air Sealing Retrofit Cost $ | Total Air Sealing Retrofit Cost $/m2
1980-2000 Built Bldgs | 30108.8676 | 1774.45 | 402.4246 | 2317 | 22005 | 5532 | 62139.7422 | 27.3743
1960-1979 Built Bldgs | 34695.5301 | 2044.7625 | 413.4075 | 2317 | 22005 | 5772 | 67247.7001 | 29.6245
pre-1960 Built Bldgs | 34695.5301 | 2044.7625 | 413.4075 | 2317 | 22005 | 5772 | 67247.7001 | 29.6245
Wall & Roof Insulation | Cost/m2 of Wall and Roof Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Wall: RSI 0.88 to 2.88 |  |  |  | 321.7055 |  |  |  | 380268.7692 |  |  |  | 167.5193
Wall: RSI 1.4 to 2.72 |  |  | 321.7055 |  |  |  | 380268.7692 |  |  |  | 167.5193
Wall: RSI 2.11 to 4.43 |  | 321.7055 |  |  |  | 380268.7692 |  |  |  | 167.5193
Roof: RSI 1.76 to 3.52 (Ext) |  | 229.2365 |  |  |  | 403123.8471 |  |  |  | 177.5876
Roof: RSI 1.76 to 5.63 (Int) |  | 195.227 |  |  |  | 343316.4409 |  |  |  | 151.2407
Roof: RSI 1.76 to 3.87 (Int+Ext) |  | 342.429 |  |  |  | 602178.5179 |  |  |  | 265.2769
Roof: RSI 1.05 to 3.69 (Ext) |  |  | 203.006 |  |  |  | 356996.2013 |  |  |  | 157.267
Roof: RSI 1.05 to 4.75 (Int) |  |  | 195.227 |  |  |  | 343316.4409 |  |  |  | 151.2407
Roof: RSI 1.05 to 4.92 (Int+Ext) |  |  | 342.429 |  |  |  | 602178.5179 |  |  |  | 265.2769
Roof: RSI 0.7 to 3.34 (Ext) |  |  |  | 203.006 |  |  |  | 356996.2013 |  |  |  | 157.267
Roof: RSI 0.7 to 4.4 (Int) |  |  |  | 195.227 |  |  |  | 343316.4409 |  |  |  | 151.2407
Roof: RSI 0.7 to 4.57 (Int+Ext) |  |  |  | 342.429 |  |  |  | 602178.5179 |  |  |  | 265.2769
Window Replacement | Cost/m2 of Window Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Upgrade to Triple LowE | 1229.8205 | 1229.8205 | 1229.8205 | 1229.8205 | 4464.2484 | 4464.2484 | 4464.2484 | 4464.2484 | 1.9666 | 1.9666 | 1.9666 | 1.9666
Note on D12: Lubun, Mike: number of storeys+1 x perimeter area
Note on B13: Lubun, Mike: below grade floor does not count for infiltration calcs for exposed perimeter
Note on M13: Lubun, Mike: estimate based upon 50 rooms, plus 10 extra
Note on F16: Lubun, Mike: same curtainwall as north plus 8 windows in office = 16 panels x 2.968 per panel x 3.806 total height + 8 windows at .9 x 1.19

## bldg 34 2A
Archetype 2A - Training Centre
Exemplar Building | B172 |  | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 3700 | Corresponding | B503 | B246 | B058a | B034
A/Grade Wall Area (m2) | 1627.48 | Building | B587 |  |  | B065
Roof Area (m2) | 2469.42 | Numbers
Window Area (m2) | 134.46
Air Sealing | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | Door Gasket $ | Door Sweep $ | Dock Seal $ | Door Blind $ | Window $/m perimeter |  | N/A | 50.1985 | 51.5685 | 51.5685
| 331 | 321 | 3789 | 2445 | Junctions $ /m length |  | N/A | 70.978 | 81.7905 | 81.7905
[5 empty] | $/Penetration Sealing |  | N/A | 230.5 | 240.5 | 240.5
| No. of Storeys | Perimeter Length (m) | Total Perimeter Area (m2) | Vertical Junction length (m) | Total Window and Curtainwall Area (m2) | Total Window and Curtainwall Perimeter Length (m) | Total Man-Door Area (m2) | Total Overhead Door Area (m2) | Total Overhead Door Perimeter Length (m) | Number of Man-Doors | Number of Overhead Doors | No. of Envelope Penetrations (excluding doors and windows)
West Orientation | 2 | 110.73 | 332.19 | 7 | 15.24 | 33.6567 | 7.84 | 0 | 0 | 2 | 0 | 4
East Orientation | 2 | 110.73 | 332.19 | 7 | 28.78 | 63.5591 | 15.68 | 0 | 0 | 4 | 0 | 4
North Orientation | 2 | 69.17 | 207.51 | 7 | 43.16 | 95.3166 | 7.84 | 0 | 0 | 2 | 0 | 4
South Orientation | 2 | 69.17 | 207.51 | 7 | 47.28 | 104.4154 | 19.6 | 0 | 0 | 5 | 0 | 4
Roof | [11 empty] | 10
Sum |  |  | 1079.4 | 28 | 134.46 | 296.9479 | 50.96 | 0 | 0 | 13 | 0 | 26
| Air Sealing Cost of Perimeter (# storeys) $ | Air Sealing Cost of Wall Junctions $ | Air Sealing Cost of Windows & Curtainwalls $ | Air Sealing Cost of Man-Doors $ | Air Sealing Cost of Overhead Doors $ | Air Sealing Cost of Envelope Penetrations $ | Total Air Sealing Retrofit Cost $ | Total Air Sealing Retrofit Cost $/m2
1980-2000 Built Bldgs | 76613.6532 | 1987.384 | 14906.3409 | 4303 | 0 | 5993 | 103803.3781 | 28.055
1960-1979 Built Bldgs | 88284.6657 | 2290.134 | 15313.1595 | 4303 | 0 | 6253 | 116443.9592 | 31.4713
pre-1960 Built Bldgs | 88284.6657 | 2290.134 | 15313.1595 | 4303 | 0 | 6253 | 116443.9592 | 31.4713
Wall & Roof Insulation | Cost/m2 of Wall and Roof Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Wall: RSI 0.88 to 2.88 |  |  |  | 279.87 |  |  |  | 455482.8276 |  |  |  | 123.1035
Wall: RSI 1.4 to 2.72 |  |  | 279.87 |  |  |  | 455482.8276 |  |  |  | 123.1035
Wall: RSI 2.11 to 4.43 |  | 279.87 |  |  |  | 455482.8276 |  |  |  | 123.1035
Roof: RSI 1.76 to 3.52 (Ext) |  | 229.2365 |  |  |  | 566081.1978 |  |  |  | 152.9949
Roof: RSI 1.76 to 5.63 (Int) |  | 145.5505 |  |  |  | 359425.3157 |  |  |  | 97.142
Roof: RSI 1.76 to 3.87 (Int+Ext) |  | 342.429 |  |  |  | 845601.0212 |  |  |  | 228.5408
Roof: RSI 1.05 to 3.69 (Ext) |  |  | 203.006 |  |  |  | 501307.0765 |  |  |  | 135.4884
Roof: RSI 1.05 to 4.75 (Int) |  |  | 195.227 |  |  |  | 482097.4583 |  |  |  | 130.2966
Roof: RSI 1.05 to 4.92 (Int+Ext) |  |  | 342.429 |  |  |  | 845601.0212 |  |  |  | 228.5408
Roof: RSI 0.7 to 3.34 (Ext) |  |  |  | 211.8345 |  |  |  | 523108.351 |  |  |  | 141.3806
Roof: RSI 0.7 to 4.4 (Int) |  |  |  | 195.227 |  |  |  | 482097.4583 |  |  |  | 130.2966
Roof: RSI 0.7 to 4.57 (Int+Ext) |  |  |  | 342.429 |  |  |  | 845601.0212 |  |  |  | 228.5408
Window Replacement | Cost/m2 of Window Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Upgrade to Triple LowE | 1229.8205 | 1229.8205 | 1229.8205 | 1229.8205 | 165361.6644 | 165361.6644 | 165361.6644 | 165361.6644 | 44.6923 | 44.6923 | 44.6923 | 44.6923
Note on D12: Lubun, Mike: number of storeys+1 x perimeter area
Note on B13: Lubun, Mike: below grade floor does not count for infiltration calcs for exposed perimeter
Note on M13: Lubun, Mike: estimate based upon 50 rooms, plus 10 extra
Note on F16: Lubun, Mike: same curtainwall as north plus 8 windows in office = 16 panels x 2.968 per panel x 3.806 total height + 8 windows at .9 x 1.19

## 6a B007
Archetype 6A - Office
Exemplar Building | B007 |  | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 3419 | Corresponding
A/Grade Wall Area (m2) | 1234.06 | Building
Roof Area (m2) | 4053.83 | Numbers
Window Area (m2) | 2540.83
Air Sealing | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | Door Gasket $ | Door Sweep $ | Dock Seal $ | Door Blind $ | Window $/m perimeter |  | N/A | 50.1985 | 51.5685 | 51.5685
| 331 | 321 | 3789 | 2445 | Junctions $ /m length |  | N/A | 70.978 | 81.7905 | 81.7905
[5 empty] | $/Penetration Sealing |  | N/A | 230.5 | 240.5 | 240.5
| No. of Storeys | Perimeter Length (m) | Total Perimeter Area (m2) | Vertical Junction length (m) | Total Window and Curtainwall Area (m2) | Total Window and Curtainwall Perimeter Length (m) | Total Man-Door Area (m2) | Total Overhead Door Area (m2) | Total Overhead Door Perimeter Length (m) | Number of Man-Doors | Number of Overhead Doors | No. of Envelope Penetrations (excluding doors and windows)
West Orientation | 1.5 | 23.5 | 58.75 | 4.1 | 9.29 | 20.5165 | 15.68 | 0 | 0 | 4 | 0 | 6
East Orientation | 1.5 | 23.24 | 58.1 | 4.1 | 26.84 | 59.2747 | 0 | 0 | 0 | 0 | 0 | 6
North Orientation | 1.5 | 50.14 | 125.35 | 4.1 | 1.32 | 2.9152 | 27.44 | 6.74 | 10.4 | 7 | 1 | 6
South Orientation | 1.5 | 49.3 | 123.25 | 4.1 | 2.64 | 5.8303 | 23.52 | 8.4 | 11.6 | 6 | 1 | 6
Roof | [11 empty] | 10
Sum |  |  | 365.45 | 16.4 | 40.09 | 88.5367 | 66.64 | 15.14 | 22 | 17 | 2 | 34
| Air Sealing Cost of Perimeter (# storeys) $ | Air Sealing Cost of Wall Junctions $ | Air Sealing Cost of Windows & Curtainwalls $ | Air Sealing Cost of Man-Doors $ | Air Sealing Cost of Overhead Doors $ | Air Sealing Cost of Envelope Penetrations $ | Total Air Sealing Retrofit Cost $ | Total Air Sealing Retrofit Cost $/m2
1980-2000 Built Bldgs | 25938.9101 | 1164.0392 | 4444.4088 | 5627 | 4890 | 7837 | 49901.3581 | 14.5953
1960-1979 Built Bldgs | 29890.3382 | 1341.3642 | 4565.704 | 5627 | 4890 | 8177 | 54491.4065 | 15.9378
pre-1960 Built Bldgs | 29890.3382 | 1341.3642 | 4565.704 | 5627 | 4890 | 8177 | 54491.4065 | 15.9378
Wall & Roof Insulation | Cost/m2 of Wall and Roof Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Wall: RSI 0.88 to 2.88 |  |  |  | 321.7055 |  |  |  | 397003.8893 |  |  |  | 116.117
Wall: RSI 1.4 to 2.72 |  |  | 321.7055 |  |  |  | 397003.8893 |  |  |  | 116.117
Wall: RSI 2.11 to 4.43 |  | 321.7055 |  |  |  | 397003.8893 |  |  |  | 116.117
Roof: RSI 1.76 to 3.52 (Ext) |  | 229.2365 |  |  |  | 929285.8008 |  |  |  | 271.8005
Roof: RSI 1.76 to 5.63 (Int) |  | 145.5505 |  |  |  | 590036.9834 |  |  |  | 172.5759
Roof: RSI 1.76 to 3.87 (Int+Ext) |  | 342.429 |  |  |  | 1388148.9531 |  |  |  | 406.0102
Roof: RSI 1.05 to 3.69 (Ext) |  |  | 211.8345 |  |  |  | 858741.0511 |  |  |  | 251.1673
Roof: RSI 1.05 to 4.75 (Int) |  |  | 195.227 |  |  |  | 791417.0694 |  |  |  | 231.4762
Roof: RSI 1.05 to 4.92 (Int+Ext) |  |  | 342.429 |  |  |  | 1388148.9531 |  |  |  | 406.0102
Roof: RSI 0.7 to 3.34 (Ext) |  |  |  | 229.2365 |  |  |  | 929285.8008 |  |  |  | 271.8005
Roof: RSI 0.7 to 4.4 (Int) |  |  |  | 195.227 |  |  |  | 791417.0694 |  |  |  | 231.4762
Roof: RSI 0.7 to 4.57 (Int+Ext) |  |  |  | 342.429 |  |  |  | 1388148.9531 |  |  |  | 406.0102
Window Replacement | Cost/m2 of Window Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Upgrade to Triple LowE | 1229.8205 | 1229.8205 | 1229.8205 | 1229.8205 | 3124764.821 | 3124764.821 | 3124764.821 | 3124764.821 | 913.9412 | 913.9412 | 913.9412 | 913.9412
Note on D12: Lubun, Mike: number of storeys+1 x perimeter area
Note on B13: Lubun, Mike: below grade floor does not count for infiltration calcs for exposed perimeter
Note on M13: Lubun, Mike: estimate based upon 50 rooms, plus 10 extra
Note on F16: Lubun, Mike: same curtainwall as north plus 8 windows in office = 16 panels x 2.968 per panel x 3.806 total height + 8 windows at .9 x 1.19

## 9a B581
Archetype 9A - Workshop
Exemplar Building | B581 |  | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 1927 | Corresponding
A/Grade Wall Area (m2) | 1603.55 | Building
Roof Area (m2) | 1810.66 | Numbers
Window Area (m2) | 60.89
Air Sealing | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | Door Gasket $ | Door Sweep $ | Dock Seal $ | Door Blind $ | Window $/m perimeter |  | N/A | 50.1985 | 51.5685 | 51.5685
| 331 | 321 | 3789 | 2445 | Junctions $ /m length |  | N/A | 70.978 | 81.7905 | 81.7905
[5 empty] | $/Penetration Sealing |  | N/A | 230.5 | 240.5 | 240.5
| No. of Storeys | Perimeter Length (m) | Total Perimeter Area (m2) | Vertical Junction length (m) | Total Window and Curtainwall Area (m2) | Total Window and Curtainwall Perimeter Length (m) | Total Man-Door Area (m2) | Total Overhead Door Area (m2) | Total Overhead Door Perimeter Length (m) | Number of Man-Doors | Number of Overhead Doors | No. of Envelope Penetrations (excluding doors and windows)
West Orientation | 2 | 35.7 | 107.1 | 9.3 | 0 | 0 | 19.6 | 16.8 | 16.4 | 5 | 1 | 5
East Orientation | 2 | 35.7 | 107.1 | 9.3 | 18.9 | 41.7397 | 15.68 | 11.2 | 13.6 | 4 | 1 | 5
North Orientation | 2 | 54.2 | 162.6 | 9.3 | 20.92 | 46.2007 | 3.92 | 0 | 0 | 1 | 0 | 8
South Orientation | 2 | 54.2 | 162.6 | 9.3 | 21.06 | 46.5099 | 7.84 | 0 | 0 | 2 | 0 | 8
Roof | [11 empty] | 20
Sum |  |  | 539.4 | 37.2 | 60.88 | 134.4503 | 47.04 | 28 | 30 | 12 | 2 | 46
| Air Sealing Cost of Perimeter (# storeys) $ | Air Sealing Cost of Wall Junctions $ | Air Sealing Cost of Windows & Curtainwalls $ | Air Sealing Cost of Man-Doors $ | Air Sealing Cost of Overhead Doors $ | Air Sealing Cost of Envelope Penetrations $ | Total Air Sealing Retrofit Cost $ | Total Air Sealing Retrofit Cost $/m2
1980-2000 Built Bldgs | 38285.5332 | 2640.3816 | 6749.2045 | 3972 | 4890 | 10603 | 67140.1193 | 34.8418
1960-1979 Built Bldgs | 44117.7957 | 3042.6066 | 6933.4014 | 3972 | 4890 | 11063 | 74018.8037 | 38.4114
pre-1960 Built Bldgs | 44117.7957 | 3042.6066 | 6933.4014 | 3972 | 4890 | 11063 | 74018.8037 | 38.4114
Wall & Roof Insulation | Cost/m2 of Wall and Roof Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Wall: RSI 0.88 to 2.88 |  |  |  | 321.7055 |  |  |  | 515870.8545 |  |  |  | 267.7067
Wall: RSI 1.4 to 2.72 |  |  | 321.7055 |  |  |  | 515870.8545 |  |  |  | 267.7067
Wall: RSI 2.11 to 4.43 |  | 321.7055 |  |  |  | 515870.8545 |  |  |  | 267.7067
Roof: RSI 1.76 to 3.52 (Ext) |  | 146.7495 |  |  |  | 265713.4497 |  |  |  | 137.8897
Roof: RSI 1.76 to 5.63 (Int) |  | 115.5585 |  |  |  | 209237.1536 |  |  |  | 108.5818
Roof: RSI 1.76 to 3.87 (Int+Ext) |  | 404.876 |  |  |  | 733092.7782 |  |  |  | 380.4322
Roof: RSI 1.05 to 3.69 (Ext) |  |  | 258.2825 |  |  |  | 467661.7915 |  |  |  | 242.689
Roof: RSI 1.05 to 4.75 (Int) |  |  | 145.7605 |  |  |  | 263922.7069 |  |  |  | 136.9604
Roof: RSI 1.05 to 4.92 (Int+Ext) |  |  | 404.876 |  |  |  | 733092.7782 |  |  |  | 380.4322
Roof: RSI 0.7 to 3.34 (Ext) |  |  |  | 258.2825 |  |  |  | 467661.7915 |  |  |  | 242.689
Roof: RSI 0.7 to 4.4 (Int) |  |  |  | 145.7605 |  |  |  | 263922.7069 |  |  |  | 136.9604
Roof: RSI 0.7 to 4.57 (Int+Ext) |  |  |  | 404.876 |  |  |  | 733092.7782 |  |  |  | 380.4322
Window Replacement | Cost/m2 of Window Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Upgrade to Triple LowE | 1229.8205 | 1229.8205 | 1229.8205 | 1229.8205 | 74883.7702 | 74883.7702 | 74883.7702 | 74883.7702 | 38.8603 | 38.8603 | 38.8603 | 38.8603
Note on D12: Lubun, Mike: number of storeys+1 x perimeter area
Note on M13: Lubun, Mike: estimate based upon 50 rooms, plus 10 extra
Note on F16: Lubun, Mike: same curtainwall as north plus 8 windows in office = 16 panels x 2.968 per panel x 3.806 total height + 8 windows at .9 x 1.19

## 5a B720
Archetype 5A - Recreation Centre
Exemplar Building | B720 |  | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 12613 | Corresponding
A/Grade Wall Area (m2) | 4237.86 | Building
Roof Area (m2) | 10118.6 | Numbers
Window Area (m2) | 197.89
Air Sealing | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | Door Gasket $ | Door Sweep $ | Dock Seal $ | Door Blind $ | Window $/m perimeter |  | N/A | 50.1985 | 51.5685 | 51.5685
| 331 | 321 | 3789 | 2445 | Junctions $ /m length |  | N/A | 70.978 | 81.7905 | 81.7905
[5 empty] | $/Penetration Sealing |  | N/A | 230.5 | 240.5 | 240.5
| No. of Storeys | Perimeter Length (m) | Total Perimeter Area (m2) | Vertical Junction length (m) | Total Window and Curtainwall Area (m2) | Total Window and Curtainwall Perimeter Length (m) | Total Man-Door Area (m2) | Total Overhead Door Area (m2) | Total Overhead Door Perimeter Length (m) | Number of Man-Doors | Number of Overhead Doors | No. of Envelope Penetrations (excluding doors and windows)
West Orientation | 1 | 125.875 | 251.75 | 8.7 | 22.55 | 49.8005 | 43.12 | 0 | 0 | 11 | 0 | 10
East Orientation | 1 | 125.875 | 251.75 | 8.7 | 175.34 | 387.2293 | 31.36 | 0 | 0 | 8 | 0 | 10
North Orientation | 1 | 80.96 | 161.92 | 8.7 | 0 | 0 | 23.52 | 0 | 0 | 6 | 0 | 10
South Orientation | 1 | 73.375 | 146.75 | 8.7 | 0 | 0 | 31.36 | 52.04 | 78.3 | 8 | 2 | 10
Roof | [11 empty] | 25
Sum |  |  | 812.17 | 34.8 | 197.89 | 437.0298 | 129.36 | 52.04 | 78.3 | 33 | 2 | 65
| Air Sealing Cost of Perimeter (# storeys) $ | Air Sealing Cost of Wall Junctions $ | Air Sealing Cost of Windows & Curtainwalls $ | Air Sealing Cost of Man-Doors $ | Air Sealing Cost of Overhead Doors $ | Air Sealing Cost of Envelope Penetrations $ | Total Air Sealing Retrofit Cost $ | Total Air Sealing Retrofit Cost $/m2
1980-2000 Built Bldgs | 57646.2023 | 2470.0344 | 21938.2403 | 10923 | 4890 | 14982.5 | 112849.977 | 8.9471
1960-1979 Built Bldgs | 66427.7904 | 2846.3094 | 22536.9711 | 10923 | 4890 | 15632.5 | 123256.5709 | 9.7722
pre-1960 Built Bldgs | 66427.7904 | 2846.3094 | 22536.9711 | 10923 | 4890 | 15632.5 | 123256.5709 | 9.7722
Wall & Roof Insulation | Cost/m2 of Wall and Roof Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Wall: RSI 0.88 to 2.88 |  |  |  | 321.7055 |  |  |  | 1363342.8702 |  |  |  | 108.0903
Wall: RSI 1.4 to 2.72 |  |  | 321.7055 |  |  |  | 1363342.8702 |  |  |  | 108.0903
Wall: RSI 2.11 to 4.43 |  | 321.7055 |  |  |  | 1363342.8702 |  |  |  | 108.0903
Roof: RSI 1.76 to 3.52 (Ext) |  | 146.7495 |  |  |  | 1484899.4907 |  |  |  | 117.7277
Roof: RSI 1.76 to 5.63 (Int) |  | 145.7605 |  |  |  | 1474892.1953 |  |  |  | 116.9343
Roof: RSI 1.76 to 3.87 (Int+Ext) |  | 404.876 |  |  |  | 4096778.2936 |  |  |  | 324.806
Roof: RSI 1.05 to 3.69 (Ext) |  |  | 258.2825 |  |  |  | 2613457.3045 |  |  |  | 207.2035
Roof: RSI 1.05 to 4.75 (Int) |  |  | 115.5585 |  |  |  | 1169290.2381 |  |  |  | 92.7052
Roof: RSI 1.05 to 4.92 (Int+Ext) |  |  | 404.876 |  |  |  | 4096778.2936 |  |  |  | 324.806
Roof: RSI 0.7 to 3.34 (Ext) |  |  |  | 258.2825 |  |  |  | 2613457.3045 |  |  |  | 207.2035
Roof: RSI 0.7 to 4.4 (Int) |  |  |  | 145.7605 |  |  |  | 1474892.1953 |  |  |  | 116.9343
Roof: RSI 0.7 to 4.57 (Int+Ext) |  |  |  | 404.876 |  |  |  | 4096778.2936 |  |  |  | 324.806
Window Replacement | Cost/m2 of Window Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Upgrade to Triple LowE | 1229.8205 | 1229.8205 | 1229.8205 | 1229.8205 | 243369.1787 | 243369.1787 | 243369.1787 | 243369.1787 | 19.2951 | 19.2951 | 19.2951 | 19.2951
Note on D12: Lubun, Mike: number of storeys+1 x perimeter area
Note on M13: Lubun, Mike: estimate based upon 50 rooms, plus 10 extra
Note on F16: Lubun, Mike: same curtainwall as north plus 8 windows in office = 16 panels x 2.968 per panel x 3.806 total height + 8 windows at .9 x 1.19

## 6b B096
Archetype 6B - Small Office
Exemplar Building | B096 |  | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 584 | Corresponding
A/Grade Wall Area (m2) | 453.16 | Building
Roof Area (m2) | 605.73 | Numbers
Window Area (m2) | 39.64
Air Sealing | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | Door Gasket $ | Door Sweep $ | Dock Seal $ | Door Blind $ | Window $/m perimeter |  | N/A | 50.1985 | 51.5685 | 51.5685
| 331 | 321 | 3789 | 2445 | Junctions $ /m length |  | N/A | 70.978 | 81.7905 | 81.7905
[5 empty] | $/Penetration Sealing |  | N/A | 230.5 | 240.5 | 240.5
| No. of Storeys | Perimeter Length (m) | Total Perimeter Area (m2) | Vertical Junction length (m) | Total Window and Curtainwall Area (m2) | Total Window and Curtainwall Perimeter Length (m) | Total Man-Door Area (m2) | Total Overhead Door Area (m2) | Total Overhead Door Perimeter Length (m) | Number of Man-Doors | Number of Overhead Doors | No. of Envelope Penetrations (excluding doors and windows)
West Orientation | 1 | 23.72 | 47.44 | 3.7 | 2.43 | 5.3665 | 3.92 | 0 | 0 | 1 | 0 | 2
East Orientation | 1 | 23.72 | 47.44 | 3.7 | 7 | 15.4591 | 11.76 | 0 | 0 | 3 | 0 | 2
North Orientation | 1 | 42.97 | 85.94 | 3.7 | 14.55 | 32.1329 | 19.6 | 0 | 0 | 5 | 0 | 5
South Orientation | 1 | 42.97 | 85.94 | 3.7 | 15.66 | 34.5843 | 7.84 | 0 | 0 | 2 | 0 | 5
Roof | [11 empty] | 10
Sum |  |  | 266.76 | 14.8 | 39.64 | 87.5429 | 43.12 | 0 | 0 | 11 | 0 | 24
| Air Sealing Cost of Perimeter (# storeys) $ | Air Sealing Cost of Wall Junctions $ | Air Sealing Cost of Windows & Curtainwalls $ | Air Sealing Cost of Man-Doors $ | Air Sealing Cost of Overhead Doors $ | Air Sealing Cost of Envelope Penetrations $ | Total Air Sealing Retrofit Cost $ | Total Air Sealing Retrofit Cost $/m2
1980-2000 Built Bldgs | 18934.0913 | 1050.4744 | 4394.5214 | 3641 | 0 | 5532 | 33552.0871 | 57.4522
1960-1979 Built Bldgs | 21818.4338 | 1210.4994 | 4514.4552 | 3641 | 0 | 5772 | 36956.3884 | 63.2815
pre-1960 Built Bldgs | 21818.4338 | 1210.4994 | 4514.4552 | 3641 | 0 | 5772 | 36956.3884 | 63.2815
Wall & Roof Insulation | Cost/m2 of Wall and Roof Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Wall: RSI 0.88 to 2.88 |  |  |  | 287.5005 |  |  |  | 130283.7266 |  |  |  | 223.0886
Wall: RSI 1.4 to 2.72 |  |  | 287.5005 |  |  |  | 130283.7266 |  |  |  | 223.0886
Wall: RSI 2.11 to 4.43 |  | 287.5005 |  |  |  | 130283.7266 |  |  |  | 223.0886
Roof: RSI 1.76 to 3.52 (Ext) |  | 146.7495 |  |  |  | 88890.5746 |  |  |  | 152.2099
Roof: RSI 1.76 to 5.63 (Int) |  | 145.7605 |  |  |  | 88291.5077 |  |  |  | 151.1841
Roof: RSI 1.76 to 3.87 (Int+Ext) |  | 404.876 |  |  |  | 245245.5395 |  |  |  | 419.941
Roof: RSI 1.05 to 3.69 (Ext) |  |  | 258.2825 |  |  |  | 156449.4587 |  |  |  | 267.8929
Roof: RSI 1.05 to 4.75 (Int) |  |  | 145.7605 |  |  |  | 88291.5077 |  |  |  | 151.1841
Roof: RSI 1.05 to 4.92 (Int+Ext) |  |  | 404.876 |  |  |  | 245245.5395 |  |  |  | 419.941
Roof: RSI 0.7 to 3.34 (Ext) |  |  |  | 258.2825 |  |  |  | 156449.4587 |  |  |  | 267.8929
Roof: RSI 0.7 to 4.4 (Int) |  |  |  | 145.7605 |  |  |  | 88291.5077 |  |  |  | 151.1841
Roof: RSI 0.7 to 4.57 (Int+Ext) |  |  |  | 404.876 |  |  |  | 245245.5395 |  |  |  | 419.941
Window Replacement | Cost/m2 of Window Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Upgrade to Triple LowE | 1229.8205 | 1229.8205 | 1229.8205 | 1229.8205 | 48750.0846 | 48750.0846 | 48750.0846 | 48750.0846 | 83.4762 | 83.4762 | 83.4762 | 83.4762
Note on D12: Lubun, Mike: number of storeys+1 x perimeter area
Note on M13: Lubun, Mike: estimate based upon 50 rooms, plus 10 extra
Note on F16: Lubun, Mike: same curtainwall as north plus 8 windows in office = 16 panels x 2.968 per panel x 3.806 total height + 8 windows at .9 x 1.19

## 9b B688
Archetype 9A - Workshop
Exemplar Building | B688 |  | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 927 | Corresponding
A/Grade Wall Area (m2) | 921.42 | Building
Roof Area (m2) | 935.87 | Numbers
Window Area (m2) | 5.6
Air Sealing | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | Door Gasket $ | Door Sweep $ | Dock Seal $ | Door Blind $ | Window $/m perimeter |  | N/A | 50.1985 | 51.5685 | 51.5685
| 331 | 321 | 3789 | 2445 | Junctions $ /m length |  | N/A | 70.978 | 81.7905 | 81.7905
[5 empty] | $/Penetration Sealing |  | N/A | 230.5 | 240.5 | 240.5
| No. of Storeys | Perimeter Length (m) | Total Perimeter Area (m2) | Vertical Junction length (m) | Total Window and Curtainwall Area (m2) | Total Window and Curtainwall Perimeter Length (m) | Total Man-Door Area (m2) | Total Overhead Door Area (m2) | Total Overhead Door Perimeter Length (m) | Number of Man-Doors | Number of Overhead Doors | No. of Envelope Penetrations (excluding doors and windows)
West Orientation | 1 | 31.32 | 62.64 | 5.25 | 0 | 0 | 0 | 33.6 | 32.8 | 0 | 2 | 4
East Orientation | 1 | 31.32 | 62.64 | 5.25 | 2.8 | 6.1837 | 15.68 | 33.6 | 32.8 | 4 | 2 | 4
North Orientation | 1 | 48.27 | 96.54 | 5.25 | 2.8 | 6.1837 | 19.6 | 0 | 0 | 5 | 0 | 4
South Orientation | 1 | 48.27 | 96.54 | 5.25 | 0 | 0 | 7.84 | 0 | 0 | 2 | 0 | 4
Roof | [11 empty] | 6
Sum |  |  | 318.36 | 21 | 5.6 | 12.3673 | 43.12 | 67.2 | 65.6 | 11 | 4 | 22
| Air Sealing Cost of Perimeter (# storeys) $ | Air Sealing Cost of Wall Junctions $ | Air Sealing Cost of Windows & Curtainwalls $ | Air Sealing Cost of Man-Doors $ | Air Sealing Cost of Overhead Doors $ | Air Sealing Cost of Envelope Penetrations $ | Total Air Sealing Retrofit Cost $ | Total Air Sealing Retrofit Cost $/m2
1980-2000 Built Bldgs | 22596.5561 | 1490.538 | 620.8204 | 3641 | 9780 | 5071 | 43199.9145 | 46.6018
1960-1979 Built Bldgs | 26038.8236 | 1717.6005 | 637.7636 | 3641 | 9780 | 5291 | 47106.1877 | 50.8157
pre-1960 Built Bldgs | 26038.8236 | 1717.6005 | 637.7636 | 3641 | 9780 | 5291 | 47106.1877 | 50.8157
Wall & Roof Insulation | Cost/m2 of Wall and Roof Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Wall: RSI 0.88 to 2.88 |  |  |  | 287.5005 |  |  |  | 264908.7107 |  |  |  | 285.7699
Wall: RSI 1.4 to 2.72 |  |  | 287.5005 |  |  |  | 264908.7107 |  |  |  | 285.7699
Wall: RSI 2.11 to 4.43 |  | 287.5005 |  |  |  | 264908.7107 |  |  |  | 285.7699
Roof: RSI 1.76 to 3.52 (Ext) |  | 146.7495 |  |  |  | 137338.4546 |  |  |  | 148.1537
Roof: RSI 1.76 to 5.63 (Int) |  | 115.5585 |  |  |  | 108147.7334 |  |  |  | 116.6642
Roof: RSI 1.76 to 3.87 (Int+Ext) |  | 404.876 |  |  |  | 378911.3021 |  |  |  | 408.7501
Roof: RSI 1.05 to 3.69 (Ext) |  |  | 169.2185 |  |  |  | 158366.5176 |  |  |  | 170.8377
Roof: RSI 1.05 to 4.75 (Int) |  |  | 115.5585 |  |  |  | 108147.7334 |  |  |  | 116.6642
Roof: RSI 1.05 to 4.92 (Int+Ext) |  |  | 404.876 |  |  |  | 378911.3021 |  |  |  | 408.7501
Roof: RSI 0.7 to 3.34 (Ext) |  |  |  | 115.5585 |  |  |  | 108147.7334 |  |  |  | 116.6642
Roof: RSI 0.7 to 4.4 (Int) |  |  |  | 145.7605 |  |  |  | 136412.8791 |  |  |  | 147.1552
Roof: RSI 0.7 to 4.57 (Int+Ext) |  |  |  | 404.876 |  |  |  | 378911.3021 |  |  |  | 408.7501
Window Replacement | Cost/m2 of Window Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Upgrade to Triple LowE | 1229.8205 | 1229.8205 | 1229.8205 | 1229.8205 | 6886.9948 | 6886.9948 | 6886.9948 | 6886.9948 | 7.4293 | 7.4293 | 7.4293 | 7.4293
Note on D12: Lubun, Mike: number of storeys+1 x perimeter area
Note on M13: Lubun, Mike: estimate based upon 50 rooms, plus 10 extra
Note on F16: Lubun, Mike: same curtainwall as north plus 8 windows in office = 16 panels x 2.968 per panel x 3.806 total height + 8 windows at .9 x 1.19

## 7a B40
Archetype 7A - Dining Hall
Exemplar Building | B40 |  | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 2568 | Corresponding
A/Grade Wall Area (m2) | 1305.36 | Building
Roof Area (m2) | 2258.41 | Numbers
Window Area (m2) | 225.87
Air Sealing | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | Door Gasket $ | Door Sweep $ | Dock Seal $ | Door Blind $ | Window $/m perimeter |  | N/A | 50.1985 | 51.5685 | 51.5685
| 331 | 321 | 3789 | 2445 | Junctions $ /m length |  | N/A | 70.978 | 81.7905 | 81.7905
[5 empty] | $/Penetration Sealing |  | N/A | 230.5 | 240.5 | 240.5
| No. of Storeys | Perimeter Length (m) | Total Perimeter Area (m2) | Vertical Junction length (m) | Total Window and Curtainwall Area (m2) | Total Window and Curtainwall Perimeter Length (m) | Total Man-Door Area (m2) | Total Overhead Door Area (m2) | Total Overhead Door Perimeter Length (m) | Number of Man-Doors | Number of Overhead Doors | No. of Envelope Penetrations (excluding doors and windows)
West Orientation | 1 | 67.21 | 134.42 | 4.5 | 71.96 | 158.9199 | 3.92 | 0 | 0 | 1 | 0 | 6
East Orientation | 1 | 67.21 | 134.42 | 4.5 | 51.29 | 113.2713 | 3.92 | 0 | 0 | 1 | 0 | 6
North Orientation | 1 | 69.03 | 138.06 | 4.5 | 64.24 | 141.8707 | 11.76 | 0 | 0 | 3 | 0 | 6
South Orientation | 1 | 69.03 | 138.06 | 4.5 | 38.38 | 84.7602 | 11.76 | 0 | 0 | 3 | 0 | 6
Roof | [11 empty] | 15
Sum |  |  | 544.96 | 18 | 225.87 | 498.8222 | 31.36 | 0 | 0 | 8 | 0 | 39
| Air Sealing Cost of Perimeter (# storeys) $ | Air Sealing Cost of Wall Junctions $ | Air Sealing Cost of Windows & Curtainwalls $ | Air Sealing Cost of Man-Doors $ | Air Sealing Cost of Overhead Doors $ | Air Sealing Cost of Envelope Penetrations $ | Total Air Sealing Retrofit Cost $ | Total Air Sealing Retrofit Cost $/m2
1980-2000 Built Bldgs | 38680.1709 | 1277.604 | 25040.125 | 2648 | 0 | 8989.5 | 76635.3999 | 29.8424
1960-1979 Built Bldgs | 44572.5509 | 1472.229 | 25723.5114 | 2648 | 0 | 9379.5 | 83795.7913 | 32.6308
pre-1960 Built Bldgs | 44572.5509 | 1472.229 | 25723.5114 | 2648 | 0 | 9379.5 | 83795.7913 | 32.6308
Wall & Roof Insulation | Cost/m2 of Wall and Roof Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Wall: RSI 0.88 to 2.88 |  |  |  | 321.7055 |  |  |  | 419941.4915 |  |  |  | 163.5286
Wall: RSI 1.4 to 2.72 |  |  | 321.7055 |  |  |  | 419941.4915 |  |  |  | 163.5286
Wall: RSI 2.11 to 4.43 |  | 321.7055 |  |  |  | 419941.4915 |  |  |  | 163.5286
Roof: RSI 1.76 to 3.52 (Ext) |  | 229.2365 |  |  |  | 517710.004 |  |  |  | 201.6005
Roof: RSI 1.76 to 5.63 (Int) |  | 145.5505 |  |  |  | 328712.7047 |  |  |  | 128.0034
Roof: RSI 1.76 to 3.87 (Int+Ext) |  | 342.429 |  |  |  | 773345.0779 |  |  |  | 301.1468
Roof: RSI 1.05 to 3.69 (Ext) |  |  | 203.006 |  |  |  | 458470.7805 |  |  |  | 178.5322
Roof: RSI 1.05 to 4.75 (Int) |  |  | 195.227 |  |  |  | 440902.6091 |  |  |  | 171.691
Roof: RSI 1.05 to 4.92 (Int+Ext) |  |  | 342.429 |  |  |  | 773345.0779 |  |  |  | 301.1468
Roof: RSI 0.7 to 3.34 (Ext) |  |  |  | 358.614 |  |  |  | 809897.4437 |  |  |  | 315.3806
Roof: RSI 0.7 to 4.4 (Int) |  |  |  | 195.227 |  |  |  | 440902.6091 |  |  |  | 171.691
Roof: RSI 0.7 to 4.57 (Int+Ext) |  |  |  | 342.429 |  |  |  | 773345.0779 |  |  |  | 301.1468
Window Replacement | Cost/m2 of Window Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Upgrade to Triple LowE | 1229.8205 | 1229.8205 | 1229.8205 | 1229.8205 | 277779.5563 | 277779.5563 | 277779.5563 | 277779.5563 | 108.1696 | 108.1696 | 108.1696 | 108.1696
Note on D12: Lubun, Mike: number of storeys+1 x perimeter area
Note on M13: Lubun, Mike: estimate based upon 50 rooms, plus 10 extra
Note on F16: Lubun, Mike: same curtainwall as north plus 8 windows in office = 16 panels x 2.968 per panel x 3.806 total height + 8 windows at .9 x 1.19

## 4c B45
Archetype 4C - Barracks
Exemplar Building | B45 |  | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 3989 | Corresponding
A/Grade Wall Area (m2) | 1783.8 | Building
Roof Area (m2) | 1582.83 | Numbers
Window Area (m2) | 307.51
Air Sealing | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | Door Gasket $ | Door Sweep $ | Dock Seal $ | Door Blind $ | Window $/m perimeter |  | N/A | 50.1985 | 51.5685 | 51.5685
| 331 | 321 | 3789 | 2445 | Junctions $ /m length |  | N/A | 70.978 | 81.7905 | 81.7905
[5 empty] | $/Penetration Sealing |  | N/A | 230.5 | 240.5 | 240.5
| No. of Storeys | Perimeter Length (m) | Total Perimeter Area (m2) | Vertical Junction length (m) | Total Window and Curtainwall Area (m2) | Total Window and Curtainwall Perimeter Length (m) | Total Man-Door Area (m2) | Total Overhead Door Area (m2) | Total Overhead Door Perimeter Length (m) | Number of Man-Doors | Number of Overhead Doors | No. of Envelope Penetrations (excluding doors and windows)
West Orientation | 3 | 34.75 | 139 | 9.39 | 41.55 | 91.761 | 0 | 0 | 0 | 0 | 0 | 10
East Orientation | 3 | 34.75 | 139 | 9.39 | 35.16 | 77.649 | 0 | 0 | 0 | 0 | 0 | 10
North Orientation | 3 | 74.3 | 297.2 | 9.39 | 93.39 | 206.247 | 7.84 | 0 | 0 | 2 | 0 | 10
South Orientation | 3 | 71.35 | 285.4 | 9.39 | 137.41 | 303.4629 | 15.68 | 0 | 0 | 4 | 0 | 10
Roof | [11 empty] | 8
Sum |  |  | 860.6 | 37.56 | 307.51 | 679.1199 | 23.52 | 0 | 0 | 6 | 0 | 48
| Air Sealing Cost of Perimeter (# storeys) $ | Air Sealing Cost of Wall Junctions $ | Air Sealing Cost of Windows & Curtainwalls $ | Air Sealing Cost of Man-Doors $ | Air Sealing Cost of Overhead Doors $ | Air Sealing Cost of Envelope Penetrations $ | Total Air Sealing Retrofit Cost $ | Total Air Sealing Retrofit Cost $/m2
1980-2000 Built Bldgs | 61083.6668 | 2665.9337 | 34090.7993 | 1986 | 0 | 11064 | 110890.3998 | 27.799
1960-1979 Built Bldgs | 70388.9043 | 3072.0512 | 35021.1936 | 1986 | 0 | 11544 | 122012.149 | 30.5872
pre-1960 Built Bldgs | 70388.9043 | 3072.0512 | 35021.1936 | 1986 | 0 | 11544 | 122012.149 | 30.5872
Wall & Roof Insulation | Cost/m2 of Wall and Roof Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Wall: RSI 0.88 to 2.88 |  |  |  | 287.5005 |  |  |  | 512843.3919 |  |  |  | 128.5644
Wall: RSI 1.4 to 2.72 |  |  | 287.5005 |  |  |  | 512843.3919 |  |  |  | 128.5644
Wall: RSI 2.11 to 4.43 |  | 287.5005 |  |  |  | 512843.3919 |  |  |  | 128.5644
Roof: RSI 1.76 to 3.52 (Ext) |  | 146.7495 |  |  |  | 232279.5111 |  |  |  | 58.23
Roof: RSI 1.76 to 5.63 (Int) |  | 115.5585 |  |  |  | 182909.4606 |  |  |  | 45.8535
Roof: RSI 1.76 to 3.87 (Int+Ext) |  | 404.876 |  |  |  | 640849.8791 |  |  |  | 160.6543
Roof: RSI 1.05 to 3.69 (Ext) |  |  | 169.2185 |  |  |  | 267844.1184 |  |  |  | 67.1457
Roof: RSI 1.05 to 4.75 (Int) |  |  | 145.7605 |  |  |  | 230714.0922 |  |  |  | 57.8376
Roof: RSI 1.05 to 4.92 (Int+Ext) |  |  | 404.876 |  |  |  | 640849.8791 |  |  |  | 160.6543
Roof: RSI 0.7 to 3.34 (Ext) |  |  |  | 258.2825 |  |  |  | 408817.2895 |  |  |  | 102.4862
Roof: RSI 0.7 to 4.4 (Int) |  |  |  | 145.7605 |  |  |  | 230714.0922 |  |  |  | 57.8376
Roof: RSI 0.7 to 4.57 (Int+Ext) |  |  |  | 404.876 |  |  |  | 640849.8791 |  |  |  | 160.6543
Window Replacement | Cost/m2 of Window Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Upgrade to Triple LowE | 1229.8205 | 1229.8205 | 1229.8205 | 1229.8205 | 378182.102 | 378182.102 | 378182.102 | 378182.102 | 94.8062 | 94.8062 | 94.8062 | 94.8062
Note on D12: Lubun, Mike: number of storeys+1 x perimeter area
Note on M13: Lubun, Mike: estimate based upon 50 rooms, plus 10 extra
Note on F16: Lubun, Mike: same curtainwall as north plus 8 windows in office = 16 panels x 2.968 per panel x 3.806 total height + 8 windows at .9 x 1.19

## 3b B782
Archetype 8B - Warehouse
Exemplar Building | B782 |  | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 1171 | Corresponding
A/Grade Wall Area (m2) | 559.7 | Building
Roof Area (m2) | 1115.58 | Numbers
Window Area (m2) | 0
Air Sealing | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | Door Gasket $ | Door Sweep $ | Dock Seal $ | Door Blind $ | Window $/m perimeter |  | N/A | 50.1985 | 51.5685 | 51.5685
| 331 | 321 | 3789 | 2445 | Junctions $ /m length |  | N/A | 70.978 | 81.7905 | 81.7905
[5 empty] | $/Penetration Sealing |  | N/A | 230.5 | 240.5 | 240.5
| No. of Storeys | Perimeter Length (m) | Total Perimeter Area (m2) | Vertical Junction length (m) | Total Window and Curtainwall Area (m2) | Total Window and Curtainwall Perimeter Length (m) | Total Man-Door Area (m2) | Total Overhead Door Area (m2) | Total Overhead Door Perimeter Length (m) | Number of Man-Doors | Number of Overhead Doors | No. of Envelope Penetrations (excluding doors and windows)
West Orientation | 1 | 16.55 | 33.1 | 6.1 | 0 | 0 | 3.92 | 22.1 | 18.9 | 1 | 1 | 4
East Orientation | 1 | 16.55 | 33.1 | 6.1 | 0 | 0 | 3.92 | 22.1 | 18.9 | 1 | 1 | 4
North Orientation | 1 | 62.074 | 124.148 | 6.1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2
South Orientation | 1 | 62.074 | 124.148 | 6.1 | 0 | 0 | 0 |  |  | 0 | 0 | 2
Roof | [11 empty] | 5
Sum |  |  | 314.496 | 24.4 | 0 | 0 | 7.84 | 44.2 | 37.8 | 2 | 2 | 17
| Air Sealing Cost of Perimeter (# storeys) $ | Air Sealing Cost of Wall Junctions $ | Air Sealing Cost of Windows & Curtainwalls $ | Air Sealing Cost of Man-Doors $ | Air Sealing Cost of Overhead Doors $ | Air Sealing Cost of Envelope Penetrations $ | Total Air Sealing Retrofit Cost $ | Total Air Sealing Retrofit Cost $/m2
1980-2000 Built Bldgs | 22322.2971 | 1731.8632 | 0 | 662 | 4890 | 3918.5 | 33524.6603 | 28.6291
1960-1979 Built Bldgs | 25722.7851 | 1995.6882 | 0 | 662 | 4890 | 4088.5 | 37358.9733 | 31.9035
pre-1960 Built Bldgs | 25722.7851 | 1995.6882 | 0 | 662 | 4890 | 4088.5 | 37358.9733 | 31.9035
Wall & Roof Insulation | Cost/m2 of Wall and Roof Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Wall: RSI 0.88 to 2.88 |  |  |  | 287.5005 |  |  |  | 160914.0299 |  |  |  | 137.4159
Wall: RSI 1.4 to 2.72 |  |  | 287.5005 |  |  |  | 160914.0299 |  |  |  | 137.4159
Wall: RSI 2.11 to 4.43 |  | 287.5005 |  |  |  | 160914.0299 |  |  |  | 137.4159
Roof: RSI 1.76 to 3.52 (Ext) |  | 146.7495 |  |  |  | 163710.8072 |  |  |  | 139.8043
Roof: RSI 1.76 to 5.63 (Int) |  | 115.5585 |  |  |  | 128914.7514 |  |  |  | 110.0895
Roof: RSI 1.76 to 3.87 (Int+Ext) |  | 404.876 |  |  |  | 451671.5681 |  |  |  | 385.7144
Roof: RSI 1.05 to 3.69 (Ext) |  |  | 169.2185 |  |  |  | 188776.7742 |  |  |  | 161.2099
Roof: RSI 1.05 to 4.75 (Int) |  |  | 145.7605 |  |  |  | 162607.4986 |  |  |  | 138.8621
Roof: RSI 1.05 to 4.92 (Int+Ext) |  |  | 404.876 |  |  |  | 451671.5681 |  |  |  | 385.7144
Roof: RSI 0.7 to 3.34 (Ext) |  |  |  | 258.2825 |  |  |  | 288134.7914 |  |  |  | 246.0587
Roof: RSI 0.7 to 4.4 (Int) |  |  |  | 145.7605 |  |  |  | 162607.4986 |  |  |  | 138.8621
Roof: RSI 0.7 to 4.57 (Int+Ext) |  |  |  | 404.876 |  |  |  | 451671.5681 |  |  |  | 385.7144
Window Replacement | Cost/m2 of Window Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Upgrade to Triple LowE | 1229.8205 | 1229.8205 | 1229.8205 | 1229.8205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on D12: Lubun, Mike: number of storeys+1 x perimeter area
Note on F16: Lubun, Mike: same curtainwall as north plus 8 windows in office = 16 panels x 2.968 per panel x 3.806 total height + 8 windows at .9 x 1.19

## 1a hanger4
Archetype 1A - Hanger
Exemplar Building | Hanger4 |  | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Floor Area (m2) | 6423 | Corresponding
A/Grade Wall Area (m2) | 2868 | Building
Roof Area (m2) | 5428.93 | Numbers
Window Area (m2) | 157.07
Air Sealing | [6 empty] | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | Door Gasket $ | Door Sweep $ | Dock Seal $ | Door Blind $ | Window $/m perimeter |  | N/A | 50.1985 | 51.5685 | 51.5685
| 331 | 321 | 3789 | 2445 | Junctions $ /m length |  | N/A | 70.978 | 81.7905 | 81.7905
[5 empty] | $/Penetration Sealing |  | N/A | 230.5 | 240.5 | 240.5
| No. of Storeys | Perimeter Length (m) | Total Perimeter Area (m2) | Vertical Junction length (m) | Total Window and Curtainwall Area (m2) | Total Window and Curtainwall Perimeter Length (m) | Total Man-Door Area (m2) | Total Overhead Door Area (m2) | Total Overhead Door Perimeter Length (m) | Number of Man-Doors | Number of Overhead Doors | No. of Envelope Penetrations (excluding doors and windows)
West Orientation | 1 | 73.711 | 221.133 | 12.7 | 1.72 | 3.7985 | 25.155 | 530.85 | 119.72 | 0 | 2 | 10
East Orientation | 1 | 73.711 | 221.133 | 12.7 | 5.45 | 12.036 | 13.545 | 530.85 | 119.72 | 0 | 2 | 10
North Orientation | 1 | 71.544 | 143.088 | 12.7 | 84.14 | 185.8188 | 9.675 | 36 | 78.5 | 4 | 0 | 10
South Orientation | 1 | 71.544 | 0 | 12.7 | 65.76 | 145.2275 | 3.87 | 52.04 | 78.3 | 4 | 0 | 10
Roof | [11 empty] | 20
Sum |  |  | 585.354 | 50.8 | 157.07 | 346.8809 | 52.245 | 1149.74 | 396.24 | 8 | 4 | 60
| Air Sealing Cost of Perimeter (# storeys) $ | Air Sealing Cost of Wall Junctions $ | Air Sealing Cost of Windows & Curtainwalls $ | Air Sealing Cost of Man-Doors $ | Air Sealing Cost of Overhead Doors $ | Air Sealing Cost of Envelope Penetrations $ | Total Air Sealing Retrofit Cost $ | Total Air Sealing Retrofit Cost $/m2
1980-2000 Built Bldgs | 41547.2562 | 3605.6824 | 17412.9032 | 2648 | 9780 | 13830 | 88823.8418 | 13.829
1960-1979 Built Bldgs | 47876.3963 | 4154.9574 | 17888.1301 | 2648 | 9780 | 14430 | 96777.4838 | 15.0673
pre-1960 Built Bldgs | 47876.3963 | 4154.9574 | 17888.1301 | 2648 | 9780 | 14430 | 96777.4838 | 15.0673
Wall & Roof Insulation | Cost/m2 of Wall and Roof Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Wall: RSI 0.88 to 2.88 |  |  |  | 321.7055 |  |  |  | 922651.374 |  |  |  | 143.648
Wall: RSI 1.4 to 2.72 |  |  | 321.7055 |  |  |  | 922651.374 |  |  |  | 143.648
Wall: RSI 2.11 to 4.43 |  | 321.7055 |  |  |  | 922651.374 |  |  |  | 143.648
Roof: RSI 1.76 to 3.52 (Ext) |  | 229.2365 |  |  |  | 1244508.9119 |  |  |  | 193.7582
Roof: RSI 1.76 to 5.63 (Int) |  | 145.5505 |  |  |  | 790183.476 |  |  |  | 123.0241
Roof: RSI 1.76 to 3.87 (Int+Ext) |  | 342.429 |  |  |  | 1859023.071 |  |  |  | 289.4322
Roof: RSI 1.05 to 3.69 (Ext) |  |  | 211.8345 |  |  |  | 1150034.6721 |  |  |  | 179.0495
Roof: RSI 1.05 to 4.75 (Int) |  |  | 195.227 |  |  |  | 1059873.7171 |  |  |  | 165.0123
Roof: RSI 1.05 to 4.92 (Int+Ext) |  |  | 342.429 |  |  |  | 1859023.071 |  |  |  | 289.4322
Roof: RSI 0.7 to 3.34 (Ext) |  |  |  | 358.614 |  |  |  | 1946890.303 |  |  |  | 303.1123
Roof: RSI 0.7 to 4.4 (Int) |  |  |  | 195.227 |  |  |  | 1059873.7171 |  |  |  | 165.0123
Roof: RSI 0.7 to 4.57 (Int+Ext) |  |  |  | 342.429 |  |  |  | 1859023.071 |  |  |  | 289.4322
Window Replacement | Cost/m2 of Window Area |  |  |  | Total Retrofit Cost |  |  |  | Cost/m2 of Building Area
| Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960 | Post-2004 | 1980-2004 | 1960-1979 | pre-1960
Retrofit Cost | ($/m2) | ($/m2) | ($/m2) | ($/m2) | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $ | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2 | Retrofit $/m2
Upgrade to Triple LowE | 1229.8205 | 1229.8205 | 1229.8205 | 1229.8205 | 193167.9059 | 193167.9059 | 193167.9059 | 193167.9059 | 30.0744 | 30.0744 | 30.0744 | 30.0744
Note on D12: Lubun, Mike: number of storeys+1 x perimeter area
Note on E13: Lubun, Mike: ground floor height= 7.3 m and 7 vertical junctions second floor extra height = 15.23 and 2 junctions
Note on E14: Lubun, Mike: full height = 22.46 and 10 junctions
Note on E15: Lubun, Mike: ground floor height= 7.3 m and 7 vertical junctions second floor extra height = 15.23 and 2 junctions
Note on E16: Lubun, Mike: ground floor height= 7.3 m and 7 vertical junctions second floor extra height = 15.23 and 2 junctions
Note on F16: Lubun, Mike: same curtainwall as north plus 8 windows in office = 16 panels x 2.968 per panel x 3.806 total height + 8 windows at .9 x 1.19

## fuel
Fuel Costs
| Unit | Cost $/Unit | $/GJ
Electricity | kWh | 0.12
Gas | m3 | 0.22

## cost
Retrofit Costs
| Materials $ | Labour $ | Design $ | Total $ | Incentive $
Wall RSI Upgrade: $/m2
Interior Metal or Concrete: blown, extra RSI 1.4 | 32.28 | 21.52 | 8.6 | 62.4
Exterior Concrete: 50 mm RSI 2, new finish | 98.99 | 148.48 | 38.73 | 286.2
Exterior Concrete: 38 mm RSI 1.32, EIFS | 107.6 | 157.1 | 36.58 | 301.28
Exterior Concrete: 38 mm RSI 1.32, foam EIFS | 83.93 | 191.52 | 43.04 | 318.49
Exterior Concrete: 55 mm RSI 2.0, EIFS | 98.99 | 148.48 | 38.73 | 286.2
Exterior Metal: 50 mm RSI 2, new finish | 77.47 | 142.03 | 34.43 | 253.93
Roof RSI Upgrade: $/m2
Deck Roof Interior: 108 mm RSI 3.87 foam old finish | 69.73 | 46.48 | 17.43 | 133.64
Deck Roof Interior: 108 mm RSI 3.87 foam, new finish | 95.98 | 59.61 | 24.1 | 179.69
Deck Roof Interior: 50 mm foam, Exterior: 78 mm RSI 4.58 | 156.02 | 103.94 | 39.17 | 299.13
Deck Roof Exterior: 78 mm RSI 2.64 new finish | 101.36 | 67.73 | 25.39 | 194.48
Deck Roof Exterior: 78 mm RSI 2.64, new deck finished | 171.73 | 114.49 | 43.04 | 329.26
Deck Roof Exterior: 78 mm RSI 2.64, new membrane | 97.05 | 64.99 | 24.32 | 186.36
Deck Roof Exterior: 50 mm RSI 1.76 new membrane | 109.75 | 73.17 | 27.55 | 210.47
Deck Roof Exterior: 50 mm RSI 1.76, Interior: 50 mm RSI 1.76 | 163.98 | 109.32 | 41.1 | 314.4
Metal Roof Exterior: 37 mm RSI 1.4, new finish | 77.9 | 52.08 | 19.58 | 149.56
Metal Roof Exterior: 50 mm RSI 1.76, old finish | 70.16 | 46.91 | 17.65 | 134.72
Metal Roof Exterior: 78 mm RSI 2.64, new finish | 123.74 | 82.42 | 30.99 | 237.15
Metal Roof Exterior: 78 mm RSI 2.64, old finish | 81.13 | 54.02 | 20.23 | 155.38
Metal Roof Interior: 152 mm RSI 3.7, new finish | 55.31 | 36.8 | 13.99 | 106.1
Metal Roof Interior: 108 mm RSI 3.87, foam new finish | 69.94 | 46.48 | 17.43 | 133.85
Metal Roof Exterior: 50 mm RSI 1.76, Interior: 37 mm foam RSI 1.4 old finish | 197.34 | 131.7 | 43.04 | 372.08
Window Upgrade $/m2
Replacement with U=1.92 W/m2-C double LowE, | 941.7 | 89.69 | 156.95 | 1188.34
Air Sealing $/unit
Overhead door gasket (2.75 m x 2.75 m door) | 75 | 175 | 40 | 290
Overhead door sweep (2.75 m x 2.75 m door) | 65 | 175 | 40 | 280
Overhead door thermal blind (2.75 m x 2.75 m door) | 1500 | 500 | 300 | 2300
Overhead door (2.75 m x 2.75 m door) dock bay seals | 2300 | 800 | 460 | 3560
Older Window (pre-1980) perimeter ($/m per) | 10.93 | 27.32 | 6.83 | 45.08
Newer Window (post-1980) perimeter ($/m per) | 9.56 | 27.32 | 6.83 | 43.71
Wall/Roof/Sill junction sealing (pre-1980 $/m lineal) | 19.67 | 36.06 | 16.39 | 72.12
Wall/Roof/Sill junction sealing (post-1980 $/m lineal) | 16.39 | 36.06 | 9.84 | 62.29
Sealing envelope penetrations (pre-1980 $/unit) | 110 | 80 | 30 | 220
Sealing envelope penetrations (post-1980 $/unit) | 100 | 80 | 30 | 210

## basecost
Retrofit Costs
Lighting Retrofit: Costing/Fixture | Materials $ | Labour $ | Design $ | Total $ | Incentive $
T8 to T5 Fluorescent per fixture | 80.5 | 57.5 | 20.7 | 158.7 | 25
400W Metal Halide to T5-High Bay per fixture | 506 | 68 | 86 | 660 | 105
250W Metal Halide to T5-High Bay per fixture | 506 | 68 | 86 | 660 | 105
HRV Retrofit: Costing/Unit
Plate HRV: 0 - 1180 L/sec capacity (ducting present) | 24725 | 8625 | 5000 | 38350 | 400
Plate HRV: 1200 - 2360 L/sec capacity (ducting present) | 28855 | 10005 | 5995 | 44855 | 700
Heat Wheel HRV: 0 - 1040 L/sec capacity (ducting present) | 40825 | 12305 | 7970 | 61100 | 600
Heat Wheel HRV: 1040 -2550 L/sec capacity (ducting present) | 57270 | 15640 | 10935 | 83845 | 1500
Heat Wheel HRV: 2600 - 5050 L/sec capacity (ducting present) | 89240 | 22425 | 16750 | 128415 | 1500
Heat Wheel HRV: 5100 - 9675 L/sec capacity (ducting present) | 166750 | 39100 | 30925 | 236775 | 1500
Demand Control Ventilation Retrofit Costing/Controller
Wall Mounted Space Sensor controlling AHU or VAV box | 512 | 276 | 118 | 906
Duct Mounted Return Air Sensor controlling AHU | 512 | 345 | 128 | 985 | 100
Space Temperature Sensor Retrofit: Costing/Controller
Pneumatic to programmable digital conversion | 506 | 173 | 101 | 780
Electric to programmable digital conversion | 173 | 69 | 36 | 278
Supply Air Temperature Reset Retrofit: Costing/Controller | 1380 | 1380 | 413 | 3173
Boiler (Hot Water) Reset Retrofit: Costing/Controller | 472 | 276 | 112 | 860
Occupancy Sensor to Control Plug Loads: Costing/Controller | 115 | 135 | 38 | 288
Retro-commissioning: Cost/building (20 room, 4 AHUs) | 0 | 4140 | 621 | 4761
Condensor Water Reset Retrofit: Costing/Controller | 2576 | 966 | 532 | 4074
DX Compressor Upgrade: Costing/Unit
0-5 ton COP upgrade to COP 4.0 scroll (R-410A refrigerant) | 3450 | 690 | 620 | 4760 | 1000
5-15 ton COP upgrade to COP 4.0 scroll (R-410A refrigerant) | 9200 | 920 | 920 | 11040 | 3000
Solarwall: Costing/100 m2 installation
Unglazed solarwall (low temperature) | 150 | 155 | 46 | 351
Glazed solarwall (high temperature) | 178 | 167 | 51 | 396
Variable Speed Pump Retrofit: Costing/Unit
10 hp pump with a pressure differential switch control | 1840 | 1380 | 482 | 3702
10 hp pump with a valve conversion control (3-way to 2-way) | 1438 | 1266 | 406 | 3110
25 hp pump with a pressure differential switch control | 2588 | 1438 | 604 | 4630
25 hp pump with a valve conversion control (3-way to 2-way) | 1898 | 1322 | 484 | 3704
Variable Frequency Drive Retrofit: Costing/Unit
5 hp 3ph upgrade | 460 | 344 | 120 | 924 | 265
10 hp 3ph upgrade | 580 | 368 | 140 | 1088 | 535
15 hp 3ph upgrade | 1036 | 460 | 224 | 1720 | 805
25 hp 3ph upgrade | 1612 | 552 | 324 | 2488 | 1340
Economizer Control for Cooling AHUs: Controller | 690 | 414 | 166 | 1270
Steam to Hot Water Heat Exchanger Conversion: Cost/Unit
Space Heating only conversion sized for up to 170 kW heating | 25300 | 9200 | 5173 | 39673
500 kW Space Heating and 500 kW DHW conversion | 63300 | 57500 | 18100 | 138900
500 kW Space Heating conversion | 40300 | 25300 | 9900 | 75500
Air Handling Unit Replacement: Costing/Unit
5 ton AHU replacement with COP 4.0 (SEER 20) DX | 9200 | 1730 | 1640 | 12570 | 1000
12-15 ton AHU replacement with COP 4.0 (SEER 20) DX | 15530 | 2300 | 1640 | 19470 | 3000
Solar DHW: Cost/System (30 m2 collector with 1500 L storage) | 28750 | 19550 | 7245 | 55545
On/OFF & Run-Time Controller for Exhaust Fans: Cost/Unit | 300 | 276 | 87 | 663
Motor Efficiency Upgrades: Cost/Unit
1 hp 3ph upgrade | 230 | 115 | 50 | 395
2 hp 3ph upgrade | 475 | 130 | 90 | 695
5 hp 3ph upgrade | 1440 | 230 | 250 | 1920
10 hp 3ph upgrade | 2590 | 245 | 425 | 3260
15 hp 3ph upgrade | 3020 | 260 | 490 | 3770
Note on F4: Lubun, Mike: OPA new fixture or retrofit
Note on F5: Lubun, Mike: OPA for T5 4-12 lamp HO fixture
Note on F6: Lubun, Mike: OPA for T5 4-12 lamp HO fixture
Note on F8: Lubun, Mike: Union Gas HRV <2000 cfm
Note on F9: Lubun, Mike: Union Gas HRV >2000 cfm
Note on F10: Lubun, Mike: Union Gas ERV <2000 cfm
Note on F11: Lubun, Mike: Union Gas ERV >2000 cfm
Note on F12: Lubun, Mike: Union Gas ERV >2000 cfm
Note on F13: Lubun, Mike: Union Gas ERV >2000 cfm
Note on F16: Lubun, Mike: Union gas, $100 per RTU/MUA if space is less than 2500 ft2 and contains a CO2 sensor, $200 for spaces greater than 2500 ft2. Incentive for offices only
Note on F26: Lubun, Mike: OPA 5 ton
Note on F27: Lubun, Mike: OPA $202/ton works out to 3000 for a 15 ton unit
Note on F37: Lubun, Mike: OPA
Note on F38: Lubun, Mike: OPA
Note on F39: Lubun, Mike: OPA
Note on F40: Lubun, Mike: OPA
Note on F47: Lubun, Mike: OPA 5 ton
Note on F48: Lubun, Mike: OPA $202/ton works out to 3000 for a 15 ton unit

## cost$
Retrofit Costs | Escalation
| 1 | 1.25 | 1.25
Lighting Retrofit: Costing/Fixture | Materials $ | Labour $ | Design $ | Total $ | Incentive $
T8 to T5 Fluorescent per fixture | 80.5 | 71.875 | 25.875 | 178.25 | 25
400W Metal Halide to T5-High Bay per fixture | 506 | 85 | 107.5 | 698.5 | 105
250W Metal Halide to T5-High Bay per fixture | 506 | 85 | 107.5 | 698.5 | 105
HRV Retrofit: Costing/Unit
Plate HRV: 0 - 1180 L/sec capacity (ducting present) | 24725 | 10781.25 | 6250 | 41756.25 | 400
Plate HRV: 1200 - 2360 L/sec capacity (ducting present) | 28855 | 12506.25 | 7493.75 | 48855 | 700
Heat Wheel HRV: 0 - 1040 L/sec capacity (ducting present) | 40825 | 15381.25 | 9962.5 | 66168.75 | 600
Heat Wheel HRV: 1040 -2550 L/sec capacity (ducting present) | 57270 | 19550 | 13668.75 | 90488.75 | 1500
Heat Wheel HRV: 2600 - 5050 L/sec capacity (ducting present) | 89240 | 28031.25 | 20937.5 | 138208.75 | 1500
Heat Wheel HRV: 5100 - 9675 L/sec capacity (ducting present) | 166750 | 48875 | 38656.25 | 254281.25 | 1500
Demand Control Ventilation Retrofit Costing/Controller
Wall Mounted Space Sensor controlling AHU or VAV box | 512 | 345 | 147.5 | 1004.5
Duct Mounted Return Air Sensor controlling AHU | 512 | 431.25 | 160 | 1103.25 | 100
Space Temperature Sensor Retrofit: Costing/Controller
Pneumatic to programmable digital conversion | 506 | 216.25 | 126.25 | 848.5
Electric to programmable digital conversion | 173 | 86.25 | 45 | 304.25
Supply Air Temperature Reset Retrofit: Costing/Controller | 1380 | 1725 | 516.25 | 3621.25
Boiler (Hot Water) Reset Retrofit: Costing/Controller | 472 | 345 | 140 | 957
Occupancy Sensor to Control Plug Loads: Costing/Controller | 115 | 168.75 | 47.5 | 331.25
Retro-commissioning: Cost/building (20 room, 4 AHUs) | 0 | 5175 | 776.25 | 5951.25
Condensor Water Reset Retrofit: Costing/Controller | 2576 | 1207.5 | 665 | 4448.5
DX Compressor Upgrade: Costing/Unit
0-5 ton COP upgrade to COP 4.0 scroll (R-410A refrigerant) | 3450 | 862.5 | 775 | 5087.5 | 1000
5-15 ton COP upgrade to COP 4.0 scroll (R-410A refrigerant) | 9200 | 1150 | 1150 | 11500 | 3000
Solarwall: Costing/100 m2 installation
Unglazed solarwall (low temperature) | 150 | 193.75 | 57.5 | 401.25
Glazed solarwall (high temperature) | 178 | 208.75 | 63.75 | 450.5
Variable Speed Pump Retrofit: Costing/Unit
10 hp pump with a pressure differential switch control | 1840 | 1725 | 602.5 | 4167.5
10 hp pump with a valve conversion control (3-way to 2-way) | 1438 | 1582.5 | 507.5 | 3528
25 hp pump with a pressure differential switch control | 2588 | 1797.5 | 755 | 5140.5
25 hp pump with a valve conversion control (3-way to 2-way) | 1898 | 1652.5 | 605 | 4155.5
Variable Frequency Drive Retrofit: Costing/Unit
5 hp 3ph upgrade | 460 | 430 | 150 | 1040 | 265
10 hp 3ph upgrade | 580 | 460 | 175 | 1215 | 535
15 hp 3ph upgrade | 1036 | 575 | 280 | 1891 | 805
25 hp 3ph upgrade | 1612 | 690 | 405 | 2707 | 1340
Economizer Control for Cooling AHUs: Controller | 690 | 517.5 | 207.5 | 1415
Steam to Hot Water Heat Exchanger Conversion: Cost/Unit
Space Heating only conversion sized for up to 170 kW heating | 25300 | 11500 | 6466.25 | 43266.25
500 kW Space Heating and 500 kW DHW conversion | 63300 | 71875 | 22625 | 157800
500 kW Space Heating conversion | 40300 | 31625 | 12375 | 84300
Air Handling Unit Replacement: Costing/Unit
5 ton AHU replacement with COP 4.0 (SEER 20) DX | 9200 | 2162.5 | 2050 | 13412.5 | 1000
12-15 ton AHU replacement with COP 4.0 (SEER 20) DX | 15530 | 2875 | 2050 | 20455 | 3000
Solar DHW: Cost/System (30 m2 collector with 1500 L storage) | 28750 | 24437.5 | 9056.25 | 62243.75
On/OFF & Run-Time Controller for Exhaust Fans: Cost/Unit | 300 | 345 | 108.75 | 753.75
Motor Efficiency Upgrades: Cost/Unit
1 hp 3ph upgrade | 230 | 143.75 | 62.5 | 436.25
2 hp 3ph upgrade | 475 | 162.5 | 112.5 | 750
5 hp 3ph upgrade | 1440 | 287.5 | 312.5 | 2040
10 hp 3ph upgrade | 2590 | 306.25 | 531.25 | 3427.5
15 hp 3ph upgrade | 3020 | 325 | 612.5 | 3957.5
Note on C2: Lubun, Mike: increase from base of 60/hr to 75/hr
Note on D2: Lubun, Mike: increase from base of 100/hr to 125/hr
Note on F4: Lubun, Mike: OPA new fixture or retrofit
Note on F5: Lubun, Mike: OPA for T5 4-12 lamp HO fixture
Note on F6: Lubun, Mike: OPA for T5 4-12 lamp HO fixture
Note on F8: Lubun, Mike: Union Gas HRV <2000 cfm
Note on F9: Lubun, Mike: Union Gas HRV >2000 cfm
Note on F10: Lubun, Mike: Union Gas ERV <2000 cfm
Note on F11: Lubun, Mike: Union Gas ERV >2000 cfm
Note on F12: Lubun, Mike: Union Gas ERV >2000 cfm
Note on F13: Lubun, Mike: Union Gas ERV >2000 cfm
Note on F16: Lubun, Mike: Union gas, $100 per RTU/MUA if space is less than 2500 ft2 and contains a CO2 sensor, $200 for spaces greater than 2500 ft2. Incentive for offices only
Note on F26: Lubun, Mike: OPA 5 ton
Note on F27: Lubun, Mike: OPA $202/ton works out to 3000 for a 15 ton unit
Note on F37: Lubun, Mike: OPA
Note on F38: Lubun, Mike: OPA
Note on F39: Lubun, Mike: OPA
Note on F40: Lubun, Mike: OPA
Note on F47: Lubun, Mike: OPA 5 ton
Note on F48: Lubun, Mike: OPA $202/ton works out to 3000 for a 15 ton unit

## mnecb
Space Function | MNECB W/m2 | MNECB Fixture Type | MNECB Fixture W
Assembly
Auditorium/Exhibit | 17.2 | 2-4ft 32W T8 w/1 elec ballast | 65
Lobby | 10.8 | 2-4ft 32W T8 w/1 elec ballast | 65
Atria | 7.5 | 2-4ft 32W T8 w/1 elec ballast | 65
Recreation/Lounge | 7.5 | 2-4ft 32W T8 w/1 elec ballast | 65
Cenference/Meeting | 19.4 | 2-4ft 32W T8 w/1 elec ballast | 65
Indoor Athletics-Seating | 10.8 | 250W Metal Halide | 250
Recreational Sports Area | 13 | 250W Metal Halide | 250
Professional Sports Area | 28 | 250W Metal Halide | 250
Locker Rooms & Shower | 8.6 | 2-4ft 32W T8 w/1 elec ballast | 65
Hotel/Motel
Banquet Room | 25.8 | 2-4ft 32W T8 w/1 elec ballast | 65
Prefunction Area | 25.8 | 2-4ft 32W T8 w/1 elec ballast | 65
Guest Rooms | 15.1 | 2-4ft 32W T8 w/1 elec ballast | 65
Lobby/Reception | 21.5 | 2-4ft 32W T8 w/1 elec ballast | 65
Shop (non-Industrial)
Machinery | 26.9 | 400W Metal Halide | 400
Electric/Electronic | 26.9 | 400W Metal Halide | 400
Painting | 17.2 | 400W Metal Halide | 400
Carpentry | 24.8 | 400W Metal Halide | 400
Welding | 12.9 | 400W Metal Halide | 400
Auto Repair | 10.8 | 400W Metal Halide | 400
Office
Cat1 - enclosed | 19.4 | 2-4ft 32W T8 w/1 elec ballast | 65
Cat2-open | 20.4 | 2-4ft 32W T8 w/1 elec ballast | 65
Cat3-partitioned | 23.7 | 2-4ft 32W T8 w/1 elec ballast | 65
Computer/Office Eqpt | 22.6 | 2-4ft 32W T8 w/1 elec ballast | 65
Filing-inactive | 10.8 | 2-4ft 32W T8 w/1 elec ballast | 65
Sorting and Mailing | 19.4 | 2-4ft 32W T8 w/1 elec ballast | 65
Retail
Type D - general merch. | 35.5 | 2-4ft 32W T8 w/1 elec ballast | 65
Type E -food & misc | 30.1 | 2-4ft 32W T8 w/1 elec ballast | 65
Food Services
Bar/Lounge | 26.9 | 2-4ft 32W T8 w/1 elec ballast | 65
Leisure Dining | 26.9 | 2-4ft 32W T8 w/1 elec ballast | 65
Cafeteria | 14 | 2-4ft 32W T8 w/1 elec ballast | 65
Kitchen | 15.1 | 2-4ft 32W T8 w/1 elec ballast | 65
Dormitory
Bedroom | 11.8 | 2-4ft 32W T8 w/1 elec ballast | 65
Study Hall | 19.4 | 2-4ft 32W T8 w/1 elec ballast | 65
Education
Classroom | 21.5 | 2-4ft 32W T8 w/1 elec ballast | 65
Library-Stack Ceiling Light | 32.3 | 2-4ft 32W T8 w/1 elec ballast | 65
Card File | 17.2 | 2-4ft 32W T8 w/1 elec ballast | 65
Reading | 20.4 | 2-4ft 32W T8 w/1 elec ballast | 65
Laboratories | 24.8 | 2-4ft 32W T8 w/1 elec ballast | 65
Storage/Warehouse
Inactive | 3.2 | 2-4ft 32W T8 w/1 elec ballast | 65
Active-Bulky | 3.2 | 2-4ft 32W T8 w/1 elec ballast | 65
Active-Fine | 7.5 | 2-4ft 32W T8 w/1 elec ballast | 65
Material Handling | 10.8 | 2-4ft 32W T8 w/1 elec ballast | 65
Services/Common
Mech/Elec room | 7.5 | 2-4ft 32W T8 w/1 elec ballast | 65
Corridors | 8.6 | 2-4ft 32W T8 w/1 elec ballast | 65
Washrooms | 8.7 | 2-4ft 32W T8 w/1 elec ballast | 65
Active Stairway | 6.5 | 2-4ft 32W T8 w/1 elec ballast | 65
Emergency Stairway/Exit | 4.3 | 2-4ft 32W T8 w/1 elec ballast | 65
Baggage Area | 10.8 | 2-4ft 32W T8 w/1 elec ballast | 65
Airway Concourse | 9.7 | 2-4ft 32W T8 w/1 elec ballast | 65
Airway Waiting/Lounge | 12.9 | 2-4ft 32W T8 w/1 elec ballast | 65
Fire Engine Room | 8.6 | 250W Metal Halide | 250
Museum-Exhibit Area | 20.4 | 2-4ft 32W T8 w/1 elec ballast | 65
Museum-Restoration | 42 | 2-4ft 32W T8 w/1 elec ballast | 65
Museum Storage-inactive | 6.5 | 2-4ft 32W T8 w/1 elec ballast | 65
Museum Storage-active | 7.5 | 2-4ft 32W T8 w/1 elec ballast | 65
Laundry-Washing | 9.7 | 2-4ft 32W T8 w/1 elec ballast | 65
Laundry-Sorting & ironing | 14 | 2-4ft 32W T8 w/1 elec ballast | 65
Medical
Dental Suite Exam | 22.6 | 2-4ft 32W T8 w/1 elec ballast | 65
Emergency | 24.7 | 2-4ft 32W T8 w/1 elec ballast | 65
Laboratories | 20.4 | 2-4ft 32W T8 w/1 elec ballast | 65
Medical Supplies | 25.8 | 2-4ft 32W T8 w/1 elec ballast | 65
Nursery | 21.5 | 2-4ft 32W T8 w/1 elec ballast | 65
Nurse Station | 22.6 | 2-4ft 32W T8 w/1 elec ballast | 65
Occ/Physical Therapy | 17.2 | 2-4ft 32W T8 w/1 elec ballast | 65
Patient Rooms | 15.1 | 2-4ft 32W T8 w/1 elec ballast | 65
Pharmacy | 18.3 | 2-4ft 32W T8 w/1 elec ballast | 65
Radiology | 22.6 | 2-4ft 32W T8 w/1 elec ballast | 65
Surgical/O.B. Suites | 22.6 | 2-4ft 32W T8 w/1 elec ballast | 65
Operating Room | 75.3 | 2-4ft 32W T8 w/1 elec ballast | 65
Recovery | 24.8 | 2-4ft 32W T8 w/1 elec ballast | 65