## Overview
Office Space Type breakdown in TSD documents.
Small and Medium office were made by PNNL, and the large office was made by NREL. There is no large office AEDG.
Baseline should match the 2004 vintage of our templates. Use this as a relative load distribution guide for other vintages in our templates
Small Office (total people, total sqft) |  | 88 | 20000 |  | Ventilation | Ventilation
Space Type | % of total area | people pe 1000 sqft | LPD (W/ft^2) | EPD (W/ft^2) | CFM per person | CFM per sqft | Infiltration (ft^3/min*ft^2 ext) | Infiltration Sch
Open Office | 20% | 5 | 1.1 |  | 5 | 0.06
Private Office | 29% | 5 | 1.1 |  | 5 | 0.06
Conference | 8% | 50 | 1.3 |  | 20 | 0.06
Corridor | 12% | 0 | 0.5 |  | 0 | 0.06
Storage/Print/Copy | 14% | 0 | 0.8 |  | 0 | 0.12
Restrooms | 4% | 0 | 0.8 |  | 0 | 0
Lounge | 2% | 50 | 1.2 |  | 5 | 0.06
Elec/MechRoom | 2% | 0 | 1.5 |  | 0 | 0
Stairs | 3% | 0 | 0.6 |  | 0 | 0.06
Lobby | 6% | 10 | 1.3 |  | 3 | 0.06
whole building | 100% | 4.4 | 1 | 0.75
Ref Bldg - sm office | 100% | 5 | 1 | 1 | 21.86 |  | 0.059449 | 25%
- TSD has 88 people in 20,000sqft building. They take 44% of building as open and closed office and 100sqft per person. This should result in a value of 8.8 people per 1000 sqft, but in table 3.1 for ventilation it results in 8.05
- Restroom requires exhast only, no separate outside air
Medium Office (total people, total sqft) |  | 268 | 54000 |  | Ventilation | Ventilation
Space Type | % of total area | people pe 1000 sqft | LPD (W/ft^2) | EPD (W/ft^2) | CFM per person | CFM per sqft | Infiltration (ft^3/min*ft^2 ext) | Infiltration Sch
Open Office | 22% |  | 1.1 |  | 5 | 0.06
Private Office | 25% |  | 1.1 |  | 5 | 0.06
Conference | 10% |  | 1.3 |  | 5 | 0.06
Corridor | 10% |  | 0.5 |  | 5 | 0.06
Storage/Print/Copy | 15% |  | 0.8 |  | 5 | 0.06
Restrooms | 4% |  | 0.8 |  | 5 | 0.06
Lounge | 3% |  | 1.2 |  | 5 | 0.06
Elec/MechRoom | 3% |  | 1.5 |  | 5 | 0.06
Stairs | 2% |  | 0.6 |  | 5 | 0.06
Lobby | 6% |  | 1.3 |  | 5 | 0.06
whole building | 100% | 4.963 | 1 | 0.75 | 5 | 0.06
Ref Bldg - md office | 100% | 5 | 1 | 1 | 26.48 |  | 0.059449 | 25%
- TSD has 268 people in 54,000sqft building. They take 50% of building as open and closed office and 100sqft per person. This should result in a value of 5 people per 1000 sqft
Large Office - Low Rise (total people, total sqft) |  | 3419* | 460800 |  | Ventilation | Ventilation
Space Type | % of total area | people pe 1000 sqft | LPD (W/ft^2) | EPD (W/ft^2) | CFM per person | CFM per sqft | Infiltration (ft^3/min*ft^2 ext) | Infiltration Sch
Open Office
Private Office
Office | 85.4% | 5 | 1.1 | 0.4 | 5 | 0.06
Conference | 3.9% | 50 | 1.3 | 0.4 | 5 | 0.06
Corridor
Storage/Print/Copy
Restrooms | 2.4% | 5 | 0.9 | 0.1 |  | 1.04
Lounge/Break | 1.5% | 70 | 0.9 | 2.6 | 7.5 | 0.18
Elec/MechRoom | 3.6% |  | 1.5 | 0
Stairs | 1.7% |  | 0.6 | 0
Lobby
Elevator | 1.5% |  | 0 | 0
whole building | 100% | 7.42 | 1.09 | 0.4
Ref Bldg - lg office | 100% | 5 | 1 | 1 | 26.48 |  | 0.059449 | 25%
- TSD has 3494 people. 7.42x460.8 = 3419
Large Office - High Rise (total people, total sqft) |  | 3313 | 460800 |  | Ventilation | Ventilation
Space Type | % of total area | people pe 1000 sqft | LPD (W/ft^2) | EPD (W/ft^2) | CFM per person | CFM per sqft | Infiltration (ft^3/min*ft^2 ext) | Infiltration Sch
Open Office
Private Office
Office | 82.6% | 5 | 1.1 | 0.4 | 5 | 0.06
Conference | 3.8% | 50 | 1.3 | 0.4 | 5 | 0.06
Corridor
Storage/Print/Copy
Restrooms | 2.4% | 5 | 0.9 | 0.1 |  | 1.04
Lounge/Break | 1.5% | 70 | 0.9 | 2.6 | 7.5 | 0.18
Elec/MechRoom | 3.6% |  | 1.5 | 0
Stairs | 1.7% |  | 0.6 | 0
Lobby
Elevator | 4.4% |  | 0 | 0
whole building | 100% | 7.19 | 1.06 | 0.39
Ref Bldg - lg office | 100% | 5 | 1 | 1 | 26.48 |  | 0.059449 | 25%
- TSD has 3453 people. 7.19x460.8 = 3313

## EPD worksheet Baseline
Small Office (total people, total sqft) |  | 88 | 20000 | AEDG Target Values |  |  | Proposed Space Type assignments for plug loads
[10 empty] | Bsaseline | AEDG
Inventory | Quantity | Load each W/each | Total W | Quantity | Load each W/each | Total W | Space Type | Percent of total area | Space Type Area | EPW contribution | EPW contribution
Computers - Servers | 2 | 65 | 130 | 2 | 54 | 108 | IT | 0.5% | 100 | 1.3 | 1.08
Computers - desktop | 44 | 65 | 2860 | 29.2239 | 54 | 1578.0896 | Open Office | 15% | 3000 | 0.325 | 0.17933
[7 empty] | Private Office | 29% | 5800 | 0.325 | 0.17933
Computers - laptop | 44 | 19 | 836 | 58.7761 | 17 | 999.194 | Open Office | 15% | 3000 | 0.095 | 0.11354
[7 empty] | Private Office | 29% | 5800 | 0.095 | 0.11354
Monitors - servers - LCD | 2 | 35 | 70 | 2 | 24 | 48 | IT | 0.5% | 100 | 0.7 | 0.48
Monitors - desktop - LCD | 88 | 35 | 3080 | 88 | 24 | 2112 | Open Office | 15% | 3000 | 0.35 | 0.24
[7 empty] | Private Office | 29% | 5800 | 0.35 | 0.24
Laser printer - network | 2 | 215 | 430 | 2 | 180 | 360 | Print Room | 2.5% | 500 | 0.86 | 0.72
Copy machine | 2 | 1100 | 2200 | 2 | 500 | 1000 | Print Room | 2.5% | 500 | 4.4 | 2
Fax machine | 2 | 35 | 70 | 2 | 17 | 34 | Print Room | 2.5% | 500 | 0.14 | 0.068
Water cooler | 2 | 350 | 700 | 2 | 193 | 386 | Corridor | 12% | 2400 | 0.29167 | 0.16083
Refrigerator | 2 | 76 | 152 | 2 | 65 | 130 | Break | 2% | 400 | 0.38 | 0.325
Vending machine | 2 | 770 | 1540 | 2 | 770 | 1540 | Vending | 2% | 400 | 3.85 | 3.85
Coffee maker | 2 | 1050 | 2100 | 2 | 1050 | 2100 | Break | 2% | 400 | 5.25 | 5.25
Portable HVAC (heaters, fans) | 30 | 30 | 900 | 30 | 30 | 900 | Open Office | 15% | 3000 | 0.10227 | 0.10227
[7 empty] | Private Office | 29% | 5800 | 0.10227 | 0.10227
other small appliances | 90 | 4 | 360 | 90 | 4 | 360 | Open Office | 15% | 3000 | 0.040909 | 0.040909
[7 empty] | Private Office | 29% | 5800 | 0.040909 | 0.040909
Total plug load |  |  | 15428 |  |  | 11655.2836
Medium Office (total people, total sqft) |  | 268 | 54000
Inventory | Quantity | Load each W/each | Total W | Quantity | Load each W/each | Total W
Computers - Servers | 8 | 65 | 520 | 8 | 54 | 432
Computers - deskto | 134 | 65 | 8710 | 89 | 54 | 4806
Computers - laptop | 134 | 19 | 2546 | 179 | 17 | 3043
Monitors - servers - LCD | 8 | 35 | 280 | 8 | 24 | 192
Monitors - desktop - LCD | 268 | 35 | 9380 | 268 | 24 | 6432
Laser printer - network | 8 | 215 | 1720 | 8 | 180 | 1440
Copy machine | 4 | 1100 | 4400 | 4 | 500 | 2000
Fax machine | 8 | 35 | 280 | 8 | 17 | 136
Water cooler | 8 | 350 | 2800 | 8 | 193 | 1544
Refrigerator | 8 | 76 | 608 | 8 | 65 | 520
Vending machine | 4 | 770 | 3080 | 4 | 770 | 3080
Coffee maker | 4 | 1050 | 4200 | 4 | 1050 | 4200
*Portable HVAC (heaters, fans) | 30 | 30 | 900 | 30 | 30 | 900
other small appliances | 250 | 4 | 1000 | 250 | 4 | 1000
Total plug load |  |  | 40424 |  |  | 29725
* interesting that number of portable HVAC was same as small office. Not sure if that was error, or if it is assumed HVAC will be better

## Proposed Space Type 2004
sources for data are ref building, TSD, and standards spreadsheet dat
|  | TSD for small has 88 people | [9 empty] | Total calculations (based on 20k sqft building)
Small Office (total people, total sqft) |  | 173 |  |  | 20000
[8 empty] | Ventilation | [8 empty] | total CFM
Space Type | % of total area | people pe 1000 sqft | Peak Occupancy Sch Value |  | LPD (W/ft^2) | EPD (W/ft^2) | AEDG EPD (W/ft^2) | CFM per person | CFM per sqft | Infiltration (ft^3/min*ft^2 ext) | Infiltration Sch | design.peop | sch adj. people | light w | equip w | AEDG equip w | cfm/person | cfm/area
OfficeClosed | 15% | 4.75 | 0.85 | Office Work Occ | 1.1 | 0.86752 | 0.64225 | 20 |  | 0.0595 | Office Infil Quarter On | 14.25 | 12.1125 | 3300 | 2602.5682 | 1926.7566 | 95 | 0
OfficeOpen | 29% | 5.25 | 0.85 | Office Work Occ | 1.1 | 0.95884 | 0.70986 | 20 |  | 0.0595 | Office Infil Quarter On | 30.45 | 25.8825 | 6380 | 5561.2773 | 4117.1747 | 105 | 0
Conference | 8% | 50 | 0.4 | Office Misc Occ | 1.3 | 1 | 0.37016 | 20 |  | 0.0595 | Office Infil Quarter On | 80 | 32 | 2080 | 1600 | 592.2632 | 1000 | 0
Corridor | 12% | 1 | 0.85 | Office Work Occ | 0.5 | 0.29167 | 0.16083 |  | 0.05 | 0.0595 | Office Infil Quarter On | 2.4 | 2.04 | 1200 | 700 | 386 | 0.05 | 120
Storage | 14% |  |  |  | 0.8 | 0 | 0 |  | 0.05 | 0.0595 | Office Infil Quarter On | 0 | 0 | 2240 | 0 | 0 | 0 | 140
Restroom | 4% | 10 | 0.4 | Office Misc Occ | 0.8 | 0.27 | 0.07 |  | 0.96 | 0.0595 | Office Infil Quarter On | 8 | 3.2 | 640 | 216 | 56 | 0 | 768
BreakRoom | 2% | 50 | 0.4 | Office Misc Occ | 1.2 | 5.63 | 4.46 | 15 |  | 0.0595 | Office Infil Quarter On | 20 | 8 | 480 | 2252 | 1784 | 750 | 0
Elec/MechRoom | 2% |  |  |  | 1.5 | 0.27 | 0.27 | 20 |  | 0.0595 | Office Infil Quarter On | 0 | 0 | 600 | 108 | 108 | 0 | 0
Stair | 3% |  |  |  | 0.6 | 0 | 0 |  | 0.05 | 0.0595 | Office Infil Quarter On | 0 | 0 | 360 | 0 | 0 | 0 | 30
Lobby | 6% | 10 | 0.4 | Office Misc Occ | 1.3 | 0.27 | 0.07 | 15 |  | 0.0595 | Office Infil Quarter On | 12 | 4.8 | 1560 | 324 | 84 | 150 | 0
IT_Room | 0.5% | 5 | 0.4 | Office Misc Occ | 1.1 | 2 | 1.56 |  | 0.05 | 0.0595 | Office Infil Quarter On | 0.5 | 0.2 | 110 | 200 | 156 | 0 | 5
Vending | 2% | 1 | 0.4 | Office Misc Occ | 0.5 | 3.85 | 3.85 |  | 0.05 | 0.0595 | Office Infil Quarter On | 0.4 | 0.16 | 200 | 1540 | 1540 | 0 | 20
PrintRoom | 2.5% | 10 | 0.4 | Office Misc Occ | 1.1 | 5.4 | 2.788 |  | 0.05 | 0.0595 | Office Infil Quarter On | 5 | 2 | 550 | 2700 | 1394 | 0 | 25
whole building | 100% | 8.65 |  |  | 0.985 | 0.89019 | 0.60721 | 12.139 | 0.0554 | 0.0595 | Office Infil Quarter On | 173 | 90.395 | 19700 | 17803.8455 | 12144.1944 | 2100.05 | 1108
Ref Bldg - sm office | 100% | 5 |  |  | 1 | 1 |  | 21.86 |  | 0.059449 | 25% |  | 4.5198 | (schedule adjusted peak people - multi-space)
Ref Bldg - md office | 100% | 5 |  |  | 1 | 1 |  | 26.48 |  | 0.059449 | 25% |  | 4.75 | (ref sm office schedule adjusted peak people - ref)
Ref Bldg - lg office | 100% | 5 |  |  | 1 | 1 |  | 26.48 |  | 0.059449 | 25% |  | 4.18 | (TSD sm office schedule adjusted peak people - ref)
This does seem really high, but if they are good design values for the other spaces, then
| Peak schedule values | Ref Building | Proposed
| People | 0.95 | see table above
| LPD | 0.9 | see table above
| EPD | 0.9 | see table above
note: I'm currently using0.96 cfm/sqft (TSD's use exhaust instead and have no ventilation)
Total ventilation worksheet
|  | Multi-Space Type | sml Ref Bldg | md/lg ref Bldg
| cfm person total | 2100.05 | 2186 | 2648
| cfm area total | 1108
| total | 3208.05 | 2186 | 2648
It seems like small and medium office should have different occupancy and load densities from each other
Talking to Shanti, may make sense to slightly raise the people and plug load density for open office, and increase the lighting for closed. Look at 62.1
| Good link from wbdg.org |  | http://www.wbdg.org/design/office_st.php
Should Elevator be a space type, and if so what should it look like
Look at infiltration for different vintages. Here is what spreadhseet shows
Not sure of the source of these values.
On Demand
(ft^3/min*ft^2 ext)
| Pre 1980 | 0.2232
| 1980-2004 | 0.2232
| 2004 | 0.0595
| 2009 1-3 | 0.0595
| 2009 4-8 | 0.0446