## SheetMap
|  |  | SheetMap | Prototype Inputs | Templates | Standards | Climate Zones | Climate Zone Sets | Space Types | Ventilation | Occupancy | Interior Lighting | Construction Sets | Construction Properties | Constructions | Materials | Schedules | Exterior | Chillers | Unitary ACs | Heat Pumps | Boilers | Motors | Curve Biquadratics | Curve Bicubics | Curve Quadratics | Curve Cubics | Ground Temperatures | Lookups
64 | 65 | A |  | Template | Name | Name | Name | Name | Template | VlookupColumn | VlookupColumn | VLookupColumn | Template | Template | Name | Name | Name | #REF! | Template | Template | Template | Template | Template | Name | Name | Name | Name | Building Type
64 | 66 | B |  | Building Type | Notes |  | Standard | Climate Zone | Building Type | Ventilation Standard | Ventilation Standard | Lighting Standard | Building Type | Climate Zone Set | Intended Surface Type | Material Type | Category | #REF! | Cooling Type | Cooling Type | Cooling Type | Fluid Type | Number of Poles | coeff_1 | coeff_1 | coeff_1 | coeff_1 | Template | Intended Surface Type Lookup
64 | 67 | C |  | CHW Pumping Type |  |  | Representative City | Climate Zone2 | Space Type | Primary Space Type | Primary Space Type | Primary Space Type | Space Type | Intended Surface Type | Standards Construction Type | Roughness | Units | #REF! | Condenser Type | Heating Type | Heating Type | Fuel Type | Type | coeff_2 | coeff_2 | coeff_2 | coeff_2 | Climate Zone
64 | 68 | D | SheetMap | Chiller Cooling Type |  |  | BCL Weather Component ID | Climate Zone3 | RGB | Secondary Space Type | Secondary Space Type | Secondary Space Type | Is Residential | Standards Construction Type | Insulation Layer | Thickness (in) | Day Types | #REF! | Compressor Type | Subcategory | Subcategory | Minimum Capacity (Btu/hr) | Synchronous Speed (RPM) | coeff_3 | coeff_3 | coeff_3 | coeff_3 | Jan | Standards Construction Type Lookup
64 | 69 | E | Prototype Inputs | Chiller Condenser Type |  |  |  | Climate Zone4 | Lighting Standard | ft^3/min*person | people/1000 ft^2 | W/ft^2 | Exterior Wall Standards Construction Type | Building Category | Material 1 | Conductivity (Btu*in/hr*ft^2*F) | Start Date | #REF! | Absorption Type | Minimum Capacity (Btu/hr) | Minimum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Minimum Capacity (HP) | coeff_4 | coeff_4 | min_x | coeff_4 | Feb
64 | 70 | F | Templates | Chiller Compressor Type |  |  |  | Climate Zone5 | Lighting Primary Space Type | ft^3/min*ft^2 | Notes | W/ft | Exterior Wall Building Category | Construction | Material 2 | Resistance (hr*ft^2*F/Btu) | End Date | #REF! | Minimum Capacity (Tons) | Maximum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Minimum Annual Fuel Utilization Efficiency (AFUE) | Maximum Capacity (HP) | coeff_5 | coeff_5 | max_x | min_x | Mar | Building Type Lookup
64 | 71 | G | Standards | Chiller Capacity Guess (Tons) |  |  |  | Climate Zone6 | Lighting Secondary Space Type | ach |  | Import Order | Exterior Floor Standards Construction Type | Minimum Percent of Surface | Material 3 | Density (lb/ft^3) | Type | #REF! | Maximum Capacity (Tons) | Minimum Seasonal Energy Efficiency Ratio (SEER) | Minimum Seasonal Efficiency (SEER) | Minimum Thermal Efficiency (%) | Nominal Full Load Efficiency (%) | coeff_6 | coeff_6 | notes | max_x | Apr
64 | 72 | H | Climate Zones | PSZAC Cooling Type |  |  |  | Climate Zone7 | LookupColumn | Notes |  |  | Exterior Floor Building Category | Maximum Percent of Surface | Material 4 | Specific Heat (Btu/lbm*F) | Hr 1 | #REF! | Minimum Full Load Efficiency (kW/ton) | Minimum Energy Efficiency Ratio (EER) | Minimum Full Load Efficiency (EER) | Minimum Combustion Efficiency (%) | Notes | min_x | coeff_7 |  | notes | May | Space Type Lookup
64 | 73 | I | Climate Zone Sets | PSZAC Heating Type |  |  |  | Climate Zone8 | Lighting per Area (W/ft^2) |  |  |  | Exterior Roof Standards Construction Type | Assembly Maximum U-Value | Material 5 | Thermal Absorptance | Hr 2 | #REF! | Minimum Integrated Part Load Value (kW/ton) | Minimum Integrated Part Load Value (kW/ton) | Minimum IPLV | EFFFPLR |  | max_x | coeff_8 |  |  | Jun
64 | 74 | J | Space Types | PSZAC Fan Type |  |  |  | Climate Zone9 | Lighting per Person (W/person) |  |  |  | Exterior Roof Building Category | Assembly Maximum F Factor | Material 6 | Solar Absorptance | Hr 3 | #REF! | CAPFT | Minimum Integrated Energy Efficiency Ratio (IEER) | COOL CAP FT | Notes |  | min_y | coeff_9 |  |  | Jul | Lighting Standards Lookup
64 | 75 | K | Ventilation | PSZAC Supplemental Heating Type |  |  |  | Climate Zone10 | Lighting per Length (W/ft) |  |  |  | Interior Walls | Assembly Maximum C Factor | Sort | Visible Absorptance | Hr 4 | #REF! | EIRFT | PTAC_EER_Coefficient_1 | COOL CAP FFLOW |  |  | max_y | coeff_10 |  |  | Aug
64 | 76 | L | Occupancy | PSZAC Operation Schedule |  |  |  | Climate Zone11 | Additional Lighting per Area (W/ft^2) |  |  |  | Interior Floors | Assembly Maximum Solar Heat Gain Coefficient |  | Gas Type | Hr 5 | #REF! | EIRFPLR | PTAC_EER_Coefficient_2 | COOL EIR FT |  |  | notes | min_x |  |  | Sep | Ventilation Standards Lookup
64 | 77 | M | Interior Lighting | PSZAC OA Damper Schedule |  |  |  | Climate Zone12 | Lighting Fraction to Return Air |  |  |  | Interior Ceilings | Assembly Minimum VT SHGC |  | U-Factor (Btu/hr*ft^2*F) | Hr 6 | #REF! | Notes | COOL CAP FT | COOL EIR FFLOW |  |  |  | max_x |  |  | Oct
64 | 78 | N | Construction Sets | PSZAC Operation Schedule 2 |  |  |  | Climate Zone13 | Lighting Fraction Radiant |  |  |  | Ground Contact Wall Standards Construction Type | sort order |  | Solar Heat Gain Coefficient | Hr 7 | #REF! |  | COOL CAP FFLOW | COOL PLF FPLR |  |  |  | min_y |  |  | Nov | Material Type Lookup
64 | 79 | O | Construction Properties | PSZAC OA Damper Schedule 2 |  |  |  | Climate Zone14 | Lighting Fraction Visible |  |  |  | Ground Contact Wall Building Category |  |  | Visible Transmittance | Hr 8 | #REF! |  | COOL EIR FT | Notes |  |  |  | max_y |  |  | Dec
64 | 80 | P | Constructions | PSZAC Operation Schedule 3 |  |  |  | Climate Zone15 | Lighting Schedule |  |  |  | Ground Contact Floor Standards Construction Type |  |  | Optical Data Type | Hr 9 | #REF! |  | COOL EIR FFLOW |  |  |  |  | notes |  |  |  | Construction Category Lookup
64 | 81 | Q | Materials | PSZAC OA Damper Schedule 3 |  |  |  | Climate Zone16 | Ventilation Standard |  |  |  | Ground Contact Floor Building Category |  |  | Solar Transmittance At Normal Incidence | Hr 10 | #REF! |  | COOL PLF FPLR
64 | 82 | R | Schedules | Occ Sensing Exterior Lighting Power (W) |  |  |  | Climate Zone17 | Ventilation Primary Space Type |  |  |  | Ground Contact Ceiling Standards Construction Type |  |  | Front Side Solar Reflectance At Normal Incidence | Hr 11 | #REF! |  | Notes
64 | 83 | S | Exterior | Occ Sensing Exterior Lighting Schedule |  |  |  | Climate Zone18 | Ventilation Secondary Space Type |  |  |  | Ground Contact Ceiling Building Category |  |  | Back Side Solar Reflectance At Normal Incidence | Hr 12 | #REF!
64 | 84 | T | Chillers | NonDimming Exterior Lighting Power (W) |  |  |  | Climate Zone19 | Lookup |  |  |  | Exterior Fixed Window Standards Construction Type |  |  | Visible Transmittance At Normal Incidence | Hr 13 | #REF!
64 | 85 | U | Unitary ACs | NonDimming Exterior Lighting Schedule |  |  |  | Climate Zone20 | Ventilation per Area (ft^3/min*ft^2) |  |  |  | Exterior Fixed Window Building Category |  |  | Front Side Visible Reflectance At Normal Incidence | Hr 14 | #REF!
64 | 86 | V | Heat Pumps | Exterior Fuel Equipment1 Power (W) |  |  |  | Climate Zone21 | Ventilation per Person (ft^3/min*person) |  |  |  | Exterior Operable Window Standards Construction Type |  |  | Back Side Visible Reflectance At Normal Incidence | Hr 15 | #REF!
64 | 87 | W | Boilers | Exterior Fuel Equipment1 Schedule |  |  |  | Climate Zone22 | Ventilation Air Changes (ach) |  |  |  | Exterior Operable Window Building Category |  |  | Infrared Transmittance At Normal Incidence | Hr 16 | #REF!
64 | 88 | X | Motors | Exterior Fuel Equipment2 Power (W) |  |  |  | Climate Zone23 | Occupancy per Area (people/1000 ft^2) |  |  |  | Exterior Door Standards Construction Type |  |  | Front Side Infrared Hemispherical Emissivity | Hr 17 | #REF!
64 | 89 | Y | Curve Biquadratics | Exterior Fuel Equipment2 Schedule |  |  |  | Climate Zone24 | Occupancy Schedule |  |  |  | Exterior Door Building Category |  |  | Back Side Infrared Hemispherical Emissivity | Hr 18 | #REF!
64 | 90 | Z | Curve Bicubics | Main Water Heater Volume (gal) |  |  |  | Climate Zone25 | Occupancy Activity Schedule |  |  |  | Exterior Glass Doors |  |  | Dirt Correction Factor For Solar And Visible Transmittance | Hr 19 | #REF!
65 | 65 | AA | Curve Quadratics | Main Water Heater Fuel |  |  |  | Climate Zone26 | Infiltration per Exterior Area (ft^3/min*ft^2 ext) |  |  |  | Exterior Overhead Door Standards Construction Type |  |  | Solar Diffusing | Hr 20 | #REF!
65 | 66 | AB | Curve Cubics | Main Water Heater Capacity (Btu/hr) |  |  |  | Climate Zone27 | Infiltration per Exterior Wall Area (ft^3/min*ft^2 ext) |  |  |  | Exterior Overhead Door Building Category |  |  | Material Standard | Hr 21 | #REF!
65 | 67 | AC | Ground Temperatures | Main Service Water Temperature (F) |  |  |  | Climate Zone28 | Infiltration Air Changes (ach) |  |  |  | Exterior Skylight Standards Construction Type |  |  | Material Standard Source | Hr 22 | #REF!
65 | 68 | AD | Lookups | Main Service Water FlowRate Schedule |  |  |  | Climate Zone29 | Infiltration Schedule |  |  |  | Exterior Skylight Building Category |  |  | Code Category | Hr 23 | #REF!
65 | 69 | AE |  | Main Service Water Peak FlowRate (gal/min) |  |  |  | Climate Zone30 | Gas Equipment per Area (Btu/hr*ft^2) |  |  |  | Tubular Daylight Domes |  |  | Code Identifier | Hr 24 | #REF!
65 | 70 | AF |  | Main Water Use Temperature (F) |  |  |  | Climate Zone31 | Gas Equipment Fraction Latent |  |  |  | Tubular Daylight Diffusers |  |  | Framing Material | Notes | #REF!
65 | 71 | AG |  | Main Service Water Temperature at Fixture (F) |  |  |  | Climate Zone32 | Gas Equipment Fraction Radiant |  |  |  | Interior Fixed Windows |  |  | Framing Configuration |  | #REF!
65 | 72 | AH |  | Main Service Water Pump Head (Pa) |  |  |  | Climate Zone33 | Gas Equipment Fraction Lost |  |  |  | Interior Operable Windows |  |  | Framing Depth |  | #REF!
65 | 73 | AI |  | Main Service Water Pump Motor Efficiency (%) |  |  |  | Climate Zone34 | Gas Equipment Schedule |  |  |  | Interior Doors |  |  | Framing Size |  | #REF!
65 | 74 | AJ |  | Main Service Water Parasitic Fuel Consumption Rate (Btu/h) |  |  |  | Climate Zone35 | Electric Equipment per Area (W/ft^2) |  |  |  | Space Shading |  |  | Cavity Insulation (hr*ft^2*F/Btu) |  | #REF!
65 | 75 | AK |  | Laundry Water Heater Volume (gal) |  |  |  | Climate Zone36 | Electric Equipment Fraction Latent |  |  |  | Building Shading |  |  | sort |  | #REF!
65 | 76 | AL |  | Laundry Water Heater Fuel |  |  |  | Climate Zone37 | Electric Equipment Fraction Radiant |  |  |  | Site Shading |  |  |  |  | #REF!
65 | 77 | AM |  | Laundry Water Heater Capacity (Btu/hr) |  |  |  | Climate Zone38 | Electric Equipment Fraction Lost |  |  |  | Interior Partitions |  |  |  |  | #REF!
65 | 78 | AN |  | Laundry Service Water Temperature (F) |  |  |  | Climate Zone39 | Electric Equipment Schedule | [8 empty] | #REF!
65 | 79 | AO |  | Laundry Service Water FlowRate Schedule |  |  |  |  | Heating Setpoint Schedule | [8 empty] | #REF!
65 | 80 | AP |  | Laundry Service Water Peak FlowRate (gal/min) |  |  |  |  | Cooling Setpoint Schedule | [8 empty] | #REF!
65 | 81 | AQ |  | Laundry Water Use Temperature (F) |  |  |  |  | Service Water Heating Peak Flow Rate (gal/h) | [8 empty] | #REF!
65 | 82 | AR |  | Laundry Service Water Temperature at Fixture (F) |  |  |  |  | Service Water Heating Area (ft^2) | [8 empty] | #REF!
65 | 83 | AS |  | Laundry Service Water Pump Head (Pa) |  |  |  |  | Service Water Heating Peak Flow per Area (gal/h*ft^2) | [8 empty] | #REF!
65 | 84 | AT |  | Laundry Service Water Pump Motor Efficiency (%) |  |  |  |  | Service Water Heating Target Temperature (C) | [8 empty] | #REF!
65 | 85 | AU |  | Laundry Service Water Parasitic Fuel Consumption Rate (Btu/h) |  |  |  |  | Service Water Heating Fraction Sensible | [8 empty] | #REF!
65 | 86 | AV |  | Booster Water Heater Volume (gal) |  |  |  |  | Service Water Heating Fraction Latent | [8 empty] | #REF!
65 | 87 | AW |  | Booster Water Heater Fuel |  |  |  |  | Service Water Heating Schedule | [8 empty] | #REF!
65 | 88 | AX |  | Booster Water Heater Capacity (Btu/hr) |  |  |  |  | Exhaust per Area (cfm/ft2) | [8 empty] | #REF!
65 | 89 | AY |  | Booster Inlet Water Temperature (F) |  |  |  |  | Exhaust per Unit (cfm) | [8 empty] | #REF!
65 | 90 | AZ |  | Booster Service Water FlowRate Schedule |  |  |  |  | Exhaust Fan Power per Area (W/ft^2) | [8 empty] | #REF!
66 | 65 | BA |  | Booster Service Water Peak FlowRate (gal/min) |  |  |  |  | Exhaust Fan Efficiency | [8 empty] | #REF!
66 | 66 | BB |  | Booster Water Use Temperature (F) |  |  |  |  | Exhaust Fan Power (W) | [8 empty] | #REF!
66 | 67 | BC |  | Booster Water Temperature (F) |  |  |  |  | Exhaust Fan Pressure Rise (Pa) | [8 empty] | #REF!
66 | 68 | BD |  | Booster Service Water Parasitic Fuel Consumption Rate (Btu/h) |  |  |  |  | Exhaust Fan Maximum Flow Rate (cfm) | [8 empty] | #REF!
66 | 69 | BE |  | Typical Heating Setpoint |  |  |  |  | Exhaust Schedule | [8 empty] | #REF!
66 | 70 | BF |  | Typical Cooling Setpoint |  |  |  |  | Balanced Exhaust Fraction Schedule | [8 empty] | #REF!
66 | 71 | BG |  | PTAC Cooling Type |  |  |  |  | Is Residential | [8 empty] | #REF!
66 | 72 | BH |  | PTAC Heating Type | [13 empty] | #REF!
66 | 73 | BI |  | PTAC Fan Type | [13 empty] | #REF!
66 | 74 | BJ |  | PTAC Operation Schedule | [13 empty] | #REF!
66 | 75 | BK |  | PTAC OA Damper Schedule | [13 empty] | #REF!
66 | 76 | BL |  | SAC Cooling Type | [13 empty] | #REF!
66 | 77 | BM |  | SAC Heating Type | [13 empty] | #REF!
66 | 78 | BN |  | SAC Fan Type | [13 empty] | #REF!
66 | 79 | BO |  | SAC Operation Schedule | [13 empty] | #REF!
66 | 80 | BP |  | SAC Operation Schedule Meeting | [13 empty] | #REF!
66 | 81 | BQ |  | SAC OA Damper Schedule | [13 empty] | #REF!
66 | 82 | BR |  | UnitHeater Heating Type | [13 empty] | #REF!
66 | 83 | BS |  | UnitHeater Fan Type | [13 empty] | #REF!
66 | 84 | BT |  | UnitHeater Fan Control Type | [13 empty] | #REF!
66 | 85 | BU |  | UnitHeater Fan Static Pressure (inH20) | [13 empty] | #REF!
66 | 86 | BV |  | UnitHeater Operation Schedule | [13 empty] | #REF!
66 | 87 | BW |  | VAV Operation Schedule | [13 empty] | #REF!
66 | 88 | BX |  | VAV OA Damper Schedule | [13 empty] | #REF!
66 | 89 | BY |  | VAV Fan Efficiency | [13 empty] | #REF!
66 | 90 | BZ |  | VAV Fan Pressure Rise (Pa) | [13 empty] | #REF!
67 | 65 | CA |  | VAV Fan Motor Efficiency | [13 empty] | #REF!
67 | 66 | CB |  | DOAS Fan Maximum Flow Rate (cfm) | [13 empty] | #REF!
67 | 67 | CC |  | DOAS OA Damper Schedule | [13 empty] | #REF!
67 | 68 | CD |  | DOAS Economizer Control Type | [13 empty] | #REF!
67 | 69 | CE |  | Elevator Type | [13 empty] | #REF!
67 | 70 | CF |  | Number of Elevators | [13 empty] | #REF!
67 | 71 | CG |  | Elevator Schedule | [13 empty] | #REF!
67 | 72 | CH |  | Elevator Fan Schedule | [13 empty] | #REF!
67 | 73 | CI | [15 empty] | #REF!
67 | 74 | CJ | [15 empty] | #REF!
67 | 75 | CK | [15 empty] | #REF!
67 | 76 | CL | [15 empty] | #REF!
67 | 77 | CM | [15 empty] | #REF!
67 | 78 | CN | [15 empty] | #REF!
67 | 79 | CO | [15 empty] | #REF!
67 | 80 | CP | [15 empty] | #REF!
67 | 81 | CQ | [15 empty] | #REF!
67 | 82 | CR | [15 empty] | #REF!
67 | 83 | CS | [15 empty] | #REF!
67 | 84 | CT | [15 empty] | #REF!
67 | 85 | CU | [15 empty] | #REF!
67 | 86 | CV | [15 empty] | #REF!
67 | 87 | CW | [15 empty] | #REF!
67 | 88 | CX | [15 empty] | #REF!
67 | 89 | CY | [15 empty] | #REF!
67 | 90 | CZ | [15 empty] | #REF!
68 | 65 | DA | [15 empty] | #REF!
68 | 66 | DB | [15 empty] | #REF!
68 | 67 | DC | [15 empty] | #REF!
68 | 68 | DD | [15 empty] | #REF!
68 | 69 | DE | [15 empty] | #REF!
68 | 70 | DF | [15 empty] | #REF!
68 | 71 | DG | [15 empty] | #REF!
68 | 72 | DH | [15 empty] | #REF!
68 | 73 | DI | [15 empty] | #REF!
68 | 74 | DJ | [15 empty] | #REF!
68 | 75 | DK | [15 empty] | #REF!
68 | 76 | DL | [15 empty] | #REF!
68 | 77 | DM | [15 empty] | #REF!
68 | 78 | DN | [15 empty] | #REF!
68 | 79 | DO | [15 empty] | #REF!
68 | 80 | DP | [15 empty] | #REF!
68 | 81 | DQ | [15 empty] | #REF!
68 | 82 | DR | [15 empty] | #REF!
68 | 83 | DS | [15 empty] | #REF!
68 | 84 | DT | [15 empty] | #REF!
68 | 85 | DU | [15 empty] | #REF!
68 | 86 | DV | [15 empty] | #REF!
68 | 87 | DW | [15 empty] | #REF!
68 | 88 | DX | [15 empty] | #REF!
68 | 89 | DY | [15 empty] | #REF!
68 | 90 | DZ | [15 empty] | #REF!
69 | 65 | EA | [15 empty] | #REF!
69 | 66 | EB | [15 empty] | #REF!
69 | 67 | EC | [15 empty] | #REF!
69 | 68 | ED | [15 empty] | #REF!
69 | 69 | EE | [15 empty] | #REF!
69 | 70 | EF | [15 empty] | #REF!
69 | 71 | EG | [15 empty] | #REF!
69 | 72 | EH | [15 empty] | #REF!
69 | 73 | EI | [15 empty] | #REF!
69 | 74 | EJ | [15 empty] | #REF!
69 | 75 | EK | [15 empty] | #REF!
69 | 76 | EL | [15 empty] | #REF!
69 | 77 | EM | [15 empty] | #REF!
69 | 78 | EN | [15 empty] | #REF!
69 | 79 | EO | [15 empty] | #REF!
69 | 80 | EP | [15 empty] | #REF!
69 | 81 | EQ | [15 empty] | #REF!
69 | 82 | ER | [15 empty] | #REF!
69 | 83 | ES | [15 empty] | #REF!
69 | 84 | ET | [15 empty] | #REF!
69 | 85 | EU | [15 empty] | #REF!
69 | 86 | EV | [15 empty] | #REF!
69 | 87 | EW | [15 empty] | #REF!
69 | 88 | EX | [15 empty] | #REF!
69 | 89 | EY | [15 empty] | #REF!
69 | 90 | EZ | [15 empty] | #REF!
70 | 65 | FA | [15 empty] | #REF!
70 | 66 | FB | [15 empty] | #REF!
70 | 67 | FC | [15 empty] | #REF!
70 | 68 | FD | [15 empty] | #REF!
70 | 69 | FE | [15 empty] | #REF!
70 | 70 | FF | [15 empty] | #REF!
70 | 71 | FG | [15 empty] | #REF!
70 | 72 | FH | [15 empty] | #REF!
70 | 73 | FI | [15 empty] | #REF!
70 | 74 | FJ | [15 empty] | #REF!
70 | 75 | FK | [15 empty] | #REF!
70 | 76 | FL | [15 empty] | #REF!
70 | 77 | FM | [15 empty] | #REF!
70 | 78 | FN | [15 empty] | #REF!
70 | 79 | FO | [15 empty] | #REF!
70 | 80 | FP | [15 empty] | #REF!
70 | 81 | FQ | [15 empty] | #REF!
70 | 82 | FR | [15 empty] | #REF!
70 | 83 | FS | [15 empty] | #REF!
70 | 84 | FT | [15 empty] | #REF!
70 | 85 | FU | [15 empty] | #REF!
70 | 86 | FV | [15 empty] | #REF!
70 | 87 | FW | [15 empty] | #REF!
70 | 88 | FX | [15 empty] | #REF!
70 | 89 | FY | [15 empty] | #REF!
70 | 90 | FZ | [15 empty] | #REF!
71 | 65 | GA | [15 empty] | #REF!
71 | 66 | GB | [15 empty] | #REF!
71 | 67 | GC | [15 empty] | #REF!
71 | 68 | GD | [15 empty] | #REF!
71 | 69 | GE | [15 empty] | #REF!
71 | 70 | GF | [15 empty] | #REF!
71 | 71 | GG | [15 empty] | #REF!
71 | 72 | GH | [15 empty] | #REF!
71 | 73 | GI | [15 empty] | #REF!
71 | 74 | GJ | [15 empty] | #REF!
71 | 75 | GK | [15 empty] | #REF!
71 | 76 | GL | [15 empty] | #REF!
71 | 77 | GM | [15 empty] | #REF!
71 | 78 | GN | [15 empty] | #REF!
71 | 79 | GO | [15 empty] | #REF!
71 | 80 | GP | [15 empty] | #REF!
71 | 81 | GQ | [15 empty] | #REF!
71 | 82 | GR | [15 empty] | #REF!
71 | 83 | GS | [15 empty] | #REF!
71 | 84 | GT | [15 empty] | #REF!
71 | 85 | GU | [15 empty] | #REF!
71 | 86 | GV | [15 empty] | #REF!
71 | 87 | GW | [15 empty] | #REF!
71 | 88 | GX | [15 empty] | #REF!
71 | 89 | GY | [15 empty] | #REF!
71 | 90 | GZ | [15 empty] | #REF!
72 | 65 | HA | [15 empty] | #REF!
72 | 66 | HB | [15 empty] | #REF!
72 | 67 | HC | [15 empty] | #REF!
72 | 68 | HD | [15 empty] | #REF!
72 | 69 | HE | [15 empty] | #REF!
72 | 70 | HF | [15 empty] | #REF!
72 | 71 | HG | [15 empty] | #REF!
72 | 72 | HH | [15 empty] | #REF!
72 | 73 | HI | [15 empty] | #REF!
72 | 74 | HJ | [15 empty] | #REF!
72 | 75 | HK | [15 empty] | #REF!
72 | 76 | HL | [15 empty] | #REF!
72 | 77 | HM | [15 empty] | #REF!
72 | 78 | HN | [15 empty] | #REF!
72 | 79 | HO | [15 empty] | #REF!
72 | 80 | HP | [15 empty] | #REF!
72 | 81 | HQ | [15 empty] | #REF!
72 | 82 | HR | [15 empty] | #REF!
72 | 83 | HS | [15 empty] | #REF!
72 | 84 | HT | [15 empty] | #REF!
72 | 85 | HU | [15 empty] | #REF!
72 | 86 | HV | [15 empty] | #REF!
72 | 87 | HW | [15 empty] | #REF!
72 | 88 | HX | [15 empty] | #REF!
72 | 89 | HY | [15 empty] | #REF!
72 | 90 | HZ | [15 empty] | #REF!
73 | 65 | IA | [15 empty] | #REF!
73 | 66 | IB | [15 empty] | #REF!
73 | 67 | IC | [15 empty] | #REF!
73 | 68 | ID | [15 empty] | #REF!
73 | 69 | IE | [15 empty] | #REF!
73 | 70 | IF | [15 empty] | #REF!
73 | 71 | IG | [15 empty] | #REF!
73 | 72 | IH | [15 empty] | #REF!
73 | 73 | II | [15 empty] | #REF!
73 | 74 | IJ | [15 empty] | #REF!
73 | 75 | IK | [15 empty] | #REF!
73 | 76 | IL | [15 empty] | #REF!
73 | 77 | IM | [15 empty] | #REF!
73 | 78 | IN | [15 empty] | #REF!
73 | 79 | IO | [15 empty] | #REF!
73 | 80 | IP | [15 empty] | #REF!
73 | 81 | IQ | [15 empty] | #REF!
73 | 82 | IR | [15 empty] | #REF!
73 | 83 | IS | [15 empty] | #REF!
73 | 84 | IT | [15 empty] | #REF!
73 | 85 | IU | [15 empty] | #REF!
73 | 86 | IV | [15 empty] | #REF!
73 | 87 | IW | [15 empty] | #REF!
73 | 88 | IX | [15 empty] | #REF!
73 | 89 | IY | [15 empty] | #REF!
73 | 90 | IZ | [15 empty] | #REF!
74 | 65 | JA | [15 empty] | #REF!
74 | 66 | JB | [15 empty] | #REF!
74 | 67 | JC | [15 empty] | #REF!
74 | 68 | JD | [15 empty] | #REF!
74 | 69 | JE | [15 empty] | #REF!
74 | 70 | JF | [15 empty] | #REF!
74 | 71 | JG | [15 empty] | #REF!
74 | 72 | JH | [15 empty] | #REF!
74 | 73 | JI | [15 empty] | #REF!
74 | 74 | JJ | [15 empty] | #REF!
74 | 75 | JK | [15 empty] | #REF!
74 | 76 | JL | [15 empty] | #REF!
74 | 77 | JM | [15 empty] | #REF!
74 | 78 | JN | [15 empty] | #REF!
74 | 79 | JO | [15 empty] | #REF!
74 | 80 | JP | [15 empty] | #REF!
74 | 81 | JQ | [15 empty] | #REF!
74 | 82 | JR | [15 empty] | #REF!
74 | 83 | JS | [15 empty] | #REF!
74 | 84 | JT | [15 empty] | #REF!
74 | 85 | JU | [15 empty] | #REF!
74 | 86 | JV | [15 empty] | #REF!
74 | 87 | JW | [15 empty] | #REF!
74 | 88 | JX | [15 empty] | #REF!
74 | 89 | JY | [15 empty] | #REF!
74 | 90 | JZ | [15 empty] | #REF!
75 | 65 | KA | [15 empty] | #REF!
75 | 66 | KB | [15 empty] | #REF!
75 | 67 | KC | [15 empty] | #REF!
75 | 68 | KD | [15 empty] | #REF!
75 | 69 | KE | [15 empty] | #REF!
75 | 70 | KF | [15 empty] | #REF!
75 | 71 | KG | [15 empty] | #REF!
75 | 72 | KH | [15 empty] | #REF!
75 | 73 | KI | [15 empty] | #REF!
75 | 74 | KJ | [15 empty] | #REF!
75 | 75 | KK | [15 empty] | #REF!
75 | 76 | KL | [15 empty] | #REF!
75 | 77 | KM | [15 empty] | #REF!
75 | 78 | KN | [15 empty] | #REF!
75 | 79 | KO | [15 empty] | #REF!
75 | 80 | KP | [15 empty] | #REF!
75 | 81 | KQ | [15 empty] | #REF!
75 | 82 | KR | [15 empty] | #REF!
75 | 83 | KS | [15 empty] | #REF!
75 | 84 | KT | [15 empty] | #REF!
75 | 85 | KU | [15 empty] | #REF!
75 | 86 | KV | [15 empty] | #REF!
75 | 87 | KW | [15 empty] | #REF!
75 | 88 | KX | [15 empty] | #REF!
75 | 89 | KY | [15 empty] | #REF!
75 | 90 | KZ | [15 empty] | #REF!
76 | 65 | LA | [15 empty] | #REF!
76 | 66 | LB | [15 empty] | #REF!
76 | 67 | LC | [15 empty] | #REF!
76 | 68 | LD | [15 empty] | #REF!
76 | 69 | LE | [15 empty] | #REF!
76 | 70 | LF | [15 empty] | #REF!
76 | 71 | LG | [15 empty] | #REF!
76 | 72 | LH | [15 empty] | #REF!
76 | 73 | LI | [15 empty] | #REF!
76 | 74 | LJ | [15 empty] | #REF!
76 | 75 | LK | [15 empty] | #REF!
76 | 76 | LL | [15 empty] | #REF!
76 | 77 | LM | [15 empty] | #REF!
76 | 78 | LN | [15 empty] | #REF!
76 | 79 | LO | [15 empty] | #REF!
76 | 80 | LP | [15 empty] | #REF!
76 | 81 | LQ | [15 empty] | #REF!
76 | 82 | LR | [15 empty] | #REF!
76 | 83 | LS | [15 empty] | #REF!
76 | 84 | LT | [15 empty] | #REF!
76 | 85 | LU | [15 empty] | #REF!
76 | 86 | LV | [15 empty] | #REF!
76 | 87 | LW | [15 empty] | #REF!
76 | 88 | LX | [15 empty] | #REF!
76 | 89 | LY | [15 empty] | #REF!
76 | 90 | LZ | [15 empty] | #REF!
77 | 65 | MA | [15 empty] | #REF!
77 | 66 | MB | [15 empty] | #REF!
77 | 67 | MC | [15 empty] | #REF!
77 | 68 | MD | [15 empty] | #REF!
77 | 69 | ME | [15 empty] | #REF!
77 | 70 | MF | [15 empty] | #REF!
77 | 71 | MG | [15 empty] | #REF!
77 | 72 | MH | [15 empty] | #REF!
77 | 73 | MI | [15 empty] | #REF!
77 | 74 | MJ | [15 empty] | #REF!
77 | 75 | MK | [15 empty] | #REF!
77 | 76 | ML | [15 empty] | #REF!
77 | 77 | MM | [15 empty] | #REF!
77 | 78 | MN | [15 empty] | #REF!
77 | 79 | MO | [15 empty] | #REF!
77 | 80 | MP | [15 empty] | #REF!
77 | 81 | MQ | [15 empty] | #REF!
77 | 82 | MR | [15 empty] | #REF!
77 | 83 | MS | [15 empty] | #REF!
77 | 84 | MT | [15 empty] | #REF!

## Prototype Inputs
Each row contains the inputs for a specific building type/climate zone/vintage combination
[13 empty] | PSZAC has different operation schedule | [55 empty] | Gas;Electric | ConstantVolume | OnOff;Continuous
Template | Building Type | CHW Pumping Type | Chiller Cooling Type | Chiller Condenser Type | Chiller Compressor Type | Chiller Capacity Guess (Tons) | PSZAC Cooling Type | PSZAC Heating Type | PSZAC Fan Type | PSZAC Supplemental Heating Type | PSZAC Operation Schedule | PSZAC OA Damper Schedule | PSZAC Operation Schedule 2 | PSZAC OA Damper Schedule 2 | PSZAC Operation Schedule 3 | PSZAC OA Damper Schedule 3 | Occ Sensing Exterior Lighting Power (W) | Occ Sensing Exterior Lighting Schedule | NonDimming Exterior Lighting Power (W) | NonDimming Exterior Lighting Schedule | Exterior Fuel Equipment1 Power (W) | Exterior Fuel Equipment1 Schedule | Exterior Fuel Equipment2 Power (W) | Exterior Fuel Equipment2 Schedule | Main Water Heater Volume (gal) | Main Water Heater Fuel | Main Water Heater Capacity (Btu/hr) | Main Service Water Temperature (F) | Main Service Water FlowRate Schedule | Main Service Water Peak FlowRate (gal/min) | Main Water Use Temperature (F) | Main Service Water Temperature at Fixture (F) | Main Service Water Pump Head (Pa) | Main Service Water Pump Motor Efficiency (%) | Main Service Water Parasitic Fuel Consumption Rate (Btu/h) | Laundry Water Heater Volume (gal) | Laundry Water Heater Fuel | Laundry Water Heater Capacity (Btu/hr) | Laundry Service Water Temperature (F) | Laundry Service Water FlowRate Schedule | Laundry Service Water Peak FlowRate (gal/min) | Laundry Water Use Temperature (F) | Laundry Service Water Temperature at Fixture (F) | Laundry Service Water Pump Head (Pa) | Laundry Service Water Pump Motor Efficiency (%) | Laundry Service Water Parasitic Fuel Consumption Rate (Btu/h) | Booster Water Heater Volume (gal) | Booster Water Heater Fuel | Booster Water Heater Capacity (Btu/hr) | Booster Inlet Water Temperature (F) | Booster Service Water FlowRate Schedule | Booster Service Water Peak FlowRate (gal/min) | Booster Water Use Temperature (F) | Booster Water Temperature (F) | Booster Service Water Parasitic Fuel Consumption Rate (Btu/h) | Typical Heating Setpoint | Typical Cooling Setpoint | PTAC Cooling Type | PTAC Heating Type | PTAC Fan Type | PTAC Operation Schedule | PTAC OA Damper Schedule | SAC Cooling Type | SAC Heating Type | SAC Fan Type | SAC Operation Schedule | SAC Operation Schedule Meeting | SAC OA Damper Schedule | UnitHeater Heating Type | UnitHeater Fan Type | UnitHeater Fan Control Type | UnitHeater Fan Static Pressure (inH20) | UnitHeater Operation Schedule | VAV Operation Schedule | VAV OA Damper Schedule | VAV Fan Efficiency | VAV Fan Pressure Rise (Pa) | VAV Fan Motor Efficiency | DOAS Fan Maximum Flow Rate (cfm) | DOAS OA Damper Schedule | DOAS Economizer Control Type | Elevator Type | Number of Elevators | Elevator Schedule | Elevator Fan Schedule
90.1-2004 | FullServiceRestaurant | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantSitDown HVACOperationSchd | RestaurantSitDown MinOA_MotorizedDamper_Sched | [6 empty] | 3695 | RestaurantSitDown Exterior_Lgt_ALWAYS_ON |  |  |  |  | 200 | Natural Gas | 200000 | 140 | RestaurantSitDown BLDG_SWH_SCH | 2.22 | 140 | 131 | 29891 | 0.3 | 2648 | [10 empty] | 68.24 | 6 | Electricity | 27297 | 140 | RestaurantSitDown BLDG_SWH_SCH | 1.33 | 140 | 180 |  | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2007 | FullServiceRestaurant | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantSitDown HVACOperationSchd | RestaurantSitDown MinOA_MotorizedDamper_Sched | [6 empty] | 3695 | RestaurantSitDown Exterior_Lgt_ALWAYS_ON |  |  |  |  | 200 | Natural Gas | 200000 | 140 | RestaurantSitDown BLDG_SWH_SCH | 2.22 | 140 | 131 | 29891 | 0.3 | 2648 | [10 empty] | 68.24 | 6 | Electricity | 27297 | 140 | RestaurantSitDown BLDG_SWH_SCH | 1.33 | 140 | 180 |  | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2010 | FullServiceRestaurant | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantSitDown HVACOperationSchd | RestaurantSitDown MinOA_MotorizedDamper_Sched |  |  |  |  | 2302.49 | RestaurantSitDown Exterior_lighting_schedule_b | 154.01 | RestaurantSitDown Exterior_lighting_schedule_a |  |  |  |  | 200 | Natural Gas | 200000 | 140 | RestaurantSitDown BLDG_SWH_SCH | 2.22 | 140 | 131 | 29891 | 0.3 | 2443 | [10 empty] | 68.24 | 6 | Electricity | 27297 | 140 | RestaurantSitDown BLDG_SWH_SCH | 1.33 | 140 | 180 |  | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2013 | FullServiceRestaurant | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantSitDown HVACOperationSchd | RestaurantSitDown MinOA_MotorizedDamper_Sched |  |  |  |  | 2302.49 | RestaurantSitDown Exterior_lighting_schedule_b | 154.01 | RestaurantSitDown Exterior_lighting_schedule_a |  |  |  |  | 200 | Natural Gas | 200000 | 140 | RestaurantSitDown BLDG_SWH_SCH | 2.22 | 140 | 131 | 29891 | 0.3 | 2443 | [10 empty] | 68.24 | 6 | Electricity | 27297 | 140 | RestaurantSitDown BLDG_SWH_SCH | 1.33 | 140 | 180 |  | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref 1980-2004 | FullServiceRestaurant | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RestaurantSitDown HVACOperationSchd | RestaurantSitDown MinOA_MotorizedDamper_Sched | [6 empty] | 5081 | RestaurantSitDown Exterior_Lgt_ALWAYS_ON |  |  |  |  | 52.83 | Natural Gas | 2883000 | 140 | RestaurantSitDown BLDG_SWH_SCH | 2.22 | 120 | 120 | 0.1 | 1 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref Pre-1980 | FullServiceRestaurant | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RestaurantSitDown HVACOperationSchd | RestaurantSitDown MinOA_MotorizedDamper_Sched | [6 empty] | 5081 | RestaurantSitDown Exterior_Lgt_ALWAYS_ON |  |  |  |  | 52.83 | Natural Gas | 2883000 | 140 | RestaurantSitDown BLDG_SWH_SCH | 2.22 | 120 | 120 | 0.1 | 1 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2004 | Hospital
90.1-2007 | Hospital | const_pri_var_sec | WaterCooled |  |  | 400 | Water | Water | VariableVolume | Electricity | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | [6 empty] | 16636 | Hospital Exterior_Lgt_ALWAYS_ON |  |  |  |  | 600 | Natural Gas | 600000 | 140 | Hospital BLDG_SWH_SCH | 7.63 | 140 | 140 | 29891 | 0.3 | 10894 | 300 | Natural Gas | 300000 | 140 | Hospital BLDG_SWH_SCH | 2.8 | 180 | 180
90.1-2010 | Hospital | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | Water | Water | ConstantVolume |  | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | [6 empty] | 13088 | Hospital Exterior_Lgt_ALWAYS_ON |  |  |  |  | 600 | Natural Gas | 600000 | 140 | Hospital BLDG_SWH_SCH | 7.63 | 140 | 140 | 29891 | 0.3 | 68.24 | 200 | Natural Gas | 200000 | 140 | Hospital BLDG_SWH_SCH | 2.05 | 180 | 180 | 0.001 | 0.3 | 68.24 | 6 | Electricity | 64831 | 140 | Hospital BLDG_SWH_SCH | 23.7 | 180 | 180 | 68.24 | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | [16 empty] | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | 0.6045 | 1018.7736 | 0.95 |  |  |  | Traction | 8
90.1-2013 | Hospital
DOE Ref 1980-2004 | Hospital | const_pri | AirCooled | WithCondenser |  | 470 | [12 empty] | 21874 | Hospital Exterior_Lgt_ALWAYS_ON |  |  |  |  | 792 | Natural Gas | 2883259 | 140 | Hospital BLDG_SWH_SCH | 7.18 | 110 | 110 | 29891 | 0.3 | 68.24 | 200 | Natural Gas | 200000 | 140 | Hospital BLDG_SWH_SCH | 1.125 | 140 | 140 | 0.001 | 0.3 | 68.24 | [8 empty] | 68.24 | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | [16 empty] | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | 0.6045 | 1018.7736 | 0.95 |  |  |  | Traction | 8
DOE Ref Pre-1980 | Hospital | const_pri | AirCooled | WithCondenser |  | 470 | [12 empty] | 21874 | Hospital Exterior_Lgt_ALWAYS_ON |  |  |  |  | 792 | Natural Gas | 2883259 | 140 | Hospital BLDG_SWH_SCH | 7.18 | 110 | 110 | 29891 | 0.3 | 68.24 | 200 | Natural Gas | 200000 | 140 | Hospital BLDG_SWH_SCH | 1.125 | 140 | 140 | 0.001 | 0.3 | 68.24 | [8 empty] | 68.24 | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | [16 empty] | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | 0.6045 | 1018.7736 | 0.95 |  |  |  | Traction | 8
90.1-2004 | LargeHotel | const_pri_var_sec | AirCooled | WithCondenser |  | 310 | [10 empty] | 19478 | Always On |  |  | 122221.978 | HotelLarge BLDG_ELEVATORS | 971.4 | HotelLarge ELEV_LIGHT_FAN_SCH_24_7 | 600 | Natural Gas | 600000 | 140 | HotelLarge GuestRoom_SWH_Sch | 4.4 | 140 | 110 | 29891 | 0.3 | 7851.34 | 300 | Natural Gas | 300000 | 140 | HotelLarge LAUNDRY_SWH_SCH | 30.5953 | 140 | 140 |  |  | 0 | 6 | Electricity | 27297 | 140 | HotelLarge BLDG_SWH_SCH | 1.33 | 180 | 180 | 0 | [18 empty] | HotelLarge HVACOperationSchd | HotelLarge MinOA_MotorizedDamper_Sched | 0.6201 | 1389.42 | 0.954 | 4346.2446 | HotelLarge MinOA_Sched | DifferentialDrybulb | Traction | 6
90.1-2007 | LargeHotel | const_pri_var_sec | AirCooled | WithCondenser |  | 310 | [10 empty] | 19478 | Always On |  |  | 122221.978 | HotelLarge BLDG_ELEVATORS | 971.4 | HotelLarge ELEV_LIGHT_FAN_SCH_24_7 | 600 | Natural Gas | 600000 | 140 | HotelLarge GuestRoom_SWH_Sch | 4.4 | 140 | 110 | 29891 | 0.3 | 7851.34 | 300 | Natural Gas | 300000 | 140 | HotelLarge LAUNDRY_SWH_SCH | 30.5953 | 140 | 140 |  |  | 0 | 6 | Electricity | 27297 | 140 | HotelLarge BLDG_SWH_SCH | 1.33 | 180 | 180 | 0 | [18 empty] | HotelLarge HVACOperationSchd | HotelLarge MinOA_MotorizedDamper_Sched | 0.6201 | 1389.42 | 0.954 | 4346.2446 | HotelLarge MinOA_Sched | DifferentialDrybulb | Traction | 6
90.1-2010 | LargeHotel | const_pri_var_sec | AirCooled | WithCondenser |  | 310 | [10 empty] | 14952 | Always On |  |  | 122221.978 | HotelLarge BLDG_ELEVATORS | 635.4 | HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 600 | Natural Gas | 600000 | 140 | HotelLarge GuestRoom_SWH_Sch | 4.4 | 140 | 110 | 29891 | 0.3 | 7851.34 | 300 | Natural Gas | 300000 | 140 | HotelLarge LAUNDRY_SWH_SCH | 30.5953 | 140 | 140 |  |  | 0 | 6 | Electricity | 27297 | 140 | HotelLarge BLDG_SWH_SCH | 1.33 | 180 | 180 | 0 | [18 empty] | HotelLarge HVACOperationSchd | HotelLarge MinOA_MotorizedDamper_Sched | 0.6201 | 1389.42 | 0.954 | 4346.2446 | HotelLarge MinOA_Sched | DifferentialDrybulb | Traction | 6
90.1-2013 | LargeHotel | const_pri_var_sec | AirCooled | WithCondenser |  | 310 | [10 empty] | 14952 | Always On |  |  | 122221.978 | HotelLarge BLDG_ELEVATORS | 375.9 | HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 600 | Natural Gas | 600000 | 140 | HotelLarge GuestRoom_SWH_Sch | 4.4 | 140 | 110 | 29891 | 0.3 | 7851.34 | 300 | Natural Gas | 300000 | 140 | HotelLarge LAUNDRY_SWH_SCH | 30.5953 | 140 | 140 |  |  | 0 | 6 | Electricity | 27297 | 140 | HotelLarge BLDG_SWH_SCH | 1.33 | 180 | 180 | 0 | [18 empty] | HotelLarge HVACOperationSchd | HotelLarge MinOA_MotorizedDamper_Sched | 0.6201 | 1389.42 | 0.954 | 4346.2446 | HotelLarge MinOA_Sched | DifferentialDrybulb | Traction | 6
DOE Ref 1980-2004 | LargeHotel | const_pri | AirCooled | WithCondenser |  | 310 | [10 empty] | 27826 | Always On |  |  | 122221.978 | LargeHotel BLDG ELEVATORS |  |  | 528 | Natural Gas | 2883000 | 140 | HotelLarge BLDG_SWH_SCH | 4.4 | 110 | 110 | 179352 | 0.3 | 7851.34 | [38 empty] | HotelLarge HVACOperationSchd | HotelLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.945 | 4346.2446 | HotelLarge MinOA_Sched | NoEconomizer | Traction | 6
DOE Ref Pre-1980 | LargeHotel | const_pri | AirCooled | WithCondenser |  | 310 | [10 empty] | 27826 | Always On |  |  | 122221.978 | LargeHotel BLDG ELEVATORS |  |  | 528 | Natural Gas | 2883000 | 140 | HotelLarge BLDG_SWH_SCH | 4.4 | 110 | 110 | 179352 | 0.3 | 7851.34 | [38 empty] | HotelLarge HVACOperationSchd | HotelLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.945 | 4346.2446 | HotelLarge MinOA_Sched | NoEconomizer | Traction | 6
90.1-2004 | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 43305.0887 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a |  |  |  |  | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH | 0.58 | 140 | 140 | 29891 | 0.3 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Traction | 12
90.1-2007 | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 43305.0887 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a |  |  |  |  | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH | 0.58 | 140 | 140 | 29891 | 0.3 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Traction | 12
90.1-2010 | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 43305.0887 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a |  |  |  |  | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH | 0.58 | 140 | 140 | 29891 | 0.3 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Traction | 12
DOE Ref 1980-2004 | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | [12 empty] | 21874 | Always On |  |  |  |  | 792 | Natural Gas | 2883259 | 140 | OfficeLarge BLDG_SWH_SCH | 7.18 | 110 | 110 |  |  | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | [18 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Traction | 12
DOE Ref Pre-1980 | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | [12 empty] | 21874 | Always On |  |  |  |  | 792 | Natural Gas | 2883259 | 140 | OfficeLarge BLDG_SWH_SCH | 7.18 | 110 | 110 |  |  | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | [18 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Traction | 12
90.1-2004 | MediumOffice | [17 empty] | 14385 | OfficeMedium Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 100000 | 140 | OfficeMedium BLDG_SWH_SCH | 0.0567 | 140 | 131 | 29891 | 0.3 | 4718.796 | [10 empty] | 4718.796 | [8 empty] | 4718.796 | HTGSETP_SCH_PACU_VAV_bot | OfficeMedium CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7
90.1-2007 | MediumOffice | [17 empty] | 14385 | OfficeMedium Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 100000 | 140 | OfficeMedium BLDG_SWH_SCH | 0.0567 | 140 | 131 | 29891 | 0.3 | 4718.796 | [10 empty] | 4718.796 | [8 empty] | 4718.796 | HTGSETP_SCH_PACU_VAV_bot | OfficeMedium CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7
90.1-2010 | MediumOffice | [15 empty] | 7476.45 | OfficeMedium Exterior_lighting_schedule_b | 623.03 | OfficeMedium Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 100000 | 140 | OfficeMedium BLDG_SWH_SCH | 0.0567 | 140 | 131 | 29891 | 0.3 | 4357.124 | [10 empty] | 4357.124 | [8 empty] | 4357.124 | HTGSETP_SCH_PACU_VAV_bot | OfficeMedium CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF
90.1-2013 | MediumOffice | [15 empty] | 7476.45 | OfficeMedium Exterior_lighting_schedule_b | 623.03 | OfficeMedium Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 100000 | 140 | OfficeMedium BLDG_SWH_SCH | 0.0567 | 140 | 131 | 29891 | 0.3 | 4357.124 | [10 empty] | 4357.124 | [8 empty] | 4357.124 | HTGSETP_SCH_PACU_VAV_bot | OfficeMedium CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF
DOE Ref 1980-2004 | MediumOffice | [17 empty] | 17809 | OfficeMedium Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 2883000 | 140 | Medium Office Bldg Swh | 0.16484 | 140 | 110 | 179352 | 0.85 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | Medium Office HtgSetp | Medium Office ClgSetp | [16 empty] | OfficeMedium VAV Operation | OfficeMedium VAV OA Damper | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | Medium Office BLDG ELEVATORS
DOE Ref Pre-1980 | MediumOffice | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | [6 empty] | 17809 | OfficeMedium Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 2883000 | 140 | Medium Office Bldg Swh | 0.16484 | 140 | 110 | 179352 | 0.85 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | Medium Office HtgSetp | Medium Office ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | Medium Office BLDG ELEVATORS
90.1-2004 | MidriseApartment | [17 empty] | 4642 | ApartmentMidRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 1150 | Electricity | 1150000 | 140 | ApartmentMidRise APT_DHW_SCH | 0.058 | 140 | 140 | 0.01 | 1 | 87.75 | [27 empty] | Single Speed DX AC | Gas | ConstantVolume | ApartmentMidRise All On |  | ApartmentMidRise COMPACT HVAC-ALWAYS 1 | [13 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7
90.1-2007 | MidriseApartment | [17 empty] | 4642 | ApartmentMidRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 1150 | Electricity | 1150000 | 140 | ApartmentMidRise APT_DHW_SCH | 0.058 | 140 | 140 | 0.01 | 1 | 87.75 | [27 empty] | Single Speed DX AC | Gas | ConstantVolume | ApartmentMidRise All On |  | ApartmentMidRise COMPACT HVAC-ALWAYS 1 | [13 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_8
90.1-2010 | MidriseApartment | [17 empty] | 2553 | ApartmentMidRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 1150 | Electricity | 1150000 | 140 | ApartmentMidRise APT_DHW_SCH | 0.058 | 140 | 140 | 0.01 | 1 | 87.75 | [27 empty] | Single Speed DX AC | Gas | ConstantVolume | ApartmentMidRise All On |  | ApartmentMidRise COMPACT HVAC-ALWAYS 1 | [13 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_9
90.1-2013 | MidriseApartment | [17 empty] | 2553 | ApartmentMidRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 1150 | Electricity | 1150000 | 140 | ApartmentMidRise APT_DHW_SCH | 0.058 | 140 | 140 | 0.01 | 1 | 87.75 | [27 empty] | Single Speed DX AC | Gas | ConstantVolume | ApartmentMidRise All On |  | ApartmentMidRise COMPACT HVAC-ALWAYS 1 | [13 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_10
DOE Ref 1980-2004 | MidriseApartment | [17 empty] | 6436 | ApartmentMidRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 1 | Natural Gas | 721668 | 140 | ApartmentMidRise APT_DHW_SCH | 0.058 | 110 | 110 | 0.01 | 1 | 6.82 | [27 empty] | Single Speed DX AC | Gas | ConstantVolume | ApartmentMidRise All On |  | ApartmentMidRise COMPACT HVAC-ALWAYS 1 | Electric | ConstantVolume | Continuous | 0.2 | Always On | [8 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS
DOE Ref Pre-1980 | MidriseApartment | [17 empty] | 6436 | ApartmentMidRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 1 | Natural Gas | 721668 | 140 | ApartmentMidRise APT_DHW_SCH | 0.058 | 110 | 110 | 0.01 | 1 | 6.82 | [27 empty] | Single Speed DX AC | Gas | ConstantVolume | ApartmentMidRise All On |  | ApartmentMidRise COMPACT HVAC-ALWAYS 1 | Electric | ConstantVolume | Continuous | 0.2 | Always On | [8 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS
90.1-2010 | Outpatient | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | [10 empty] | 8235.9464 | OutpatientHealthCare Exterior_lighting_schedule_b | 139.05 | OutpatientHealthCare Exterior_lighting_schedule_a |  |  |  |  | 600 | Natural Gas | 600000 | 140 | OutPatientHealthCare BLDG_SWH_SCH | 7.63 | 140 | 140 | 29891 | 0.3 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | [16 empty] | OutPatientHealthCare HVACOperationSchd | OutPatientHealthCare MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 3
DOE Ref 1980-2004 | Outpatient | const_pri | AirCooled | WithCondenser |  | 470 | [12 empty] | 21874 | OutPatientHealthCare Exterior_Lgt_ALWAYS_ON |  |  |  |  | 792 | Natural Gas | 2883259 | 140 | OutPatientHealthCare BLDG_SWH_SCH | 7.18 | 110 | 110 | 29891 | 0.3 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | Outpatient HtgSetp | Outpatient ClgSetp | [16 empty] | OutPatientHealthCare HVACOperationSchd | OutPatientHealthCare MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 3
DOE Ref Pre-1980 | Outpatient | const_pri | AirCooled | WithCondenser |  | 470 | [12 empty] | 21874 | OutPatientHealthCare Exterior_Lgt_ALWAYS_ON |  |  |  |  | 792 | Natural Gas | 2883259 | 140 | OutPatientHealthCare BLDG_SWH_SCH | 7.18 | 110 | 110 | 29891 | 0.3 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | Outpatient HtgSetp | Outpatient ClgSetp | [16 empty] | OutPatientHealthCare HVACOperationSchd | OutPatientHealthCare MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 3
90.1-2004 | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | [6 empty] | 5406 | SchoolPrimary Exterior_Lgt_ALWAYS_ON |  |  |  |  | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | 2876 | [11 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [19 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2007 | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | [6 empty] | 5406 | SchoolPrimary Exterior_Lgt_ALWAYS_ON |  |  |  |  | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | 2876 | [11 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [19 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2010 | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched |  |  |  |  | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a |  |  |  |  | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | 2675 | [11 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [19 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2013 | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched |  |  |  |  | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a |  |  |  |  | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | 2675 | [11 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [19 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref 1980-2004 | PrimarySchool | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | PrimarySchool PSZ-AC Operation | PrimarySchool PSZ-AC OA Damper | [6 empty] | 10519 | PrimarySchool Exterior Lights Always On |  |  |  |  | 264 | Natural Gas | 2883259 | 140 | SchoolPrimary BLDG_SWH_SCH | 2.6 | 110 | 110 | 1 | 1 | 68.24 | [38 empty] | PrimarySchool VAV Operation | PrimarySchool VAV OA Damper | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref Pre-1980 | PrimarySchool | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | PrimarySchool PSZ-AC Operation | PrimarySchool PSZ-AC OA Damper | [6 empty] | 10519 | PrimarySchool Exterior Lights Always On |  |  |  |  | 264 | Natural Gas | 2883259 | 140 | SchoolPrimary BLDG_SWH_SCH | 2.6 | 110 | 110 | 1 | 1 | 68.24 | [38 empty] | PrimarySchool VAV Operation | PrimarySchool VAV OA Damper | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2004 | QuickServiceRestaurant | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantFastFood HVACOperationSchd | RestaurantFastFood MinOA_MotorizedDamper_Sched | [6 empty] | 1743 | RestaurantFastFood Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 100000 | 140 | RestaurantFastFood BLDG_SWH_SCH | 1.52 | 140 | 131 | 0.001 | 0.3 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2007 | QuickServiceRestaurant | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantFastFood HVACOperationSchd | RestaurantFastFood MinOA_MotorizedDamper_Sched | [6 empty] | 1743 | RestaurantFastFood Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 100000 | 140 | RestaurantFastFood BLDG_SWH_SCH | 1.52 | 140 | 131 | 0.001 | 0.3 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2013 | QuickServiceRestaurant | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantFastFood HVACOperationSchd | RestaurantFastFood MinOA_MotorizedDamper_Sched |  |  |  |  | 1039.09 | RestaurantFastFood Exterior_lighting_schedule_b | 122.81 | RestaurantFastFood Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 100000 | 140 | RestaurantFastFood BLDG_SWH_SCH | 1.52 | 140 | 131 | 0.001 | 0.3 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2010 | QuickServiceRestaurant | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantFastFood HVACOperationSchd | RestaurantFastFood MinOA_MotorizedDamper_Sched |  |  |  |  | 1039.09 | RestaurantFastFood Exterior_lighting_schedule_b | 122.81 | RestaurantFastFood Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 100000 | 140 | RestaurantFastFood BLDG_SWH_SCH | 1.52 | 140 | 131 | 0.001 | 0.3 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref 1980-2004 | QuickServiceRestaurant | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RestaurantFastFood HVACOperationSchd | RestaurantFastFood MinOA_MotorizedDamper_Sched | [6 empty] | 2963 | RestaurantFastFood Exterior_Lgt_ALWAYS_ON |  |  |  |  | 52.83 | Natural Gas | 2883000 | 140 | QuickServiceRestaurant Bldg Swh | 0.667 | 120 | 120 | 0.1 | 1 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref Pre-1980 | QuickServiceRestaurant | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RestaurantFastFood HVACOperationSchd | RestaurantFastFood MinOA_MotorizedDamper_Sched | [6 empty] | 2963 | RestaurantFastFood Exterior_Lgt_ALWAYS_ON |  |  |  |  | 52.83 | Natural Gas | 2883000 | 140 | QuickServiceRestaurant Bldg Swh | 0.667 | 120 | 120 | 0.1 | 1 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2013 | RetailStandalone | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched |  |  |  |  | 4365.06 | RetailStandalone Exterior_lighting_schedule_b | 379.58 | RetailStandalone Exterior_lighting_schedule_a |  |  |  |  | 40 | Natural Gas | 40000 | 140 | RetailStandalone BLDG_SWH_SCH | 0.3 | 120 | 131 | 0.001 | 0.3 | 68.24 | [20 empty] | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK | [11 empty] | Gas | ConstantVolume | OnOff | 2.5 | RetailStandalone FrontEntry_FanSched | [9 empty] | 0
90.1-2010 | RetailStandalone | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched |  |  |  |  | 4365.06 | RetailStandalone Exterior_lighting_schedule_b | 379.58 | RetailStandalone Exterior_lighting_schedule_a |  |  |  |  | 40 | Natural Gas | 40000 | 140 | RetailStandalone BLDG_SWH_SCH | 0.3 | 120 | 131 | 0.001 | 0.3 | 68.24 | [20 empty] | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK | [11 empty] | Gas | ConstantVolume | OnOff | 2.5 | RetailStandalone FrontEntry_FanSched | [9 empty] | 0
90.1-2007 | RetailStandalone | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched |  |  |  |  | 7322 | RetailStandalone Exterior_Lgt_ALWAYS_ON | 0 | RetailStandalone Exterior_lighting_schedule_a |  |  |  |  | 40 | Natural Gas | 40000 | 140 | RetailStandalone BLDG_SWH_SCH | 0.3 | 120 | 131 | 0.001 | 0.3 | 68.24 | [20 empty] | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK | [11 empty] | Gas | ConstantVolume | OnOff | 4.4584 | RetailStandalone FrontEntry_FanSched | [9 empty] | 0
90.1-2004 | RetailStandalone | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched |  |  |  |  | 7322 | RetailStandalone Exterior_Lgt_ALWAYS_ON | 0 | RetailStandalone Exterior_lighting_schedule_a |  |  |  |  | 40 | Natural Gas | 40000 | 140 | RetailStandalone BLDG_SWH_SCH | 0.3 | 120 | 131 | 0.001 | 0.3 | 68.24 | [20 empty] | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK | [11 empty] | Gas | ConstantVolume | OnOff | 4.4584 | RetailStandalone FrontEntry_FanSched | [9 empty] | 0
DOE Ref 1980-2004 | RetailStandalone | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | [6 empty] | 9995 | Always On |  |  |  |  | 40 | Natural Gas | 2883000 | 140 | RetailStandalone BLDG_SWH_SCH | 0.3 | 110 | 110 | 0.001 | 0.3 | 68.24 | [20 empty] | Retail HtgSetp | Retail ClgSetp | [11 empty] | Electric | ConstantVolume | OnOff | 0.2 | Always On | [9 empty] | 0
DOE Ref Pre-1980 | RetailStandalone | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | [6 empty] | 9995 | Always On |  |  |  |  | 40 | Natural Gas | 2883000 | 140 | RetailStandalone BLDG_SWH_SCH | 0.3 | 110 | 110 | 0.001 | 0.3 | 68.24 | [20 empty] | Retail HtgSetp | Retail ClgSetp | [11 empty] | Electric | ConstantVolume | OnOff | 0.2 | Always On | [9 empty] | 0
90.1-2013 | RetailStripmall | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type1_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | RetailStripmall Type2_FAN_SCH | RetailStripmall Type2_MinOA_MotorizedDamper_SCH | RetailStripmall Type3_FAN_SCH | RetailStripmall Type3_MinOA_MotorizedDamper_SCH | 5112.44 | RetailStripmall Exterior_lighting_schedule_b | 334.69 | RetailStripmall Exterior_lighting_schedule_a |  |  |  |  | 40 | Electricity | 40000 | 140 |  |  | 120 | 131 |  |  | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2010 | RetailStripmall | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type1_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | RetailStripmall Type2_FAN_SCH | RetailStripmall Type2_MinOA_MotorizedDamper_SCH | RetailStripmall Type3_FAN_SCH | RetailStripmall Type3_MinOA_MotorizedDamper_SCH | 5112.44 | RetailStripmall Exterior_lighting_schedule_b | 334.69 | RetailStripmall Exterior_lighting_schedule_a |  |  |  |  | 40 | Electricity | 40000 | 140 |  |  | 120 | 131 |  |  | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2007 | RetailStripmall | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type1_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | RetailStripmall Type2_FAN_SCH | RetailStripmall Type2_MinOA_MotorizedDamper_SCH | RetailStripmall Type3_FAN_SCH | RetailStripmall Type3_MinOA_MotorizedDamper_SCH |  |  | 9153 | RetailStripmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 40 | Electricity | 40000 | 140 |  |  | 120 | 131 |  |  | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2004 | RetailStripmall | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type1_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | RetailStripmall Type2_FAN_SCH | RetailStripmall Type2_MinOA_MotorizedDamper_SCH | RetailStripmall Type3_FAN_SCH | RetailStripmall Type3_MinOA_MotorizedDamper_SCH |  |  | 9153 | RetailStripmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 40 | Electricity | 40000 | 140 |  |  | 120 | 131 |  |  | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref 1980-2004 | RetailStripmall | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Stripmall HVACOperationSchd | Stripmall MinOA_Sched | Stripmall HVACOperationSchd | Stripmall MinOA_Sched | Stripmall HVACOperationSchd | Stripmall MinOA_Sched |  |  | 13499 | Always On | [35 empty] | StripMall HtgSetp | StripMall ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref Pre-1980 | RetailStripmall | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Stripmall HVACOperationSchd | Stripmall MinOA_Sched | Stripmall HVACOperationSchd | Stripmall MinOA_Sched | Stripmall HVACOperationSchd | Stripmall MinOA_Sched |  |  | 13499 | Always On | [35 empty] | StripMall HtgSetp | StripMall ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2004 | SecondarySchool | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | Two Speed DX AC | Gas | ConstantVolume |  | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched | [6 empty] | 14056 | SchoolSecondary Exterior_Lgt_ALWAYS_ON |  |  |  |  | 600 | Natural Gas | 600000 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.63 | 140 | 140 | 34026 | 0.3 | 3218 | [11 empty] | 6 | Electricity | 47770 | 140 | SchoolSecondary BLDG_SWH_SCH | 23.7 | 180 | 180 | [19 empty] | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | SchoolSecondary BLDG_ELEVATORS | SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7
90.1-2007 | SecondarySchool | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | Two Speed DX AC | Gas | ConstantVolume |  | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched | [6 empty] | 14056 | SchoolSecondary Exterior_Lgt_ALWAYS_ON |  |  |  |  | 600 | Natural Gas | 600000 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.63 | 140 | 140 | 34026 | 0.3 | 3218 | [11 empty] | 6 | Electricity | 47770 | 140 | SchoolSecondary BLDG_SWH_SCH | 23.7 | 180 | 180 | [19 empty] | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | SchoolSecondary BLDG_ELEVATORS | SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7
90.1-2010 | SecondarySchool | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | Two Speed DX AC | Gas | ConstantVolume |  | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched |  |  |  |  | 8427.85 | SchoolSecondary Exterior_lighting_schedule_b | 353.47 | SchoolSecondary Exterior_lighting_schedule_a |  |  |  |  | 600 | Natural Gas | 600000 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.63 | 140 | 140 | 34026 | 0.3 | 2999 | [11 empty] | 6 | Electricity | 47770 | 140 | SchoolSecondary BLDG_SWH_SCH | 23.7 | 180 | 180 | [19 empty] | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | SchoolSecondary BLDG_ELEVATORS | SchoolSecondary ELEV_LIGHT_FAN_SCH_ADD_DF
DOE Ref 1980-2004 | SecondarySchool | const_pri | AirCooled | WithCondenser |  | 470 | Single Speed DX AC | Gas | ConstantVolume |  | SecondarySchool PSZ-AC Operation | SecondarySchool PSZ-AC OA Damper | [6 empty] | 21874 | SecondarySchool Exterior Lights Always On |  |  |  |  | 792 | Natural Gas | 2883259 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.18 | 110 | 110 |  |  | 68.24 | [38 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | SecondarySchool BLDG ELEVATORS
DOE Ref Pre-1980 | SecondarySchool | const_pri | AirCooled | WithCondenser |  | 470 | Single Speed DX AC | Gas | ConstantVolume |  | SecondarySchool PSZ-AC Operation | SecondarySchool PSZ-AC OA Damper | [6 empty] | 21874 | SecondarySchool Exterior Lights Always On |  |  |  |  | 792 | Natural Gas | 2883259 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.18 | 110 | 110 |  |  | 68.24 | [38 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | SecondarySchool BLDG ELEVATORS
90.1-2004 | SmallHotel | [17 empty] | 6063 | HotelSmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | 1.852 | 140 | 140 | 29891 | 0.85 | 68.24 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | 68.24 | [8 empty] | 68.24 |  |  | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | HotelSmall Off During Unoccupied Period | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous | 0.2 | Always On |  |  | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2
90.1-2007 | SmallHotel | [17 empty] | 6063 | HotelSmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | 1.852 | 140 | 140 | 29891 | 0.85 | 68.24 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | 68.24 | [8 empty] | 68.24 |  |  | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | HotelSmall Off During Unoccupied Period | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous | 0.2 | Always On |  |  | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2
90.1-2010 | SmallHotel | [17 empty] | 4188 | HotelSmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | 1.852 | 140 | 140 | 29891 | 0.85 | 68.24 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | 68.24 | [8 empty] | 68.24 |  |  | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | HotelSmall Off During Unoccupied Period | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous | 0.2 | Always On |  |  | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2
90.1-2013 | SmallHotel | [17 empty] | 4188 | HotelSmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | 1.852 | 140 | 140 | 29891 | 0.85 | 68.24 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | 68.24 | [8 empty] | 68.24 |  |  | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | HotelSmall Off During Unoccupied Period | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous | 0.2 | Always On |  |  | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2
DOE Ref 1980-2004 | SmallHotel | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallHotel PSZ-AC Operation | SmallHotel PSZ-AC OA Damper | [6 empty] | 16715 | SmallHotel Exterior Lights |  |  |  |  | 528.3 | Natural Gas | 2883000 | 140 | HotelSmall GuestRoom_SHW_Sch | 3.361 | 110 | 110 | 179352 | 0.9 | 68.24 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 1.125 | 140 | 140 | 0.001 | 0.3 | 68.24 | [8 empty] | 68.24 |  |  | Single Speed DX AC | Electric | Cycling | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | [6 empty] | Electric | ConstantVolume | Cycling | 0.2 | Always On |  |  | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2
DOE Ref Pre-1980 | SmallHotel | [17 empty] | 16715 | SmallHotel Exterior Lights |  |  |  |  | 528.3 | Natural Gas | 2883000 | 140 | HotelSmall GuestRoom_SHW_Sch | 3.361 | 110 | 110 | 179352 | 0.9 | 68.24 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 1.125 | 140 | 140 | 0.001 | 0.3 | 68.24 | [8 empty] | 68.24 |  |  | Single Speed DX AC | Electric | Cycling | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | [6 empty] | Electric | ConstantVolume | Cycling | 0.2 | Always On |  |  | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2
90.1-2004 | SmallOffice | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_MotorizedDamper_Sched | [6 empty] | 1634 | OfficeSmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.064 | 120 | 131 |  |  | 1948.33 | [10 empty] | 1948.33 | [8 empty] | 1948.33 | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2007 | SmallOffice | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_MotorizedDamper_Sched | [6 empty] | 1634 | OfficeSmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.064 | 120 | 131 |  |  | 1948.33 | [10 empty] | 1948.33 | [8 empty] | 1948.33 | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2010 | SmallOffice | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_MotorizedDamper_Sched |  |  |  |  | 896.07 | OfficeSmall Exterior_lighting_schedule_b | 40.54 | OfficeSmall Exterior_lighting_schedule_a |  |  |  |  | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.064 | 120 | 131 |  |  | 1948.33 | [10 empty] | 1948.33 | [8 empty] | 1948.33 | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2013 | SmallOffice | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_MotorizedDamper_Sched |  |  |  |  | 896.07 | OfficeSmall Exterior_lighting_schedule_b | 40.54 | OfficeSmall Exterior_lighting_schedule_a |  |  |  |  | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.064 | 120 | 131 |  |  | 1948.33 | [10 empty] | 1948.33 | [8 empty] | 1948.33 | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref 1980-2004 | SmallOffice | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallOffice PSZ-AC Operation | SmallOffice PSZ-AC OA Damper | [6 empty] | 2766 | SmallOffice Exterior Lights Always On |  |  |  |  | 40 | Natural Gas | 2883000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.05 | 110 | 110 |  |  | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | Small Office HtgSetp | Small Office ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref Pre-1980 | SmallOffice | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallOffice PSZ-AC Operation | SmallOffice PSZ-AC OA Damper | [6 empty] | 2766 | SmallOffice Exterior Lights Always On |  |  |  |  | 40 | Natural Gas | 2883000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.05 | 110 | 110 |  |  | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | Small Office HtgSetp | Small Office ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2010 | Warehouse | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched |  |  |  |  | 91 | Warehouse Exterior_lighting_schedule_b | 6123.42 | Warehouse Exterior_lighting_schedule_a |  |  |  |  | 40 | Electricity | 40000 | 140 |  |  | 120 | 131 |  |  | 1948.33 | [10 empty] | 1948.33 | [8 empty] | 1948.33 | Warehouse HtgSetp BulkStorage | Warehouse CLGSETP_SCH | [11 empty] | Gas | ConstantVolume | OnOff | 0.2 | Always On |  |  | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref 1980-2004 | Warehouse | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | [6 empty] | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON |  |  |  |  | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 |  |  | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | Warehouse HtgSetp | Warehouse ClgSetp | [11 empty] | Gas | ConstantVolume | OnOff | 0.2 | Always On |  |  | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref Pre-1980 | Warehouse | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | [6 empty] | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON |  |  |  |  | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 |  |  | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | Warehouse HtgSetp | Warehouse ClgSetp | [11 empty] | Gas | ConstantVolume | OnOff | 0.2 | Always On |  |  | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
NECB 2011 | NECB
NECB 2011 | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 43305.0887 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a |  |  |  |  | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH | 0.58 | 140 | 140 | 29891 | 0.3 | 68.24 | [10 empty] | 68.24 | [8 empty] | 68.24 | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Traction | 12

## Templates
Templates combine standards and prototype data to create space types and construction sets, templates for each building type are exported to OSM format
0 | 1
Name | Notes
DOE Ref Pre-1980 | Numbers taken from the DOE Pre-1980 reference buildings, with values mapped back to the original data source (standards, etc) where possible. The infiltration numbers were taken from the reference buildings but converted to cfm/ft^2 of exterior surface area. Color scheme is based on redder for more public spaces, bluer for more private spaces. Occupancy from ventilation standards was not used by reference buildings because numbers were generally found to be too high for modeling, representing very conservative design scenarios.
DOE Ref 1980-2004 | Numbers taken from the DOE 1980-2004 reference buildings, with values mapped back to the original data source (standards, etc) where possible. The infiltration numbers were taken from the reference buildings but converted to cfm/ft^2 of exterior surface area. Color scheme is based on redder for more public spaces, bluer for more private spaces. Occupancy from ventilation standards was not used by reference buildings because numbers were generally found to be too high for modeling, representing very conservative design scenarios.
90.1-2004 | Numbers taken from the DOE 2004 reference buildings, with values mapped back to the original data source (standards, etc) where possible. The infiltration numbers were taken from the reference buildings but converted to cfm/ft^2 of exterior surface area. Color scheme is based on redder for more public spaces, bluer for more private spaces. Occupancy from ventilation standards was not used by reference buildings because numbers were generally found to be too high for modeling, representing very conservative design scenarios.
189.1-2009 | Lighting, equipment, infiltration, and ventilation taken from the EnergyPlus example file generator low-energy case. Schedules and occupancy taken from DOE Ref 2004 template.
90.1-2007 | Lighting and ventilation taken from 90.1-2007. Equipment and infiltration taken from 189.1-2009 template. Schedules and occupancy taken from DOE Ref 2004 template.
90.1-2010 | Lighting and ventilation taken from 90.1-2010. Equipment and infiltration taken from 189.1-2009 template. Schedules and occupancy taken from DOE Ref 2004 template.
90.1-2013 | Lighting and ventilation taken from 90.1-2013. Equipment and infiltration taken from 189.1-2009 template. Schedules and occupancy taken from DOE Ref 2004 template.
NECB 2011 | Taken from the Canadian NECB 2011

## Standards
Standards are actual standards documents issued by a standards organization
Name
AIA 2001
ASHRAE 169-2006
ASHRAE 189.1-2009
ASHRAE 62.1-1999
ASHRAE 62.1-2004
ASHRAE 62.1-2007
ASHRAE 90.1-1999
ASHRAE 90.1-2001
ASHRAE 90.1-2004
ASHRAE 90.1-2007
ASHRAE 90.1-2010
ASHRAE 90.1-2013
GGHC v2.2
CEC Title24-2005
CEC Title24-2008
CEC Title24-2013
NECB 2011

## Climate Zones
A climate zone is a geographic area defined in a standards document
0 | 1 | 2 | 3
Name | Standard | Representative City | BCL Weather Component ID
ASHRAE 169-2006-1A | ASHRAE 169-2006
ASHRAE 169-2006-1B | ASHRAE 169-2006
ASHRAE 169-2006-2A | ASHRAE 169-2006
ASHRAE 169-2006-2B | ASHRAE 169-2006
ASHRAE 169-2006-3A | ASHRAE 169-2006
ASHRAE 169-2006-3B | ASHRAE 169-2006
ASHRAE 169-2006-3C | ASHRAE 169-2006
ASHRAE 169-2006-4A | ASHRAE 169-2006
ASHRAE 169-2006-4B | ASHRAE 169-2006
ASHRAE 169-2006-4C | ASHRAE 169-2006
ASHRAE 169-2006-5A | ASHRAE 169-2006
ASHRAE 169-2006-5B | ASHRAE 169-2006
ASHRAE 169-2006-5C | ASHRAE 169-2006
ASHRAE 169-2006-6A | ASHRAE 169-2006
ASHRAE 169-2006-6B | ASHRAE 169-2006
ASHRAE 169-2006-7A | ASHRAE 169-2006
ASHRAE 169-2006-7B | ASHRAE 169-2006
ASHRAE 169-2006-8A | ASHRAE 169-2006
ASHRAE 169-2006-8B | ASHRAE 169-2006
CEC 2005-1 | CEC Title24-2005
CEC 2005-2 | CEC Title24-2005
CEC 2005-3 | CEC Title24-2005
CEC 2005-4 | CEC Title24-2005
CEC 2005-5 | CEC Title24-2005
CEC 2005-6 | CEC Title24-2005
CEC 2005-7 | CEC Title24-2005
CEC 2005-8 | CEC Title24-2005
CEC 2005-9 | CEC Title24-2005
CEC 2005-10 | CEC Title24-2005
CEC 2008-1 | CEC Title24-2008
CEC 2008-2 | CEC Title24-2008
CEC 2008-3 | CEC Title24-2008
CEC 2008-4 | CEC Title24-2008
CEC 2008-5 | CEC Title24-2008
CEC 2008-6 | CEC Title24-2008
CEC 2008-7 | CEC Title24-2008
CEC 2008-8 | CEC Title24-2008
CEC 2008-9 | CEC Title24-2008
CEC 2008-10 | CEC Title24-2008
NECB-CNEB-4 | NECB 2011
NECB-CNEB-5 | NECB 2011
NECB-CNEB-6 | NECB 2011
NECB-CNEB-7a | NECB 2011
NECB-CNEB-7b | NECB 2011
NECB-CNEB-8 | NECB 2011

## Climate Zone Sets
A climate zone set is a group of climate zones
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39
Name | Climate Zone | Climate Zone2 | Climate Zone3 | Climate Zone4 | Climate Zone5 | Climate Zone6 | Climate Zone7 | Climate Zone8 | Climate Zone9 | Climate Zone10 | Climate Zone11 | Climate Zone12 | Climate Zone13 | Climate Zone14 | Climate Zone15 | Climate Zone16 | Climate Zone17 | Climate Zone18 | Climate Zone19 | Climate Zone20 | Climate Zone21 | Climate Zone22 | Climate Zone23 | Climate Zone24 | Climate Zone25 | Climate Zone26 | Climate Zone27 | Climate Zone28 | Climate Zone29 | Climate Zone30 | Climate Zone31 | Climate Zone32 | Climate Zone33 | Climate Zone34 | Climate Zone35 | Climate Zone36 | Climate Zone37 | Climate Zone38 | Climate Zone39
ClimateZone 1 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B
ClimateZone 2 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B
ClimateZone 2A | ASHRAE 169-2006-2A
ClimateZone 2B | ASHRAE 169-2006-2B
ClimateZone 3 | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C
ClimateZone 3A | ASHRAE 169-2006-3A
ClimateZone 3B | ASHRAE 169-2006-3B
ClimateZone 3C | ASHRAE 169-2006-3C
ClimateZone 4 | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C
ClimateZone 4A | ASHRAE 169-2006-4A
ClimateZone 4B | ASHRAE 169-2006-4B
ClimateZone 4C | ASHRAE 169-2006-4C
ClimateZone 5 | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C
ClimateZone 5A | ASHRAE 169-2006-5A
ClimateZone 5B | ASHRAE 169-2006-5B
ClimateZone 5C | ASHRAE 169-2006-5C
ClimateZone 6 | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B
ClimateZone 6A | ASHRAE 169-2006-6A
ClimateZone 6B | ASHRAE 169-2006-6B
ClimateZone 7 | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B
ClimateZone 8 | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B
NECB-CNEB ClimatZone 4-8 | NECB-CNEB-4 | NECB-CNEB-5 | NECB-CNEB-6 | NECB-CNEB-7a | NECB-CNEB-7b | NECB-CNEB-8

## Ventilation
Each row represents ventilation requirements for a particular space type in a particular standard. Values are referenced on Space Types tab.
|  |  |  | ventilation | ventilation | ventilation
VlookupColumn | Ventilation Standard | Primary Space Type | Secondary Space Type | ft^3/min*person | ft^3/min*ft^2 | ach | Notes
AIA 2001AncillaryX-Ray (Surgical/Critical Care and Catheterization) | AIA 2001 | Ancillary | X-Ray (Surgical/Critical Care and Catheterization) |  |  | 3
AIA 2001NursingPatient Room | AIA 2001 | Nursing | Patient Room |  |  | 2
AIA 2001NursingNewborn Nursery Suite | AIA 2001 | Nursing | Newborn Nursery Suite |  |  | 2
AIA 2001NursingProtective Environment Room | AIA 2001 | Nursing | Protective Environment Room |  |  | 2
AIA 2001NursingAirborne Infection Isolation Room | AIA 2001 | Nursing | Airborne Infection Isolation Room |  |  | 2
AIA 2001NursingLabor/Delivery/Recovery | AIA 2001 | Nursing | Labor/Delivery/Recovery |  |  | 2
AIA 2001NursingLabor/Delivery/Recovery/Postpartum | AIA 2001 | Nursing | Labor/Delivery/Recovery/Postpartum |  |  | 2
AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms |  |  | 3
AIA 2001Surgery and Critical CareDelivery Room | AIA 2001 | Surgery and Critical Care | Delivery Room |  |  | 3
AIA 2001Surgery and Critical CareRecovery Room | AIA 2001 | Surgery and Critical Care | Recovery Room |  |  | 2
AIA 2001Surgery and Critical CareCritical and Intensive Care | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care |  |  | 2
AIA 2001Surgery and Critical CareNewborn Intensive Care | AIA 2001 | Surgery and Critical Care | Newborn Intensive Care |  |  | 2
AIA 2001Surgery and Critical CareTrauma Room | AIA 2001 | Surgery and Critical Care | Trauma Room |  |  | 3
AIA 2001Surgery and Critical CareEndoscopy | AIA 2001 | Surgery and Critical Care | Endoscopy |  |  | 2
AIA 2001Surgery and Critical CareBronchoscopy | AIA 2001 | Surgery and Critical Care | Bronchoscopy |  |  | 2
AIA 2001Surgery and Critical CareER Waiting Room | AIA 2001 | Surgery and Critical Care | ER Waiting Room |  |  | 2
AIA 2001Surgery and Critical CareTriage | AIA 2001 | Surgery and Critical Care | Triage |  |  | 2
AIA 2001Surgery and Critical CareRadiology Waiting Rooms | AIA 2001 | Surgery and Critical Care | Radiology Waiting Rooms |  |  | 2
AIA 2001Surgery and Critical CareProcedure Room | AIA 2001 | Surgery and Critical Care | Procedure Room |  |  | 3
ASHRAE 62.1-1999Correctional FacilitiesCell | ASHRAE 62.1-1999 | Correctional Facilities | Cell | 20 | 0
ASHRAE 62.1-1999Correctional FacilitiesDining halls | ASHRAE 62.1-1999 | Correctional Facilities | Dining halls | 15 | 0
ASHRAE 62.1-1999Correctional FacilitiesGuard stations | ASHRAE 62.1-1999 | Correctional Facilities | Guard stations | 15 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial laundry | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial laundry | 25 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial dry cleaner | 30 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesStorage, pick up | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Storage, pick up | 35 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated laundries | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated laundries | 15 | 0
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated dry cleaner | 15 | 0
ASHRAE 62.1-1999EducationClassroom | ASHRAE 62.1-1999 | Education | Classroom | 16.95 | 0
ASHRAE 62.1-1999EducationLaboratories | ASHRAE 62.1-1999 | Education | Laboratories | 20 | 0
ASHRAE 62.1-1999EducationTraining shop | ASHRAE 62.1-1999 | Education | Training shop | 20 | 0
ASHRAE 62.1-1999EducationMusic rooms | ASHRAE 62.1-1999 | Education | Music rooms | 15 | 0
ASHRAE 62.1-1999EducationLibraries | ASHRAE 62.1-1999 | Education | Libraries | 16.95 | 0
ASHRAE 62.1-1999EducationAuditorium | ASHRAE 62.1-1999 | Education | Auditorium | 15 | 0
ASHRAE 62.1-1999EducationSmoking lounges | ASHRAE 62.1-1999 | Education | Smoking lounges | 60 | 0
ASHRAE 62.1-1999EducationCorridors | ASHRAE 62.1-1999 | Education | Corridors | 0 | 0.1
ASHRAE 62.1-1999EducationLocker rooms | ASHRAE 62.1-1999 | Education | Locker rooms | 0 | 0.5
ASHRAE 62.1-1999Food and Beverage ServiceDining rooms | ASHRAE 62.1-1999 | Food and Beverage Service | Dining rooms | 20 | 0
ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | 20 | 0
ASHRAE 62.1-1999Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-1999 | Food and Beverage Service | Bars, cocktail lounges | 30 | 0
ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | 15 | 0 |  | Exhaust >= 1.5 cfm/ft2, 7.5 L/s m2
ASHRAE 62.1-1999Garages, Repair, Service StationsEnclosed parking garage | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Enclosed parking garage | 0 | 1.5
ASHRAE 62.1-1999Garages, Repair, Service StationsAuto repair rooms | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Auto repair rooms | 0 | 1.5
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 25 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 15 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 30 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 15 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 15 | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 0 | 0.5
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBedrooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Bedrooms | 0 | 0.1 |  | 35 cfm/room, refer to PNNL Scorecard for SmallHotel
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLiving rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Living rooms | 0 | 0.085 |  | Used for setting of bedroom, 30 cfm/room, for the two pre 2004 vintages
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBaths | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Baths | 0 | -9999 |  | 35 cfm/room, 18 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesApartment | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Apartment | 36 | 0 |  | Not originally in the stadards, added specifically for apartment (1 bedroom, 1 livingroom, 1 bathroom)
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | 15 | 0 |  | 20 => 15
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | 20 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesAssembly rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Assembly rooms | 15 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | 15 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesGambling casinos | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Gambling casinos | 30 | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDining rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dining rooms | 21.2 | 0
ASHRAE 62.1-1999OfficesOffice space | ASHRAE 62.1-1999 | Offices | Office space | 20 | 0 |  | 21.2 => 20
ASHRAE 62.1-1999OfficesReception areas | ASHRAE 62.1-1999 | Offices | Reception areas | 15 | 0
ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | 20 | 0
ASHRAE 62.1-1999OfficesConference rooms | ASHRAE 62.1-1999 | Offices | Conference rooms | 20 | 0
ASHRAE 62.1-1999Office BuildingsWhole Building | ASHRAE 62.1-1999 | Office Buildings | Whole Building |  | 0.1 |  | From DOE Reference Buildings, where many space types are combined into one
ASHRAE 62.1-1999Public SpacesSmoking lounge | ASHRAE 62.1-1999 | Public Spaces | Smoking lounge | 60 | 0
ASHRAE 62.1-1999Public SpacesCorridors and utilities | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | 0 | 0.05
ASHRAE 62.1-1999Public SpacesLocker and dressing rooms | ASHRAE 62.1-1999 | Public Spaces | Locker and dressing rooms | 0 | 0.5
ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | 0 | 0.96 |  | 50 cfm/wc or urinal, 25 L/s wc or urinal
ASHRAE 62.1-1999Public SpacesPublic restrooms | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | 0 | 0 |  | For SmallHotel
ASHRAE 62.1-1999Public SpacesElevators | ASHRAE 62.1-1999 | Public Spaces | Elevators | 0 | 1
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsSmoking lounge | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Smoking lounge | 60 | 0
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | 0 | 0.05
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | 0 | 0.15
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | 0 | 0.15
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsUpper floors | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Upper floors | 0 | 0.2
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsDressing rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Dressing rooms | 0 | 0.2
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsMalls and arcades | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Malls and arcades | 0 | 0.2
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | 0 | 0.3
ASHRAE 62.1-1999Specialty ShopsBarber | ASHRAE 62.1-1999 | Specialty Shops | Barber | 15 | 0
ASHRAE 62.1-1999Specialty ShopsBeauty | ASHRAE 62.1-1999 | Specialty Shops | Beauty | 25 | 0
ASHRAE 62.1-1999Specialty ShopsReducing salons | ASHRAE 62.1-1999 | Specialty Shops | Reducing salons | 15 | 0
ASHRAE 62.1-1999Specialty ShopsFlorists | ASHRAE 62.1-1999 | Specialty Shops | Florists | 15 | 0
ASHRAE 62.1-1999Specialty ShopsHardware, drugs, fabric | ASHRAE 62.1-1999 | Specialty Shops | Hardware, drugs, fabric | 15 | 0
ASHRAE 62.1-1999Specialty ShopsSupermarket | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | 15 | 0
ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | 0 | 0.3
ASHRAE 62.1-1999Specialty ShopsPet shops | ASHRAE 62.1-1999 | Specialty Shops | Pet shops | 0 | 1
ASHRAE 62.1-1999Sports and AmusementSpectator areas | ASHRAE 62.1-1999 | Sports and Amusement | Spectator areas | 15 | 0
ASHRAE 62.1-1999Sports and AmusementGame rooms | ASHRAE 62.1-1999 | Sports and Amusement | Game rooms | 25 | 0
ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | 20 | 0 |  | 21.2 => 20
ASHRAE 62.1-1999Sports and AmusementBallrooms and discos | ASHRAE 62.1-1999 | Sports and Amusement | Ballrooms and discos | 25 | 0
ASHRAE 62.1-1999Sports and AmusementBowling alleys (seating areas) | ASHRAE 62.1-1999 | Sports and Amusement | Bowling alleys (seating areas) | 25 | 0
ASHRAE 62.1-1999Sports and AmusementIce arenas (playing areas) | ASHRAE 62.1-1999 | Sports and Amusement | Ice arenas (playing areas) | 0 | 0.5 |  | Higher may be needed if internal combustion engines are operated for maintenance
ASHRAE 62.1-1999Sports and AmusementSwimming pools (pool and deck areas) | ASHRAE 62.1-1999 | Sports and Amusement | Swimming pools (pool and deck areas) | 0 | 0.5 |  | Higher may be needed for humidity control
ASHRAE 62.1-1999TheatersTicket booths | ASHRAE 62.1-1999 | Theaters | Ticket booths | 20 | 0
ASHRAE 62.1-1999TheatersLobbies | ASHRAE 62.1-1999 | Theaters | Lobbies | 20 | 0
ASHRAE 62.1-1999TheatersAuditorium | ASHRAE 62.1-1999 | Theaters | Auditorium | 15 | 0
ASHRAE 62.1-1999TheatersStages, studios | ASHRAE 62.1-1999 | Theaters | Stages, studios | 15 | 0
ASHRAE 62.1-1999TransportationWaiting rooms | ASHRAE 62.1-1999 | Transportation | Waiting rooms | 15 | 0
ASHRAE 62.1-1999TransportationPlatforms | ASHRAE 62.1-1999 | Transportation | Platforms | 15 | 0
ASHRAE 62.1-1999TransportationVehicles | ASHRAE 62.1-1999 | Transportation | Vehicles | 15 | 0
ASHRAE 62.1-1999WorkroomsMeat processing | ASHRAE 62.1-1999 | Workrooms | Meat processing | 15 | 0
ASHRAE 62.1-1999WorkroomsPhoto studios | ASHRAE 62.1-1999 | Workrooms | Photo studios | 15 | 0
ASHRAE 62.1-1999WorkroomsPharmacy | ASHRAE 62.1-1999 | Workrooms | Pharmacy | 15 | 0
ASHRAE 62.1-1999WorkroomsBank vaults | ASHRAE 62.1-1999 | Workrooms | Bank vaults | 15 | 0
ASHRAE 62.1-1999WorkroomsDarkrooms | ASHRAE 62.1-1999 | Workrooms | Darkrooms | 0 | 0.5
ASHRAE 62.1-1999WorkroomsDuplicating, printing | ASHRAE 62.1-1999 | Workrooms | Duplicating, printing | 0 | 0.5
ASHRAE 62.1-2004Correctional FacilitiesDay room | ASHRAE 62.1-2004 | Correctional Facilities | Day room | 5 | 0.06
ASHRAE 62.1-2004Correctional FacilitiesGuard stations | ASHRAE 62.1-2004 | Correctional Facilities | Guard stations | 5 | 0.06
ASHRAE 62.1-2004Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2004 | Correctional Facilities | Booking/waiting | 7.5 | 0.06
ASHRAE 62.1-2004Correctional FacilitiesCell | ASHRAE 62.1-2004 | Correctional Facilities | Cell | 5 | 0.12
ASHRAE 62.1-2004Educational FacilitiesLecture classroom | ASHRAE 62.1-2004 | Educational Facilities | Lecture classroom | 7.5 | 0.06
ASHRAE 62.1-2004Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2004 | Educational Facilities | Lecture hall (fixed seats) | 7.5 | 0.06
ASHRAE 62.1-2004Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2004 | Educational Facilities | Music/theater/dance | 10 | 0.06
ASHRAE 62.1-2004Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2004 | Educational Facilities | Multiuse assembly | 7.5 | 0.06
ASHRAE 62.1-2004Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (ages 5-8) | 10 | 0.12
ASHRAE 62.1-2004Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (age 9 plus) | 10 | 0.12
ASHRAE 62.1-2004Educational FacilitiesComputer lab | ASHRAE 62.1-2004 | Educational Facilities | Computer lab | 10 | 0.12
ASHRAE 62.1-2004Educational FacilitiesMedia center | ASHRAE 62.1-2004 | Educational Facilities | Media center | 10 | 0.12 |  | A
ASHRAE 62.1-2004Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2004 | Educational Facilities | Daycare (through age 4) | 10 | 0.18
ASHRAE 62.1-2004Educational FacilitiesArt classroom | ASHRAE 62.1-2004 | Educational Facilities | Art classroom | 10 | 0.18
ASHRAE 62.1-2004Educational FacilitiesScience laboratories | ASHRAE 62.1-2004 | Educational Facilities | Science laboratories | 10 | 0.18 |  | E
ASHRAE 62.1-2004Educational FacilitiesWood/metal shop | ASHRAE 62.1-2004 | Educational Facilities | Wood/metal shop | 10 | 0.18
ASHRAE 62.1-2004Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2004 | Food and Beverage Service | Restaurant dining rooms | 7.5 | 0.18
ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | 7.5 | 0.18
ASHRAE 62.1-2004Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2004 | Food and Beverage Service | Bars, cocktail lounges | 7.5 | 0.18
ASHRAE 62.1-2004GeneralConference/meeting | ASHRAE 62.1-2004 | General | Conference/meeting | 5 | 0.06
ASHRAE 62.1-2004GeneralCorridors | ASHRAE 62.1-2004 | General | Corridors |  | 0.06
ASHRAE 62.1-2004GeneralStorage rooms | ASHRAE 62.1-2004 | General | Storage rooms |  | 0.12 |  | B
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 25 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 30 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms |  | 0.5 |  | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 15
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 5 | 0.06
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesApartment | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Apartment | 0 | 0 | 0.35
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 5 | 0.06
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 7.5 | 0.06
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2004 | Miscellaneous Spaces | Bank vaults/safe deposit | 5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Computer (not printing) | 5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2004 | Miscellaneous Spaces | Transportation waiting | 7.5 | 0.06
ASHRAE 62.1-2004Miscellaneous SpacesWarehouses | ASHRAE 62.1-2004 | Miscellaneous Spaces | Warehouses |  | 0.06 |  | B
ASHRAE 62.1-2004Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2004 | Miscellaneous Spaces | Photo studios | 5 | 0.12
ASHRAE 62.1-2004Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2004 | Miscellaneous Spaces | Shipping/receiving |  | 0.12 |  | B
ASHRAE 62.1-2004Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Pharmacy (prep. area) | 5 | 0.18
ASHRAE 62.1-2004Office BuildingsOffice space | ASHRAE 62.1-2004 | Office Buildings | Office space | 5 | 0.06
ASHRAE 62.1-2004Office BuildingsReception areas | ASHRAE 62.1-2004 | Office Buildings | Reception areas | 5 | 0.06
ASHRAE 62.1-2004Office BuildingsTelephone/data entry | ASHRAE 62.1-2004 | Office Buildings | Telephone/data entry | 5 | 0.06
ASHRAE 62.1-2004Office BuildingsMain entry lobbies | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | 5 | 0.06
ASHRAE 62.1-2004Office BuildingsWhole Building | ASHRAE 62.1-2004 | Office Buildings | Whole Building |  | 0.085 |  | From DOE Reference Buildings, where many space types are combined into one
ASHRAE 62.1-2004Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2004 | Public Assembly Spaces | Auditorium seating area | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2004 | Public Assembly Spaces | Places of religious worship | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesCourtrooms | ASHRAE 62.1-2004 | Public Assembly Spaces | Courtrooms | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2004 | Public Assembly Spaces | Legislative chambers | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesLobbies | ASHRAE 62.1-2004 | Public Assembly Spaces | Lobbies | 5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums/galleries | 7.5 | 0.06
ASHRAE 62.1-2004Public Assembly SpacesLibraries | ASHRAE 62.1-2004 | Public Assembly Spaces | Libraries | 5 | 0.12
ASHRAE 62.1-2004Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums (children’s) | 7.5 | 0.12
ASHRAE 62.1-2004RetailGeneral Sales combined by area | ASHRAE 62.1-2004 | Retail | General Sales combined by area | 0 | 0.2325
ASHRAE 62.1-2004RetailMall common areas | ASHRAE 62.1-2004 | Retail | Mall common areas | 7.5 | 0.06
ASHRAE 62.1-2004RetailBarber shop | ASHRAE 62.1-2004 | Retail | Barber shop | 7.5 | 0.06
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 7.5 | 0.06
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 7.5 | 0.06
ASHRAE 62.1-2004RetailCoinoperated laundries | ASHRAE 62.1-2004 | Retail | Coinoperated laundries | 7.5 | 0.06
ASHRAE 62.1-2004RetailGeneral Sales | ASHRAE 62.1-2004 | Retail | General Sales | 7.5 | 0.12
ASHRAE 62.1-2004RetailBeauty and nail salons | ASHRAE 62.1-2004 | Retail | Beauty and nail salons | 20 | 0.12
ASHRAE 62.1-2004RetailPet shops (animal areas) | ASHRAE 62.1-2004 | Retail | Pet shops (animal areas) | 7.5 | 0.18
ASHRAE 62.1-2004Sports and EntertainmentSpectator areas | ASHRAE 62.1-2004 | Sports and Entertainment | Spectator areas | 7.5 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2004 | Sports and Entertainment | Disco/dance floors | 20 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/aerobics room | 20 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/weight rooms | 20 | 0.06
ASHRAE 62.1-2004Sports and EntertainmentStages, studios | ASHRAE 62.1-2004 | Sports and Entertainment | Stages, studios | 10 | 0.06 |  | D
ASHRAE 62.1-2004Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2004 | Sports and Entertainment | Bowling alley (seating) | 10 | 0.12
ASHRAE 62.1-2004Sports and EntertainmentGambling casinos | ASHRAE 62.1-2004 | Sports and Entertainment | Gambling casinos | 7.5 | 0.18
ASHRAE 62.1-2004Sports and EntertainmentGame arcades | ASHRAE 62.1-2004 | Sports and Entertainment | Game arcades | 7.5 | 0.18
ASHRAE 62.1-2004Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Sports arena (play area) |  | 0.3
ASHRAE 62.1-2004Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Gym, stadium (play area) |  | 0.3
ASHRAE 62.1-2004Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2004 | Sports and Entertainment | Swimming (pool & deck) |  | 0.48 |  | C
ASHRAE 62.1-2007Correctional FacilitiesDay room | ASHRAE 62.1-2007 | Correctional Facilities | Day room | 5 | 0.06
ASHRAE 62.1-2007Correctional FacilitiesGuard stations | ASHRAE 62.1-2007 | Correctional Facilities | Guard stations | 5 | 0.06
ASHRAE 62.1-2007Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2007 | Correctional Facilities | Booking/waiting | 7.5 | 0.06
ASHRAE 62.1-2007Correctional FacilitiesCell | ASHRAE 62.1-2007 | Correctional Facilities | Cell | 5 | 0.12
ASHRAE 62.1-2007Educational FacilitiesLecture classroom | ASHRAE 62.1-2007 | Educational Facilities | Lecture classroom | 7.5 | 0.06
ASHRAE 62.1-2007Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2007 | Educational Facilities | Lecture hall (fixed seats) | 7.5 | 0.06
ASHRAE 62.1-2007Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2007 | Educational Facilities | Music/theater/dance | 10 | 0.06
ASHRAE 62.1-2007Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2007 | Educational Facilities | Multiuse assembly | 7.5 | 0.06
ASHRAE 62.1-2007Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (ages 5-8) | 10 | 0.12
ASHRAE 62.1-2007Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (age 9 plus) | 10 | 0.12
ASHRAE 62.1-2007Educational FacilitiesComputer lab | ASHRAE 62.1-2007 | Educational Facilities | Computer lab | 10 | 0.12
ASHRAE 62.1-2007Educational FacilitiesMedia center | ASHRAE 62.1-2007 | Educational Facilities | Media center | 10 | 0.12 |  | A
ASHRAE 62.1-2007Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2007 | Educational Facilities | Daycare (through age 4) | 10 | 0.18
ASHRAE 62.1-2007Educational FacilitiesArt classroom | ASHRAE 62.1-2007 | Educational Facilities | Art classroom | 10 | 0.18
ASHRAE 62.1-2007Educational FacilitiesScience laboratories | ASHRAE 62.1-2007 | Educational Facilities | Science laboratories | 10 | 0.18 |  | E
ASHRAE 62.1-2007Educational FacilitiesWood/metal shop | ASHRAE 62.1-2007 | Educational Facilities | Wood/metal shop | 10 | 0.18
ASHRAE 62.1-2007Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2007 | Food and Beverage Service | Restaurant dining rooms | 7.5 | 0.18
ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | 7.5 | 0.18
ASHRAE 62.1-2007Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2007 | Food and Beverage Service | Bars, cocktail lounges | 7.5 | 0.18
ASHRAE 62.1-2007GeneralConference/meeting | ASHRAE 62.1-2007 | General | Conference/meeting | 5 | 0.06
ASHRAE 62.1-2007GeneralCorridors | ASHRAE 62.1-2007 | General | Corridors |  | 0.06
ASHRAE 62.1-2007GeneralStorage rooms | ASHRAE 62.1-2007 | General | Storage rooms |  | 0.12 |  | B
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 25 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 30 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 15 |  |  | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms |  | 0.5 |  | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 15
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 5 | 0.06
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesApartment | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Apartment | 0 | 0 | 0.35
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 5 | 0.06
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 7.5 | 0.06
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 5 | 0.06
ASHRAE 62.1-2007Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2007 | Miscellaneous Spaces | Bank vaults/safe deposit | 5 | 0.06
ASHRAE 62.1-2007Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Computer (not printing) | 5 | 0.06
ASHRAE 62.1-2007Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2007 | Miscellaneous Spaces | Transportation waiting | 7.5 | 0.06
ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses |  | 0.06 |  | B
ASHRAE 62.1-2007Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2007 | Miscellaneous Spaces | Photo studios | 5 | 0.12
ASHRAE 62.1-2007Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2007 | Miscellaneous Spaces | Shipping/receiving |  | 0.12 |  | B
ASHRAE 62.1-2007Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Pharmacy (prep. area) | 5 | 0.18
ASHRAE 62.1-2007Office BuildingsOffice space | ASHRAE 62.1-2007 | Office Buildings | Office space | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsReception areas | ASHRAE 62.1-2007 | Office Buildings | Reception areas | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsTelephone/data entry | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsMain entry lobbies | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | 5 | 0.06
ASHRAE 62.1-2007Office BuildingsWhole Building | ASHRAE 62.1-2007 | Office Buildings | Whole Building |  | 0.085 |  | From DOE Reference Buildings, where many space types are combined into one
ASHRAE 62.1-2007Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2007 | Public Assembly Spaces | Auditorium seating area | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2007 | Public Assembly Spaces | Places of religious worship | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesCourtrooms | ASHRAE 62.1-2007 | Public Assembly Spaces | Courtrooms | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2007 | Public Assembly Spaces | Legislative chambers | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesLobbies | ASHRAE 62.1-2007 | Public Assembly Spaces | Lobbies | 5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums/galleries | 7.5 | 0.06
ASHRAE 62.1-2007Public Assembly SpacesLibraries | ASHRAE 62.1-2007 | Public Assembly Spaces | Libraries | 5 | 0.12
ASHRAE 62.1-2007Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums (children’s) | 7.5 | 0.12
ASHRAE 62.1-2007RetailGeneral Sales combined by area | ASHRAE 62.1-2007 | Retail | General Sales combined by area | 0 | 0.2325
ASHRAE 62.1-2007RetailMall common areas | ASHRAE 62.1-2007 | Retail | Mall common areas | 7.5 | 0.06
ASHRAE 62.1-2007RetailBarber shop | ASHRAE 62.1-2007 | Retail | Barber shop | 7.5 | 0.06
ASHRAE 62.1-2007RetailSupermarket | ASHRAE 62.1-2007 | Retail | Supermarket | 7.5 | 0.06
ASHRAE 62.1-2007RetailCoinoperated laundries | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | 7.5 | 0.06
ASHRAE 62.1-2007RetailGeneral Sales | ASHRAE 62.1-2007 | Retail | General Sales | 7.5 | 0.12
ASHRAE 62.1-2007RetailBeauty and nail salons | ASHRAE 62.1-2007 | Retail | Beauty and nail salons | 20 | 0.12
ASHRAE 62.1-2007RetailPet shops (animal areas) | ASHRAE 62.1-2007 | Retail | Pet shops (animal areas) | 7.5 | 0.18
ASHRAE 62.1-2007Sports and EntertainmentSpectator areas | ASHRAE 62.1-2007 | Sports and Entertainment | Spectator areas | 7.5 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2007 | Sports and Entertainment | Disco/dance floors | 20 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/aerobics room | 20 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/weight rooms | 20 | 0.06
ASHRAE 62.1-2007Sports and EntertainmentStages, studios | ASHRAE 62.1-2007 | Sports and Entertainment | Stages, studios | 10 | 0.06 |  | D
ASHRAE 62.1-2007Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2007 | Sports and Entertainment | Bowling alley (seating) | 10 | 0.12
ASHRAE 62.1-2007Sports and EntertainmentGambling casinos | ASHRAE 62.1-2007 | Sports and Entertainment | Gambling casinos | 7.5 | 0.18
ASHRAE 62.1-2007Sports and EntertainmentGame arcades | ASHRAE 62.1-2007 | Sports and Entertainment | Game arcades | 7.5 | 0.18
ASHRAE 62.1-2007Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Sports arena (play area) |  | 0.3
ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) |  | 0.3
ASHRAE 62.1-2007Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2007 | Sports and Entertainment | Swimming (pool & deck) |  | 0.48 |  | C
GGHC v2.2Health CareBathroom/ Public | GGHC v2.2 | Health Care | Bathroom/ Public |  | 0.15
GGHC v2.2Health CareBedpan Room | GGHC v2.2 | Health Care | Bedpan Room |  | 0.15
GGHC v2.2Health CareLobby | GGHC v2.2 | Health Care | Lobby |  | 0.15
GGHC v2.2Health CareLockers | GGHC v2.2 | Health Care | Lockers |  | 0.15
GGHC v2.2Health CareMechanical Equipment Room | GGHC v2.2 | Health Care | Mechanical Equipment Room |  | 0.15
GGHC v2.2Health CareMedical Records | GGHC v2.2 | Health Care | Medical Records |  | 0.15
GGHC v2.2Health CareNursing Stations- General | GGHC v2.2 | Health Care | Nursing Stations- General |  | 0.15
GGHC v2.2Health CareStairways | GGHC v2.2 | Health Care | Stairways |  | 0.15
GGHC v2.2Health CareWaiting Areas/Lounges | GGHC v2.2 | Health Care | Waiting Areas/Lounges |  | 0.15
GGHC v2.2Health CareAngiographic-All Other Types | GGHC v2.2 | Health Care | Angiographic-All Other Types |  | 0.3
GGHC v2.2Health CareAutopsy | GGHC v2.2 | Health Care | Autopsy |  | 0.3
GGHC v2.2Health CareCast Room | GGHC v2.2 | Health Care | Cast Room |  | 0.3
GGHC v2.2Health CareClean Linen Storage | GGHC v2.2 | Health Care | Clean Linen Storage |  | 0.3
GGHC v2.2Health CareClean Utility / Workroom | GGHC v2.2 | Health Care | Clean Utility / Workroom |  | 0.3
GGHC v2.2Health CareCorridors | GGHC v2.2 | Health Care | Corridors |  | 0.3
GGHC v2.2Health CareDarkroom | GGHC v2.2 | Health Care | Darkroom |  | 0.3
GGHC v2.2Health CareDecontamination | GGHC v2.2 | Health Care | Decontamination |  | 0.3
GGHC v2.2Health CareDietary Day Storage | GGHC v2.2 | Health Care | Dietary Day Storage |  | 0.3
GGHC v2.2Health CareDishwashing | GGHC v2.2 | Health Care | Dishwashing |  | 0.3
GGHC v2.2Health CareEndoscopy | GGHC v2.2 | Health Care | Endoscopy |  | 0.3
GGHC v2.2Health CareHistology | GGHC v2.2 | Health Care | Histology |  | 0.3
GGHC v2.2Health CareIsolation | GGHC v2.2 | Health Care | Isolation |  | 0.3
GGHC v2.2Health CareKitchen, Food Preparation | GGHC v2.2 | Health Care | Kitchen, Food Preparation |  | 0.3
GGHC v2.2Health CareLabor/ Delivery/Recovery | GGHC v2.2 | Health Care | Labor/ Delivery/Recovery |  | 0.3
GGHC v2.2Health CareL / D / R / Post Partum | GGHC v2.2 | Health Care | L / D / R / Post Partum |  | 0.3
GGHC v2.2Health CareLaboratory | GGHC v2.2 | Health Care | Laboratory |  | 0.3
GGHC v2.2Health CareLinen Storage, Clean | GGHC v2.2 | Health Care | Linen Storage, Clean |  | 0.3
GGHC v2.2Health CareMammography | GGHC v2.2 | Health Care | Mammography |  | 0.3
GGHC v2.2Health CareNuclear Medicine, Hot Lab | GGHC v2.2 | Health Care | Nuclear Medicine, Hot Lab |  | 0.3
GGHC v2.2Health CarePathology | GGHC v2.2 | Health Care | Pathology |  | 0.3
GGHC v2.2Health CarePatient Room | GGHC v2.2 | Health Care | Patient Room |  | 0.3
GGHC v2.2Health CarePharmacy / Medicine Room | GGHC v2.2 | Health Care | Pharmacy / Medicine Room |  | 0.3
GGHC v2.2Health CarePhysical Therapy and Hydrotherapy | GGHC v2.2 | Health Care | Physical Therapy and Hydrotherapy |  | 0.3
GGHC v2.2Health CareRecovery | GGHC v2.2 | Health Care | Recovery |  | 0.3
GGHC v2.2Health CareScrub Up Area, Surgical Corridor | GGHC v2.2 | Health Care | Scrub Up Area, Surgical Corridor |  | 0.3
GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic |  | 0.3
GGHC v2.2Health CareSub-Sterile | GGHC v2.2 | Health Care | Sub-Sterile |  | 0.3
GGHC v2.2Health CareSurgical Supply | GGHC v2.2 | Health Care | Surgical Supply |  | 0.3
GGHC v2.2Health CareTreatment / Examination | GGHC v2.2 | Health Care | Treatment / Examination |  | 0.3
GGHC v2.2Health CareUnsterile Supply | GGHC v2.2 | Health Care | Unsterile Supply |  | 0.3
GGHC v2.2Health CareX-ray, Diagnostic and Treatment | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment |  | 0.3
GGHC v2.2Health CareNursery, General | GGHC v2.2 | Health Care | Nursery, General |  | 0.45
GGHC v2.2Health CareNursery, Exam | GGHC v2.2 | Health Care | Nursery, Exam |  | 0.45
GGHC v2.2Health CareConference Rooms | GGHC v2.2 | Health Care | Conference Rooms |  | 0.5
GGHC v2.2Health CareAngiographic-Heart Only | GGHC v2.2 | Health Care | Angiographic-Heart Only |  | 0.75
GGHC v2.2Health CareCystoscopy | GGHC v2.2 | Health Care | Cystoscopy |  | 0.75
GGHC v2.2Health CareDelivery Room | GGHC v2.2 | Health Care | Delivery Room |  | 0.75
GGHC v2.2Health CareOperating Room | GGHC v2.2 | Health Care | Operating Room |  | 0.75
GGHC v2.2Health CareSpecial Procedure Room, Invasive | GGHC v2.2 | Health Care | Special Procedure Room, Invasive |  | 0.75
GGHC v2.2Health CareTrauma | GGHC v2.2 | Health Care | Trauma |  | 0.75
GGHC v2.2Health CareAnesthesia Storage | GGHC v2.2 | Health Care | Anesthesia Storage |  | 1.2
GGHC v2.2Health CareDining Room | GGHC v2.2 | Health Care | Dining Room |  | 1.5
GGHC v2.2Health CareJanitors Closet / Utility | GGHC v2.2 | Health Care | Janitors Closet / Utility |  | 1.5
GGHC v2.2Health CareSoiled Linen, Sorting | GGHC v2.2 | Health Care | Soiled Linen, Sorting |  | 1.5
GGHC v2.2Health CareSterilizer Room | GGHC v2.2 | Health Care | Sterilizer Room |  | 1.5
GGHC v2.2Health CareTrash Chute Room | GGHC v2.2 | Health Care | Trash Chute Room |  | 1.5
NECB 2011Automotive facilityWholeBuilding | NECB 2011 | Automotive facility | WholeBuilding |  |  | 0.001151
NECB 2011Convention centreWholeBuilding | NECB 2011 | Convention centre | WholeBuilding |  |  | 0.00074769
NECB 2011CourthouseWholeBuilding | NECB 2011 | Courthouse | WholeBuilding |  |  | 0.00046238
NECB 2011Dining - bar/loungeWholeBuilding | NECB 2011 | Dining - bar/lounge | WholeBuilding |  |  | 0.0012691
NECB 2011Dining - cafeteriaWholeBuilding | NECB 2011 | Dining - cafeteria | WholeBuilding |  |  | 0.0012691
NECB 2011Dining - familyWholeBuilding | NECB 2011 | Dining - family | WholeBuilding |  |  | 0.0012691
NECB 2011DormitoryWholeBuilding | NECB 2011 | Dormitory | WholeBuilding |  |  | 0.00038368
NECB 2011Exercise centreWholeBuilding | NECB 2011 | Exercise centre | WholeBuilding |  |  | 0.0012494
NECB 2011Fire stationWholeBuilding | NECB 2011 | Fire station | WholeBuilding |  |  | 0.00075162
NECB 2011GymnasiumWholeBuilding | NECB 2011 | Gymnasium | WholeBuilding |  |  | 0.0012494
NECB 2011Health-care clinicWholeBuilding | NECB 2011 | Health-care clinic | WholeBuilding |  |  | 0.0022873
NECB 2011HospitalWholeBuilding | NECB 2011 | Hospital | WholeBuilding |  |  | 0.0022873
NECB 2011HotelWholeBuilding | NECB 2011 | Hotel | WholeBuilding |  |  | 0.00039942
NECB 2011LibraryWholeBuilding | NECB 2011 | Library | WholeBuilding |  |  | 0.00072801
NECB 2011Manufacturing facilityWholeBuilding | NECB 2011 | Manufacturing facility | WholeBuilding |  |  | 0.0010723
NECB 2011MotelWholeBuilding | NECB 2011 | Motel | WholeBuilding |  |  | 0.00039942
NECB 2011Motion picture theatreWholeBuilding | NECB 2011 | Motion picture theatre | WholeBuilding |  |  | 0.00060012
NECB 2011Multi-unit residentialWholeBuilding | NECB 2011 | Multi-unit residential | WholeBuilding |  |  | 0.00034433
NECB 2011MuseumWholeBuilding | NECB 2011 | Museum | WholeBuilding |  |  | 0.00048206
NECB 2011OfficeWholeBuilding | NECB 2011 | Office | WholeBuilding |  |  | 0.00039942
NECB 2011Parking garageWholeBuilding | NECB 2011 | Parking garage | WholeBuilding |  |  | 0.0003097
NECB 2011PenitentiaryWholeBuilding | NECB 2011 | Penitentiary | WholeBuilding |  |  | 0.00038368
NECB 2011Performing arts theatreWholeBuilding | NECB 2011 | Performing arts theatre | WholeBuilding |  |  | 0.00060012
NECB 2011Police stationWholeBuilding | NECB 2011 | Police station | WholeBuilding |  |  | 0.00039942
NECB 2011Post officeWholeBuilding | NECB 2011 | Post office | WholeBuilding |  |  | 0.00075162
NECB 2011ReligiousWholeBuilding | NECB 2011 | Religious | WholeBuilding |  |  | 0.0007772
NECB 2011RetailWholeBuilding | NECB 2011 | Retail | WholeBuilding |  |  | 0.00042303
NECB 2011School/universityWholeBuilding | NECB 2011 | School/university | WholeBuilding |  |  | 0.00074769
NECB 2011Sports arenaWholeBuilding | NECB 2011 | Sports arena | WholeBuilding |  |  | 0.00065914
NECB 2011Town hallWholeBuilding | NECB 2011 | Town hall | WholeBuilding |  |  | 0.00039942
NECB 2011TransportationWholeBuilding | NECB 2011 | Transportation | WholeBuilding |  |  | 0.00054109
NECB 2011WarehouseWholeBuilding | NECB 2011 | Warehouse | WholeBuilding |  |  | 0.00030813
NECB 2011WorkshopWholeBuilding | NECB 2011 | Workshop | WholeBuilding |  |  | 0.0010723
NECB 2011Space FunctionDwelling Unit(s) | NECB 2011 | Space Function | Dwelling Unit(s) |  |  | 0.00034433
NECB 2011Space FunctionAtrium - H < 13m | NECB 2011 | Space Function | Atrium - H < 13m |  |  | 0.00030498
NECB 2011Space FunctionAtrium - H > 13m | NECB 2011 | Space Function | Atrium - H > 13m |  |  | 0.00030498
NECB 2011Space FunctionAudience - auditorium | NECB 2011 | Space Function | Audience - auditorium |  |  | 0.0041172
NECB 2011Space FunctionAudience - performance arts | NECB 2011 | Space Function | Audience - performance arts |  |  | 0.0041172
NECB 2011Space FunctionAudience - motion picture | NECB 2011 | Space Function | Audience - motion picture |  |  | 0.0041172
NECB 2011Space FunctionClassroom/lecture/training | NECB 2011 | Space Function | Classroom/lecture/training |  |  | 0.0027829
NECB 2011Space FunctionConf./meet./multi-purpose | NECB 2011 | Space Function | Conf./meet./multi-purpose |  |  | 0.0015757
NECB 2011Space FunctionCorr. >= 2.4m wide | NECB 2011 | Space Function | Corr. >= 2.4m wide |  |  | 0.00030498
NECB 2011Space FunctionCorr. < 2.4m wide | NECB 2011 | Space Function | Corr. < 2.4m wide |  |  | 0.00030498
NECB 2011Space FunctionDining - bar lounge/leisure | NECB 2011 | Space Function | Dining - bar lounge/leisure |  |  | 0.0035835
NECB 2011Space FunctionDining - family space | NECB 2011 | Space Function | Dining - family space |  |  | 0.0035835
NECB 2011Space FunctionDining - other | NECB 2011 | Space Function | Dining - other |  |  | 0.0035835
NECB 2011Space FunctionDress./fitt. - performance arts | NECB 2011 | Space Function | Dress./fitt. - performance arts |  |  | 0.0011818
NECB 2011Space FunctionElectrical/Mechanical | NECB 2011 | Space Function | Electrical/Mechanical |  |  | 0.00030498
NECB 2011Space FunctionFood preparation | NECB 2011 | Space Function | Food preparation |  |  | 0.0013724
NECB 2011Space FunctionLab - classrooms | NECB 2011 | Space Function | Lab - classrooms |  |  | 0.0021857
NECB 2011Space FunctionLab - research | NECB 2011 | Space Function | Lab - research |  |  | 0.0021857
NECB 2011Space FunctionLobby - elevator | NECB 2011 | Space Function | Lobby - elevator |  |  | 0.0041172
NECB 2011Space FunctionLobby - performance arts | NECB 2011 | Space Function | Lobby - performance arts |  |  | 0.0041172
NECB 2011Space FunctionLobby - motion picture | NECB 2011 | Space Function | Lobby - motion picture |  |  | 0.0041172
NECB 2011Space FunctionLobby - other | NECB 2011 | Space Function | Lobby - other |  |  | 0.0041172
NECB 2011Space FunctionLocker room | NECB 2011 | Space Function | Locker room |  |  | 0.00094035
NECB 2011Space FunctionLounge/recreation | NECB 2011 | Space Function | Lounge/recreation |  |  | 0.00094035
NECB 2011Space FunctionOffice - enclosed | NECB 2011 | Space Function | Office - enclosed |  |  | 0.00043205
NECB 2011Space FunctionOffice - open plan | NECB 2011 | Space Function | Office - open plan |  |  | 0.00043205
NECB 2011Space FunctionSales area | NECB 2011 | Space Function | Sales area |  |  | 0.0011818
NECB 2011Space FunctionStairway | NECB 2011 | Space Function | Stairway |  |  | 0.00030498
NECB 2011Space FunctionStorage area | NECB 2011 | Space Function | Storage area |  |  | 0.00035581
NECB 2011Space FunctionWashroom | NECB 2011 | Space Function | Washroom |  |  | 0.00030498
NECB 2011Space FunctionWorkshop space | NECB 2011 | Space Function | Workshop space |  |  | 0.0019315
NECB 2011Space FunctionAutomotive - repair | NECB 2011 | Space Function | Automotive - repair |  |  | 0.0012707
NECB 2011Space FunctionBank - banking and offices | NECB 2011 | Space Function | Bank - banking and offices |  |  | 0.00087681
NECB 2011Space FunctionConvention centre - audience | NECB 2011 | Space Function | Convention centre - audience |  |  | 0.0041172
NECB 2011Space FunctionConvention centre - exhibit | NECB 2011 | Space Function | Convention centre - exhibit |  |  | 0.0008641
NECB 2011Space FunctionCourthouse - courtroom | NECB 2011 | Space Function | Courthouse - courtroom |  |  | 0.002084
NECB 2011Space FunctionCourthouse - cell | NECB 2011 | Space Function | Courthouse - cell |  |  | 0.0012453
NECB 2011Space FunctionCourthouse - chambers | NECB 2011 | Space Function | Courthouse - chambers |  |  | 0.00043205
NECB 2011Space FunctionPenitentiary - audience | NECB 2011 | Space Function | Penitentiary - audience |  |  | 0.002084
NECB 2011Space FunctionPenitentiary - classroom | NECB 2011 | Space Function | Penitentiary - classroom |  |  | 0.0027829
NECB 2011Space FunctionPenitentiary - dining | NECB 2011 | Space Function | Penitentiary - dining |  |  | 0.0035835
NECB 2011Space FunctionDormitory - living quarters | NECB 2011 | Space Function | Dormitory - living quarters |  |  | 0.00055913
NECB 2011Space FunctionFire station - engine room | NECB 2011 | Space Function | Fire station - engine room |  |  | 0.0012707
NECB 2011Space FunctionFire station - quarters | NECB 2011 | Space Function | Fire station - quarters |  |  | 0.00081327
NECB 2011Space FunctionGym - fitness | NECB 2011 | Space Function | Gym - fitness |  |  | 0.0043713
NECB 2011Space FunctionGym - audience | NECB 2011 | Space Function | Gym - audience |  |  | 0.0041172
NECB 2011Space FunctionGym - play | NECB 2011 | Space Function | Gym - play |  |  | 0.0015249
NECB 2011Space FunctionHospital corr. >= 2.4m | NECB 2011 | Space Function | Hospital corr. >= 2.4m |  |  | 0.00076244
NECB 2011Space FunctionHospital corr. < 2.4m | NECB 2011 | Space Function | Hospital corr. < 2.4m |  |  | 0.00076244
NECB 2011Space FunctionHospital - emergency | NECB 2011 | Space Function | Hospital - emergency |  |  | 0.0030498
NECB 2011Space FunctionHospital - exam | NECB 2011 | Space Function | Hospital - exam |  |  | 0.0015249
NECB 2011Space FunctionHospital - laundry/washing | NECB 2011 | Space Function | Hospital - laundry/washing |  |  | 0.0022873
NECB 2011Space FunctionHospital - lounge/recreation | NECB 2011 | Space Function | Hospital - lounge/recreation |  |  | 0.0012707
NECB 2011Space FunctionHospital - medical supply | NECB 2011 | Space Function | Hospital - medical supply |  |  | 0.0015249
NECB 2011Space FunctionHospital - nursery | NECB 2011 | Space Function | Hospital - nursery |  |  | 0.0015249
NECB 2011Space FunctionHospital - nurses' station | NECB 2011 | Space Function | Hospital - nurses' station |  |  | 0.0015249
NECB 2011Space FunctionHospital - operating room | NECB 2011 | Space Function | Hospital - operating room |  |  | 0.0045747
NECB 2011Space FunctionHospital - patient room | NECB 2011 | Space Function | Hospital - patient room |  |  | 0.0015249
NECB 2011Space FunctionHospital - pharmacy | NECB 2011 | Space Function | Hospital - pharmacy |  |  | 0.0022873
NECB 2011Space FunctionHospital - physical therapy | NECB 2011 | Space Function | Hospital - physical therapy |  |  | 0.0022873
NECB 2011Space FunctionHospital - radiology/imaging | NECB 2011 | Space Function | Hospital - radiology/imaging |  |  | 0.0022873
NECB 2011Space FunctionHospital - recovery | NECB 2011 | Space Function | Hospital - recovery |  |  | 0.0045747
NECB 2011Space FunctionHotel/Motel - dining | NECB 2011 | Space Function | Hotel/Motel - dining |  |  | 0.0035835
NECB 2011Space FunctionHotel/Motel - rooms | NECB 2011 | Space Function | Hotel/Motel - rooms |  |  | 0.00055913
NECB 2011Space FunctionHotel/Motel - lobby | NECB 2011 | Space Function | Hotel/Motel - lobby |  |  | 0.0014486
NECB 2011Space FunctionHway lodging - dining | NECB 2011 | Space Function | Hway lodging - dining |  |  | 0.0035835
NECB 2011Space FunctionHway lodging - rooms | NECB 2011 | Space Function | Hway lodging - rooms |  |  | 0.00055913
NECB 2011Space FunctionLibrary - cataloging | NECB 2011 | Space Function | Library - cataloging |  |  | 0.0008641
NECB 2011Space FunctionLibrary - reading | NECB 2011 | Space Function | Library - reading |  |  | 0.0008641
NECB 2011Space FunctionLibrary - stacks | NECB 2011 | Space Function | Library - stacks |  |  | 0.0008641
NECB 2011Space FunctionMfg - corr. >= 2.4m | NECB 2011 | Space Function | Mfg - corr. >= 2.4m |  |  | 0.0012707
NECB 2011Space FunctionMfg - corr. < 2.4m | NECB 2011 | Space Function | Mfg - corr. < 2.4m |  |  | 0.0012707
NECB 2011Space FunctionMfg - detailed | NECB 2011 | Space Function | Mfg - detailed |  |  | 0.0012707
NECB 2011Space FunctionMfg - equipment | NECB 2011 | Space Function | Mfg - equipment |  |  | 0.0012707
NECB 2011Space FunctionMfg - bay H > 15m | NECB 2011 | Space Function | Mfg - bay H > 15m |  |  | 0.0012707
NECB 2011Space FunctionMfg - 7.5 <= bay H <= 15m | NECB 2011 | Space Function | Mfg - 7.5 <= bay H <= 15m |  |  | 0.0012707
NECB 2011Space FunctionMfg - bay H < 7.5m | NECB 2011 | Space Function | Mfg - bay H < 7.5m |  |  | 0.0012707
NECB 2011Space FunctionMuseum - exhibition | NECB 2011 | Space Function | Museum - exhibition |  |  | 0.0018299
NECB 2011Space FunctionMuseum - restoration | NECB 2011 | Space Function | Museum - restoration |  |  | 0.0008641
NECB 2011Space FunctionParking garage space | NECB 2011 | Space Function | Parking garage space |  |  | 0.0025415
NECB 2011Space FunctionPost office sorting | NECB 2011 | Space Function | Post office sorting |  |  | 0.00087681
NECB 2011Space FunctionReligious - audience | NECB 2011 | Space Function | Religious - audience |  |  | 0.0033548
NECB 2011Space FunctionReligious - fellowship hall | NECB 2011 | Space Function | Religious - fellowship hall |  |  | 0.0033548
NECB 2011Space FunctionReligious - pulpit/choir | NECB 2011 | Space Function | Religious - pulpit/choir |  |  | 0.0033548
NECB 2011Space FunctionRetail - dressing/fitting | NECB 2011 | Space Function | Retail - dressing/fitting |  |  | 0.0011818
NECB 2011Space FunctionRetail - mall concourse | NECB 2011 | Space Function | Retail - mall concourse |  |  | 0.0018299
NECB 2011Space FunctionRetail - sales | NECB 2011 | Space Function | Retail - sales |  |  | 0.0011818
NECB 2011Space FunctionSports arena - audience | NECB 2011 | Space Function | Sports arena - audience |  |  | 0.0060233
NECB 2011Space FunctionSports arena - court c4 | NECB 2011 | Space Function | Sports arena - court c4 |  |  | 0.0015249
NECB 2011Space FunctionSports arena - court c3 | NECB 2011 | Space Function | Sports arena - court c3 |  |  | 0.0015249
NECB 2011Space FunctionSports arena - court c2 | NECB 2011 | Space Function | Sports arena - court c2 |  |  | 0.0015249
NECB 2011Space FunctionSports arena - court c1 | NECB 2011 | Space Function | Sports arena - court c1 |  |  | 0.0015249
NECB 2011Space FunctionSports arena - ring | NECB 2011 | Space Function | Sports arena - ring |  |  | 0.0015249
NECB 2011Space FunctionTransp. baggage | NECB 2011 | Space Function | Transp. baggage |  |  | 0.00087681
NECB 2011Space FunctionTransp. seating | NECB 2011 | Space Function | Transp. seating |  |  | 0.0041172
NECB 2011Space FunctionTransp. concourse | NECB 2011 | Space Function | Transp. concourse |  |  | 0.0041172
NECB 2011Space FunctionTransp. counter | NECB 2011 | Space Function | Transp. counter |  |  | 0.00087681
NECB 2011Space FunctionWarehouse - fine | NECB 2011 | Space Function | Warehouse - fine |  |  | 0.00030498
NECB 2011Space FunctionWarehouse - med/blk | NECB 2011 | Space Function | Warehouse - med/blk |  |  | 0.00030498
NECB 2011Space FunctionWarehouse - med/blk2 | NECB 2011 | Space Function | Warehouse - med/blk2 |  |  | 0.00030498

## Occupancy
Each row represents typical design occupancy for a particular space type in a particular standard. Values may be referenced on Space Types tab.
occupancy
VlookupColumn | Ventilation Standard | Primary Space Type | Secondary Space Type | people/1000 ft^2 | Notes
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial laundry | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial laundry | 10
ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial dry cleaner | 30
ASHRAE 62.1-1999Dry Cleaners, LaundriesStorage, pick up | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Storage, pick up | 30
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated laundries | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated laundries | 20
ASHRAE 62.1-1999Dry Cleaners, LaundriesCoin-operated dry cleaner | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Coin-operated dry cleaner | 20
ASHRAE 62.1-1999Food and Beverage ServiceDining rooms | ASHRAE 62.1-1999 | Food and Beverage Service | Dining rooms | 70
ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | 100
ASHRAE 62.1-1999Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-1999 | Food and Beverage Service | Bars, cocktail lounges | 100
ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | 20 | Exhaust >= 1.5 cfm/ft2, 7.5 L/s m2
ASHRAE 62.1-1999Garages, Repair, Service StationsEnclosed parking garage | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Enclosed parking garage | 0
ASHRAE 62.1-1999Garages, Repair, Service StationsAuto repair rooms | ASHRAE 62.1-1999 | Garages, Repair, Service Stations | Auto repair rooms | 0
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBedrooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Bedrooms | 0 | 30 cfm/room, 15 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLiving rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Living rooms | 0 | 30 cfm/room, 15 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBaths | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Baths | 0 | 35 cfm/room, 18 L/s room
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | 30
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | 50
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesAssembly rooms | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Assembly rooms | 120
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | 20
ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesGambling casinos | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Gambling casinos | 120
ASHRAE 62.1-1999OfficesOffice space | ASHRAE 62.1-1999 | Offices | Office space | 7
ASHRAE 62.1-1999OfficesReception areas | ASHRAE 62.1-1999 | Offices | Reception areas | 60
ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | 60
ASHRAE 62.1-1999OfficesConference rooms | ASHRAE 62.1-1999 | Offices | Conference rooms | 50
ASHRAE 62.1-1999Public SpacesCorridors and utilities | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | 0
ASHRAE 62.1-1999Public SpacesPublic restrooms | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | 0 | (Assume 12 toilet/625 ft^2) 50 cfm/wc or urinal, 25 L/s wc or urinal
ASHRAE 62.1-1999Public SpacesLocker and dressing rooms | ASHRAE 62.1-1999 | Public Spaces | Locker and dressing rooms | 0
ASHRAE 62.1-1999Public SpacesSmoking lounge | ASHRAE 62.1-1999 | Public Spaces | Smoking lounge | 70
ASHRAE 62.1-1999Public SpacesElevators | ASHRAE 62.1-1999 | Public Spaces | Elevators | 0
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | 30
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsUpper floors | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Upper floors | 20
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | 15
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsDressing rooms | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Dressing rooms | 0
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsMalls and arcades | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Malls and arcades | 20
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | 10
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | 5
ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsSmoking lounge | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Smoking lounge | 70
ASHRAE 62.1-1999Specialty ShopsBarber | ASHRAE 62.1-1999 | Specialty Shops | Barber | 25
ASHRAE 62.1-1999Specialty ShopsBeauty | ASHRAE 62.1-1999 | Specialty Shops | Beauty | 25
ASHRAE 62.1-1999Specialty ShopsReducing salons | ASHRAE 62.1-1999 | Specialty Shops | Reducing salons | 20
ASHRAE 62.1-1999Specialty ShopsFlorists | ASHRAE 62.1-1999 | Specialty Shops | Florists | 8
ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | 0
ASHRAE 62.1-1999Specialty ShopsHardware, drugs, fabric | ASHRAE 62.1-1999 | Specialty Shops | Hardware, drugs, fabric | 8
ASHRAE 62.1-1999Specialty ShopsSupermarket | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | 8
ASHRAE 62.1-1999Specialty ShopsPet shops | ASHRAE 62.1-1999 | Specialty Shops | Pet shops | 0
ASHRAE 62.1-1999Sports and AmusementSpectator areas | ASHRAE 62.1-1999 | Sports and Amusement | Spectator areas | 150
ASHRAE 62.1-1999Sports and AmusementGame rooms | ASHRAE 62.1-1999 | Sports and Amusement | Game rooms | 70
ASHRAE 62.1-1999Sports and AmusementIce arenas (playing areas) | ASHRAE 62.1-1999 | Sports and Amusement | Ice arenas (playing areas) | 0 | Higher may be needed if internal combustion engines are operated for maintenance
ASHRAE 62.1-1999Sports and AmusementSwimming pools (pool and deck areas) | ASHRAE 62.1-1999 | Sports and Amusement | Swimming pools (pool and deck areas) | 0 | Higher may be needed for humidity control
ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | 30
ASHRAE 62.1-1999Sports and AmusementBallrooms and discos | ASHRAE 62.1-1999 | Sports and Amusement | Ballrooms and discos | 100
ASHRAE 62.1-1999Sports and AmusementBowling alleys (seating areas) | ASHRAE 62.1-1999 | Sports and Amusement | Bowling alleys (seating areas) | 70
ASHRAE 62.1-1999TheatersTicket booths | ASHRAE 62.1-1999 | Theaters | Ticket booths | 60
ASHRAE 62.1-1999TheatersLobbies | ASHRAE 62.1-1999 | Theaters | Lobbies | 150
ASHRAE 62.1-1999TheatersAuditorium | ASHRAE 62.1-1999 | Theaters | Auditorium | 150
ASHRAE 62.1-1999TheatersStages, studios | ASHRAE 62.1-1999 | Theaters | Stages, studios | 70
ASHRAE 62.1-1999TransportationWaiting rooms | ASHRAE 62.1-1999 | Transportation | Waiting rooms | 100
ASHRAE 62.1-1999TransportationPlatforms | ASHRAE 62.1-1999 | Transportation | Platforms | 100
ASHRAE 62.1-1999TransportationVehicles | ASHRAE 62.1-1999 | Transportation | Vehicles | 150
ASHRAE 62.1-1999WorkroomsMeat processing | ASHRAE 62.1-1999 | Workrooms | Meat processing | 10
ASHRAE 62.1-1999WorkroomsPhoto studios | ASHRAE 62.1-1999 | Workrooms | Photo studios | 10
ASHRAE 62.1-1999WorkroomsDarkrooms | ASHRAE 62.1-1999 | Workrooms | Darkrooms | 10
ASHRAE 62.1-1999WorkroomsPharmacy | ASHRAE 62.1-1999 | Workrooms | Pharmacy | 20
ASHRAE 62.1-1999WorkroomsBank vaults | ASHRAE 62.1-1999 | Workrooms | Bank vaults | 5
ASHRAE 62.1-1999WorkroomsDuplicating, printing | ASHRAE 62.1-1999 | Workrooms | Duplicating, printing | 0
ASHRAE 62.1-1999EducationClassroom | ASHRAE 62.1-1999 | Education | Classroom | 50
ASHRAE 62.1-1999EducationLaboratories | ASHRAE 62.1-1999 | Education | Laboratories | 30
ASHRAE 62.1-1999EducationTraining shop | ASHRAE 62.1-1999 | Education | Training shop | 30
ASHRAE 62.1-1999EducationMusic rooms | ASHRAE 62.1-1999 | Education | Music rooms | 50
ASHRAE 62.1-1999EducationLibraries | ASHRAE 62.1-1999 | Education | Libraries | 20
ASHRAE 62.1-1999EducationLocker rooms | ASHRAE 62.1-1999 | Education | Locker rooms | 0
ASHRAE 62.1-1999EducationCorridors | ASHRAE 62.1-1999 | Education | Corridors | 0
ASHRAE 62.1-1999EducationAuditorium | ASHRAE 62.1-1999 | Education | Auditorium | 150
ASHRAE 62.1-1999EducationSmoking lounges | ASHRAE 62.1-1999 | Education | Smoking lounges | 70
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 10
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 20
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 20
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 20
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 0
ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 20
ASHRAE 62.1-1999Correctional FacilitiesCell | ASHRAE 62.1-1999 | Correctional Facilities | Cell | 20
ASHRAE 62.1-1999Correctional FacilitiesDining halls | ASHRAE 62.1-1999 | Correctional Facilities | Dining halls | 100
ASHRAE 62.1-1999Correctional FacilitiesGuard stations | ASHRAE 62.1-1999 | Correctional Facilities | Guard stations | 40
ASHRAE 62.1-2004Correctional FacilitiesCell | ASHRAE 62.1-2004 | Correctional Facilities | Cell | 25
ASHRAE 62.1-2004Correctional FacilitiesDay room | ASHRAE 62.1-2004 | Correctional Facilities | Day room | 30
ASHRAE 62.1-2004Correctional FacilitiesGuard stations | ASHRAE 62.1-2004 | Correctional Facilities | Guard stations | 15
ASHRAE 62.1-2004Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2004 | Correctional Facilities | Booking/waiting | 50
ASHRAE 62.1-2004Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2004 | Educational Facilities | Daycare (through age 4) | 25
ASHRAE 62.1-2004Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (ages 5-8) | 25
ASHRAE 62.1-2004Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (age 9 plus) | 35
ASHRAE 62.1-2004Educational FacilitiesLecture classroom | ASHRAE 62.1-2004 | Educational Facilities | Lecture classroom | 65
ASHRAE 62.1-2004Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2004 | Educational Facilities | Lecture hall (fixed seats) | 150
ASHRAE 62.1-2004Educational FacilitiesArt classroom | ASHRAE 62.1-2004 | Educational Facilities | Art classroom | 20
ASHRAE 62.1-2004Educational FacilitiesScience laboratories | ASHRAE 62.1-2004 | Educational Facilities | Science laboratories | 25 | E
ASHRAE 62.1-2004Educational FacilitiesWood/metal shop | ASHRAE 62.1-2004 | Educational Facilities | Wood/metal shop | 20
ASHRAE 62.1-2004Educational FacilitiesComputer lab | ASHRAE 62.1-2004 | Educational Facilities | Computer lab | 25
ASHRAE 62.1-2004Educational FacilitiesMedia center | ASHRAE 62.1-2004 | Educational Facilities | Media center | 25 | A
ASHRAE 62.1-2004Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2004 | Educational Facilities | Music/theater/dance | 35
ASHRAE 62.1-2004Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2004 | Educational Facilities | Multiuse assembly | 100
ASHRAE 62.1-2004Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2004 | Food and Beverage Service | Restaurant dining rooms | 70
ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | 100
ASHRAE 62.1-2004Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2004 | Food and Beverage Service | Bars, cocktail lounges | 100
ASHRAE 62.1-2004GeneralConference/meeting | ASHRAE 62.1-2004 | General | Conference/meeting | 50
ASHRAE 62.1-2004GeneralCorridors | ASHRAE 62.1-2004 | General | Corridors | 0
ASHRAE 62.1-2004GeneralStorage rooms | ASHRAE 62.1-2004 | General | Storage rooms | 0 | B
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 10
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 20
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 30
ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 120
ASHRAE 62.1-2004Office BuildingsOffice space | ASHRAE 62.1-2004 | Office Buildings | Office space | 5
ASHRAE 62.1-2004Office BuildingsReception areas | ASHRAE 62.1-2004 | Office Buildings | Reception areas | 30
ASHRAE 62.1-2004Office BuildingsTelephone/data entry | ASHRAE 62.1-2004 | Office Buildings | Telephone/data entry | 60
ASHRAE 62.1-2004Office BuildingsMain entry lobbies | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | 10
ASHRAE 62.1-2004Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2004 | Miscellaneous Spaces | Bank vaults/safe deposit | 5
ASHRAE 62.1-2004Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Computer (not printing) | 4
ASHRAE 62.1-2004Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2004 | Miscellaneous Spaces | Pharmacy (prep. area) | 10
ASHRAE 62.1-2004Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2004 | Miscellaneous Spaces | Photo studios | 10
ASHRAE 62.1-2004Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2004 | Miscellaneous Spaces | Shipping/receiving | 0 | B
ASHRAE 62.1-2004Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2004 | Miscellaneous Spaces | Transportation waiting | 100
ASHRAE 62.1-2004Miscellaneous SpacesWarehouses | ASHRAE 62.1-2004 | Miscellaneous Spaces | Warehouses | 0 | B
ASHRAE 62.1-2004Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2004 | Public Assembly Spaces | Auditorium seating area | 150
ASHRAE 62.1-2004Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2004 | Public Assembly Spaces | Places of religious worship | 120
ASHRAE 62.1-2004Public Assembly SpacesCourtrooms | ASHRAE 62.1-2004 | Public Assembly Spaces | Courtrooms | 70
ASHRAE 62.1-2004Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2004 | Public Assembly Spaces | Legislative chambers | 50
ASHRAE 62.1-2004Public Assembly SpacesLibraries | ASHRAE 62.1-2004 | Public Assembly Spaces | Libraries | 10
ASHRAE 62.1-2004Public Assembly SpacesLobbies | ASHRAE 62.1-2004 | Public Assembly Spaces | Lobbies | 150
ASHRAE 62.1-2004Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums (children’s) | 40
ASHRAE 62.1-2004Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2004 | Public Assembly Spaces | Museums/galleries | 40
ASHRAE 62.1-2004RetailGeneral Sales | ASHRAE 62.1-2004 | Retail | General Sales | 15
ASHRAE 62.1-2004RetailMall common areas | ASHRAE 62.1-2004 | Retail | Mall common areas | 40
ASHRAE 62.1-2004RetailBarber shop | ASHRAE 62.1-2004 | Retail | Barber shop | 25
ASHRAE 62.1-2004RetailBeauty and nail salons | ASHRAE 62.1-2004 | Retail | Beauty and nail salons | 25
ASHRAE 62.1-2004RetailPet shops (animal areas) | ASHRAE 62.1-2004 | Retail | Pet shops (animal areas) | 10
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 8
ASHRAE 62.1-2004RetailSupermarket | ASHRAE 62.1-2004 | Retail | Supermarket | 8
ASHRAE 62.1-2004RetailCoinoperated laundries | ASHRAE 62.1-2004 | Retail | Coinoperated laundries | 20
ASHRAE 62.1-2004Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Sports arena (play area) | 0
ASHRAE 62.1-2004Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2004 | Sports and Entertainment | Gym, stadium (play area) | 30
ASHRAE 62.1-2004Sports and EntertainmentSpectator areas | ASHRAE 62.1-2004 | Sports and Entertainment | Spectator areas | 150
ASHRAE 62.1-2004Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2004 | Sports and Entertainment | Swimming (pool & deck) | 0 | C
ASHRAE 62.1-2004Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2004 | Sports and Entertainment | Disco/dance floors | 100
ASHRAE 62.1-2004Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/aerobics room | 40
ASHRAE 62.1-2004Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/weight rooms | 10
ASHRAE 62.1-2004Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2004 | Sports and Entertainment | Bowling alley (seating) | 40
ASHRAE 62.1-2004Sports and EntertainmentGambling casinos | ASHRAE 62.1-2004 | Sports and Entertainment | Gambling casinos | 120
ASHRAE 62.1-2004Sports and EntertainmentGame arcades | ASHRAE 62.1-2004 | Sports and Entertainment | Game arcades | 20
ASHRAE 62.1-2004Sports and EntertainmentStages, studios | ASHRAE 62.1-2004 | Sports and Entertainment | Stages, studios | 70 | D
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 10 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 20 | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 20
ASHRAE 62.1-2007Correctional FacilitiesCell | ASHRAE 62.1-2007 | Correctional Facilities | Cell | 25
ASHRAE 62.1-2007Correctional FacilitiesDay room | ASHRAE 62.1-2007 | Correctional Facilities | Day room | 30
ASHRAE 62.1-2007Correctional FacilitiesGuard stations | ASHRAE 62.1-2007 | Correctional Facilities | Guard stations | 15
ASHRAE 62.1-2007Correctional FacilitiesBooking/waiting | ASHRAE 62.1-2007 | Correctional Facilities | Booking/waiting | 50
ASHRAE 62.1-2007Educational FacilitiesDaycare (through age 4) | ASHRAE 62.1-2007 | Educational Facilities | Daycare (through age 4) | 25
ASHRAE 62.1-2007Educational FacilitiesClassrooms (ages 5-8) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (ages 5-8) | 25
ASHRAE 62.1-2007Educational FacilitiesClassrooms (age 9 plus) | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (age 9 plus) | 35
ASHRAE 62.1-2007Educational FacilitiesLecture classroom | ASHRAE 62.1-2007 | Educational Facilities | Lecture classroom | 65
ASHRAE 62.1-2007Educational FacilitiesLecture hall (fixed seats) | ASHRAE 62.1-2007 | Educational Facilities | Lecture hall (fixed seats) | 150
ASHRAE 62.1-2007Educational FacilitiesArt classroom | ASHRAE 62.1-2007 | Educational Facilities | Art classroom | 20
ASHRAE 62.1-2007Educational FacilitiesScience laboratories | ASHRAE 62.1-2007 | Educational Facilities | Science laboratories | 25 | E
ASHRAE 62.1-2007Educational FacilitiesWood/metal shop | ASHRAE 62.1-2007 | Educational Facilities | Wood/metal shop | 20
ASHRAE 62.1-2007Educational FacilitiesComputer lab | ASHRAE 62.1-2007 | Educational Facilities | Computer lab | 25
ASHRAE 62.1-2007Educational FacilitiesMedia center | ASHRAE 62.1-2007 | Educational Facilities | Media center | 25 | A
ASHRAE 62.1-2007Educational FacilitiesMusic/theater/dance | ASHRAE 62.1-2007 | Educational Facilities | Music/theater/dance | 35
ASHRAE 62.1-2007Educational FacilitiesMultiuse assembly | ASHRAE 62.1-2007 | Educational Facilities | Multiuse assembly | 100
ASHRAE 62.1-2007Food and Beverage ServiceRestaurant dining rooms | ASHRAE 62.1-2007 | Food and Beverage Service | Restaurant dining rooms | 70
ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | 100
ASHRAE 62.1-2007Food and Beverage ServiceBars, cocktail lounges | ASHRAE 62.1-2007 | Food and Beverage Service | Bars, cocktail lounges | 100
ASHRAE 62.1-2007GeneralConference/meeting | ASHRAE 62.1-2007 | General | Conference/meeting | 50
ASHRAE 62.1-2007GeneralCorridors | ASHRAE 62.1-2007 | General | Corridors | 0
ASHRAE 62.1-2007GeneralStorage rooms | ASHRAE 62.1-2007 | General | Storage rooms | 0 | B
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | 10
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBarracks sleeping areas | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Barracks sleeping areas | 20
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | 30
ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | 120
ASHRAE 62.1-2007Office BuildingsOffice space | ASHRAE 62.1-2007 | Office Buildings | Office space | 5
ASHRAE 62.1-2007Office BuildingsReception areas | ASHRAE 62.1-2007 | Office Buildings | Reception areas | 30
ASHRAE 62.1-2007Office BuildingsTelephone/data entry | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | 60
ASHRAE 62.1-2007Office BuildingsMain entry lobbies | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | 10
ASHRAE 62.1-2007Miscellaneous SpacesBank vaults/safe deposit | ASHRAE 62.1-2007 | Miscellaneous Spaces | Bank vaults/safe deposit | 5
ASHRAE 62.1-2007Miscellaneous SpacesComputer (not printing) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Computer (not printing) | 4
ASHRAE 62.1-2007Miscellaneous SpacesPharmacy (prep. area) | ASHRAE 62.1-2007 | Miscellaneous Spaces | Pharmacy (prep. area) | 10
ASHRAE 62.1-2007Miscellaneous SpacesPhoto studios | ASHRAE 62.1-2007 | Miscellaneous Spaces | Photo studios | 10
ASHRAE 62.1-2007Miscellaneous SpacesShipping/receiving | ASHRAE 62.1-2007 | Miscellaneous Spaces | Shipping/receiving | 0 | B
ASHRAE 62.1-2007Miscellaneous SpacesTransportation waiting | ASHRAE 62.1-2007 | Miscellaneous Spaces | Transportation waiting | 100
ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses | 0 | B
ASHRAE 62.1-2007Public Assembly SpacesAuditorium seating area | ASHRAE 62.1-2007 | Public Assembly Spaces | Auditorium seating area | 150
ASHRAE 62.1-2007Public Assembly SpacesPlaces of religious worship | ASHRAE 62.1-2007 | Public Assembly Spaces | Places of religious worship | 120
ASHRAE 62.1-2007Public Assembly SpacesCourtrooms | ASHRAE 62.1-2007 | Public Assembly Spaces | Courtrooms | 70
ASHRAE 62.1-2007Public Assembly SpacesLegislative chambers | ASHRAE 62.1-2007 | Public Assembly Spaces | Legislative chambers | 50
ASHRAE 62.1-2007Public Assembly SpacesLibraries | ASHRAE 62.1-2007 | Public Assembly Spaces | Libraries | 10
ASHRAE 62.1-2007Public Assembly SpacesLobbies | ASHRAE 62.1-2007 | Public Assembly Spaces | Lobbies | 150
ASHRAE 62.1-2007Public Assembly SpacesMuseums (children’s) | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums (children’s) | 40
ASHRAE 62.1-2007Public Assembly SpacesMuseums/galleries | ASHRAE 62.1-2007 | Public Assembly Spaces | Museums/galleries | 40
ASHRAE 62.1-2007RetailGeneral Sales | ASHRAE 62.1-2007 | Retail | General Sales | 15
ASHRAE 62.1-2007RetailMall common areas | ASHRAE 62.1-2007 | Retail | Mall common areas | 40
ASHRAE 62.1-2007RetailBarber shop | ASHRAE 62.1-2007 | Retail | Barber shop | 25
ASHRAE 62.1-2007RetailBeauty and nail salons | ASHRAE 62.1-2007 | Retail | Beauty and nail salons | 25
ASHRAE 62.1-2007RetailPet shops (animal areas) | ASHRAE 62.1-2007 | Retail | Pet shops (animal areas) | 10
ASHRAE 62.1-2007RetailSupermarket | ASHRAE 62.1-2007 | Retail | Supermarket | 8
ASHRAE 62.1-2007RetailCoinoperated laundries | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | 20
ASHRAE 62.1-2007Sports and EntertainmentSports arena (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Sports arena (play area) | 0
ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) | 30
ASHRAE 62.1-2007Sports and EntertainmentSpectator areas | ASHRAE 62.1-2007 | Sports and Entertainment | Spectator areas | 150
ASHRAE 62.1-2007Sports and EntertainmentSwimming (pool & deck) | ASHRAE 62.1-2007 | Sports and Entertainment | Swimming (pool & deck) | 0 | C
ASHRAE 62.1-2007Sports and EntertainmentDisco/dance floors | ASHRAE 62.1-2007 | Sports and Entertainment | Disco/dance floors | 100
ASHRAE 62.1-2007Sports and EntertainmentHealth club/aerobics room | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/aerobics room | 40
ASHRAE 62.1-2007Sports and EntertainmentHealth club/weight rooms | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/weight rooms | 10
ASHRAE 62.1-2007Sports and EntertainmentBowling alley (seating) | ASHRAE 62.1-2007 | Sports and Entertainment | Bowling alley (seating) | 40
ASHRAE 62.1-2007Sports and EntertainmentGambling casinos | ASHRAE 62.1-2007 | Sports and Entertainment | Gambling casinos | 120
ASHRAE 62.1-2007Sports and EntertainmentGame arcades | ASHRAE 62.1-2007 | Sports and Entertainment | Game arcades | 20
ASHRAE 62.1-2007Sports and EntertainmentStages, studios | ASHRAE 62.1-2007 | Sports and Entertainment | Stages, studios | 70 | D
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPatient rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Patient rooms | 10 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesMedical procedure | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Medical procedure | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesOperating rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Operating rooms | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesRecovery and ICU | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Recovery and ICU | 20 | Special requirements or codes and pressure relationships may determine minimum ventilation rates and filter efficiency. Procedures generating contaminants may require higher rates.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesAutopsy rooms | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Autopsy rooms | 20 | Air shall not be recirculated into other spaces.
ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | 20
GGHC v2.2Health CareAnesthesia Storage | GGHC v2.2 | Health Care | Anesthesia Storage | 5
GGHC v2.2Health CareAngiographic-All Other Types | GGHC v2.2 | Health Care | Angiographic-All Other Types | 5
GGHC v2.2Health CareAngiographic-Heart Only | GGHC v2.2 | Health Care | Angiographic-Heart Only | 5
GGHC v2.2Health CareAutopsy | GGHC v2.2 | Health Care | Autopsy | 5
GGHC v2.2Health CareBathroom/ Public | GGHC v2.2 | Health Care | Bathroom/ Public | 3.3
GGHC v2.2Health CareBedpan Room | GGHC v2.2 | Health Care | Bedpan Room | 5
GGHC v2.2Health CareCast Room | GGHC v2.2 | Health Care | Cast Room | 5
GGHC v2.2Health CareClean Linen Storage | GGHC v2.2 | Health Care | Clean Linen Storage | 1
GGHC v2.2Health CareClean Utility / Workroom | GGHC v2.2 | Health Care | Clean Utility / Workroom | 5
GGHC v2.2Health CareConference Rooms | GGHC v2.2 | Health Care | Conference Rooms | 20
GGHC v2.2Health CareCorridors | GGHC v2.2 | Health Care | Corridors | 10
GGHC v2.2Health CareCystoscopy | GGHC v2.2 | Health Care | Cystoscopy | 5
GGHC v2.2Health CareDarkroom | GGHC v2.2 | Health Care | Darkroom | 5
GGHC v2.2Health CareDecontamination | GGHC v2.2 | Health Care | Decontamination | 5
GGHC v2.2Health CareDelivery Room | GGHC v2.2 | Health Care | Delivery Room | 5
GGHC v2.2Health CareDietary Day Storage | GGHC v2.2 | Health Care | Dietary Day Storage | 2
GGHC v2.2Health CareDining Room | GGHC v2.2 | Health Care | Dining Room | 10
GGHC v2.2Health CareDishwashing | GGHC v2.2 | Health Care | Dishwashing | 5
GGHC v2.2Health CareEndoscopy | GGHC v2.2 | Health Care | Endoscopy | 5
GGHC v2.2Health CareHistology | GGHC v2.2 | Health Care | Histology | 5
GGHC v2.2Health CareIsolation | GGHC v2.2 | Health Care | Isolation | 5
GGHC v2.2Health CareJanitors Closet / Utility | GGHC v2.2 | Health Care | Janitors Closet / Utility | 1
GGHC v2.2Health CareKitchen, Food Preparation | GGHC v2.2 | Health Care | Kitchen, Food Preparation | 5
GGHC v2.2Health CareLabor/ Delivery/Recovery | GGHC v2.2 | Health Care | Labor/ Delivery/Recovery | 5
GGHC v2.2Health CareL / D / R / Post Partum | GGHC v2.2 | Health Care | L / D / R / Post Partum | 5
GGHC v2.2Health CareLaboratory | GGHC v2.2 | Health Care | Laboratory | 5
GGHC v2.2Health CareLinen Storage, Clean | GGHC v2.2 | Health Care | Linen Storage, Clean | 2
GGHC v2.2Health CareLobby | GGHC v2.2 | Health Care | Lobby | 10
GGHC v2.2Health CareLockers | GGHC v2.2 | Health Care | Lockers | 10
GGHC v2.2Health CareMammography | GGHC v2.2 | Health Care | Mammography | 5
GGHC v2.2Health CareMechanical Equipment Room | GGHC v2.2 | Health Care | Mechanical Equipment Room | 0.5
GGHC v2.2Health CareMedical Records | GGHC v2.2 | Health Care | Medical Records | 2
GGHC v2.2Health CareNuclear Medicine, Hot Lab | GGHC v2.2 | Health Care | Nuclear Medicine, Hot Lab | 5
GGHC v2.2Health CareNursery, General | GGHC v2.2 | Health Care | Nursery, General | 5
GGHC v2.2Health CareNursery, Exam | GGHC v2.2 | Health Care | Nursery, Exam | 5
GGHC v2.2Health CareNursing Stations- General | GGHC v2.2 | Health Care | Nursing Stations- General | 5
GGHC v2.2Health CareOperating Room | GGHC v2.2 | Health Care | Operating Room | 5
GGHC v2.2Health CarePathology | GGHC v2.2 | Health Care | Pathology | 5
GGHC v2.2Health CarePatient Room | GGHC v2.2 | Health Care | Patient Room | 5
GGHC v2.2Health CarePharmacy / Medicine Room | GGHC v2.2 | Health Care | Pharmacy / Medicine Room | 5
GGHC v2.2Health CarePhysical Therapy and Hydrotherapy | GGHC v2.2 | Health Care | Physical Therapy and Hydrotherapy | 5
GGHC v2.2Health CareRecovery | GGHC v2.2 | Health Care | Recovery | 5
GGHC v2.2Health CareScrub Up Area, Surgical Corridor | GGHC v2.2 | Health Care | Scrub Up Area, Surgical Corridor | 5
GGHC v2.2Health CareSoiled Linen, Sorting | GGHC v2.2 | Health Care | Soiled Linen, Sorting | 5
GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | 5
GGHC v2.2Health CareSpecial Procedure Room, Invasive | GGHC v2.2 | Health Care | Special Procedure Room, Invasive | 5
GGHC v2.2Health CareStairways | GGHC v2.2 | Health Care | Stairways | 1
GGHC v2.2Health CareSterilizer Room | GGHC v2.2 | Health Care | Sterilizer Room | 5
GGHC v2.2Health CareSub-Sterile | GGHC v2.2 | Health Care | Sub-Sterile | 5
GGHC v2.2Health CareSurgical Supply | GGHC v2.2 | Health Care | Surgical Supply | 5
GGHC v2.2Health CareTrash Chute Room | GGHC v2.2 | Health Care | Trash Chute Room | 0.5
GGHC v2.2Health CareTrauma | GGHC v2.2 | Health Care | Trauma | 5
GGHC v2.2Health CareTreatment / Examination | GGHC v2.2 | Health Care | Treatment / Examination | 5
GGHC v2.2Health CareUnsterile Supply | GGHC v2.2 | Health Care | Unsterile Supply | 2
GGHC v2.2Health CareWaiting Areas/Lounges | GGHC v2.2 | Health Care | Waiting Areas/Lounges | 10
GGHC v2.2Health CareX-ray, Diagnostic and Treatment | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | 5
NECB 2011Automotive facilityWholeBuilding | NECB 2011 | Automotive facility | WholeBuilding | 4.65
NECB 2011Convention centreWholeBuilding | NECB 2011 | Convention centre | WholeBuilding | 11.61
NECB 2011CourthouseWholeBuilding | NECB 2011 | Courthouse | WholeBuilding | 6.19
NECB 2011Dining - bar/loungeWholeBuilding | NECB 2011 | Dining - bar/lounge | WholeBuilding | 9.29
NECB 2011Dining - cafeteriaWholeBuilding | NECB 2011 | Dining - cafeteria | WholeBuilding | 9.29
NECB 2011Dining - familyWholeBuilding | NECB 2011 | Dining - family | WholeBuilding | 9.29
NECB 2011DormitoryWholeBuilding | NECB 2011 | Dormitory | WholeBuilding | 3.1
NECB 2011Exercise centreWholeBuilding | NECB 2011 | Exercise centre | WholeBuilding | 9.29
NECB 2011Fire stationWholeBuilding | NECB 2011 | Fire station | WholeBuilding | 3.72
NECB 2011GymnasiumWholeBuilding | NECB 2011 | Gymnasium | WholeBuilding | 9.29
NECB 2011Health-care clinicWholeBuilding | NECB 2011 | Health-care clinic | WholeBuilding | 4.65
NECB 2011HospitalWholeBuilding | NECB 2011 | Hospital | WholeBuilding | 4.65
NECB 2011HotelWholeBuilding | NECB 2011 | Hotel | WholeBuilding | 3.72
NECB 2011LibraryWholeBuilding | NECB 2011 | Library | WholeBuilding | 4.65
NECB 2011Manufacturing facilityWholeBuilding | NECB 2011 | Manufacturing facility | WholeBuilding | 3.1
NECB 2011MotelWholeBuilding | NECB 2011 | Motel | WholeBuilding | 3.72
NECB 2011Motion picture theatreWholeBuilding | NECB 2011 | Motion picture theatre | WholeBuilding | 11.61
NECB 2011Multi-unit residentialWholeBuilding | NECB 2011 | Multi-unit residential | WholeBuilding | 1.55
NECB 2011MuseumWholeBuilding | NECB 2011 | Museum | WholeBuilding | 4.65
NECB 2011OfficeWholeBuilding | NECB 2011 | Office | WholeBuilding | 3.72
NECB 2011Parking garageWholeBuilding | NECB 2011 | Parking garage | WholeBuilding | 0.09
NECB 2011PenitentiaryWholeBuilding | NECB 2011 | Penitentiary | WholeBuilding | 3.1
NECB 2011Performing arts theatreWholeBuilding | NECB 2011 | Performing arts theatre | WholeBuilding | 11.61
NECB 2011Police stationWholeBuilding | NECB 2011 | Police station | WholeBuilding | 3.72
NECB 2011Post officeWholeBuilding | NECB 2011 | Post office | WholeBuilding | 3.72
NECB 2011ReligiousWholeBuilding | NECB 2011 | Religious | WholeBuilding | 18.58
NECB 2011RetailWholeBuilding | NECB 2011 | Retail | WholeBuilding | 3.1
NECB 2011School/universityWholeBuilding | NECB 2011 | School/university | WholeBuilding | 11.61
NECB 2011Sports arenaWholeBuilding | NECB 2011 | Sports arena | WholeBuilding | 9.29
NECB 2011Town hallWholeBuilding | NECB 2011 | Town hall | WholeBuilding | 3.72
NECB 2011TransportationWholeBuilding | NECB 2011 | Transportation | WholeBuilding | 6.19
NECB 2011WarehouseWholeBuilding | NECB 2011 | Warehouse | WholeBuilding | 0.06
NECB 2011WorkshopWholeBuilding | NECB 2011 | Workshop | WholeBuilding | 3.1
NECB 2011Space FunctionDwelling Unit(s) | NECB 2011 | Space Function | Dwelling Unit(s) | 1.55
NECB 2011Space FunctionAtrium - H < 13m | NECB 2011 | Space Function | Atrium - H < 13m | 9.29
NECB 2011Space FunctionAtrium - H > 13m | NECB 2011 | Space Function | Atrium - H > 13m | 9.29
NECB 2011Space FunctionAudience - auditorium | NECB 2011 | Space Function | Audience - auditorium | 18.58
NECB 2011Space FunctionAudience - performance arts | NECB 2011 | Space Function | Audience - performance arts | 12.39
NECB 2011Space FunctionAudience - motion picture | NECB 2011 | Space Function | Audience - motion picture | 18.58
NECB 2011Space FunctionClassroom/lecture/training | NECB 2011 | Space Function | Classroom/lecture/training | 12.39
NECB 2011Space FunctionConf./meet./multi-purpose | NECB 2011 | Space Function | Conf./meet./multi-purpose | 18.58
NECB 2011Space FunctionCorr. >= 2.4m wide | NECB 2011 | Space Function | Corr. >= 2.4m wide | 0.93
NECB 2011Space FunctionCorr. < 2.4m wide | NECB 2011 | Space Function | Corr. < 2.4m wide | 0.93
NECB 2011Space FunctionDining - bar lounge/leisure | NECB 2011 | Space Function | Dining - bar lounge/leisure | 9.29
NECB 2011Space FunctionDining - family space | NECB 2011 | Space Function | Dining - family space | 9.29
NECB 2011Space FunctionDining - other | NECB 2011 | Space Function | Dining - other | 9.29
NECB 2011Space FunctionDress./fitt. - performance arts | NECB 2011 | Space Function | Dress./fitt. - performance arts | 3.1
NECB 2011Space FunctionElectrical/Mechanical | NECB 2011 | Space Function | Electrical/Mechanical | 0.46
NECB 2011Space FunctionFood preparation | NECB 2011 | Space Function | Food preparation | 4.65
NECB 2011Space FunctionLab - classrooms | NECB 2011 | Space Function | Lab - classrooms | 4.65
NECB 2011Space FunctionLab - research | NECB 2011 | Space Function | Lab - research | 4.65
NECB 2011Space FunctionLobby - elevator | NECB 2011 | Space Function | Lobby - elevator | 9.29
NECB 2011Space FunctionLobby - performance arts | NECB 2011 | Space Function | Lobby - performance arts | 9.29
NECB 2011Space FunctionLobby - motion picture | NECB 2011 | Space Function | Lobby - motion picture | 9.29
NECB 2011Space FunctionLobby - other | NECB 2011 | Space Function | Lobby - other | 9.29
NECB 2011Space FunctionLocker room | NECB 2011 | Space Function | Locker room | 9.29
NECB 2011Space FunctionLounge/recreation | NECB 2011 | Space Function | Lounge/recreation | 9.29
NECB 2011Space FunctionOffice - enclosed | NECB 2011 | Space Function | Office - enclosed | 4.65
NECB 2011Space FunctionOffice - open plan | NECB 2011 | Space Function | Office - open plan | 4.65
NECB 2011Space FunctionSales area | NECB 2011 | Space Function | Sales area | 3.1
NECB 2011Space FunctionStairway | NECB 2011 | Space Function | Stairway | 0.46
NECB 2011Space FunctionStorage area | NECB 2011 | Space Function | Storage area | 0.93
NECB 2011Space FunctionWashroom | NECB 2011 | Space Function | Washroom | 3.1
NECB 2011Space FunctionWorkshop space | NECB 2011 | Space Function | Workshop space | 3.1
NECB 2011Space FunctionAutomotive - repair | NECB 2011 | Space Function | Automotive - repair | 4.65
NECB 2011Space FunctionBank - banking and offices | NECB 2011 | Space Function | Bank - banking and offices | 3.72
NECB 2011Space FunctionConvention centre - audience | NECB 2011 | Space Function | Convention centre - audience | 18.58
NECB 2011Space FunctionConvention centre - exhibit | NECB 2011 | Space Function | Convention centre - exhibit | 18.58
NECB 2011Space FunctionCourthouse - courtroom | NECB 2011 | Space Function | Courthouse - courtroom | 18.58
NECB 2011Space FunctionCourthouse - cell | NECB 2011 | Space Function | Courthouse - cell | 3.72
NECB 2011Space FunctionCourthouse - chambers | NECB 2011 | Space Function | Courthouse - chambers | 4.65
NECB 2011Space FunctionPenitentiary - audience | NECB 2011 | Space Function | Penitentiary - audience | 18.58
NECB 2011Space FunctionPenitentiary - classroom | NECB 2011 | Space Function | Penitentiary - classroom | 12.39
NECB 2011Space FunctionPenitentiary - dining | NECB 2011 | Space Function | Penitentiary - dining | 9.29
NECB 2011Space FunctionDormitory - living quarters | NECB 2011 | Space Function | Dormitory - living quarters | 3.72
NECB 2011Space FunctionFire station - engine room | NECB 2011 | Space Function | Fire station - engine room | 3.72
NECB 2011Space FunctionFire station - quarters | NECB 2011 | Space Function | Fire station - quarters | 3.72
NECB 2011Space FunctionGym - fitness | NECB 2011 | Space Function | Gym - fitness | 18.58
NECB 2011Space FunctionGym - audience | NECB 2011 | Space Function | Gym - audience | 18.58
NECB 2011Space FunctionGym - play | NECB 2011 | Space Function | Gym - play | 18.58
NECB 2011Space FunctionHospital corr. >= 2.4m | NECB 2011 | Space Function | Hospital corr. >= 2.4m | 0.93
NECB 2011Space FunctionHospital corr. < 2.4m | NECB 2011 | Space Function | Hospital corr. < 2.4m | 0.93
NECB 2011Space FunctionHospital - emergency | NECB 2011 | Space Function | Hospital - emergency | 4.65
NECB 2011Space FunctionHospital - exam | NECB 2011 | Space Function | Hospital - exam | 4.65
NECB 2011Space FunctionHospital - laundry/washing | NECB 2011 | Space Function | Hospital - laundry/washing | 4.65
NECB 2011Space FunctionHospital - lounge/recreation | NECB 2011 | Space Function | Hospital - lounge/recreation | 9.29
NECB 2011Space FunctionHospital - medical supply | NECB 2011 | Space Function | Hospital - medical supply | 4.65
NECB 2011Space FunctionHospital - nursery | NECB 2011 | Space Function | Hospital - nursery | 4.65
NECB 2011Space FunctionHospital - nurses' station | NECB 2011 | Space Function | Hospital - nurses' station | 4.65
NECB 2011Space FunctionHospital - operating room | NECB 2011 | Space Function | Hospital - operating room | 4.65
NECB 2011Space FunctionHospital - patient room | NECB 2011 | Space Function | Hospital - patient room | 4.65
NECB 2011Space FunctionHospital - pharmacy | NECB 2011 | Space Function | Hospital - pharmacy | 4.65
NECB 2011Space FunctionHospital - physical therapy | NECB 2011 | Space Function | Hospital - physical therapy | 4.65
NECB 2011Space FunctionHospital - radiology/imaging | NECB 2011 | Space Function | Hospital - radiology/imaging | 4.65
NECB 2011Space FunctionHospital - recovery | NECB 2011 | Space Function | Hospital - recovery | 4.65
NECB 2011Space FunctionHotel/Motel - dining | NECB 2011 | Space Function | Hotel/Motel - dining | 9.29
NECB 2011Space FunctionHotel/Motel - rooms | NECB 2011 | Space Function | Hotel/Motel - rooms | 3.72
NECB 2011Space FunctionHotel/Motel - lobby | NECB 2011 | Space Function | Hotel/Motel - lobby | 9.29
NECB 2011Space FunctionHway lodging - dining | NECB 2011 | Space Function | Hway lodging - dining | 9.29
NECB 2011Space FunctionHway lodging - rooms | NECB 2011 | Space Function | Hway lodging - rooms | 3.72
NECB 2011Space FunctionLibrary - cataloging | NECB 2011 | Space Function | Library - cataloging | 4.65
NECB 2011Space FunctionLibrary - reading | NECB 2011 | Space Function | Library - reading | 4.65
NECB 2011Space FunctionLibrary - stacks | NECB 2011 | Space Function | Library - stacks | 4.65
NECB 2011Space FunctionMfg - corr. >= 2.4m | NECB 2011 | Space Function | Mfg - corr. >= 2.4m | 0.93
NECB 2011Space FunctionMfg - corr. < 2.4m | NECB 2011 | Space Function | Mfg - corr. < 2.4m | 0.93
NECB 2011Space FunctionMfg - detailed | NECB 2011 | Space Function | Mfg - detailed | 3.1
NECB 2011Space FunctionMfg - equipment | NECB 2011 | Space Function | Mfg - equipment | 3.1
NECB 2011Space FunctionMfg - bay H > 15m | NECB 2011 | Space Function | Mfg - bay H > 15m | 3.1
NECB 2011Space FunctionMfg - 7.5 <= bay H <= 15m | NECB 2011 | Space Function | Mfg - 7.5 <= bay H <= 15m | 3.1
NECB 2011Space FunctionMfg - bay H < 7.5m | NECB 2011 | Space Function | Mfg - bay H < 7.5m | 3.1
NECB 2011Space FunctionMuseum - exhibition | NECB 2011 | Space Function | Museum - exhibition | 18.58
NECB 2011Space FunctionMuseum - restoration | NECB 2011 | Space Function | Museum - restoration | 4.65
NECB 2011Space FunctionParking garage space | NECB 2011 | Space Function | Parking garage space | 0.09
NECB 2011Space FunctionPost office sorting | NECB 2011 | Space Function | Post office sorting | 4.65
NECB 2011Space FunctionReligious - audience | NECB 2011 | Space Function | Religious - audience | 18.58
NECB 2011Space FunctionReligious - fellowship hall | NECB 2011 | Space Function | Religious - fellowship hall | 18.58
NECB 2011Space FunctionReligious - pulpit/choir | NECB 2011 | Space Function | Religious - pulpit/choir | 18.58
NECB 2011Space FunctionRetail - dressing/fitting | NECB 2011 | Space Function | Retail - dressing/fitting | 3.1
NECB 2011Space FunctionRetail - mall concourse | NECB 2011 | Space Function | Retail - mall concourse | 4.65
NECB 2011Space FunctionRetail - sales | NECB 2011 | Space Function | Retail - sales | 3.1
NECB 2011Space FunctionSports arena - audience | NECB 2011 | Space Function | Sports arena - audience | 18.58
NECB 2011Space FunctionSports arena - court c4 | NECB 2011 | Space Function | Sports arena - court c4 | 18.58
NECB 2011Space FunctionSports arena - court c3 | NECB 2011 | Space Function | Sports arena - court c3 | 18.58
NECB 2011Space FunctionSports arena - court c2 | NECB 2011 | Space Function | Sports arena - court c2 | 18.58
NECB 2011Space FunctionSports arena - court c1 | NECB 2011 | Space Function | Sports arena - court c1 | 18.58
NECB 2011Space FunctionSports arena - ring | NECB 2011 | Space Function | Sports arena - ring | 18.58
NECB 2011Space FunctionTransp. baggage | NECB 2011 | Space Function | Transp. baggage | 4.65
NECB 2011Space FunctionTransp. seating | NECB 2011 | Space Function | Transp. seating | 9.29
NECB 2011Space FunctionTransp. concourse | NECB 2011 | Space Function | Transp. concourse | 4.65
NECB 2011Space FunctionTransp. counter | NECB 2011 | Space Function | Transp. counter | 9.29
NECB 2011Space FunctionWarehouse - fine | NECB 2011 | Space Function | Warehouse - fine | 1.86
NECB 2011Space FunctionWarehouse - med/blk | NECB 2011 | Space Function | Warehouse - med/blk | 0.93
NECB 2011Space FunctionWarehouse - med/blk2 | NECB 2011 | Space Function | Warehouse - med/blk2 | 0.93

## Interior Lighting
Each row represents interior lighting power limits for a particular space type in a particular standard. Values are referenced on Space Types tab.
VLookupColumn | Lighting Standard | Primary Space Type | Secondary Space Type | W/ft^2 | W/ft | Import Order
ASHRAE 90.1-1999Whole BuildingAutomotive Facility | ASHRAE 90.1-1999 | Whole Building | Automotive Facility | 1.5 |  | 1
ASHRAE 90.1-1999Whole BuildingConvention Center | ASHRAE 90.1-1999 | Whole Building | Convention Center | 1.4 |  | 2
ASHRAE 90.1-1999Whole BuildingCourt House | ASHRAE 90.1-1999 | Whole Building | Court House | 1.4 |  | 3
ASHRAE 90.1-1999Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-1999 | Whole Building | Dining: Bar Lounge/Leisure | 1.5 |  | 4
ASHRAE 90.1-1999Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-1999 | Whole Building | Dining: Cafeteria/Fast Food | 1.8 |  | 5
ASHRAE 90.1-1999Whole BuildingDining: Family | ASHRAE 90.1-1999 | Whole Building | Dining: Family | 1.9 |  | 6
ASHRAE 90.1-1999Whole BuildingDormitory | ASHRAE 90.1-1999 | Whole Building | Dormitory | 1.5 |  | 7
ASHRAE 90.1-1999Whole BuildingExercise Center | ASHRAE 90.1-1999 | Whole Building | Exercise Center | 1.4 |  | 8
ASHRAE 90.1-1999Whole BuildingGymnasium | ASHRAE 90.1-1999 | Whole Building | Gymnasium | 1.7 |  | 9
ASHRAE 90.1-1999Whole BuildingHealth Care-Clinic | ASHRAE 90.1-1999 | Whole Building | Health Care-Clinic | 1.6 |  | 10
ASHRAE 90.1-1999Whole BuildingHospital | ASHRAE 90.1-1999 | Whole Building | Hospital | 1.6 |  | 11
ASHRAE 90.1-1999Whole BuildingHotel | ASHRAE 90.1-1999 | Whole Building | Hotel | 1.7 |  | 12
ASHRAE 90.1-1999Whole BuildingLibrary | ASHRAE 90.1-1999 | Whole Building | Library | 1.5 |  | 13
ASHRAE 90.1-1999Whole BuildingManufacturing Facility | ASHRAE 90.1-1999 | Whole Building | Manufacturing Facility | 2.2 |  | 14
ASHRAE 90.1-1999Whole BuildingMotel | ASHRAE 90.1-1999 | Whole Building | Motel | 2 |  | 15
ASHRAE 90.1-1999Whole BuildingMotion Picture Theater | ASHRAE 90.1-1999 | Whole Building | Motion Picture Theater | 1.6 |  | 16
ASHRAE 90.1-1999Whole BuildingMulti-Family | ASHRAE 90.1-1999 | Whole Building | Multi-Family | 1 |  | 17
ASHRAE 90.1-1999Whole BuildingMuseum | ASHRAE 90.1-1999 | Whole Building | Museum | 1.6 |  | 18
ASHRAE 90.1-1999Whole BuildingOffice | ASHRAE 90.1-1999 | Whole Building | Office | 1.3 |  | 19
ASHRAE 90.1-1999Whole BuildingParking Garage | ASHRAE 90.1-1999 | Whole Building | Parking Garage | 0.3 |  | 20
ASHRAE 90.1-1999Whole BuildingPenitentiary | ASHRAE 90.1-1999 | Whole Building | Penitentiary | 1.2 |  | 21
ASHRAE 90.1-1999Whole BuildingPerforming Arts Theater | ASHRAE 90.1-1999 | Whole Building | Performing Arts Theater | 1.5 |  | 22
ASHRAE 90.1-1999Whole BuildingPolice/Fire Station | ASHRAE 90.1-1999 | Whole Building | Police/Fire Station | 1.3 |  | 23
ASHRAE 90.1-1999Whole BuildingPost Office | ASHRAE 90.1-1999 | Whole Building | Post Office | 1.6 |  | 24
ASHRAE 90.1-1999Whole BuildingReligious Building | ASHRAE 90.1-1999 | Whole Building | Religious Building | 2.2 |  | 25
ASHRAE 90.1-1999Whole BuildingRetail | ASHRAE 90.1-1999 | Whole Building | Retail | 1.9 |  | 26
ASHRAE 90.1-1999Whole BuildingSchool/University | ASHRAE 90.1-1999 | Whole Building | School/University | 1.5 |  | 27
ASHRAE 90.1-1999Whole BuildingSports Arena | ASHRAE 90.1-1999 | Whole Building | Sports Arena | 1.5 |  | 28
ASHRAE 90.1-1999Whole BuildingTown Hall | ASHRAE 90.1-1999 | Whole Building | Town Hall | 1.4 |  | 29
ASHRAE 90.1-1999Whole BuildingTransportation | ASHRAE 90.1-1999 | Whole Building | Transportation | 1.2 |  | 30
ASHRAE 90.1-1999Whole BuildingWarehouse | ASHRAE 90.1-1999 | Whole Building | Warehouse | 1.2 |  | 31
ASHRAE 90.1-1999Whole BuildingWorkshop | ASHRAE 90.1-1999 | Whole Building | Workshop | 1.7 |  | 32
ASHRAE 90.1-1999Office-EnclosedGeneral | ASHRAE 90.1-1999 | Office-Enclosed | General | 1.5 |  | 33
ASHRAE 90.1-1999Office-Open PlanGeneral | ASHRAE 90.1-1999 | Office-Open Plan | General | 1.3 |  | 34
ASHRAE 90.1-1999Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-1999 | Conference/Meeting/Multipurpose | General | 1.5 |  | 35
ASHRAE 90.1-1999Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-1999 | Classroom/Lecture/Training | General | 1.6 |  | 36
ASHRAE 90.1-1999Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-1999 | Classroom/Lecture/Training | For Penitentiary | 1.4 |  | 37
ASHRAE 90.1-1999LobbyGeneral | ASHRAE 90.1-1999 | Lobby | General | 1.8 |  | 38
ASHRAE 90.1-1999LobbyFor Hotel | ASHRAE 90.1-1999 | Lobby | For Hotel | 1.8 |  | 39
ASHRAE 90.1-1999LobbyFor Performing Arts Theater | ASHRAE 90.1-1999 | Lobby | For Performing Arts Theater | 1.2 |  | 40
ASHRAE 90.1-1999LobbyFor Motion Picture Theater | ASHRAE 90.1-1999 | Lobby | For Motion Picture Theater | 0.8 |  | 41
ASHRAE 90.1-1999Audience/Seating AreaGeneral | ASHRAE 90.1-1999 | Audience/Seating Area | General | 0.5 |  | 42
ASHRAE 90.1-1999Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-1999 | Audience/Seating Area | For Gymnasium | 0.5 |  | 43
ASHRAE 90.1-1999Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-1999 | Audience/Seating Area | For Exercise Center | 0.5 |  | 44
ASHRAE 90.1-1999Audience/Seating AreaFor Convention Center | ASHRAE 90.1-1999 | Audience/Seating Area | For Convention Center | 0.5 |  | 45
ASHRAE 90.1-1999Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-1999 | Audience/Seating Area | For Penitentiary | 1.9 |  | 46
ASHRAE 90.1-1999Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-1999 | Audience/Seating Area | For Religious Buildings | 3.2 |  | 47
ASHRAE 90.1-1999Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-1999 | Audience/Seating Area | For Sports Arena | 0.5 |  | 48
ASHRAE 90.1-1999Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-1999 | Audience/Seating Area | For Performing Arts Theater | 1.8 |  | 49
ASHRAE 90.1-1999Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-1999 | Audience/Seating Area | For Motion Picture Theater | 1.3 |  | 50
ASHRAE 90.1-1999Audience/Seating AreaFor Transportation | ASHRAE 90.1-1999 | Audience/Seating Area | For Transportation | 1 |  | 51
ASHRAE 90.1-1999AtriumFirst Three Floors | ASHRAE 90.1-1999 | Atrium | First Three Floors | 1.3 |  | 52
ASHRAE 90.1-1999AtriumEach Floor over First Three Floors | ASHRAE 90.1-1999 | Atrium | Each Floor over First Three Floors | 0.2 |  | 53
ASHRAE 90.1-1999Lounge/RecreationGeneral | ASHRAE 90.1-1999 | Lounge/Recreation | General | 1.4 |  | 54
ASHRAE 90.1-1999Lounge/RecreationFor Hospital | ASHRAE 90.1-1999 | Lounge/Recreation | For Hospital | 1.4 |  | 55
ASHRAE 90.1-1999Dining AreaGeneral | ASHRAE 90.1-1999 | Dining Area | General | 1.4 |  | 56
ASHRAE 90.1-1999Dining AreaFor Penitentiary | ASHRAE 90.1-1999 | Dining Area | For Penitentiary | 1.4 |  | 57
ASHRAE 90.1-1999Dining AreaFor Hotel | ASHRAE 90.1-1999 | Dining Area | For Hotel | 1 |  | 58
ASHRAE 90.1-1999Dining AreaFor Motel | ASHRAE 90.1-1999 | Dining Area | For Motel | 1.2 |  | 59
ASHRAE 90.1-1999Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-1999 | Dining Area | For Bar Lounge/Leisure Dining | 1.2 |  | 60
ASHRAE 90.1-1999Dining AreaFor Family Dining | ASHRAE 90.1-1999 | Dining Area | For Family Dining | 2.2 |  | 61
ASHRAE 90.1-1999Food PreparationGeneral | ASHRAE 90.1-1999 | Food Preparation | General | 2.2 |  | 62
ASHRAE 90.1-1999LaboratoryGeneral | ASHRAE 90.1-1999 | Laboratory | General | 1.8 |  | 63
ASHRAE 90.1-1999RestroomsGeneral | ASHRAE 90.1-1999 | Restrooms | General | 1 |  | 64
ASHRAE 90.1-1999Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-1999 | Dressing/Locker/Fitting Room | General | 0.8 |  | 65
ASHRAE 90.1-1999Corridor/TransitionGeneral | ASHRAE 90.1-1999 | Corridor/Transition | General | 0.7 |  | 66
ASHRAE 90.1-1999Corridor/TransitionFor Hospital | ASHRAE 90.1-1999 | Corridor/Transition | For Hospital | 1.6 |  | 67
ASHRAE 90.1-1999Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-1999 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 68
ASHRAE 90.1-1999Stairs—ActiveGeneral | ASHRAE 90.1-1999 | Stairs—Active | General | 0.9 |  | 69
ASHRAE 90.1-1999Active StorageGeneral | ASHRAE 90.1-1999 | Active Storage | General | 1.1 |  | 70
ASHRAE 90.1-1999Active StorageFor Hospital | ASHRAE 90.1-1999 | Active Storage | For Hospital | 2.9 |  | 71
ASHRAE 90.1-1999Inactive storageGeneral | ASHRAE 90.1-1999 | Inactive storage | General | 0.3 |  | 72
ASHRAE 90.1-1999Inactive storageFor Museum | ASHRAE 90.1-1999 | Inactive storage | For Museum | 1.4 |  | 73
ASHRAE 90.1-1999Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-1999 | Gymnasium/Exercise Center | Playing Area | 1.9 |  | 74
ASHRAE 90.1-1999Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-1999 | Gymnasium/Exercise Center | Exercise Area | 1.1 |  | 75
ASHRAE 90.1-1999Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-1999 | Courthouse/Police Station/Penitentiary | Courtroom | 2.1 |  | 76
ASHRAE 90.1-1999Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-1999 | Courthouse/Police Station/Penitentiary | Confinement Cells | 1.1 |  | 77
ASHRAE 90.1-1999Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-1999 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.1 |  | 78
ASHRAE 90.1-1999Fire StationsFire Station Engine Room | ASHRAE 90.1-1999 | Fire Stations | Fire Station Engine Room | 0.9 |  | 79
ASHRAE 90.1-1999Fire StationsSleeping Quarters | ASHRAE 90.1-1999 | Fire Stations | Sleeping Quarters | 1.1 |  | 80
ASHRAE 90.1-1999Post OfficeSorting Area | ASHRAE 90.1-1999 | Post Office | Sorting Area | 1.7 |  | 81
ASHRAE 90.1-1999Convention CenterExhibit Space | ASHRAE 90.1-1999 | Convention Center | Exhibit Space | 3.3 |  | 82
ASHRAE 90.1-1999LibraryCard File and Cataloging | ASHRAE 90.1-1999 | Library | Card File and Cataloging | 1.4 |  | 83
ASHRAE 90.1-1999LibraryStacks | ASHRAE 90.1-1999 | Library | Stacks | 1.9 |  | 84
ASHRAE 90.1-1999LibraryReading Area | ASHRAE 90.1-1999 | Library | Reading Area | 1.8 |  | 85
ASHRAE 90.1-1999HospitalEmergency | ASHRAE 90.1-1999 | Hospital | Emergency | 2.8 |  | 86
ASHRAE 90.1-1999HospitalRecovery | ASHRAE 90.1-1999 | Hospital | Recovery | 2.6 |  | 87
ASHRAE 90.1-1999HospitalNurse Station | ASHRAE 90.1-1999 | Hospital | Nurse Station | 1.8 |  | 88
ASHRAE 90.1-1999HospitalExam/Treatment | ASHRAE 90.1-1999 | Hospital | Exam/Treatment | 1.6 |  | 89
ASHRAE 90.1-1999HospitalPharmacy | ASHRAE 90.1-1999 | Hospital | Pharmacy | 2.3 |  | 90
ASHRAE 90.1-1999HospitalPatient Room | ASHRAE 90.1-1999 | Hospital | Patient Room | 1.2 |  | 91
ASHRAE 90.1-1999HospitalOperating Room | ASHRAE 90.1-1999 | Hospital | Operating Room | 7.6 |  | 92
ASHRAE 90.1-1999HospitalNursery | ASHRAE 90.1-1999 | Hospital | Nursery | 1 |  | 93
ASHRAE 90.1-1999HospitalMedical Supply | ASHRAE 90.1-1999 | Hospital | Medical Supply | 3 |  | 94
ASHRAE 90.1-1999HospitalPhysical Therapy | ASHRAE 90.1-1999 | Hospital | Physical Therapy | 1.9 |  | 95
ASHRAE 90.1-1999HospitalRadiology | ASHRAE 90.1-1999 | Hospital | Radiology | 0.4 |  | 96
ASHRAE 90.1-1999HospitalLaundry—Washing | ASHRAE 90.1-1999 | Hospital | Laundry—Washing | 0.7 |  | 97
ASHRAE 90.1-1999AutomotiveService/Repair | ASHRAE 90.1-1999 | Automotive | Service/Repair | 1.4 |  | 98
ASHRAE 90.1-1999ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-1999 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 2.1 |  | 99
ASHRAE 90.1-1999ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-1999 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 3 |  | 100
ASHRAE 90.1-1999ManufacturingDetailed Manufacturing | ASHRAE 90.1-1999 | Manufacturing | Detailed Manufacturing | 6.2 |  | 101
ASHRAE 90.1-1999ManufacturingEquipment Room | ASHRAE 90.1-1999 | Manufacturing | Equipment Room | 0.8 |  | 102
ASHRAE 90.1-1999ManufacturingControl Room | ASHRAE 90.1-1999 | Manufacturing | Control Room | 0.5 |  | 103
ASHRAE 90.1-1999Hotel/MotelGuest Rooms | ASHRAE 90.1-1999 | Hotel/Motel | Guest Rooms | 2.5 |  | 104
ASHRAE 90.1-1999DormitoryLiving Quarters | ASHRAE 90.1-1999 | Dormitory | Living Quarters | 1.9 |  | 105
ASHRAE 90.1-1999MuseumGeneral Exhibition | ASHRAE 90.1-1999 | Museum | General Exhibition | 1.6 |  | 106
ASHRAE 90.1-1999MuseumRestoration | ASHRAE 90.1-1999 | Museum | Restoration | 2.5 |  | 107
ASHRAE 90.1-1999Electrical/MechanicalGeneral | ASHRAE 90.1-1999 | Electrical/Mechanical | General | 1.3 |  | 108
ASHRAE 90.1-1999WorkshopGeneral | ASHRAE 90.1-1999 | Workshop | General | 2.5 |  | 109
ASHRAE 90.1-1999Bank/OfficeBanking Activity Area | ASHRAE 90.1-1999 | Bank/Office | Banking Activity Area | 2.4 |  | 110
ASHRAE 90.1-1999Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-1999 | Religious Buildings | Worship Pulpit, Choir | 5.2 |  | 111
ASHRAE 90.1-1999Religious BuildingsFellowship Hall | ASHRAE 90.1-1999 | Religious Buildings | Fellowship Hall | 2.3 |  | 112
ASHRAE 90.1-1999Retail (not including accent lighting)Sales Area | ASHRAE 90.1-1999 | Retail (not including accent lighting) | Sales Area | 2.1 |  | 113
ASHRAE 90.1-1999Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-1999 | Retail (not including accent lighting) | Mall Concourse | 1.8 |  | 114
ASHRAE 90.1-1999Sports ArenaRing Sports Area | ASHRAE 90.1-1999 | Sports Arena | Ring Sports Area | 3.8 |  | 115
ASHRAE 90.1-1999Sports ArenaCourt Sports Area | ASHRAE 90.1-1999 | Sports Arena | Court Sports Area | 4.3 |  | 116
ASHRAE 90.1-1999Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-1999 | Sports Arena | Indoor Playing Field Area | 1.9 |  | 117
ASHRAE 90.1-1999WarehouseFine Material Storage | ASHRAE 90.1-1999 | Warehouse | Fine Material Storage | 1.6 |  | 118
ASHRAE 90.1-1999WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-1999 | Warehouse | Medium/Bulky Material Storage | 1.1 |  | 119
ASHRAE 90.1-1999Parking GarageGarage Area | ASHRAE 90.1-1999 | Parking Garage | Garage Area | 0.2 |  | 120
ASHRAE 90.1-1999TransportationAirport—Concourse | ASHRAE 90.1-1999 | Transportation | Airport—Concourse | 0.7 |  | 121
ASHRAE 90.1-1999TransportationAir/Train/Bus—Baggage Area | ASHRAE 90.1-1999 | Transportation | Air/Train/Bus—Baggage Area | 1.3 |  | 122
ASHRAE 90.1-1999TransportationTerminal—Ticket Counter | ASHRAE 90.1-1999 | Transportation | Terminal—Ticket Counter | 1.8 |  | 123
ASHRAE 90.1-1999Exterior SpacesGeneral | ASHRAE 90.1-1999 | Exterior Spaces | General | 0 |  | 124
ASHRAE 90.1-1999AtticsGeneral | ASHRAE 90.1-1999 | Attics | General | 0 |  | 125
ASHRAE 90.1-2001Whole BuildingAutomotive Facility | ASHRAE 90.1-2001 | Whole Building | Automotive Facility | 0.9 |  | 126
ASHRAE 90.1-2001Whole BuildingConvention Center | ASHRAE 90.1-2001 | Whole Building | Convention Center | 1.2 |  | 127
ASHRAE 90.1-2001Whole BuildingCourt House | ASHRAE 90.1-2001 | Whole Building | Court House | 1.2 |  | 128
ASHRAE 90.1-2001Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2001 | Whole Building | Dining: Bar Lounge/Leisure | 1.3 |  | 129
ASHRAE 90.1-2001Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2001 | Whole Building | Dining: Cafeteria/Fast Food | 1.4 |  | 130
ASHRAE 90.1-2001Whole BuildingDining: Family | ASHRAE 90.1-2001 | Whole Building | Dining: Family | 1.6 |  | 131
ASHRAE 90.1-2001Whole BuildingDormitory | ASHRAE 90.1-2001 | Whole Building | Dormitory | 1 |  | 132
ASHRAE 90.1-2001Whole BuildingExercise Center | ASHRAE 90.1-2001 | Whole Building | Exercise Center | 1 |  | 133
ASHRAE 90.1-2001Whole BuildingGymnasium | ASHRAE 90.1-2001 | Whole Building | Gymnasium | 1.1 |  | 134
ASHRAE 90.1-2001Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2001 | Whole Building | Health Care-Clinic | 1 |  | 135
ASHRAE 90.1-2001Whole BuildingHospital | ASHRAE 90.1-2001 | Whole Building | Hospital | 1.2 |  | 136
ASHRAE 90.1-2001Whole BuildingHotel | ASHRAE 90.1-2001 | Whole Building | Hotel | 1 |  | 137
ASHRAE 90.1-2001Whole BuildingLibrary | ASHRAE 90.1-2001 | Whole Building | Library | 1.3 |  | 138
ASHRAE 90.1-2001Whole BuildingManufacturing Facility | ASHRAE 90.1-2001 | Whole Building | Manufacturing Facility | 1.3 |  | 139
ASHRAE 90.1-2001Whole BuildingMotel | ASHRAE 90.1-2001 | Whole Building | Motel | 1 |  | 140
ASHRAE 90.1-2001Whole BuildingMotion Picture Theater | ASHRAE 90.1-2001 | Whole Building | Motion Picture Theater | 1.2 |  | 141
ASHRAE 90.1-2001Whole BuildingMulti-Family | ASHRAE 90.1-2001 | Whole Building | Multi-Family | 0.7 |  | 142
ASHRAE 90.1-2001Whole BuildingMuseum | ASHRAE 90.1-2001 | Whole Building | Museum | 1.1 |  | 143
ASHRAE 90.1-2001Whole BuildingOffice | ASHRAE 90.1-2001 | Whole Building | Office | 1 |  | 144
ASHRAE 90.1-2001Whole BuildingParking Garage | ASHRAE 90.1-2001 | Whole Building | Parking Garage | 0.3 |  | 145
ASHRAE 90.1-2001Whole BuildingPenitentiary | ASHRAE 90.1-2001 | Whole Building | Penitentiary | 1 |  | 146
ASHRAE 90.1-2001Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2001 | Whole Building | Performing Arts Theater | 1.6 |  | 147
ASHRAE 90.1-2001Whole BuildingPolice/Fire Station | ASHRAE 90.1-2001 | Whole Building | Police/Fire Station | 1 |  | 148
ASHRAE 90.1-2001Whole BuildingPost Office | ASHRAE 90.1-2001 | Whole Building | Post Office | 1.1 |  | 149
ASHRAE 90.1-2001Whole BuildingReligious Building | ASHRAE 90.1-2001 | Whole Building | Religious Building | 1.3 |  | 150
ASHRAE 90.1-2001Whole BuildingRetail | ASHRAE 90.1-2001 | Whole Building | Retail | 1.5 |  | 151
ASHRAE 90.1-2001Whole BuildingSchool/University | ASHRAE 90.1-2001 | Whole Building | School/University | 1.2 |  | 152
ASHRAE 90.1-2001Whole BuildingSports Arena | ASHRAE 90.1-2001 | Whole Building | Sports Arena | 1.1 |  | 153
ASHRAE 90.1-2001Whole BuildingTown Hall | ASHRAE 90.1-2001 | Whole Building | Town Hall | 1.1 |  | 154
ASHRAE 90.1-2001Whole BuildingTransportation | ASHRAE 90.1-2001 | Whole Building | Transportation | 1 |  | 155
ASHRAE 90.1-2001Whole BuildingWarehouse | ASHRAE 90.1-2001 | Whole Building | Warehouse | 0.8 |  | 156
ASHRAE 90.1-2001Whole BuildingWorkshop | ASHRAE 90.1-2001 | Whole Building | Workshop | 1.4 |  | 157
ASHRAE 90.1-2001Office-EnclosedGeneral | ASHRAE 90.1-2001 | Office-Enclosed | General | 1.1 |  | 158
ASHRAE 90.1-2001Office-Open PlanGeneral | ASHRAE 90.1-2001 | Office-Open Plan | General | 1.1 |  | 159
ASHRAE 90.1-2001Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2001 | Conference/Meeting/Multipurpose | General | 1.3 |  | 160
ASHRAE 90.1-2001Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2001 | Classroom/Lecture/Training | General | 1.4 |  | 161
ASHRAE 90.1-2001Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2001 | Classroom/Lecture/Training | For Penitentiary | 1.3 |  | 162
ASHRAE 90.1-2001LobbyGeneral | ASHRAE 90.1-2001 | Lobby | General | 1.3 |  | 163
ASHRAE 90.1-2001LobbyFor Hotel | ASHRAE 90.1-2001 | Lobby | For Hotel | 1.1 |  | 164
ASHRAE 90.1-2001LobbyFor Performing Arts Theater | ASHRAE 90.1-2001 | Lobby | For Performing Arts Theater | 3.3 |  | 165
ASHRAE 90.1-2001LobbyFor Motion Picture Theater | ASHRAE 90.1-2001 | Lobby | For Motion Picture Theater | 1.1 |  | 166
ASHRAE 90.1-2001Audience/Seating AreaGeneral | ASHRAE 90.1-2001 | Audience/Seating Area | General | 0.9 |  | 167
ASHRAE 90.1-2001Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2001 | Audience/Seating Area | For Gymnasium | 0.4 |  | 168
ASHRAE 90.1-2001Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-2001 | Audience/Seating Area | For Exercise Center | 0.3 |  | 169
ASHRAE 90.1-2001Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2001 | Audience/Seating Area | For Convention Center | 0.7 |  | 170
ASHRAE 90.1-2001Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2001 | Audience/Seating Area | For Penitentiary | 0.7 |  | 171
ASHRAE 90.1-2001Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2001 | Audience/Seating Area | For Religious Buildings | 1.7 |  | 172
ASHRAE 90.1-2001Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-2001 | Audience/Seating Area | For Sports Arena | 0.4 |  | 173
ASHRAE 90.1-2001Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-2001 | Audience/Seating Area | For Performing Arts Theater | 2.6 |  | 174
ASHRAE 90.1-2001Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2001 | Audience/Seating Area | For Motion Picture Theater | 1.2 |  | 175
ASHRAE 90.1-2001Audience/Seating AreaFor Transportation | ASHRAE 90.1-2001 | Audience/Seating Area | For Transportation | 0.5 |  | 176
ASHRAE 90.1-2001AtriumFirst Three Floors | ASHRAE 90.1-2001 | Atrium | First Three Floors | 0.6 |  | 177
ASHRAE 90.1-2001AtriumEach Floor over First Three Floors | ASHRAE 90.1-2001 | Atrium | Each Floor over First Three Floors | 0.2 |  | 178
ASHRAE 90.1-2001Lounge/RecreationGeneral | ASHRAE 90.1-2001 | Lounge/Recreation | General | 1.2 |  | 179
ASHRAE 90.1-2001Lounge/RecreationFor Hospital | ASHRAE 90.1-2001 | Lounge/Recreation | For Hospital | 0.8 |  | 180
ASHRAE 90.1-2001Dining AreaGeneral | ASHRAE 90.1-2001 | Dining Area | General | 0.9 |  | 181
ASHRAE 90.1-2001Dining AreaFor Penitentiary | ASHRAE 90.1-2001 | Dining Area | For Penitentiary | 1.3 |  | 182
ASHRAE 90.1-2001Dining AreaFor Hotel | ASHRAE 90.1-2001 | Dining Area | For Hotel | 1.3 |  | 183
ASHRAE 90.1-2001Dining AreaFor Motel | ASHRAE 90.1-2001 | Dining Area | For Motel | 1.2 |  | 184
ASHRAE 90.1-2001Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2001 | Dining Area | For Bar Lounge/Leisure Dining | 1.4 |  | 185
ASHRAE 90.1-2001Dining AreaFor Family Dining | ASHRAE 90.1-2001 | Dining Area | For Family Dining | 2.1 |  | 186
ASHRAE 90.1-2001Food PreparationGeneral | ASHRAE 90.1-2001 | Food Preparation | General | 1.2 |  | 187
ASHRAE 90.1-2001LaboratoryGeneral | ASHRAE 90.1-2001 | Laboratory | General | 1.4 |  | 188
ASHRAE 90.1-2001RestroomsGeneral | ASHRAE 90.1-2001 | Restrooms | General | 0.9 |  | 189
ASHRAE 90.1-2001Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-2001 | Dressing/Locker/Fitting Room | General | 0.6 |  | 190
ASHRAE 90.1-2001Corridor/TransitionGeneral | ASHRAE 90.1-2001 | Corridor/Transition | General | 0.5 |  | 191
ASHRAE 90.1-2001Corridor/TransitionFor Hospital | ASHRAE 90.1-2001 | Corridor/Transition | For Hospital | 1 |  | 192
ASHRAE 90.1-2001Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-2001 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 193
ASHRAE 90.1-2001Stairs—ActiveGeneral | ASHRAE 90.1-2001 | Stairs—Active | General | 0.6 |  | 194
ASHRAE 90.1-2001Active StorageGeneral | ASHRAE 90.1-2001 | Active Storage | General | 0.8 |  | 195
ASHRAE 90.1-2001Active StorageFor Hospital | ASHRAE 90.1-2001 | Active Storage | For Hospital | 0.9 |  | 196
ASHRAE 90.1-2001Inactive storageGeneral | ASHRAE 90.1-2001 | Inactive storage | General | 0.3 |  | 197
ASHRAE 90.1-2001Inactive storageFor Museum | ASHRAE 90.1-2001 | Inactive storage | For Museum | 0.8 |  | 198
ASHRAE 90.1-2001Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-2001 | Gymnasium/Exercise Center | Playing Area | 1.4 |  | 199
ASHRAE 90.1-2001Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-2001 | Gymnasium/Exercise Center | Exercise Area | 0.9 |  | 200
ASHRAE 90.1-2001Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-2001 | Courthouse/Police Station/Penitentiary | Courtroom | 1.9 |  | 201
ASHRAE 90.1-2001Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-2001 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.9 |  | 202
ASHRAE 90.1-2001Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-2001 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.3 |  | 203
ASHRAE 90.1-2001Fire StationsFire Station Engine Room | ASHRAE 90.1-2001 | Fire Stations | Fire Station Engine Room | 0.8 |  | 204
ASHRAE 90.1-2001Fire StationsSleeping Quarters | ASHRAE 90.1-2001 | Fire Stations | Sleeping Quarters | 0.3 |  | 205
ASHRAE 90.1-2001Post OfficeSorting Area | ASHRAE 90.1-2001 | Post Office | Sorting Area | 1.2 |  | 206
ASHRAE 90.1-2001Convention CenterExhibit Space | ASHRAE 90.1-2001 | Convention Center | Exhibit Space | 1.3 |  | 207
ASHRAE 90.1-2001LibraryCard File and Cataloging | ASHRAE 90.1-2001 | Library | Card File and Cataloging | 1.1 |  | 208
ASHRAE 90.1-2001LibraryStacks | ASHRAE 90.1-2001 | Library | Stacks | 1.7 |  | 209
ASHRAE 90.1-2001LibraryReading Area | ASHRAE 90.1-2001 | Library | Reading Area | 1.2 |  | 210
ASHRAE 90.1-2001HospitalEmergency | ASHRAE 90.1-2001 | Hospital | Emergency | 2.7 |  | 211
ASHRAE 90.1-2001HospitalRecovery | ASHRAE 90.1-2001 | Hospital | Recovery | 0.8 |  | 212
ASHRAE 90.1-2001HospitalNurse Station | ASHRAE 90.1-2001 | Hospital | Nurse Station | 1 |  | 213
ASHRAE 90.1-2001HospitalExam/Treatment | ASHRAE 90.1-2001 | Hospital | Exam/Treatment | 1.5 |  | 214
ASHRAE 90.1-2001HospitalPharmacy | ASHRAE 90.1-2001 | Hospital | Pharmacy | 1.2 |  | 215
ASHRAE 90.1-2001HospitalPatient Room | ASHRAE 90.1-2001 | Hospital | Patient Room | 0.7 |  | 216
ASHRAE 90.1-2001HospitalOperating Room | ASHRAE 90.1-2001 | Hospital | Operating Room | 2.2 |  | 217
ASHRAE 90.1-2001HospitalNursery | ASHRAE 90.1-2001 | Hospital | Nursery | 0.6 |  | 218
ASHRAE 90.1-2001HospitalMedical Supply | ASHRAE 90.1-2001 | Hospital | Medical Supply | 1.4 |  | 219
ASHRAE 90.1-2001HospitalPhysical Therapy | ASHRAE 90.1-2001 | Hospital | Physical Therapy | 0.9 |  | 220
ASHRAE 90.1-2001HospitalRadiology | ASHRAE 90.1-2001 | Hospital | Radiology | 0.4 |  | 221
ASHRAE 90.1-2001HospitalLaundry—Washing | ASHRAE 90.1-2001 | Hospital | Laundry—Washing | 0.6 |  | 222
ASHRAE 90.1-2001AutomotiveService/Repair | ASHRAE 90.1-2001 | Automotive | Service/Repair | 0.7 |  | 223
ASHRAE 90.1-2001ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2001 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.2 |  | 224
ASHRAE 90.1-2001ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-2001 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.7 |  | 225
ASHRAE 90.1-2001ManufacturingDetailed Manufacturing | ASHRAE 90.1-2001 | Manufacturing | Detailed Manufacturing | 2.1 |  | 226
ASHRAE 90.1-2001ManufacturingEquipment Room | ASHRAE 90.1-2001 | Manufacturing | Equipment Room | 1.2 |  | 227
ASHRAE 90.1-2001ManufacturingControl Room | ASHRAE 90.1-2001 | Manufacturing | Control Room | 0.5 |  | 228
ASHRAE 90.1-2001Hotel/MotelGuest Rooms | ASHRAE 90.1-2001 | Hotel/Motel | Guest Rooms | 1.1 |  | 229
ASHRAE 90.1-2001DormitoryLiving Quarters | ASHRAE 90.1-2001 | Dormitory | Living Quarters | 1.1 |  | 230
ASHRAE 90.1-2001MuseumGeneral Exhibition | ASHRAE 90.1-2001 | Museum | General Exhibition | 1 |  | 231
ASHRAE 90.1-2001MuseumRestoration | ASHRAE 90.1-2001 | Museum | Restoration | 1.7 |  | 232
ASHRAE 90.1-2001Electrical/MechanicalGeneral | ASHRAE 90.1-2001 | Electrical/Mechanical | General | 1.5 |  | 233
ASHRAE 90.1-2001WorkshopGeneral | ASHRAE 90.1-2001 | Workshop | General | 1.9 |  | 234
ASHRAE 90.1-2001Bank/OfficeBanking Activity Area | ASHRAE 90.1-2001 | Bank/Office | Banking Activity Area | 1.5 |  | 235
ASHRAE 90.1-2001Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2001 | Religious Buildings | Worship Pulpit, Choir | 2.4 |  | 236
ASHRAE 90.1-2001Religious BuildingsFellowship Hall | ASHRAE 90.1-2001 | Religious Buildings | Fellowship Hall | 0.9 |  | 237
ASHRAE 90.1-2001Retail (not including accent lighting)Sales Area | ASHRAE 90.1-2001 | Retail (not including accent lighting) | Sales Area | 2.1 |  | 238
ASHRAE 90.1-2001Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-2001 | Retail (not including accent lighting) | Mall Concourse | 1.7 |  | 239
ASHRAE 90.1-2001Sports ArenaRing Sports Area | ASHRAE 90.1-2001 | Sports Arena | Ring Sports Area | 2.7 |  | 240
ASHRAE 90.1-2001Sports ArenaCourt Sports Area | ASHRAE 90.1-2001 | Sports Arena | Court Sports Area | 2.3 |  | 241
ASHRAE 90.1-2001Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-2001 | Sports Arena | Indoor Playing Field Area | 1.4 |  | 242
ASHRAE 90.1-2001WarehouseFine Material Storage | ASHRAE 90.1-2001 | Warehouse | Fine Material Storage | 1.4 |  | 243
ASHRAE 90.1-2001WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2001 | Warehouse | Medium/Bulky Material Storage | 0.9 |  | 244
ASHRAE 90.1-2001Parking GarageGarage Area | ASHRAE 90.1-2001 | Parking Garage | Garage Area | 0.2 |  | 245
ASHRAE 90.1-2001TransportationAirport—Concourse | ASHRAE 90.1-2001 | Transportation | Airport—Concourse | 0.6 |  | 246
ASHRAE 90.1-2001TransportationAir/Train/Bus—Baggage Area | ASHRAE 90.1-2001 | Transportation | Air/Train/Bus—Baggage Area | 1 |  | 247
ASHRAE 90.1-2001TransportationTerminal—Ticket Counter | ASHRAE 90.1-2001 | Transportation | Terminal—Ticket Counter | 1.5 |  | 248
ASHRAE 90.1-2001Exterior SpacesGeneral | ASHRAE 90.1-2001 | Exterior Spaces | General | 0 |  | 249
ASHRAE 90.1-2001AtticsGeneral | ASHRAE 90.1-2001 | Attics | General | 0 |  | 250
ASHRAE 90.1-2004AtticsGeneral | ASHRAE 90.1-2004 | Attics | General | 0 |  | 375
ASHRAE 90.1-2004Exterior SpacesGeneral | ASHRAE 90.1-2004 | Exterior Spaces | General | 0 |  | 374
ASHRAE 90.1-2004AtriumEach Floor over First Three Floors | ASHRAE 90.1-2004 | Atrium | Each Floor over First Three Floors | 0.2 |  | 303
ASHRAE 90.1-2004Parking GarageGarage Area | ASHRAE 90.1-2004 | Parking Garage | Garage Area | 0.2 |  | 370
ASHRAE 90.1-2004Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-2004 | Audience/Seating Area | For Exercise Center | 0.3 |  | 294
ASHRAE 90.1-2004Fire StationsSleeping Quarters | ASHRAE 90.1-2004 | Fire Stations | Sleeping Quarters | 0.3 |  | 330
ASHRAE 90.1-2004Inactive storageGeneral | ASHRAE 90.1-2004 | Inactive storage | General | 0.3 |  | 322
ASHRAE 90.1-2004Whole BuildingParking Garage | ASHRAE 90.1-2004 | Whole Building | Parking Garage | 0.3 |  | 270
ASHRAE 90.1-2004Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2004 | Audience/Seating Area | For Gymnasium | 0.4 |  | 293
ASHRAE 90.1-2004Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-2004 | Audience/Seating Area | For Sports Arena | 0.4 |  | 298
ASHRAE 90.1-2004HospitalRadiology | ASHRAE 90.1-2004 | Hospital | Radiology | 0.4 |  | 346
ASHRAE 90.1-2004Audience/Seating AreaFor Transportation | ASHRAE 90.1-2004 | Audience/Seating Area | For Transportation | 0.5 |  | 301
ASHRAE 90.1-2004Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-2004 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 318
ASHRAE 90.1-2004Corridor/TransitionGeneral | ASHRAE 90.1-2004 | Corridor/Transition | General | 0.5 |  | 316
ASHRAE 90.1-2004ManufacturingGeneral | ASHRAE 90.1-2004 | Manufacturing | General | 0.5 |  | 353
ASHRAE 90.1-2004AtriumFirst Three Floors | ASHRAE 90.1-2004 | Atrium | First Three Floors | 0.6 |  | 302
ASHRAE 90.1-2004Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-2004 | Dressing/Locker/Fitting Room | General | 0.6 |  | 315
ASHRAE 90.1-2004HospitalLaundry-Washing | ASHRAE 90.1-2004 | Hospital | Laundry-Washing | 0.6 |  | 347
ASHRAE 90.1-2004HospitalNursery | ASHRAE 90.1-2004 | Hospital | Nursery | 0.6 |  | 343
ASHRAE 90.1-2004Stairs-ActiveGeneral | ASHRAE 90.1-2004 | Stairs-Active | General | 0.6 |  | 319
ASHRAE 90.1-2004TransportationAirport—Concourse | ASHRAE 90.1-2004 | Transportation | Airport—Concourse | 0.6 |  | 371
ASHRAE 90.1-2004Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2004 | Audience/Seating Area | For Convention Center | 0.7 |  | 295
ASHRAE 90.1-2004Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2004 | Audience/Seating Area | For Penitentiary | 0.7 |  | 296
ASHRAE 90.1-2004AutomotiveService/Repair | ASHRAE 90.1-2004 | Automotive | Service/Repair | 0.7 |  | 348
ASHRAE 90.1-2004HospitalPatient Room | ASHRAE 90.1-2004 | Hospital | Patient Room | 0.7 |  | 341
ASHRAE 90.1-2004Whole BuildingMulti-Family | ASHRAE 90.1-2004 | Whole Building | Multi-Family | 0.7 |  | 267
ASHRAE 90.1-2004Active StorageGeneral | ASHRAE 90.1-2004 | Active Storage | General | 0.8 |  | 320
ASHRAE 90.1-2004Fire StationsFire Station Engine Room | ASHRAE 90.1-2004 | Fire Stations | Fire Station Engine Room | 0.8 |  | 329
ASHRAE 90.1-2004HospitalRecovery | ASHRAE 90.1-2004 | Hospital | Recovery | 0.8 |  | 337
ASHRAE 90.1-2004Inactive storageFor Museum | ASHRAE 90.1-2004 | Inactive storage | For Museum | 0.8 |  | 323
ASHRAE 90.1-2004Lounge/RecreationFor Hospital | ASHRAE 90.1-2004 | Lounge/Recreation | For Hospital | 0.8 |  | 305
ASHRAE 90.1-2004Whole BuildingWarehouse | ASHRAE 90.1-2004 | Whole Building | Warehouse | 0.8 |  | 281
ASHRAE 90.1-2004Active StorageFor Hospital | ASHRAE 90.1-2004 | Active Storage | For Hospital | 0.9 |  | 321
ASHRAE 90.1-2004Audience/Seating AreaGeneral | ASHRAE 90.1-2004 | Audience/Seating Area | General | 0.9 |  | 292
ASHRAE 90.1-2004Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-2004 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.9 |  | 327
ASHRAE 90.1-2004BasementFor Hotel | ASHRAE 90.1-2004 | Basement | For Hotel | 0.9
ASHRAE 90.1-2004Dining AreaGeneral | ASHRAE 90.1-2004 | Dining Area | General | 0.9 |  | 306
ASHRAE 90.1-2004Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Exercise Area | 0.9 |  | 325
ASHRAE 90.1-2004HospitalPhysical Therapy | ASHRAE 90.1-2004 | Hospital | Physical Therapy | 0.9 |  | 345
ASHRAE 90.1-2004Religious BuildingsFellowship Hall | ASHRAE 90.1-2004 | Religious Buildings | Fellowship Hall | 0.9 |  | 362
ASHRAE 90.1-2004RestroomsGeneral | ASHRAE 90.1-2004 | Restrooms | General | 0.9 |  | 314
ASHRAE 90.1-2004WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2004 | Warehouse | Medium/Bulky Material Storage | 0.9 |  | 369
ASHRAE 90.1-2004Whole BuildingAutomotive Facility | ASHRAE 90.1-2004 | Whole Building | Automotive Facility | 0.9 |  | 251
ASHRAE 90.1-2004Corridor/TransitionFor Hospital | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | 1 |  | 317
ASHRAE 90.1-2004HospitalNurse Station | ASHRAE 90.1-2004 | Hospital | Nurse Station | 1 |  | 338
ASHRAE 90.1-2004MuseumGeneral Exhibition | ASHRAE 90.1-2004 | Museum | General Exhibition | 1 |  | 356
ASHRAE 90.1-2004TransportationAir/Train/Bus—Baggage Area | ASHRAE 90.1-2004 | Transportation | Air/Train/Bus—Baggage Area | 1 |  | 372
ASHRAE 90.1-2004Whole BuildingDormitory | ASHRAE 90.1-2004 | Whole Building | Dormitory | 1 |  | 257
ASHRAE 90.1-2004Whole BuildingExercise Center | ASHRAE 90.1-2004 | Whole Building | Exercise Center | 1 |  | 258
ASHRAE 90.1-2004Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2004 | Whole Building | Health Care-Clinic | 1 |  | 260
ASHRAE 90.1-2004Whole BuildingHotel | ASHRAE 90.1-2004 | Whole Building | Hotel | 1 |  | 262
ASHRAE 90.1-2004Whole BuildingMotel | ASHRAE 90.1-2004 | Whole Building | Motel | 1 |  | 265
ASHRAE 90.1-2004Whole BuildingOffice | ASHRAE 90.1-2004 | Whole Building | Office | 1 |  | 269
ASHRAE 90.1-2004Whole BuildingPenitentiary | ASHRAE 90.1-2004 | Whole Building | Penitentiary | 1 |  | 271
ASHRAE 90.1-2004Whole BuildingPolice/Fire Station | ASHRAE 90.1-2004 | Whole Building | Police/Fire Station | 1 |  | 273
ASHRAE 90.1-2004Whole BuildingTransportation | ASHRAE 90.1-2004 | Whole Building | Transportation | 1 |  | 280
ASHRAE 90.1-2004DormitoryLiving Quarters | ASHRAE 90.1-2004 | Dormitory | Living Quarters | 1.1 |  | 355
ASHRAE 90.1-2004Hotel/MotelGuest Rooms | ASHRAE 90.1-2004 | Hotel/Motel | Guest Rooms | 1.1 |  | 354
ASHRAE 90.1-2004LibraryCard File and Cataloging | ASHRAE 90.1-2004 | Library | Card File and Cataloging | 1.1 |  | 333
ASHRAE 90.1-2004LobbyFor Motion Picture Theater | ASHRAE 90.1-2004 | Lobby | For Motion Picture Theater | 1.1 |  | 291
ASHRAE 90.1-2004Office-EnclosedGeneral | ASHRAE 90.1-2004 | Office-Enclosed | General | 1.1 |  | 283
ASHRAE 90.1-2004Office-Open PlanGeneral | ASHRAE 90.1-2004 | Office-Open Plan | General | 1.1 |  | 284
ASHRAE 90.1-2004Whole BuildingGymnasium | ASHRAE 90.1-2004 | Whole Building | Gymnasium | 1.1 |  | 259
ASHRAE 90.1-2004Whole BuildingMuseum | ASHRAE 90.1-2004 | Whole Building | Museum | 1.1 |  | 268
ASHRAE 90.1-2004Whole BuildingPost Office | ASHRAE 90.1-2004 | Whole Building | Post Office | 1.1 |  | 274
ASHRAE 90.1-2004Whole BuildingSports Arena | ASHRAE 90.1-2004 | Whole Building | Sports Arena | 1.1 |  | 278
ASHRAE 90.1-2004Whole BuildingTown Hall | ASHRAE 90.1-2004 | Whole Building | Town Hall | 1.1 |  | 279
ASHRAE 90.1-2004LobbyFor Hotel | ASHRAE 90.1-2004 | Lobby | For Hotel | 1.1 |  | 289
ASHRAE 90.1-2004Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2004 | Audience/Seating Area | For Motion Picture Theater | 1.2 |  | 300
ASHRAE 90.1-2004Dining AreaFor Motel | ASHRAE 90.1-2004 | Dining Area | For Motel | 1.2 |  | 309
ASHRAE 90.1-2004Food PreparationGeneral | ASHRAE 90.1-2004 | Food Preparation | General | 1.2 |  | 312
ASHRAE 90.1-2004HospitalPharmacy | ASHRAE 90.1-2004 | Hospital | Pharmacy | 1.2 |  | 340
ASHRAE 90.1-2004LibraryReading Area | ASHRAE 90.1-2004 | Library | Reading Area | 1.2 |  | 335
ASHRAE 90.1-2004Lounge/RecreationGeneral | ASHRAE 90.1-2004 | Lounge/Recreation | General | 1.2 |  | 304
ASHRAE 90.1-2004ManufacturingGeneral | ASHRAE 90.1-2004 | Manufacturing | General | 1.2 |  | 352
ASHRAE 90.1-2004ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2004 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.2 |  | 349
ASHRAE 90.1-2004Post OfficeSorting Area | ASHRAE 90.1-2004 | Post Office | Sorting Area | 1.2 |  | 331
ASHRAE 90.1-2004Whole BuildingConvention Center | ASHRAE 90.1-2004 | Whole Building | Convention Center | 1.2 |  | 252
ASHRAE 90.1-2004Whole BuildingCourt House | ASHRAE 90.1-2004 | Whole Building | Court House | 1.2 |  | 253
ASHRAE 90.1-2004Whole BuildingHospital | ASHRAE 90.1-2004 | Whole Building | Hospital | 1.2 |  | 261
ASHRAE 90.1-2004Whole BuildingMotion Picture Theater | ASHRAE 90.1-2004 | Whole Building | Motion Picture Theater | 1.2 |  | 266
ASHRAE 90.1-2004Whole BuildingSchool/University | ASHRAE 90.1-2004 | Whole Building | School/University | 1.2 |  | 277
ASHRAE 90.1-2004Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2004 | Classroom/Lecture/Training | For Penitentiary | 1.3 |  | 287
ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | 1.3 |  | 285
ASHRAE 90.1-2004Convention CenterExhibit Space | ASHRAE 90.1-2004 | Convention Center | Exhibit Space | 1.3 |  | 332
ASHRAE 90.1-2004Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-2004 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.3 |  | 328
ASHRAE 90.1-2004Dining AreaFor Penitentiary | ASHRAE 90.1-2004 | Dining Area | For Penitentiary | 1.3 |  | 307
ASHRAE 90.1-2004Dining AreaFor Hotel | ASHRAE 90.1-2004 | Dining Area | For Hotel | 1.3 |  | 308
ASHRAE 90.1-2004LobbyGeneral | ASHRAE 90.1-2004 | Lobby | General | 1.3 |  | 288
ASHRAE 90.1-2004Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2004 | Whole Building | Dining: Bar Lounge/Leisure | 1.3 |  | 254
ASHRAE 90.1-2004Whole BuildingLibrary | ASHRAE 90.1-2004 | Whole Building | Library | 1.3 |  | 263
ASHRAE 90.1-2004Whole BuildingManufacturing Facility | ASHRAE 90.1-2004 | Whole Building | Manufacturing Facility | 1.3 |  | 264
ASHRAE 90.1-2004Whole BuildingReligious Building | ASHRAE 90.1-2004 | Whole Building | Religious Building | 1.3 |  | 275
ASHRAE 90.1-2004Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2004 | Classroom/Lecture/Training | General | 1.4 |  | 286
ASHRAE 90.1-2004Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2004 | Dining Area | For Bar Lounge/Leisure Dining | 1.4 |  | 310
ASHRAE 90.1-2004Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Playing Area | 1.4 |  | 324
ASHRAE 90.1-2004HospitalMedical Supply | ASHRAE 90.1-2004 | Hospital | Medical Supply | 1.4 |  | 344
ASHRAE 90.1-2004LaboratoryGeneral | ASHRAE 90.1-2004 | Laboratory | General | 1.4 |  | 313
ASHRAE 90.1-2004Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-2004 | Sports Arena | Indoor Playing Field Area | 1.4 |  | 367
ASHRAE 90.1-2004WarehouseFine Material Storage | ASHRAE 90.1-2004 | Warehouse | Fine Material Storage | 1.4 |  | 368
ASHRAE 90.1-2004Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2004 | Whole Building | Dining: Cafeteria/Fast Food | 1.4 |  | 255
ASHRAE 90.1-2004Whole BuildingWorkshop | ASHRAE 90.1-2004 | Whole Building | Workshop | 1.4 |  | 282
ASHRAE 90.1-2004Bank/OfficeBanking Activity Area | ASHRAE 90.1-2004 | Bank/Office | Banking Activity Area | 1.5 |  | 360
ASHRAE 90.1-2004Electrical/MechanicalGeneral | ASHRAE 90.1-2004 | Electrical/Mechanical | General | 1.5 |  | 358
ASHRAE 90.1-2004HospitalExam/Treatment | ASHRAE 90.1-2004 | Hospital | Exam/Treatment | 1.5 |  | 339
ASHRAE 90.1-2004TransportationTerminal—Ticket Counter | ASHRAE 90.1-2004 | Transportation | Terminal—Ticket Counter | 1.5 |  | 373
ASHRAE 90.1-2004Whole BuildingRetail | ASHRAE 90.1-2004 | Whole Building | Retail | 1.5 |  | 276
ASHRAE 90.1-2004Whole BuildingDining: Family | ASHRAE 90.1-2004 | Whole Building | Dining: Family | 1.6 |  | 256
ASHRAE 90.1-2004Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2004 | Whole Building | Performing Arts Theater | 1.6 |  | 272
ASHRAE 90.1-2004Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2004 | Audience/Seating Area | For Religious Buildings | 1.7 |  | 297
ASHRAE 90.1-2004LibraryStacks | ASHRAE 90.1-2004 | Library | Stacks | 1.7 |  | 334
ASHRAE 90.1-2004ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-2004 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.7 |  | 350
ASHRAE 90.1-2004MuseumRestoration | ASHRAE 90.1-2004 | Museum | Restoration | 1.7 |  | 357
ASHRAE 90.1-2004Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Mall Concourse | 1.7 |  | 364
ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | 1.7 |  | 363
ASHRAE 90.1-2004Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-2004 | Courthouse/Police Station/Penitentiary | Courtroom | 1.9 |  | 326
ASHRAE 90.1-2004WorkshopWorkshop | ASHRAE 90.1-2004 | Workshop | Workshop | 1.9 |  | 359
ASHRAE 90.1-2004Dining AreaFor Family Dining | ASHRAE 90.1-2004 | Dining Area | For Family Dining | 2.1 |  | 311
ASHRAE 90.1-2004ManufacturingDetailed Manufacturing | ASHRAE 90.1-2004 | Manufacturing | Detailed Manufacturing | 2.1 |  | 351
ASHRAE 90.1-2004HospitalOperating Room | ASHRAE 90.1-2004 | Hospital | Operating Room | 2.2 |  | 342
ASHRAE 90.1-2004Sports ArenaCourt Sports Area | ASHRAE 90.1-2004 | Sports Arena | Court Sports Area | 2.3 |  | 366
ASHRAE 90.1-2004Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2004 | Religious Buildings | Worship Pulpit, Choir | 2.4 |  | 361
ASHRAE 90.1-2004Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-2004 | Audience/Seating Area | For Performing Arts Theater | 2.6 |  | 299
ASHRAE 90.1-2004HospitalEmergency | ASHRAE 90.1-2004 | Hospital | Emergency | 2.7 |  | 336
ASHRAE 90.1-2004Sports ArenaRing Sports Area | ASHRAE 90.1-2004 | Sports Arena | Ring Sports Area | 2.7 |  | 365
ASHRAE 90.1-2007Whole BuildingAutomotive Facility | ASHRAE 90.1-2007 | Whole Building | Automotive Facility | 0.9 |  | 376
ASHRAE 90.1-2007Whole BuildingConvention Center | ASHRAE 90.1-2007 | Whole Building | Convention Center | 1.2 |  | 377
ASHRAE 90.1-2007Whole BuildingCourt House | ASHRAE 90.1-2007 | Whole Building | Court House | 1.2 |  | 378
ASHRAE 90.1-2007Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2007 | Whole Building | Dining: Bar Lounge/Leisure | 1.3 |  | 379
ASHRAE 90.1-2007Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2007 | Whole Building | Dining: Cafeteria/Fast Food | 1.4 |  | 380
ASHRAE 90.1-2007Whole BuildingDining: Family | ASHRAE 90.1-2007 | Whole Building | Dining: Family | 1.6 |  | 381
ASHRAE 90.1-2007Whole BuildingDormitory | ASHRAE 90.1-2007 | Whole Building | Dormitory | 1 |  | 382
ASHRAE 90.1-2007Whole BuildingExercise Center | ASHRAE 90.1-2007 | Whole Building | Exercise Center | 1 |  | 383
ASHRAE 90.1-2007Whole BuildingGymnasium | ASHRAE 90.1-2007 | Whole Building | Gymnasium | 1.1 |  | 384
ASHRAE 90.1-2007Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2007 | Whole Building | Health Care-Clinic | 1 |  | 385
ASHRAE 90.1-2007Whole BuildingHospital | ASHRAE 90.1-2007 | Whole Building | Hospital | 1.2 |  | 386
ASHRAE 90.1-2007Whole BuildingHotel | ASHRAE 90.1-2007 | Whole Building | Hotel | 1 |  | 387
ASHRAE 90.1-2007Whole BuildingLibrary | ASHRAE 90.1-2007 | Whole Building | Library | 1.3 |  | 388
ASHRAE 90.1-2007Whole BuildingManufacturing Facility | ASHRAE 90.1-2007 | Whole Building | Manufacturing Facility | 1.3 |  | 389
ASHRAE 90.1-2007Whole BuildingMotel | ASHRAE 90.1-2007 | Whole Building | Motel | 1 |  | 390
ASHRAE 90.1-2007Whole BuildingMotion Picture Theater | ASHRAE 90.1-2007 | Whole Building | Motion Picture Theater | 1.2 |  | 391
ASHRAE 90.1-2007Whole BuildingMulti-Family | ASHRAE 90.1-2007 | Whole Building | Multi-Family | 0.7 |  | 392
ASHRAE 90.1-2007Whole BuildingMuseum | ASHRAE 90.1-2007 | Whole Building | Museum | 1.1 |  | 393
ASHRAE 90.1-2007Whole BuildingOffice | ASHRAE 90.1-2007 | Whole Building | Office | 1 |  | 394
ASHRAE 90.1-2007Whole BuildingParking Garage | ASHRAE 90.1-2007 | Whole Building | Parking Garage | 0.3 |  | 395
ASHRAE 90.1-2007Whole BuildingPenitentiary | ASHRAE 90.1-2007 | Whole Building | Penitentiary | 1 |  | 396
ASHRAE 90.1-2007Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2007 | Whole Building | Performing Arts Theater | 1.6 |  | 397
ASHRAE 90.1-2007Whole BuildingPolice/Fire Station | ASHRAE 90.1-2007 | Whole Building | Police/Fire Station | 1 |  | 398
ASHRAE 90.1-2007Whole BuildingPost Office | ASHRAE 90.1-2007 | Whole Building | Post Office | 1.1 |  | 399
ASHRAE 90.1-2007Whole BuildingReligious Building | ASHRAE 90.1-2007 | Whole Building | Religious Building | 1.3 |  | 400
ASHRAE 90.1-2007Whole BuildingRetail | ASHRAE 90.1-2007 | Whole Building | Retail | 1.5 |  | 401
ASHRAE 90.1-2007Whole BuildingSchool/University | ASHRAE 90.1-2007 | Whole Building | School/University | 1.2 |  | 402
ASHRAE 90.1-2007Whole BuildingSports Arena | ASHRAE 90.1-2007 | Whole Building | Sports Arena | 1.1 |  | 403
ASHRAE 90.1-2007Whole BuildingTown Hall | ASHRAE 90.1-2007 | Whole Building | Town Hall | 1.1 |  | 404
ASHRAE 90.1-2007Whole BuildingTransportation | ASHRAE 90.1-2007 | Whole Building | Transportation | 1 |  | 405
ASHRAE 90.1-2007Whole BuildingWarehouse | ASHRAE 90.1-2007 | Whole Building | Warehouse | 0.8 |  | 406
ASHRAE 90.1-2007Whole BuildingWorkshop | ASHRAE 90.1-2007 | Whole Building | Workshop | 1.4 |  | 407
ASHRAE 90.1-2007Office-EnclosedGeneral | ASHRAE 90.1-2007 | Office-Enclosed | General | 1.1 |  | 408
ASHRAE 90.1-2007Office-Open PlanGeneral | ASHRAE 90.1-2007 | Office-Open Plan | General | 1.1 |  | 409
ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | 1.3 |  | 410
ASHRAE 90.1-2007Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2007 | Classroom/Lecture/Training | General | 1.4 |  | 411
ASHRAE 90.1-2007Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2007 | Classroom/Lecture/Training | For Penitentiary | 1.3 |  | 412
ASHRAE 90.1-2007LobbyGeneral | ASHRAE 90.1-2007 | Lobby | General | 1.3 |  | 413
ASHRAE 90.1-2007Dining AreaFor Hotel | ASHRAE 90.1-2007 | Dining Area | For Hotel | 1.3 |  | 433
ASHRAE 90.1-2007LobbyFor Performing Arts Theater | ASHRAE 90.1-2007 | Lobby | For Performing Arts Theater | 3.3 |  | 415
ASHRAE 90.1-2007LobbyFor Motion Picture Theater | ASHRAE 90.1-2007 | Lobby | For Motion Picture Theater | 1.1 |  | 416
ASHRAE 90.1-2007Audience/Seating AreaGeneral | ASHRAE 90.1-2007 | Audience/Seating Area | General | 0.9 |  | 417
ASHRAE 90.1-2007Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2007 | Audience/Seating Area | For Gymnasium | 0.4 |  | 418
ASHRAE 90.1-2007Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-2007 | Audience/Seating Area | For Exercise Center | 0.3 |  | 419
ASHRAE 90.1-2007Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2007 | Audience/Seating Area | For Convention Center | 0.7 |  | 420
ASHRAE 90.1-2007Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2007 | Audience/Seating Area | For Penitentiary | 0.7 |  | 421
ASHRAE 90.1-2007Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2007 | Audience/Seating Area | For Religious Buildings | 1.7 |  | 422
ASHRAE 90.1-2007Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-2007 | Audience/Seating Area | For Sports Arena | 0.4 |  | 423
ASHRAE 90.1-2007Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-2007 | Audience/Seating Area | For Performing Arts Theater | 2.6 |  | 424
ASHRAE 90.1-2007Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2007 | Audience/Seating Area | For Motion Picture Theater | 1.2 |  | 425
ASHRAE 90.1-2007Audience/Seating AreaFor Transportation | ASHRAE 90.1-2007 | Audience/Seating Area | For Transportation | 0.5 |  | 426
ASHRAE 90.1-2007AtriumFirst Three Floors | ASHRAE 90.1-2007 | Atrium | First Three Floors | 0.6 |  | 427
ASHRAE 90.1-2007AtriumEach Floor over First Three Floors | ASHRAE 90.1-2007 | Atrium | Each Floor over First Three Floors | 0.2 |  | 428
ASHRAE 90.1-2007Lounge/RecreationGeneral | ASHRAE 90.1-2007 | Lounge/Recreation | General | 1.2 |  | 429
ASHRAE 90.1-2007Lounge/RecreationFor Hospital | ASHRAE 90.1-2007 | Lounge/Recreation | For Hospital | 0.8 |  | 430
ASHRAE 90.1-2007Dining AreaGeneral | ASHRAE 90.1-2007 | Dining Area | General | 0.9 |  | 431
ASHRAE 90.1-2007Dining AreaFor Penitentiary | ASHRAE 90.1-2007 | Dining Area | For Penitentiary | 1.3 |  | 432
ASHRAE 90.1-2010Dining AreaFor Hotel | ASHRAE 90.1-2010 | Dining Area | For Hotel | 0.89
ASHRAE 90.1-2007Dining AreaFor Motel | ASHRAE 90.1-2007 | Dining Area | For Motel | 1.2 |  | 434
ASHRAE 90.1-2007Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2007 | Dining Area | For Bar Lounge/Leisure Dining | 1.4 |  | 435
ASHRAE 90.1-2007Dining AreaFor Family Dining | ASHRAE 90.1-2007 | Dining Area | For Family Dining | 2.1 |  | 436
ASHRAE 90.1-2007Food PreparationGeneral | ASHRAE 90.1-2007 | Food Preparation | General | 1.2 |  | 437
ASHRAE 90.1-2007LaboratoryGeneral | ASHRAE 90.1-2007 | Laboratory | General | 1.4 |  | 438
ASHRAE 90.1-2007RestroomsGeneral | ASHRAE 90.1-2007 | Restrooms | General | 0.9 |  | 439
ASHRAE 90.1-2007Dressing/Locker/Fitting RoomGeneral | ASHRAE 90.1-2007 | Dressing/Locker/Fitting Room | General | 0.6 |  | 440
ASHRAE 90.1-2007Corridor/TransitionGeneral | ASHRAE 90.1-2007 | Corridor/Transition | General | 0.5 |  | 441
ASHRAE 90.1-2007Corridor/TransitionFor Hospital | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | 1 |  | 442
ASHRAE 90.1-2007Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-2007 | Corridor/Transition | For Manufacturing Facility | 0.5 |  | 443
ASHRAE 90.1-2007Stairs-ActiveGeneral | ASHRAE 90.1-2007 | Stairs-Active | General | 0.6 |  | 444
ASHRAE 90.1-2007Active StorageGeneral | ASHRAE 90.1-2007 | Active Storage | General | 0.8 |  | 445
ASHRAE 90.1-2007Active StorageFor Hospital | ASHRAE 90.1-2007 | Active Storage | For Hospital | 0.9 |  | 446
ASHRAE 90.1-2007Inactive storageGeneral | ASHRAE 90.1-2007 | Inactive storage | General | 0.3 |  | 447
ASHRAE 90.1-2007Inactive storageFor Museum | ASHRAE 90.1-2007 | Inactive storage | For Museum | 0.8 |  | 448
ASHRAE 90.1-2007Gymnasium/Exercise CenterPlaying Area | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Playing Area | 1.4 |  | 449
ASHRAE 90.1-2007Gymnasium/Exercise CenterExercise Area | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Exercise Area | 0.9 |  | 450
ASHRAE 90.1-2007Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-2007 | Courthouse/Police Station/Penitentiary | Courtroom | 1.9 |  | 451
ASHRAE 90.1-2007Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-2007 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.9 |  | 452
ASHRAE 90.1-2007Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-2007 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.3 |  | 453
ASHRAE 90.1-2007Fire StationsFire Station Engine Room | ASHRAE 90.1-2007 | Fire Stations | Fire Station Engine Room | 0.8 |  | 454
ASHRAE 90.1-2007Fire StationsSleeping Quarters | ASHRAE 90.1-2007 | Fire Stations | Sleeping Quarters | 0.3 |  | 455
ASHRAE 90.1-2007Post OfficeSorting Area | ASHRAE 90.1-2007 | Post Office | Sorting Area | 1.2 |  | 456
ASHRAE 90.1-2007Convention CenterExhibit Space | ASHRAE 90.1-2007 | Convention Center | Exhibit Space | 1.3 |  | 457
ASHRAE 90.1-2007LibraryCard File and Cataloging | ASHRAE 90.1-2007 | Library | Card File and Cataloging | 1.1 |  | 458
ASHRAE 90.1-2007LibraryStacks | ASHRAE 90.1-2007 | Library | Stacks | 1.7 |  | 459
ASHRAE 90.1-2007LibraryReading Area | ASHRAE 90.1-2007 | Library | Reading Area | 1.2 |  | 460
ASHRAE 90.1-2007HospitalEmergency | ASHRAE 90.1-2007 | Hospital | Emergency | 2.7 |  | 461
ASHRAE 90.1-2007HospitalRecovery | ASHRAE 90.1-2007 | Hospital | Recovery | 0.8 |  | 462
ASHRAE 90.1-2007HospitalNurse Station | ASHRAE 90.1-2007 | Hospital | Nurse Station | 1 |  | 463
ASHRAE 90.1-2007HospitalExam/Treatment | ASHRAE 90.1-2007 | Hospital | Exam/Treatment | 1.5 |  | 464
ASHRAE 90.1-2007HospitalPharmacy | ASHRAE 90.1-2007 | Hospital | Pharmacy | 1.2 |  | 465
ASHRAE 90.1-2007HospitalPatient Room | ASHRAE 90.1-2007 | Hospital | Patient Room | 0.7 |  | 466
ASHRAE 90.1-2007HospitalOperating Room | ASHRAE 90.1-2007 | Hospital | Operating Room | 2.2 |  | 467
ASHRAE 90.1-2007HospitalNursery | ASHRAE 90.1-2007 | Hospital | Nursery | 0.6 |  | 468
ASHRAE 90.1-2007HospitalMedical Supply | ASHRAE 90.1-2007 | Hospital | Medical Supply | 1.4 |  | 469
ASHRAE 90.1-2007HospitalPhysical Therapy | ASHRAE 90.1-2007 | Hospital | Physical Therapy | 0.9 |  | 470
ASHRAE 90.1-2007HospitalRadiology | ASHRAE 90.1-2007 | Hospital | Radiology | 0.4 |  | 471
ASHRAE 90.1-2007HospitalLaundry-Washing | ASHRAE 90.1-2007 | Hospital | Laundry-Washing | 0.6 |  | 472
ASHRAE 90.1-2007AutomotiveService/Repair | ASHRAE 90.1-2007 | Automotive | Service/Repair | 0.7 |  | 473
ASHRAE 90.1-2007ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2007 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.2 |  | 474
ASHRAE 90.1-2007ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 90.1-2007 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.7 |  | 475
ASHRAE 90.1-2007ManufacturingDetailed Manufacturing | ASHRAE 90.1-2007 | Manufacturing | Detailed Manufacturing | 2.1 |  | 476
ASHRAE 90.1-2007ManufacturingEquipment Room | ASHRAE 90.1-2007 | Manufacturing | Equipment Room | 1.2 |  | 477
ASHRAE 90.1-2007ManufacturingControl Room | ASHRAE 90.1-2007 | Manufacturing | Control Room | 0.5 |  | 478
ASHRAE 90.1-2007Hotel/MotelGuest Rooms | ASHRAE 90.1-2007 | Hotel/Motel | Guest Rooms | 1.1 |  | 479
ASHRAE 90.1-2007DormitoryLiving Quarters | ASHRAE 90.1-2007 | Dormitory | Living Quarters | 1.1 |  | 480
ASHRAE 90.1-2007MuseumGeneral Exhibition | ASHRAE 90.1-2007 | Museum | General Exhibition | 1 |  | 481
ASHRAE 90.1-2007MuseumRestoration | ASHRAE 90.1-2007 | Museum | Restoration | 1.7 |  | 482
ASHRAE 90.1-2007Electrical/MechanicalGeneral | ASHRAE 90.1-2007 | Electrical/Mechanical | General | 1.5 |  | 483
ASHRAE 90.1-2007WorkshopGeneral | ASHRAE 90.1-2007 | Workshop | General | 1.9 |  | 484
ASHRAE 90.1-2007Bank/OfficeBanking Activity Area | ASHRAE 90.1-2007 | Bank/Office | Banking Activity Area | 1.5 |  | 485
ASHRAE 90.1-2007Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2007 | Religious Buildings | Worship Pulpit, Choir | 2.4 |  | 486
ASHRAE 90.1-2007Religious BuildingsFellowship Hall | ASHRAE 90.1-2007 | Religious Buildings | Fellowship Hall | 0.9 |  | 487
ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | 1.7 |  | 488
ASHRAE 90.1-2007Retail (not including accent lighting)Mall Concourse | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Mall Concourse | 1.7 |  | 489
ASHRAE 90.1-2007Sports ArenaRing Sports Area | ASHRAE 90.1-2007 | Sports Arena | Ring Sports Area | 2.7 |  | 490
ASHRAE 90.1-2007Sports ArenaCourt Sports Area | ASHRAE 90.1-2007 | Sports Arena | Court Sports Area | 2.3 |  | 491
ASHRAE 90.1-2007Sports ArenaIndoor Playing Field Area | ASHRAE 90.1-2007 | Sports Arena | Indoor Playing Field Area | 1.4 |  | 492
ASHRAE 90.1-2007WarehouseFine Material Storage | ASHRAE 90.1-2007 | Warehouse | Fine Material Storage | 1.4 |  | 493
ASHRAE 90.1-2007WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2007 | Warehouse | Medium/Bulky Material Storage | 0.9 |  | 494
ASHRAE 90.1-2007Parking GarageGarage Area | ASHRAE 90.1-2007 | Parking Garage | Garage Area | 0.2 |  | 495
ASHRAE 90.1-2007TransportationAirport-Concourse | ASHRAE 90.1-2007 | Transportation | Airport-Concourse | 0.6 |  | 496
ASHRAE 90.1-2007TransportationAir/Train/Bus-Baggage Area | ASHRAE 90.1-2007 | Transportation | Air/Train/Bus-Baggage Area | 1 |  | 497
ASHRAE 90.1-2007TransportationTerminal-Ticket Counter | ASHRAE 90.1-2007 | Transportation | Terminal-Ticket Counter | 1.5 |  | 498
ASHRAE 90.1-2007Exterior SpacesGeneral | ASHRAE 90.1-2007 | Exterior Spaces | General | 0 |  | 499
ASHRAE 90.1-2007AtticsGeneral | ASHRAE 90.1-2007 | Attics | General | 0 |  | 500
GGHC v2.2Health CareAnesthesia Storage | GGHC v2.2 | Health Care | Anesthesia Storage | 3 |  | 501
GGHC v2.2Health CareAngiographic-All Other Types | GGHC v2.2 | Health Care | Angiographic-All Other Types | 3 |  | 502
GGHC v2.2Health CareAngiographic-Heart Only | GGHC v2.2 | Health Care | Angiographic-Heart Only | 3 |  | 503
GGHC v2.2Health CareAutopsy | GGHC v2.2 | Health Care | Autopsy | 1.2 |  | 504
GGHC v2.2Health CareBathroom/ Public | GGHC v2.2 | Health Care | Bathroom/ Public | 0.6 |  | 505
GGHC v2.2Health CareBedpan Room | GGHC v2.2 | Health Care | Bedpan Room | 0.5 |  | 506
GGHC v2.2Health CareCast Room | GGHC v2.2 | Health Care | Cast Room | 3 |  | 507
GGHC v2.2Health CareClean Linen Storage | GGHC v2.2 | Health Care | Clean Linen Storage | 0.5 |  | 508
GGHC v2.2Health CareClean Utility / Workroom | GGHC v2.2 | Health Care | Clean Utility / Workroom | 1.2 |  | 509
GGHC v2.2Health CareConference Rooms | GGHC v2.2 | Health Care | Conference Rooms | 1.2 |  | 510
GGHC v2.2Health CareCorridors | GGHC v2.2 | Health Care | Corridors | 0.6 |  | 511
GGHC v2.2Health CareCystoscopy | GGHC v2.2 | Health Care | Cystoscopy | 3 |  | 512
GGHC v2.2Health CareDarkroom | GGHC v2.2 | Health Care | Darkroom | 0.3 |  | 513
GGHC v2.2Health CareDecontamination | GGHC v2.2 | Health Care | Decontamination | 1.2 |  | 514
GGHC v2.2Health CareDelivery Room | GGHC v2.2 | Health Care | Delivery Room | 4.5 |  | 515
GGHC v2.2Health CareDietary Day Storage | GGHC v2.2 | Health Care | Dietary Day Storage | 0.5 |  | 516
GGHC v2.2Health CareDining Room | GGHC v2.2 | Health Care | Dining Room | 1.1 |  | 517
GGHC v2.2Health CareDishwashing | GGHC v2.2 | Health Care | Dishwashing | 1.7 |  | 518
GGHC v2.2Health CareEndoscopy | GGHC v2.2 | Health Care | Endoscopy | 3 |  | 519
GGHC v2.2Health CareHistology | GGHC v2.2 | Health Care | Histology | 4.5 |  | 520
GGHC v2.2Health CareIsolation | GGHC v2.2 | Health Care | Isolation | 0.5 |  | 521
GGHC v2.2Health CareJanitors Closet / Utility | GGHC v2.2 | Health Care | Janitors Closet / Utility | 0.5 |  | 522
GGHC v2.2Health CareKitchen, Food Preparation | GGHC v2.2 | Health Care | Kitchen, Food Preparation | 1.7 |  | 523
GGHC v2.2Health CareLabor/ Delivery/Recovery | GGHC v2.2 | Health Care | Labor/ Delivery/Recovery | 4.5 |  | 524
GGHC v2.2Health CareL / D / R / Post Partum | GGHC v2.2 | Health Care | L / D / R / Post Partum | 0.7 |  | 525
GGHC v2.2Health CareLaboratory | GGHC v2.2 | Health Care | Laboratory | 3 |  | 526
GGHC v2.2Health CareLinen Storage, Clean | GGHC v2.2 | Health Care | Linen Storage, Clean | 0.5 |  | 527
GGHC v2.2Health CareLobby | GGHC v2.2 | Health Care | Lobby | 1.1 |  | 528
GGHC v2.2Health CareLockers | GGHC v2.2 | Health Care | Lockers | 0.7 |  | 529
GGHC v2.2Health CareMammography | GGHC v2.2 | Health Care | Mammography | 3 |  | 530
GGHC v2.2Health CareMechanical Equipment Room | GGHC v2.2 | Health Care | Mechanical Equipment Room | 0.7 |  | 531
GGHC v2.2Health CareMedical Records | GGHC v2.2 | Health Care | Medical Records | 3 |  | 532
GGHC v2.2Health CareNuclear Medicine, Hot Lab | GGHC v2.2 | Health Care | Nuclear Medicine, Hot Lab | 1.2 |  | 533
GGHC v2.2Health CareNursery, General | GGHC v2.2 | Health Care | Nursery, General | 3 |  | 534
GGHC v2.2Health CareNursery, Exam | GGHC v2.2 | Health Care | Nursery, Exam | 0.7 |  | 535
GGHC v2.2Health CareNursing Stations- General | GGHC v2.2 | Health Care | Nursing Stations- General | 1.2 |  | 536
GGHC v2.2Health CareOperating Room | GGHC v2.2 | Health Care | Operating Room | 4.5 |  | 537
GGHC v2.2Health CarePathology | GGHC v2.2 | Health Care | Pathology | 3 |  | 538
GGHC v2.2Health CarePatient Room | GGHC v2.2 | Health Care | Patient Room | 0.5 |  | 539
GGHC v2.2Health CarePharmacy / Medicine Room | GGHC v2.2 | Health Care | Pharmacy / Medicine Room | 3 |  | 540
GGHC v2.2Health CarePhysical Therapy and Hydrotherapy | GGHC v2.2 | Health Care | Physical Therapy and Hydrotherapy | 1.2 |  | 541
GGHC v2.2Health CareRecovery | GGHC v2.2 | Health Care | Recovery | 3 |  | 542
GGHC v2.2Health CareScrub Up Area, Surgical Corridor | GGHC v2.2 | Health Care | Scrub Up Area, Surgical Corridor | 4.5 |  | 543
GGHC v2.2Health CareSoiled Linen, Sorting | GGHC v2.2 | Health Care | Soiled Linen, Sorting | 1.2 |  | 544
GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | 3 |  | 545
GGHC v2.2Health CareSpecial Procedure Room, Invasive | GGHC v2.2 | Health Care | Special Procedure Room, Invasive | 3 |  | 546
GGHC v2.2Health CareStairways | GGHC v2.2 | Health Care | Stairways | 0.6 |  | 547
GGHC v2.2Health CareSterilizer Room | GGHC v2.2 | Health Care | Sterilizer Room | 1.2 |  | 548
GGHC v2.2Health CareSub-Sterile | GGHC v2.2 | Health Care | Sub-Sterile | 0.7 |  | 549
GGHC v2.2Health CareSurgical Supply | GGHC v2.2 | Health Care | Surgical Supply | 1.2 |  | 550
GGHC v2.2Health CareTrash Chute Room | GGHC v2.2 | Health Care | Trash Chute Room | 0.5 |  | 551
GGHC v2.2Health CareTrauma | GGHC v2.2 | Health Care | Trauma | 3 |  | 552
GGHC v2.2Health CareTreatment / Examination | GGHC v2.2 | Health Care | Treatment / Examination | 1.2 |  | 553
GGHC v2.2Health CareUnsterile Supply | GGHC v2.2 | Health Care | Unsterile Supply | 0.5 |  | 554
GGHC v2.2Health CareWaiting Areas/Lounges | GGHC v2.2 | Health Care | Waiting Areas/Lounges | 1.1 |  | 555
GGHC v2.2Health CareX-ray, Diagnostic and Treatment | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | 3 |  | 556
ASHRAE 189.1-2009Whole BuildingAutomotive Facility | ASHRAE 189.1-2009 | Whole Building | Automotive Facility | 0.81
ASHRAE 189.1-2009Whole BuildingConvention Center | ASHRAE 189.1-2009 | Whole Building | Convention Center | 1.08
ASHRAE 189.1-2009Whole BuildingCourt House | ASHRAE 189.1-2009 | Whole Building | Court House | 1.08
ASHRAE 189.1-2009Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 189.1-2009 | Whole Building | Dining: Bar Lounge/Leisure | 1.17
ASHRAE 189.1-2009Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 189.1-2009 | Whole Building | Dining: Cafeteria/Fast Food | 1.26
ASHRAE 189.1-2009Whole BuildingDining: Family | ASHRAE 189.1-2009 | Whole Building | Dining: Family | 1.44
ASHRAE 189.1-2009Whole BuildingDormitory | ASHRAE 189.1-2009 | Whole Building | Dormitory | 0.9
ASHRAE 189.1-2009Whole BuildingExercise Center | ASHRAE 189.1-2009 | Whole Building | Exercise Center | 0.9
ASHRAE 189.1-2009Whole BuildingGymnasium | ASHRAE 189.1-2009 | Whole Building | Gymnasium | 0.99
ASHRAE 189.1-2009Whole BuildingHealth Care-Clinic | ASHRAE 189.1-2009 | Whole Building | Health Care-Clinic | 0.9
ASHRAE 189.1-2009Whole BuildingHospital | ASHRAE 189.1-2009 | Whole Building | Hospital | 1.08
ASHRAE 189.1-2009Whole BuildingHotel | ASHRAE 189.1-2009 | Whole Building | Hotel | 0.9
ASHRAE 189.1-2009Whole BuildingLibrary | ASHRAE 189.1-2009 | Whole Building | Library | 1.17
ASHRAE 189.1-2009Whole BuildingManufacturing Facility | ASHRAE 189.1-2009 | Whole Building | Manufacturing Facility | 1.17
ASHRAE 189.1-2009Whole BuildingMotel | ASHRAE 189.1-2009 | Whole Building | Motel | 0.9
ASHRAE 189.1-2009Whole BuildingMotion Picture Theater | ASHRAE 189.1-2009 | Whole Building | Motion Picture Theater | 1.08
ASHRAE 189.1-2009Whole BuildingMulti-Family | ASHRAE 189.1-2009 | Whole Building | Multi-Family | 0.63
ASHRAE 189.1-2009Whole BuildingMuseum | ASHRAE 189.1-2009 | Whole Building | Museum | 0.99
ASHRAE 189.1-2009Whole BuildingOffice | ASHRAE 189.1-2009 | Whole Building | Office | 0.9
ASHRAE 189.1-2009Whole BuildingParking Garage | ASHRAE 189.1-2009 | Whole Building | Parking Garage | 0.27
ASHRAE 189.1-2009Whole BuildingPenitentiary | ASHRAE 189.1-2009 | Whole Building | Penitentiary | 0.9
ASHRAE 189.1-2009Whole BuildingPerforming Arts Theater | ASHRAE 189.1-2009 | Whole Building | Performing Arts Theater | 1.44
ASHRAE 189.1-2009Whole BuildingPolice/Fire Station | ASHRAE 189.1-2009 | Whole Building | Police/Fire Station | 0.9
ASHRAE 189.1-2009Whole BuildingPost Office | ASHRAE 189.1-2009 | Whole Building | Post Office | 0.99
ASHRAE 189.1-2009Whole BuildingReligious Building | ASHRAE 189.1-2009 | Whole Building | Religious Building | 1.17
ASHRAE 189.1-2009Whole BuildingRetail | ASHRAE 189.1-2009 | Whole Building | Retail | 1.35
ASHRAE 189.1-2009Whole BuildingSchool/University | ASHRAE 189.1-2009 | Whole Building | School/University | 1.08
ASHRAE 189.1-2009Whole BuildingSports Arena | ASHRAE 189.1-2009 | Whole Building | Sports Arena | 0.99
ASHRAE 189.1-2009Whole BuildingTown Hall | ASHRAE 189.1-2009 | Whole Building | Town Hall | 0.99
ASHRAE 189.1-2009Whole BuildingTransportation | ASHRAE 189.1-2009 | Whole Building | Transportation | 0.9
ASHRAE 189.1-2009Whole BuildingWarehouse | ASHRAE 189.1-2009 | Whole Building | Warehouse | 0.72
ASHRAE 189.1-2009Whole BuildingWorkshop | ASHRAE 189.1-2009 | Whole Building | Workshop | 1.26
ASHRAE 189.1-2009Office-EnclosedGeneral | ASHRAE 189.1-2009 | Office-Enclosed | General | 0.99
ASHRAE 189.1-2009Office-Open PlanGeneral | ASHRAE 189.1-2009 | Office-Open Plan | General | 0.99
ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | 1.17
ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | 1.26
ASHRAE 189.1-2009Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 189.1-2009 | Classroom/Lecture/Training | For Penitentiary | 1.17
ASHRAE 189.1-2009LobbyGeneral | ASHRAE 189.1-2009 | Lobby | General | 1.17
ASHRAE 189.1-2009LobbyFor Hotel | ASHRAE 189.1-2009 | Lobby | For Hotel | 0.99
ASHRAE 189.1-2009LobbyFor Performing Arts Theater | ASHRAE 189.1-2009 | Lobby | For Performing Arts Theater | 2.97
ASHRAE 189.1-2009LobbyFor Motion Picture Theater | ASHRAE 189.1-2009 | Lobby | For Motion Picture Theater | 0.99
ASHRAE 189.1-2009Audience/Seating AreaGeneral | ASHRAE 189.1-2009 | Audience/Seating Area | General | 0.81
ASHRAE 189.1-2009Audience/Seating AreaFor Gymnasium | ASHRAE 189.1-2009 | Audience/Seating Area | For Gymnasium | 0.36
ASHRAE 189.1-2009Audience/Seating AreaFor Exercise Center | ASHRAE 189.1-2009 | Audience/Seating Area | For Exercise Center | 0.27
ASHRAE 189.1-2009Audience/Seating AreaFor Convention Center | ASHRAE 189.1-2009 | Audience/Seating Area | For Convention Center | 0.63
ASHRAE 189.1-2009Audience/Seating AreaFor Penitentiary | ASHRAE 189.1-2009 | Audience/Seating Area | For Penitentiary | 0.63
ASHRAE 189.1-2009Audience/Seating AreaFor Religious Buildings | ASHRAE 189.1-2009 | Audience/Seating Area | For Religious Buildings | 1.53
ASHRAE 189.1-2009Audience/Seating AreaFor Sports Arena | ASHRAE 189.1-2009 | Audience/Seating Area | For Sports Arena | 0.36
ASHRAE 189.1-2009Audience/Seating AreaFor Performing Arts Theater | ASHRAE 189.1-2009 | Audience/Seating Area | For Performing Arts Theater | 2.34
ASHRAE 189.1-2009Audience/Seating AreaFor Motion Picture Theater | ASHRAE 189.1-2009 | Audience/Seating Area | For Motion Picture Theater | 1.08
ASHRAE 189.1-2009Audience/Seating AreaFor Transportation | ASHRAE 189.1-2009 | Audience/Seating Area | For Transportation | 0.45
ASHRAE 189.1-2009AtriumFirst Three Floors | ASHRAE 189.1-2009 | Atrium | First Three Floors | 0.54
ASHRAE 189.1-2009AtriumEach Floor over First Three Floors | ASHRAE 189.1-2009 | Atrium | Each Floor over First Three Floors | 0.18
ASHRAE 189.1-2009Lounge/RecreationGeneral | ASHRAE 189.1-2009 | Lounge/Recreation | General | 1.08
ASHRAE 189.1-2009Lounge/RecreationFor Hospital | ASHRAE 189.1-2009 | Lounge/Recreation | For Hospital | 0.72
ASHRAE 189.1-2009Dining AreaGeneral | ASHRAE 189.1-2009 | Dining Area | General | 0.81
ASHRAE 189.1-2009Dining AreaFor Penitentiary | ASHRAE 189.1-2009 | Dining Area | For Penitentiary | 1.17
ASHRAE 189.1-2009Dining AreaFor Hotel | ASHRAE 189.1-2009 | Dining Area | For Hotel | 1.17
ASHRAE 189.1-2009Dining AreaFor Motel | ASHRAE 189.1-2009 | Dining Area | For Motel | 1.08
ASHRAE 189.1-2009Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 189.1-2009 | Dining Area | For Bar Lounge/Leisure Dining | 1.26
ASHRAE 189.1-2009Dining AreaFor Family Dining | ASHRAE 189.1-2009 | Dining Area | For Family Dining | 1.89
ASHRAE 189.1-2009Food PreparationGeneral | ASHRAE 189.1-2009 | Food Preparation | General | 1.08
ASHRAE 189.1-2009LaboratoryGeneral | ASHRAE 189.1-2009 | Laboratory | General | 1.26
ASHRAE 189.1-2009RestroomsGeneral | ASHRAE 189.1-2009 | Restrooms | General | 0.81
ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | 0.54
ASHRAE 189.1-2009Corridor/TransitionGeneral | ASHRAE 189.1-2009 | Corridor/Transition | General | 0.45
ASHRAE 189.1-2009Corridor/TransitionFor Hospital | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | 0.9
ASHRAE 189.1-2009Corridor/TransitionFor Manufacturing Facility | ASHRAE 189.1-2009 | Corridor/Transition | For Manufacturing Facility | 0.45
ASHRAE 189.1-2009Stairs-ActiveGeneral | ASHRAE 189.1-2009 | Stairs-Active | General | 0.54
ASHRAE 189.1-2009Active StorageGeneral | ASHRAE 189.1-2009 | Active Storage | General | 0.72
ASHRAE 189.1-2009Active StorageFor Hospital | ASHRAE 189.1-2009 | Active Storage | For Hospital | 0.81
ASHRAE 189.1-2009Inactive storageGeneral | ASHRAE 189.1-2009 | Inactive storage | General | 0.27
ASHRAE 189.1-2009Inactive storageFor Museum | ASHRAE 189.1-2009 | Inactive storage | For Museum | 0.72
ASHRAE 189.1-2009Gymnasium/Exercise CenterPlaying Area | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Playing Area | 1.26
ASHRAE 189.1-2009Gymnasium/Exercise CenterExercise Area | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Exercise Area | 0.81
ASHRAE 189.1-2009Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 189.1-2009 | Courthouse/Police Station/Penitentiary | Courtroom | 1.71
ASHRAE 189.1-2009Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 189.1-2009 | Courthouse/Police Station/Penitentiary | Confinement Cells | 0.81
ASHRAE 189.1-2009Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 189.1-2009 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.17
ASHRAE 189.1-2009Fire StationsFire Station Engine Room | ASHRAE 189.1-2009 | Fire Stations | Fire Station Engine Room | 0.72
ASHRAE 189.1-2009Fire StationsSleeping Quarters | ASHRAE 189.1-2009 | Fire Stations | Sleeping Quarters | 0.27
ASHRAE 189.1-2009Post OfficeSorting Area | ASHRAE 189.1-2009 | Post Office | Sorting Area | 1.08
ASHRAE 189.1-2009Convention CenterExhibit Space | ASHRAE 189.1-2009 | Convention Center | Exhibit Space | 1.17
ASHRAE 189.1-2009LibraryCard File and Cataloging | ASHRAE 189.1-2009 | Library | Card File and Cataloging | 0.99
ASHRAE 189.1-2009LibraryStacks | ASHRAE 189.1-2009 | Library | Stacks | 1.53
ASHRAE 189.1-2009LibraryReading Area | ASHRAE 189.1-2009 | Library | Reading Area | 1.08
ASHRAE 189.1-2009HospitalEmergency | ASHRAE 189.1-2009 | Hospital | Emergency | 2.43
ASHRAE 189.1-2009HospitalRecovery | ASHRAE 189.1-2009 | Hospital | Recovery | 0.72
ASHRAE 189.1-2009HospitalNurse Station | ASHRAE 189.1-2009 | Hospital | Nurse Station | 0.9
ASHRAE 189.1-2009HospitalExam/Treatment | ASHRAE 189.1-2009 | Hospital | Exam/Treatment | 1.35
ASHRAE 189.1-2009HospitalPharmacy | ASHRAE 189.1-2009 | Hospital | Pharmacy | 1.08
ASHRAE 189.1-2009HospitalPatient Room | ASHRAE 189.1-2009 | Hospital | Patient Room | 0.63
ASHRAE 189.1-2009HospitalOperating Room | ASHRAE 189.1-2009 | Hospital | Operating Room | 1.98
ASHRAE 189.1-2009HospitalNursery | ASHRAE 189.1-2009 | Hospital | Nursery | 0.54
ASHRAE 189.1-2009HospitalMedical Supply | ASHRAE 189.1-2009 | Hospital | Medical Supply | 1.26
ASHRAE 189.1-2009HospitalPhysical Therapy | ASHRAE 189.1-2009 | Hospital | Physical Therapy | 0.81
ASHRAE 189.1-2009HospitalRadiology | ASHRAE 189.1-2009 | Hospital | Radiology | 0.36
ASHRAE 189.1-2009HospitalLaundry-Washing | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | 0.54
ASHRAE 189.1-2009AutomotiveService/Repair | ASHRAE 189.1-2009 | Automotive | Service/Repair | 0.63
ASHRAE 189.1-2009ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 189.1-2009 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.08
ASHRAE 189.1-2009ManufacturingHigh Bay (≥25 ft Floor to Ceiling Height) | ASHRAE 189.1-2009 | Manufacturing | High Bay (≥25 ft Floor to Ceiling Height) | 1.53
ASHRAE 189.1-2009ManufacturingDetailed Manufacturing | ASHRAE 189.1-2009 | Manufacturing | Detailed Manufacturing | 1.89
ASHRAE 189.1-2009ManufacturingEquipment Room | ASHRAE 189.1-2009 | Manufacturing | Equipment Room | 1.08
ASHRAE 189.1-2009ManufacturingControl Room | ASHRAE 189.1-2009 | Manufacturing | Control Room | 0.45
ASHRAE 189.1-2009Hotel/MotelGuest Rooms | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | 0.99
ASHRAE 189.1-2009DormitoryLiving Quarters | ASHRAE 189.1-2009 | Dormitory | Living Quarters | 0.99
ASHRAE 189.1-2009MuseumGeneral Exhibition | ASHRAE 189.1-2009 | Museum | General Exhibition | 0.9
ASHRAE 189.1-2009MuseumRestoration | ASHRAE 189.1-2009 | Museum | Restoration | 1.53
ASHRAE 189.1-2009Electrical/MechanicalGeneral | ASHRAE 189.1-2009 | Electrical/Mechanical | General | 1.35
ASHRAE 189.1-2009WorkshopGeneral | ASHRAE 189.1-2009 | Workshop | General | 1.71
ASHRAE 189.1-2009Bank/OfficeBanking Activity Area | ASHRAE 189.1-2009 | Bank/Office | Banking Activity Area | 1.35
ASHRAE 189.1-2009Religious BuildingsWorship Pulpit, Choir | ASHRAE 189.1-2009 | Religious Buildings | Worship Pulpit, Choir | 2.16
ASHRAE 189.1-2009Religious BuildingsFellowship Hall | ASHRAE 189.1-2009 | Religious Buildings | Fellowship Hall | 0.81
ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | 1.53
ASHRAE 189.1-2009Retail (not including accent lighting)Mall Concourse | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Mall Concourse | 1.53
ASHRAE 189.1-2009Sports ArenaRing Sports Area | ASHRAE 189.1-2009 | Sports Arena | Ring Sports Area | 2.43
ASHRAE 189.1-2009Sports ArenaCourt Sports Area | ASHRAE 189.1-2009 | Sports Arena | Court Sports Area | 2.07
ASHRAE 189.1-2009Sports ArenaIndoor Playing Field Area | ASHRAE 189.1-2009 | Sports Arena | Indoor Playing Field Area | 1.26
ASHRAE 189.1-2009WarehouseFine Material Storage | ASHRAE 189.1-2009 | Warehouse | Fine Material Storage | 1.26
ASHRAE 189.1-2009WarehouseMedium/Bulky Material Storage | ASHRAE 189.1-2009 | Warehouse | Medium/Bulky Material Storage | 0.81
ASHRAE 189.1-2009Parking GarageGarage Area | ASHRAE 189.1-2009 | Parking Garage | Garage Area | 0.18
ASHRAE 189.1-2009TransportationAirport-Concourse | ASHRAE 189.1-2009 | Transportation | Airport-Concourse | 0.54
ASHRAE 189.1-2009TransportationAir/Train/Bus-Baggage Area | ASHRAE 189.1-2009 | Transportation | Air/Train/Bus-Baggage Area | 0.9
ASHRAE 189.1-2009TransportationTerminal-Ticket Counter | ASHRAE 189.1-2009 | Transportation | Terminal-Ticket Counter | 1.35
ASHRAE 189.1-2009Exterior SpacesGeneral | ASHRAE 189.1-2009 | Exterior Spaces | General | 0
ASHRAE 189.1-2009AtticsGeneral | ASHRAE 189.1-2009 | Attics | General | 0
ASHRAE 90.1-2010Whole BuildingAutomotive Facility | ASHRAE 90.1-2010 | Whole Building | Automotive Facility | 0.82
ASHRAE 90.1-2010Whole BuildingConvention Center | ASHRAE 90.1-2010 | Whole Building | Convention Center | 1.08
ASHRAE 90.1-2010Whole BuildingCourt House | ASHRAE 90.1-2010 | Whole Building | Court House | 1.05
ASHRAE 90.1-2010Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2010 | Whole Building | Dining: Bar Lounge/Leisure | 0.99
ASHRAE 90.1-2010Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2010 | Whole Building | Dining: Cafeteria/Fast Food | 0.9
ASHRAE 90.1-2010Whole BuildingDining: Family | ASHRAE 90.1-2010 | Whole Building | Dining: Family | 0.89
ASHRAE 90.1-2010Whole BuildingDormitory | ASHRAE 90.1-2010 | Whole Building | Dormitory | 0.61
ASHRAE 90.1-2010Whole BuildingExercise Center | ASHRAE 90.1-2010 | Whole Building | Exercise Center | 0.88
ASHRAE 90.1-2010Whole BuildingFire Station | ASHRAE 90.1-2010 | Whole Building | Fire Station | 0.71
ASHRAE 90.1-2010Whole BuildingGymnasium | ASHRAE 90.1-2010 | Whole Building | Gymnasium | 1
ASHRAE 90.1-2010Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2010 | Whole Building | Health Care-Clinic | 0.87
ASHRAE 90.1-2010Whole BuildingHospital | ASHRAE 90.1-2010 | Whole Building | Hospital | 1.21
ASHRAE 90.1-2010Whole BuildingHotel | ASHRAE 90.1-2010 | Whole Building | Hotel | 1
ASHRAE 90.1-2010Whole BuildingLibrary | ASHRAE 90.1-2010 | Whole Building | Library | 1.18
ASHRAE 90.1-2010Whole BuildingManufacturing Facility | ASHRAE 90.1-2010 | Whole Building | Manufacturing Facility | 1.11
ASHRAE 90.1-2010Whole BuildingMotel | ASHRAE 90.1-2010 | Whole Building | Motel | 0.88
ASHRAE 90.1-2010Whole BuildingMotion Picture Theater | ASHRAE 90.1-2010 | Whole Building | Motion Picture Theater | 0.83
ASHRAE 90.1-2010Whole BuildingMulti-Family | ASHRAE 90.1-2010 | Whole Building | Multi-Family | 0.6
ASHRAE 90.1-2010Whole BuildingMuseum | ASHRAE 90.1-2010 | Whole Building | Museum | 1.06
ASHRAE 90.1-2010Whole BuildingOffice | ASHRAE 90.1-2010 | Whole Building | Office | 0.9
ASHRAE 90.1-2010Whole BuildingParking Garage | ASHRAE 90.1-2010 | Whole Building | Parking Garage | 0.25
ASHRAE 90.1-2010Whole BuildingPenitentiary | ASHRAE 90.1-2010 | Whole Building | Penitentiary | 0.97
ASHRAE 90.1-2010Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2010 | Whole Building | Performing Arts Theater | 1.39
ASHRAE 90.1-2010Whole BuildingPolice Station | ASHRAE 90.1-2010 | Whole Building | Police Station | 0.96
ASHRAE 90.1-2010Whole BuildingPost Office | ASHRAE 90.1-2010 | Whole Building | Post Office | 0.87
ASHRAE 90.1-2010Whole BuildingReligious Building | ASHRAE 90.1-2010 | Whole Building | Religious Building | 1.05
ASHRAE 90.1-2010Whole BuildingRetail | ASHRAE 90.1-2010 | Whole Building | Retail | 1.4
ASHRAE 90.1-2010Whole BuildingSchool/University | ASHRAE 90.1-2010 | Whole Building | School/University | 0.99
ASHRAE 90.1-2010Whole BuildingSports Arena | ASHRAE 90.1-2010 | Whole Building | Sports Arena | 0.78
ASHRAE 90.1-2010Whole BuildingTown Hall | ASHRAE 90.1-2010 | Whole Building | Town Hall | 0.92
ASHRAE 90.1-2010Whole BuildingTransportation | ASHRAE 90.1-2010 | Whole Building | Transportation | 0.77
ASHRAE 90.1-2010Whole BuildingWarehouse | ASHRAE 90.1-2010 | Whole Building | Warehouse | 0.66
ASHRAE 90.1-2010Whole BuildingWorkshop | ASHRAE 90.1-2010 | Whole Building | Workshop | 1.2
ASHRAE 90.1-2010Office-EnclosedGeneral | ASHRAE 90.1-2010 | Office-Enclosed | General | 1.11
ASHRAE 90.1-2010Office-Open PlanGeneral | ASHRAE 90.1-2010 | Office-Open Plan | General | 0.98
ASHRAE 90.1-2010Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2010 | Conference/Meeting/Multipurpose | General | 1.23
ASHRAE 90.1-2010Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2010 | Classroom/Lecture/Training | General | 1.24
ASHRAE 90.1-2010Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2010 | Classroom/Lecture/Training | For Penitentiary | 1.34
ASHRAE 90.1-2010LobbyGeneral | ASHRAE 90.1-2010 | Lobby | General | 0.9
ASHRAE 90.1-2010LobbyFor Elevator | ASHRAE 90.1-2010 | Lobby | For Elevator | 0.64
ASHRAE 90.1-2010Guest RoomFor Hotel | ASHRAE 90.1-2010 | Guest Room | For Hotel | 1.11
ASHRAE 90.1-2010LobbyFor Performing Arts Theater | ASHRAE 90.1-2010 | Lobby | For Performing Arts Theater | 2
ASHRAE 90.1-2010LobbyFor Motion Picture Theater | ASHRAE 90.1-2010 | Lobby | For Motion Picture Theater | 0.52
ASHRAE 90.1-2010Audience/Seating AreaFor Auditorium | ASHRAE 90.1-2010 | Audience/Seating Area | For Auditorium | 0.79
ASHRAE 90.1-2010Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2010 | Audience/Seating Area | For Gymnasium | 0.43
ASHRAE 90.1-2010Audience/Seating AreaFor Exercise Center | ASHRAE 90.1-2010 | Audience/Seating Area | For Exercise Center
ASHRAE 90.1-2010Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2010 | Audience/Seating Area | For Convention Center | 0.82
ASHRAE 90.1-2010Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2010 | Audience/Seating Area | For Penitentiary | 0.43
ASHRAE 90.1-2010Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2010 | Audience/Seating Area | For Religious Buildings | 1.53
ASHRAE 90.1-2010Audience/Seating AreaFor Sports Arena | ASHRAE 90.1-2010 | Audience/Seating Area | For Sports Arena | 0.43
ASHRAE 90.1-2010Audience/Seating AreaFor Performing Arts Theater | ASHRAE 90.1-2010 | Audience/Seating Area | For Performing Arts Theater | 2.43
ASHRAE 90.1-2010Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2010 | Audience/Seating Area | For Motion Picture Theater | 1.14
ASHRAE 90.1-2010Audience/Seating AreaFor Transportation | ASHRAE 90.1-2010 | Audience/Seating Area | For Transportation | 0.54
ASHRAE 90.1-2010AtriumFirst Forty Feet in Height | ASHRAE 90.1-2010 | Atrium | First Forty Feet in Height | 0.03
ASHRAE 90.1-2010AtriumHeight Above Forty Feet | ASHRAE 90.1-2010 | Atrium | Height Above Forty Feet | 0.02
ASHRAE 90.1-2010Lounge/RecreationGeneral | ASHRAE 90.1-2010 | Lounge/Recreation | General | 0.73
ASHRAE 90.1-2010Lounge/RecreationFor Hospital | ASHRAE 90.1-2010 | Lounge/Recreation | For Hospital | 1.07
ASHRAE 90.1-2004LobbyFor Performing Arts Theater | ASHRAE 90.1-2004 | Lobby | For Performing Arts Theater | 3.3 |  | 290
ASHRAE 90.1-2010Dining AreaGeneral | ASHRAE 90.1-2010 | Dining Area | General | 0.65
ASHRAE 90.1-2010Dining AreaFor Penitentiary | ASHRAE 90.1-2010 | Dining Area | For Penitentiary | 1.07
ASHRAE 90.1-2007LobbyFor Hotel | ASHRAE 90.1-2007 | Lobby | For Hotel | 1.1 |  | 414
ASHRAE 90.1-2010Dining AreaFor Highway Lodging | ASHRAE 90.1-2010 | Dining Area | For Highway Lodging | 0.88
ASHRAE 90.1-2010Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2010 | Dining Area | For Bar Lounge/Leisure Dining | 1.31
ASHRAE 90.1-2010Dining AreaFor Family Dining | ASHRAE 90.1-2010 | Dining Area | For Family Dining | 0.89
ASHRAE 90.1-2010Food PreparationGeneral | ASHRAE 90.1-2010 | Food Preparation | General | 0.99
ASHRAE 90.1-2010LaboratoryFor Classrooms | ASHRAE 90.1-2010 | Laboratory | For Classrooms | 1.28
ASHRAE 90.1-2010LaboratoryFor Medical/Industrial/Research | ASHRAE 90.1-2010 | Laboratory | For Medical/Industrial/Research | 1.81
ASHRAE 90.1-2010RestroomsGeneral | ASHRAE 90.1-2010 | Restrooms | General | 0.98
ASHRAE 90.1-2010Dressing/Fitting RoomFor Performing Arts Theater | ASHRAE 90.1-2010 | Dressing/Fitting Room | For Performing Arts Theater | 0.4
ASHRAE 90.1-2010Dressing/Fitting RoomFor Retail | ASHRAE 90.1-2010 | Dressing/Fitting Room | For Retail | 0.87
ASHRAE 90.1-2010Locker RoomGeneral | ASHRAE 90.1-2010 | Locker Room | General | 0.75
ASHRAE 90.1-2010Corridor/TransitionGeneral | ASHRAE 90.1-2010 | Corridor/Transition | General | 0.66
ASHRAE 90.1-2010Corridor/TransitionFor Hospital | ASHRAE 90.1-2010 | Corridor/Transition | For Hospital | 0.89
ASHRAE 90.1-2010Corridor/TransitionFor Manufacturing Facility | ASHRAE 90.1-2010 | Corridor/Transition | For Manufacturing Facility | 0.41
ASHRAE 90.1-2010StairwayGeneral | ASHRAE 90.1-2010 | Stairway | General | 0.69
ASHRAE 90.1-2010StorageGeneral | ASHRAE 90.1-2010 | Storage | General | 0.63
ASHRAE 90.1-2010Gymnasium/Fitness CenterPlaying Area | ASHRAE 90.1-2010 | Gymnasium/Fitness Center | Playing Area | 1.2
ASHRAE 90.1-2010Gymnasium/Fitness CenterFitness Area | ASHRAE 90.1-2010 | Gymnasium/Fitness Center | Fitness Area | 0.72
ASHRAE 90.1-2010Courthouse/Police Station/PenitentiaryCourtroom | ASHRAE 90.1-2010 | Courthouse/Police Station/Penitentiary | Courtroom | 1.72
ASHRAE 90.1-2010Courthouse/Police Station/PenitentiaryConfinement Cells | ASHRAE 90.1-2010 | Courthouse/Police Station/Penitentiary | Confinement Cells | 1.1
ASHRAE 90.1-2010Courthouse/Police Station/PenitentiaryJudges Chambers | ASHRAE 90.1-2010 | Courthouse/Police Station/Penitentiary | Judges Chambers | 1.17
ASHRAE 90.1-2010Fire StationEngine Room | ASHRAE 90.1-2010 | Fire Station | Engine Room | 0.56
ASHRAE 90.1-2010Fire StationSleeping Quarters | ASHRAE 90.1-2010 | Fire Station | Sleeping Quarters | 0.25
ASHRAE 90.1-2010Post OfficeSorting Area | ASHRAE 90.1-2010 | Post Office | Sorting Area | 0.94
ASHRAE 90.1-2010Convention CenterExhibit Space | ASHRAE 90.1-2010 | Convention Center | Exhibit Space | 1.45
ASHRAE 90.1-2010LibraryCard File and Cataloging | ASHRAE 90.1-2010 | Library | Card File and Cataloging | 0.72
ASHRAE 90.1-2010LibraryStacks | ASHRAE 90.1-2010 | Library | Stacks | 1.71
ASHRAE 90.1-2010LibraryReading Area | ASHRAE 90.1-2010 | Library | Reading Area | 0.93
ASHRAE 90.1-2010HospitalEmergency | ASHRAE 90.1-2010 | Hospital | Emergency | 2.26
ASHRAE 90.1-2010HospitalRecovery | ASHRAE 90.1-2010 | Hospital | Recovery | 1.15
ASHRAE 90.1-2010HospitalNurse Station | ASHRAE 90.1-2010 | Hospital | Nurse Station | 0.87
ASHRAE 90.1-2010HospitalExam/Treatment | ASHRAE 90.1-2010 | Hospital | Exam/Treatment | 1.66
ASHRAE 90.1-2010HospitalPharmacy | ASHRAE 90.1-2010 | Hospital | Pharmacy | 1.14
ASHRAE 90.1-2010HospitalPatient Room | ASHRAE 90.1-2010 | Hospital | Patient Room | 0.62
ASHRAE 90.1-2010HospitalOperating Room | ASHRAE 90.1-2010 | Hospital | Operating Room | 1.89
ASHRAE 90.1-2010HospitalNursery | ASHRAE 90.1-2010 | Hospital | Nursery | 0.88
ASHRAE 90.1-2010HospitalMedical Supply | ASHRAE 90.1-2010 | Hospital | Medical Supply | 1.27
ASHRAE 90.1-2010HospitalPhysical Therapy | ASHRAE 90.1-2010 | Hospital | Physical Therapy | 0.91
ASHRAE 90.1-2010HospitalRadiology/Imaging | ASHRAE 90.1-2010 | Hospital | Radiology/Imaging | 1.32
ASHRAE 90.1-2010HospitalLaundry-Washing | ASHRAE 90.1-2010 | Hospital | Laundry-Washing | 0.6
ASHRAE 90.1-2010AutomotiveService/Repair | ASHRAE 90.1-2010 | Automotive | Service/Repair | 0.67
ASHRAE 90.1-2010ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2010 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.19
ASHRAE 90.1-2010ManufacturingHigh Bay (25-50 ft Floor to Ceiling Height) | ASHRAE 90.1-2010 | Manufacturing | High Bay (25-50 ft Floor to Ceiling Height) | 1.23
ASHRAE 90.1-2010ManufacturingExtra High Bay (>50 ft Floor to Ceiling Height) | ASHRAE 90.1-2010 | Manufacturing | Extra High Bay (>50 ft Floor to Ceiling Height) | 1.05
ASHRAE 90.1-2010ManufacturingDetailed Manufacturing | ASHRAE 90.1-2010 | Manufacturing | Detailed Manufacturing | 1.29
ASHRAE 90.1-2010ManufacturingEquipment Room | ASHRAE 90.1-2010 | Manufacturing | Equipment Room | 0.95
ASHRAE 90.1-2010Guest RoomFor Highway Lodging | ASHRAE 90.1-2010 | Guest Room | For Highway Lodging | 0.75
ASHRAE 90.1-2010LobbyFor Hotel | ASHRAE 90.1-2010 | Lobby | For Hotel | 1.06
ASHRAE 90.1-2010DormitoryLiving Quarters | ASHRAE 90.1-2010 | Dormitory | Living Quarters | 0.38
ASHRAE 90.1-2010MuseumGeneral Exhibition | ASHRAE 90.1-2010 | Museum | General Exhibition | 1.05
ASHRAE 90.1-2010MuseumRestoration | ASHRAE 90.1-2010 | Museum | Restoration | 1.02
ASHRAE 90.1-2010Electrical/MechanicalGeneral | ASHRAE 90.1-2010 | Electrical/Mechanical | General | 0.95
ASHRAE 90.1-2010WorkshopGeneral | ASHRAE 90.1-2010 | Workshop | General | 1.59
ASHRAE 90.1-2010Bank/OfficeBanking Activity Area | ASHRAE 90.1-2010 | Bank/Office | Banking Activity Area | 1.38
ASHRAE 90.1-2010Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2010 | Religious Buildings | Worship Pulpit, Choir | 1.53
ASHRAE 90.1-2010Religious BuildingsFellowship Hall | ASHRAE 90.1-2010 | Religious Buildings | Fellowship Hall | 0.64
ASHRAE 90.1-2010Sales AreaFor Retail | ASHRAE 90.1-2010 | Sales Area | For Retail | 1.68
ASHRAE 90.1-2010Sales AreaGeneral | ASHRAE 90.1-2010 | Sales Area | General | 1.68
ASHRAE 90.1-2010RetailFor Hotel | ASHRAE 90.1-2010 | Retail | For Hotel | 1.4
ASHRAE 90.1-2010RetailMall Concourse | ASHRAE 90.1-2010 | Retail | Mall Concourse | 1.1
ASHRAE 90.1-2010Sports ArenaRing Sports Arena | ASHRAE 90.1-2010 | Sports Arena | Ring Sports Arena | 2.68
ASHRAE 90.1-2010Sports ArenaCourt Sports Arena - Class 4 | ASHRAE 90.1-2010 | Sports Arena | Court Sports Arena - Class 4 | 0.72
ASHRAE 90.1-2010Sports ArenaCourt Sports Arena - Class 3 | ASHRAE 90.1-2010 | Sports Arena | Court Sports Arena - Class 3 | 1.2
ASHRAE 90.1-2010Sports ArenaCourt Sports Arena - Class 2 | ASHRAE 90.1-2010 | Sports Arena | Court Sports Arena - Class 2 | 1.92
ASHRAE 90.1-2010Sports ArenaCourt Sports Arena - Class 1 | ASHRAE 90.1-2010 | Sports Arena | Court Sports Arena - Class 1 | 3.01
ASHRAE 90.1-2010WarehouseFine Material Storage | ASHRAE 90.1-2010 | Warehouse | Fine Material Storage | 0.95
ASHRAE 90.1-2010WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2010 | Warehouse | Medium/Bulky Material Storage | 0.58
ASHRAE 90.1-2010Parking GarageGarage Area | ASHRAE 90.1-2010 | Parking Garage | Garage Area | 0.19
ASHRAE 90.1-2010TransportationAirport-Concourse | ASHRAE 90.1-2010 | Transportation | Airport-Concourse | 0.36
ASHRAE 90.1-2010TransportationAir/Train/Bus-Baggage Area | ASHRAE 90.1-2010 | Transportation | Air/Train/Bus-Baggage Area | 0.76
ASHRAE 90.1-2010TransportationTerminal-Ticket Counter | ASHRAE 90.1-2010 | Transportation | Terminal-Ticket Counter | 1.08
DOE Ref 1980-2004OutpatientAnesthesia | DOE Ref 1980-2004 | Outpatient | Anesthesia | 2.1
DOE Ref Pre-1980OutpatientAnesthesia | DOE Ref Pre-1980 | Outpatient | Anesthesia | 2.1
ASHRAE 90.1-2004MidriseApartmentApartment | ASHRAE 90.1-2004 | MidriseApartment | Apartment | 0.36
DOE Ref Pre-1980MidriseApartmentApartment | DOE Ref Pre-1980 | MidriseApartment | Apartment | 0.36
DOE Ref 1980-2004OfficeAttic | DOE Ref 1980-2004 | Office | Attic | 0
DOE Ref Pre-1980OfficeAttic | DOE Ref Pre-1980 | Office | Attic | 0
DOE Ref 1980-2004SmallHotelAttic | DOE Ref 1980-2004 | SmallHotel | Attic | 0
DOE Ref Pre-1980SmallHotelAttic | DOE Ref Pre-1980 | SmallHotel | Attic | 0
DOE Ref 1980-2004SecondarySchoolAuditorium | DOE Ref 1980-2004 | SecondarySchool | Auditorium | 1.12
DOE Ref Pre-1980SecondarySchoolAuditorium | DOE Ref Pre-1980 | SecondarySchool | Auditorium | 1.12
DOE Ref 1980-2004LargeHotelBasement | DOE Ref 1980-2004 | LargeHotel | Basement | 0.7
DOE Ref Pre-1980LargeHotelBasement | DOE Ref Pre-1980 | LargeHotel | Basement | 0.7
DOE Ref 1980-2004RetailBack_Space | DOE Ref 1980-2004 | Retail | Back_Space | 1.17
DOE Ref Pre-1980RetailBack_Space | DOE Ref Pre-1980 | Retail | Back_Space | 0.77
DOE Ref 1980-2004LargeHotelBanquet | DOE Ref 1980-2004 | LargeHotel | Banquet | 2.56
DOE Ref Pre-1980LargeHotelBanquet | DOE Ref Pre-1980 | LargeHotel | Banquet | 2.77
DOE Ref 1980-2004OutpatientBioHazard | DOE Ref 1980-2004 | Outpatient | BioHazard | 1
DOE Ref Pre-1980OutpatientBioHazard | DOE Ref Pre-1980 | Outpatient | BioHazard | 1
DOE Ref 1980-2004OfficeBreakRoom | DOE Ref 1980-2004 | Office | BreakRoom | 1.884
DOE Ref Pre-1980OfficeBreakRoom | DOE Ref Pre-1980 | Office | BreakRoom | 2.28
DOE Ref 1980-2004WarehouseBulk | DOE Ref 1980-2004 | Warehouse | Bulk | 0.31
DOE Ref Pre-1980WarehouseBulk | DOE Ref Pre-1980 | Warehouse | Bulk | 0.62
DOE Ref 1980-2004LargeHotelCafe | DOE Ref 1980-2004 | LargeHotel | Cafe | 1.46
DOE Ref Pre-1980LargeHotelCafe | DOE Ref Pre-1980 | LargeHotel | Cafe | 3.7
DOE Ref 1980-2004OutpatientCafe | DOE Ref 1980-2004 | Outpatient | Cafe | 1.3
DOE Ref Pre-1980OutpatientCafe | DOE Ref Pre-1980 | Outpatient | Cafe | 1.3
DOE Ref 1980-2004PrimarySchoolCafeteria | DOE Ref 1980-2004 | PrimarySchool | Cafeteria | 1.4
DOE Ref Pre-1980PrimarySchoolCafeteria | DOE Ref Pre-1980 | PrimarySchool | Cafeteria | 1.4
DOE Ref 1980-2004SecondarySchoolCafeteria | DOE Ref 1980-2004 | SecondarySchool | Cafeteria | 1.34
DOE Ref Pre-1980SecondarySchoolCafeteria | DOE Ref Pre-1980 | SecondarySchool | Cafeteria | 1.34
DOE Ref 1980-2004PrimarySchoolClassroom | DOE Ref 1980-2004 | PrimarySchool | Classroom | 2
DOE Ref Pre-1980PrimarySchoolClassroom | DOE Ref Pre-1980 | PrimarySchool | Classroom | 2
DOE Ref 1980-2004SecondarySchoolClassroom | DOE Ref 1980-2004 | SecondarySchool | Classroom | 2
DOE Ref Pre-1980SecondarySchoolClassroom | DOE Ref Pre-1980 | SecondarySchool | Classroom | 2
DOE Ref 1980-2004OutpatientCleanWork | DOE Ref 1980-2004 | Outpatient | CleanWork | 1.3
DOE Ref Pre-1980OutpatientCleanWork | DOE Ref Pre-1980 | Outpatient | CleanWork | 1.3
DOE Ref 1980-2004OfficeClosedOffice | DOE Ref 1980-2004 | Office | ClosedOffice | 1.727
DOE Ref Pre-1980OfficeClosedOffice | DOE Ref Pre-1980 | Office | ClosedOffice | 2.09
DOE Ref 1980-2004OfficeConference | DOE Ref 1980-2004 | Office | Conference | 1.84
DOE Ref Pre-1980OfficeConference | DOE Ref Pre-1980 | Office | Conference | 2.47
DOE Ref 1980-2004OutpatientConference | DOE Ref 1980-2004 | Outpatient | Conference | 1.8
DOE Ref Pre-1980OutpatientConference | DOE Ref Pre-1980 | Outpatient | Conference | 1.8
DOE Ref 1980-2004HospitalCorridor | DOE Ref 1980-2004 | Hospital | Corridor | 1.36
DOE Ref Pre-1980HospitalCorridor | DOE Ref Pre-1980 | Hospital | Corridor | 1.32
DOE Ref 1980-2004LargeHotelCorridor | DOE Ref 1980-2004 | LargeHotel | Corridor | 1.22
DOE Ref Pre-1980LargeHotelCorridor | DOE Ref Pre-1980 | LargeHotel | Corridor | 0.6
ASHRAE 90.1-2010MidriseApartmentCorridor | ASHRAE 90.1-2010 | MidriseApartment | Corridor | 0.792
ASHRAE 90.1-2004MidriseApartmentCorridor | ASHRAE 90.1-2004 | MidriseApartment | Corridor | 0.5
DOE Ref Pre-1980MidriseApartmentCorridor | DOE Ref Pre-1980 | MidriseApartment | Corridor | 0.92
DOE Ref 1980-2004OfficeCorridor | DOE Ref 1980-2004 | Office | Corridor | 0.785
DOE Ref Pre-1980OfficeCorridor | DOE Ref Pre-1980 | Office | Corridor | 0.95
DOE Ref 1980-2004PrimarySchoolCorridor | DOE Ref 1980-2004 | PrimarySchool | Corridor | 0.9
DOE Ref Pre-1980PrimarySchoolCorridor | DOE Ref Pre-1980 | PrimarySchool | Corridor | 0.9
DOE Ref 1980-2004SecondarySchoolCorridor | DOE Ref 1980-2004 | SecondarySchool | Corridor | 0.86
DOE Ref Pre-1980SecondarySchoolCorridor | DOE Ref Pre-1980 | SecondarySchool | Corridor | 0.86
DOE Ref 1980-2004SmallHotelCorridor | DOE Ref 1980-2004 | SmallHotel | Corridor | 0.86
DOE Ref Pre-1980SmallHotelCorridor | DOE Ref Pre-1980 | SmallHotel | Corridor | 0.86
DOE Ref 1980-2004SuperMarketDeli/Bakery | DOE Ref 1980-2004 | SuperMarket | Deli/Bakery | 2.78
DOE Ref Pre-1980SuperMarketDeli/Bakery | DOE Ref Pre-1980 | SuperMarket | Deli/Bakery | 5.04
DOE Ref 1980-2004FullServiceRestaurantDining | DOE Ref 1980-2004 | FullServiceRestaurant | Dining | 2.54
DOE Ref Pre-1980FullServiceRestaurantDining | DOE Ref Pre-1980 | FullServiceRestaurant | Dining | 2.54
DOE Ref 1980-2004HospitalDining | DOE Ref 1980-2004 | Hospital | Dining | 2.58
DOE Ref Pre-1980HospitalDining | DOE Ref Pre-1980 | Hospital | Dining | 2.77
DOE Ref 1980-2004QuickServiceRestaurantDining | DOE Ref 1980-2004 | QuickServiceRestaurant | Dining | 1.44
DOE Ref Pre-1980QuickServiceRestaurantDining | DOE Ref Pre-1980 | QuickServiceRestaurant | Dining | 3.7
DOE Ref 1980-2004OutpatientDressingRoom | DOE Ref 1980-2004 | Outpatient | DressingRoom | 1.8
DOE Ref Pre-1980OutpatientDressingRoom | DOE Ref Pre-1980 | Outpatient | DressingRoom | 1.8
DOE Ref 1980-2004SuperMarketDryStorage | DOE Ref 1980-2004 | SuperMarket | DryStorage | 1.1
DOE Ref Pre-1980SuperMarketDryStorage | DOE Ref Pre-1980 | SuperMarket | DryStorage | 0.77
DOE Ref 1980-2004OfficeElec/MechRoom | DOE Ref 1980-2004 | Office | Elec/MechRoom | 2.355
DOE Ref Pre-1980OfficeElec/MechRoom | DOE Ref Pre-1980 | Office | Elec/MechRoom | 2.85
DOE Ref 1980-2004OutpatientElec/MechRoom | DOE Ref 1980-2004 | Outpatient | Elec/MechRoom | 0.7
DOE Ref Pre-1980OutpatientElec/MechRoom | DOE Ref Pre-1980 | Outpatient | Elec/MechRoom | 0.7
DOE Ref 1980-2004SmallHotelElec/MechRoom | DOE Ref 1980-2004 | SmallHotel | Elec/MechRoom | 0
DOE Ref Pre-1980SmallHotelElec/MechRoom | DOE Ref Pre-1980 | SmallHotel | Elec/MechRoom | 0
DOE Ref 1980-2004SmallHotelElevatorCore | DOE Ref 1980-2004 | SmallHotel | ElevatorCore | 0
DOE Ref Pre-1980SmallHotelElevatorCore | DOE Ref Pre-1980 | SmallHotel | ElevatorCore | 0
DOE Ref 1980-2004RetailEntry | DOE Ref 1980-2004 | Retail | Entry | 3.37
DOE Ref Pre-1980RetailEntry | DOE Ref Pre-1980 | Retail | Entry | 5.04
DOE Ref 1980-2004HospitalER_Exam | DOE Ref 1980-2004 | Hospital | ER_Exam | 3.84
DOE Ref Pre-1980HospitalER_Exam | DOE Ref Pre-1980 | Hospital | ER_Exam | 5
DOE Ref 1980-2004HospitalER_NurseStn | DOE Ref 1980-2004 | Hospital | ER_NurseStn | 1.66
DOE Ref Pre-1980HospitalER_NurseStn | DOE Ref Pre-1980 | Hospital | ER_NurseStn | 1.64
DOE Ref 1980-2004HospitalER_Trauma | DOE Ref 1980-2004 | Hospital | ER_Trauma | 3.84
DOE Ref Pre-1980HospitalER_Trauma | DOE Ref Pre-1980 | Hospital | ER_Trauma | 5
DOE Ref 1980-2004HospitalER_Triage | DOE Ref 1980-2004 | Hospital | ER_Triage | 3.84
DOE Ref Pre-1980HospitalER_Triage | DOE Ref Pre-1980 | Hospital | ER_Triage | 5
DOE Ref 1980-2004OutpatientExam | DOE Ref 1980-2004 | Outpatient | Exam | 1.6
DOE Ref Pre-1980OutpatientExam | DOE Ref Pre-1980 | Outpatient | Exam | 1.6
DOE Ref 1980-2004SmallHotelExercise | DOE Ref 1980-2004 | SmallHotel | Exercise | 1.37
DOE Ref Pre-1980SmallHotelExercise | DOE Ref Pre-1980 | SmallHotel | Exercise | 1.37
DOE Ref 1980-2004WarehouseFine | DOE Ref 1980-2004 | Warehouse | Fine | 1.08
DOE Ref Pre-1980WarehouseFine | DOE Ref Pre-1980 | Warehouse | Fine | 1.08
DOE Ref 1980-2004SmallHotelGuestLounge | DOE Ref 1980-2004 | SmallHotel | GuestLounge | 1.31
DOE Ref Pre-1980SmallHotelGuestLounge | DOE Ref Pre-1980 | SmallHotel | GuestLounge | 1.31
DOE Ref 1980-2004LargeHotelGuestRoom | DOE Ref 1980-2004 | LargeHotel | GuestRoom | 1.77
DOE Ref Pre-1980LargeHotelGuestRoom | DOE Ref Pre-1980 | LargeHotel | GuestRoom | 1.4
DOE Ref 1980-2004SmallHotelGuestRoom | DOE Ref 1980-2004 | SmallHotel | GuestRoom | 1.74
DOE Ref Pre-1980SmallHotelGuestRoom | DOE Ref Pre-1980 | SmallHotel | GuestRoom | 1.74
DOE Ref 1980-2004PrimarySchoolGym | DOE Ref 1980-2004 | PrimarySchool | Gym | 1.07
DOE Ref Pre-1980PrimarySchoolGym | DOE Ref Pre-1980 | PrimarySchool | Gym | 1.07
DOE Ref 1980-2004SecondarySchoolGym | DOE Ref 1980-2004 | SecondarySchool | Gym | 1.06
DOE Ref Pre-1980SecondarySchoolGym | DOE Ref Pre-1980 | SecondarySchool | Gym | 1.06
DOE Ref 1980-2004OutpatientHall | DOE Ref 1980-2004 | Outpatient | Hall | 0.8
DOE Ref Pre-1980OutpatientHall | DOE Ref Pre-1980 | Outpatient | Hall | 0.8
DOE Ref 1980-2004HospitalICU_NurseStn | DOE Ref 1980-2004 | Hospital | ICU_NurseStn | 1.71
DOE Ref Pre-1980HospitalICU_NurseStn | DOE Ref Pre-1980 | Hospital | ICU_NurseStn | 1.64
DOE Ref 1980-2004HospitalICU_Open | DOE Ref 1980-2004 | Hospital | ICU_Open | 3.84
DOE Ref Pre-1980HospitalICU_Open | DOE Ref Pre-1980 | Hospital | ICU_Open | 4.22
DOE Ref 1980-2004HospitalICU_PatRm | DOE Ref 1980-2004 | Hospital | ICU_PatRm | 3.84
DOE Ref Pre-1980HospitalICU_PatRm | DOE Ref Pre-1980 | Hospital | ICU_PatRm | 4.22
DOE Ref 1980-2004OfficeIT_Room | DOE Ref 1980-2004 | Office | IT_Room | 1.55
DOE Ref Pre-1980OfficeIT_Room | DOE Ref Pre-1980 | Office | IT_Room | 2.09
DOE Ref 1980-2004OutpatientIT_Room | DOE Ref 1980-2004 | Outpatient | IT_Room | 1.8
DOE Ref Pre-1980OutpatientIT_Room | DOE Ref Pre-1980 | Outpatient | IT_Room | 1.8
DOE Ref 1980-2004OutpatientJanitor | DOE Ref 1980-2004 | Outpatient | Janitor | 1
DOE Ref Pre-1980OutpatientJanitor | DOE Ref Pre-1980 | Outpatient | Janitor | 1
DOE Ref 1980-2004FullServiceRestaurantKitchen | DOE Ref 1980-2004 | FullServiceRestaurant | Kitchen | 1.52
DOE Ref Pre-1980FullServiceRestaurantKitchen | DOE Ref Pre-1980 | FullServiceRestaurant | Kitchen | 1.52
DOE Ref 1980-2004HospitalKitchen | DOE Ref 1980-2004 | Hospital | Kitchen | 1.42
DOE Ref Pre-1980HospitalKitchen | DOE Ref Pre-1980 | Hospital | Kitchen | 2.24
DOE Ref 1980-2004LargeHotelKitchen | DOE Ref 1980-2004 | LargeHotel | Kitchen | 1.56
DOE Ref Pre-1980LargeHotelKitchen | DOE Ref Pre-1980 | LargeHotel | Kitchen | 2.24
DOE Ref 1980-2004PrimarySchoolKitchen | DOE Ref 1980-2004 | PrimarySchool | Kitchen | 1.6
DOE Ref Pre-1980PrimarySchoolKitchen | DOE Ref Pre-1980 | PrimarySchool | Kitchen | 1.6
DOE Ref 1980-2004QuickServiceRestaurantKitchen | DOE Ref 1980-2004 | QuickServiceRestaurant | Kitchen | 1.55
DOE Ref Pre-1980QuickServiceRestaurantKitchen | DOE Ref Pre-1980 | QuickServiceRestaurant | Kitchen | 2.24
DOE Ref 1980-2004SecondarySchoolKitchen | DOE Ref 1980-2004 | SecondarySchool | Kitchen | 1.56
DOE Ref Pre-1980SecondarySchoolKitchen | DOE Ref Pre-1980 | SecondarySchool | Kitchen | 1.56
DOE Ref 1980-2004HospitalLab | DOE Ref 1980-2004 | Hospital | Lab | 2.1
DOE Ref Pre-1980HospitalLab | DOE Ref Pre-1980 | Hospital | Lab | 1.9
DOE Ref 1980-2004LargeHotelLaundry | DOE Ref 1980-2004 | LargeHotel | Laundry | 1.14
DOE Ref Pre-1980LargeHotelLaundry | DOE Ref Pre-1980 | LargeHotel | Laundry | 0.7
DOE Ref 1980-2004SmallHotelLaundry | DOE Ref 1980-2004 | SmallHotel | Laundry | 1.04
DOE Ref Pre-1980SmallHotelLaundry | DOE Ref Pre-1980 | SmallHotel | Laundry | 1.04
DOE Ref 1980-2004PrimarySchoolLibrary | DOE Ref 1980-2004 | PrimarySchool | Library | 2.11
DOE Ref Pre-1980PrimarySchoolLibrary | DOE Ref Pre-1980 | PrimarySchool | Library | 2.11
DOE Ref 1980-2004SecondarySchoolLibrary | DOE Ref 1980-2004 | SecondarySchool | Library | 1.52
DOE Ref Pre-1980SecondarySchoolLibrary | DOE Ref Pre-1980 | SecondarySchool | Library | 1.52
DOE Ref 1980-2004HospitalLobby | DOE Ref 1980-2004 | Hospital | Lobby | 1.46
DOE Ref Pre-1980HospitalLobby | DOE Ref Pre-1980 | Hospital | Lobby | 1.49
DOE Ref 1980-2004LargeHotelLobby | DOE Ref 1980-2004 | LargeHotel | Lobby | 1.88
DOE Ref Pre-1980LargeHotelLobby | DOE Ref Pre-1980 | LargeHotel | Lobby | 1.45
DOE Ref 1980-2004OfficeLobby | DOE Ref 1980-2004 | Office | Lobby | 2.04
DOE Ref Pre-1980OfficeLobby | DOE Ref Pre-1980 | Office | Lobby | 2.47
DOE Ref 1980-2004OutpatientLobby | DOE Ref 1980-2004 | Outpatient | Lobby | 1
DOE Ref Pre-1980OutpatientLobby | DOE Ref Pre-1980 | Outpatient | Lobby | 1
DOE Ref 1980-2004PrimarySchoolLobby | DOE Ref 1980-2004 | PrimarySchool | Lobby | 1.14
DOE Ref Pre-1980PrimarySchoolLobby | DOE Ref Pre-1980 | PrimarySchool | Lobby | 1.14
DOE Ref 1980-2004SecondarySchoolLobby | DOE Ref 1980-2004 | SecondarySchool | Lobby | 1.11
DOE Ref Pre-1980SecondarySchoolLobby | DOE Ref Pre-1980 | SecondarySchool | Lobby | 1.11
DOE Ref 1980-2004OutpatientLockerRoom | DOE Ref 1980-2004 | Outpatient | LockerRoom | 0.9
DOE Ref Pre-1980OutpatientLockerRoom | DOE Ref Pre-1980 | Outpatient | LockerRoom | 0.9
DOE Ref 1980-2004OutpatientLounge | DOE Ref 1980-2004 | Outpatient | Lounge | 0.9
DOE Ref Pre-1980OutpatientLounge | DOE Ref Pre-1980 | Outpatient | Lounge | 0.9
DOE Ref 1980-2004LargeHotelMechanical | DOE Ref 1980-2004 | LargeHotel | Mechanical | 0.8
DOE Ref Pre-1980LargeHotelMechanical | DOE Ref Pre-1980 | LargeHotel | Mechanical | 0.6
DOE Ref 1980-2004PrimarySchoolMechanical | DOE Ref 1980-2004 | PrimarySchool | Mechanical | 0.77
DOE Ref Pre-1980PrimarySchoolMechanical | DOE Ref Pre-1980 | PrimarySchool | Mechanical | 0.77
DOE Ref 1980-2004SecondarySchoolMechanical | DOE Ref 1980-2004 | SecondarySchool | Mechanical | 0.75
DOE Ref Pre-1980SecondarySchoolMechanical | DOE Ref Pre-1980 | SecondarySchool | Mechanical | 0.75
DOE Ref 1980-2004SmallHotelMechanical | DOE Ref 1980-2004 | SmallHotel | Mechanical | 0.96
DOE Ref Pre-1980SmallHotelMechanical | DOE Ref Pre-1980 | SmallHotel | Mechanical | 0.96
DOE Ref 1980-2004OutpatientMedGas | DOE Ref 1980-2004 | Outpatient | MedGas | 1
DOE Ref Pre-1980OutpatientMedGas | DOE Ref Pre-1980 | Outpatient | MedGas | 1
DOE Ref 1980-2004SmallHotelMeeting | DOE Ref 1980-2004 | SmallHotel | Meeting | 2.13
DOE Ref Pre-1980SmallHotelMeeting | DOE Ref Pre-1980 | SmallHotel | Meeting | 2.13
DOE Ref 1980-2004OutpatientMRI | DOE Ref 1980-2004 | Outpatient | MRI | 2.1
DOE Ref Pre-1980OutpatientMRI | DOE Ref Pre-1980 | Outpatient | MRI | 2.1
DOE Ref 1980-2004OutpatientMRI_Control | DOE Ref 1980-2004 | Outpatient | MRI_Control | 2.1
DOE Ref Pre-1980OutpatientMRI_Control | DOE Ref Pre-1980 | Outpatient | MRI_Control | 2.1
DOE Ref 1980-2004OutpatientNurseStation | DOE Ref 1980-2004 | Outpatient | NurseStation | 2.1
DOE Ref Pre-1980OutpatientNurseStation | DOE Ref Pre-1980 | Outpatient | NurseStation | 2.1
DOE Ref 1980-2004HospitalNurseStn | DOE Ref 1980-2004 | Hospital | NurseStn | 1.46
DOE Ref Pre-1980HospitalNurseStn | DOE Ref Pre-1980 | Hospital | NurseStn | 1.53
DOE Ref 1980-2004HospitalOffice | DOE Ref 1980-2004 | Hospital | Office | 2.4
DOE Ref Pre-1980HospitalOffice | DOE Ref Pre-1980 | Hospital | Office | 1.9
ASHRAE 90.1-2004MidriseApartmentOffice | ASHRAE 90.1-2004 | MidriseApartment | Office | 1.11
DOE Ref Pre-1980MidriseApartmentOffice | DOE Ref Pre-1980 | MidriseApartment | Office | 2.04
DOE Ref 1980-2004OutpatientOffice | DOE Ref 1980-2004 | Outpatient | Office | 1.8
DOE Ref Pre-1980OutpatientOffice | DOE Ref Pre-1980 | Outpatient | Office | 1.8
DOE Ref 1980-2004PrimarySchoolOffice | DOE Ref 1980-2004 | PrimarySchool | Office | 1.89
DOE Ref Pre-1980PrimarySchoolOffice | DOE Ref Pre-1980 | PrimarySchool | Office | 1.89
DOE Ref 1980-2004SecondarySchoolOffice | DOE Ref 1980-2004 | SecondarySchool | Office | 1.87
DOE Ref Pre-1980SecondarySchoolOffice | DOE Ref Pre-1980 | SecondarySchool | Office | 1.87
DOE Ref 1980-2004SmallHotelOffice | DOE Ref 1980-2004 | SmallHotel | Office | 2.01
DOE Ref Pre-1980SmallHotelOffice | DOE Ref Pre-1980 | SmallHotel | Office | 2.01
DOE Ref 1980-2004SuperMarketOffice | DOE Ref 1980-2004 | SuperMarket | Office | 1.98
DOE Ref Pre-1980SuperMarketOffice | DOE Ref Pre-1980 | SuperMarket | Office | 2.9
DOE Ref 1980-2004WarehouseOffice | DOE Ref 1980-2004 | Warehouse | Office | 2.02
DOE Ref Pre-1980WarehouseOffice | DOE Ref Pre-1980 | Warehouse | Office | 2.9
DOE Ref 1980-2004OfficeOpenOffice | DOE Ref 1980-2004 | Office | OpenOffice | 1.73
DOE Ref Pre-1980OfficeOpenOffice | DOE Ref Pre-1980 | Office | OpenOffice | 2.09
DOE Ref 1980-2004HospitalOR | DOE Ref 1980-2004 | Hospital | OR | 9.75
DOE Ref Pre-1980HospitalOR | DOE Ref Pre-1980 | Hospital | OR | 10
DOE Ref 1980-2004OutpatientOR | DOE Ref 1980-2004 | Outpatient | OR | 7
DOE Ref Pre-1980OutpatientOR | DOE Ref Pre-1980 | Outpatient | OR | 7
DOE Ref 1980-2004OutpatientPACU | DOE Ref 1980-2004 | Outpatient | PACU | 2.3
DOE Ref Pre-1980OutpatientPACU | DOE Ref Pre-1980 | Outpatient | PACU | 2.3
DOE Ref 1980-2004HospitalPatCorridor | DOE Ref 1980-2004 | Hospital | PatCorridor | 1.36
DOE Ref Pre-1980HospitalPatCorridor | DOE Ref Pre-1980 | Hospital | PatCorridor | 1.32
DOE Ref 1980-2004HospitalPatRoom | DOE Ref 1980-2004 | Hospital | PatRoom | 2.19
DOE Ref Pre-1980HospitalPatRoom | DOE Ref Pre-1980 | Hospital | PatRoom | 1.85
DOE Ref 1980-2004OutpatientPhysicalTherapy | DOE Ref 1980-2004 | Outpatient | PhysicalTherapy | 1.6
DOE Ref Pre-1980OutpatientPhysicalTherapy | DOE Ref Pre-1980 | Outpatient | PhysicalTherapy | 1.6
DOE Ref 1980-2004HospitalPhysTherapy | DOE Ref 1980-2004 | Hospital | PhysTherapy | 2.5
DOE Ref Pre-1980HospitalPhysTherapy | DOE Ref Pre-1980 | Hospital | PhysTherapy | 2.51
DOE Ref 1980-2004RetailPoint_of_Sale | DOE Ref 1980-2004 | Retail | Point_of_Sale | 3.37
DOE Ref Pre-1980RetailPoint_of_Sale | DOE Ref Pre-1980 | Retail | Point_of_Sale | 5.04
DOE Ref 1980-2004OutpatientPreOp | DOE Ref 1980-2004 | Outpatient | PreOp | 1.4
DOE Ref Pre-1980OutpatientPreOp | DOE Ref Pre-1980 | Outpatient | PreOp | 1.4
DOE Ref 1980-2004OfficePrintRoom | DOE Ref 1980-2004 | Office | PrintRoom | 1.55
DOE Ref Pre-1980OfficePrintRoom | DOE Ref Pre-1980 | Office | PrintRoom | 1.881
DOE Ref 1980-2004OutpatientProcedureRoom | DOE Ref 1980-2004 | Outpatient | ProcedureRoom | 1.6
DOE Ref Pre-1980OutpatientProcedureRoom | DOE Ref Pre-1980 | Outpatient | ProcedureRoom | 1.6
DOE Ref 1980-2004SmallHotelPublicRestroom | DOE Ref 1980-2004 | SmallHotel | PublicRestroom | 1.1
DOE Ref Pre-1980SmallHotelPublicRestroom | DOE Ref Pre-1980 | SmallHotel | PublicRestroom | 1.1
DOE Ref 1980-2004HospitalRadiology | DOE Ref 1980-2004 | Hospital | Radiology | 2.21
DOE Ref Pre-1980HospitalRadiology | DOE Ref Pre-1980 | Hospital | Radiology | 3.3
DOE Ref 1980-2004OfficeRestroom | DOE Ref 1980-2004 | Office | Restroom | 1.41
DOE Ref Pre-1980OfficeRestroom | DOE Ref Pre-1980 | Office | Restroom | 1.71
DOE Ref 1980-2004PrimarySchoolRestroom | DOE Ref 1980-2004 | PrimarySchool | Restroom | 0.9
DOE Ref Pre-1980PrimarySchoolRestroom | DOE Ref Pre-1980 | PrimarySchool | Restroom | 0.9
DOE Ref 1980-2004SecondarySchoolRestroom | DOE Ref 1980-2004 | SecondarySchool | Restroom | 0.89
DOE Ref Pre-1980SecondarySchoolRestroom | DOE Ref Pre-1980 | SecondarySchool | Restroom | 0.89
DOE Ref 1980-2004LargeHotelRetail | DOE Ref 1980-2004 | LargeHotel | Retail | 3.54
DOE Ref Pre-1980LargeHotelRetail | DOE Ref Pre-1980 | LargeHotel | Retail | 5.04
DOE Ref 1980-2004RetailRetail | DOE Ref 1980-2004 | Retail | Retail | 3.37
DOE Ref Pre-1980RetailRetail | DOE Ref Pre-1980 | Retail | Retail | 5.04
DOE Ref 1980-2004SuperMarketSales/Produce | DOE Ref 1980-2004 | SuperMarket | Sales/Produce | 2.78
DOE Ref Pre-1980SuperMarketSales/Produce | DOE Ref Pre-1980 | SuperMarket | Sales/Produce | 5.04
DOE Ref 1980-2004OutpatientSoil Work | DOE Ref 1980-2004 | Outpatient | Soil Work | 0.9
DOE Ref Pre-1980OutpatientSoil Work | DOE Ref Pre-1980 | Outpatient | Soil Work | 0.9
DOE Ref 1980-2004SmallHotelStaffLounge | DOE Ref 1980-2004 | SmallHotel | StaffLounge | 1.65
DOE Ref Pre-1980SmallHotelStaffLounge | DOE Ref Pre-1980 | SmallHotel | StaffLounge | 1.65
DOE Ref 1980-2004OfficeStair | DOE Ref 1980-2004 | Office | Stair | 0.942
DOE Ref Pre-1980OfficeStair | DOE Ref Pre-1980 | Office | Stair | 1.14
DOE Ref 1980-2004OutpatientStair | DOE Ref 1980-2004 | Outpatient | Stair | 0.8
DOE Ref Pre-1980OutpatientStair | DOE Ref Pre-1980 | Outpatient | Stair | 0.8
DOE Ref 1980-2004SmallHotelStair | DOE Ref 1980-2004 | SmallHotel | Stair | 0.82
DOE Ref Pre-1980SmallHotelStair | DOE Ref Pre-1980 | SmallHotel | Stair | 0.82
DOE Ref 1980-2004LargeHotelStorage | DOE Ref 1980-2004 | LargeHotel | Storage | 0.37
DOE Ref Pre-1980LargeHotelStorage | DOE Ref Pre-1980 | LargeHotel | Storage | 0.62
DOE Ref 1980-2004OfficeStorage | DOE Ref 1980-2004 | Office | Storage | 1.27
DOE Ref Pre-1980OfficeStorage | DOE Ref Pre-1980 | Office | Storage | 1.539
DOE Ref 1980-2004SmallHotelStorage | DOE Ref 1980-2004 | SmallHotel | Storage | 0.45
DOE Ref Pre-1980SmallHotelStorage | DOE Ref Pre-1980 | SmallHotel | Storage | 0.45
DOE Ref 1980-2004OutpatientToilet | DOE Ref 1980-2004 | Outpatient | Toilet | 0.8
DOE Ref Pre-1980OutpatientToilet | DOE Ref Pre-1980 | Outpatient | Toilet | 0.8
DOE Ref 1980-2004OfficeVending | DOE Ref 1980-2004 | Office | Vending | 1.57
DOE Ref Pre-1980OfficeVending | DOE Ref Pre-1980 | Office | Vending | 0.95
DOE Ref 1980-2004StripMallWholeBuilding | DOE Ref 1980-2004 | StripMall | WholeBuilding | 3.58
DOE Ref Pre-1980StripMallWholeBuilding | DOE Ref Pre-1980 | StripMall | WholeBuilding | 4.81
DOE Ref 1980-2004OfficeWholeBuilding - Lg Office | DOE Ref 1980-2004 | Office | WholeBuilding - Lg Office | 1
DOE Ref Pre-1980OfficeWholeBuilding - Lg Office | DOE Ref Pre-1980 | Office | WholeBuilding - Lg Office | 1.5
DOE Ref 1980-2004OfficeWholeBuilding - Md Office | DOE Ref 1980-2004 | Office | WholeBuilding - Md Office | 1.57
DOE Ref Pre-1980OfficeWholeBuilding - Md Office | DOE Ref Pre-1980 | Office | WholeBuilding - Md Office | 1.9
DOE Ref 1980-2004OfficeWholeBuilding - Sm Office | DOE Ref 1980-2004 | Office | WholeBuilding - Sm Office | 1.81
DOE Ref Pre-1980OfficeWholeBuilding - Sm Office | DOE Ref Pre-1980 | Office | WholeBuilding - Sm Office | 1.81
DOE Ref 1980-2004OutpatientXray | DOE Ref 1980-2004 | Outpatient | Xray | 2.1
DOE Ref Pre-1980OutpatientXray | DOE Ref Pre-1980 | Outpatient | Xray | 2.1
NECB 2011Automotive facilityWholeBuilding | NECB 2011 | Automotive facility | WholeBuilding | 0.81754
NECB 2011Convention centreWholeBuilding | NECB 2011 | Convention centre | WholeBuilding | 1.0777
NECB 2011CourthouseWholeBuilding | NECB 2011 | Courthouse | WholeBuilding | 1.0498
NECB 2011Dining - bar/loungeWholeBuilding | NECB 2011 | Dining - bar/lounge | WholeBuilding | 0.99405
NECB 2011Dining - cafeteriaWholeBuilding | NECB 2011 | Dining - cafeteria | WholeBuilding | 0.90115
NECB 2011Dining - familyWholeBuilding | NECB 2011 | Dining - family | WholeBuilding | 0.89186
NECB 2011DormitoryWholeBuilding | NECB 2011 | Dormitory | WholeBuilding | 0.61315
NECB 2011Exercise centreWholeBuilding | NECB 2011 | Exercise centre | WholeBuilding | 0.88257
NECB 2011Fire stationWholeBuilding | NECB 2011 | Fire station | WholeBuilding | 0.70606
NECB 2011GymnasiumWholeBuilding | NECB 2011 | Gymnasium | WholeBuilding | 1.0033
NECB 2011Health-care clinicWholeBuilding | NECB 2011 | Health-care clinic | WholeBuilding | 0.87328
NECB 2011HospitalWholeBuilding | NECB 2011 | Hospital | WholeBuilding | 1.2077
NECB 2011HotelWholeBuilding | NECB 2011 | Hotel | WholeBuilding | 1.0033
NECB 2011LibraryWholeBuilding | NECB 2011 | Library | WholeBuilding | 1.1799
NECB 2011Manufacturing facilityWholeBuilding | NECB 2011 | Manufacturing facility | WholeBuilding | 1.1055
NECB 2011MotelWholeBuilding | NECB 2011 | Motel | WholeBuilding | 0.88257
NECB 2011Motion picture theatreWholeBuilding | NECB 2011 | Motion picture theatre | WholeBuilding | 0.82683
NECB 2011Multi-unit residentialWholeBuilding | NECB 2011 | Multi-unit residential | WholeBuilding | 0.60386
NECB 2011MuseumWholeBuilding | NECB 2011 | Museum | WholeBuilding | 1.0591
NECB 2011OfficeWholeBuilding | NECB 2011 | Office | WholeBuilding | 0.90115
NECB 2011Parking garageWholeBuilding | NECB 2011 | Parking garage | WholeBuilding | 0.25084
NECB 2011PenitentiaryWholeBuilding | NECB 2011 | Penitentiary | WholeBuilding | 0.96618
NECB 2011Performing arts theatreWholeBuilding | NECB 2011 | Performing arts theatre | WholeBuilding | 1.3935
NECB 2011Police stationWholeBuilding | NECB 2011 | Police station | WholeBuilding | 0.95689
NECB 2011Post officeWholeBuilding | NECB 2011 | Post office | WholeBuilding | 0.87328
NECB 2011ReligiousWholeBuilding | NECB 2011 | Religious | WholeBuilding | 1.0498
NECB 2011RetailWholeBuilding | NECB 2011 | Retail | WholeBuilding | 1.4028
NECB 2011School/universityWholeBuilding | NECB 2011 | School/university | WholeBuilding | 0.99405
NECB 2011Sports arenaWholeBuilding | NECB 2011 | Sports arena | WholeBuilding | 0.78038
NECB 2011Town hallWholeBuilding | NECB 2011 | Town hall | WholeBuilding | 0.91973
NECB 2011TransportationWholeBuilding | NECB 2011 | Transportation | WholeBuilding | 0.77109
NECB 2011WarehouseWholeBuilding | NECB 2011 | Warehouse | WholeBuilding | 0.65961
NECB 2011WorkshopWholeBuilding | NECB 2011 | Workshop | WholeBuilding | 1.1984
NECB 2011Space FunctionDwelling Unit(s) | NECB 2011 | Space Function | Dwelling Unit(s) | 0.46451
NECB 2011Space FunctionAtrium - H < 13m | NECB 2011 | Space Function | Atrium - H < 13m | 0
NECB 2011Space FunctionAtrium - H > 13m | NECB 2011 | Space Function | Atrium - H > 13m | 0
NECB 2011Space FunctionAudience - auditorium | NECB 2011 | Space Function | Audience - auditorium | 0.78967
NECB 2011Space FunctionAudience - performance arts | NECB 2011 | Space Function | Audience - performance arts | 2.434
NECB 2011Space FunctionAudience - motion picture | NECB 2011 | Space Function | Audience - motion picture | 1.1427
NECB 2011Space FunctionClassroom/lecture/training | NECB 2011 | Space Function | Classroom/lecture/training | 1.2356
NECB 2011Space FunctionConf./meet./multi-purpose | NECB 2011 | Space Function | Conf./meet./multi-purpose | 1.2263
NECB 2011Space FunctionCorr. >= 2.4m wide | NECB 2011 | Space Function | Corr. >= 2.4m wide | 0.65961
NECB 2011Space FunctionCorr. < 2.4m wide | NECB 2011 | Space Function | Corr. < 2.4m wide | 0.78038
NECB 2011Space FunctionDining - bar lounge/leisure | NECB 2011 | Space Function | Dining - bar lounge/leisure | 1.3099
NECB 2011Space FunctionDining - family space | NECB 2011 | Space Function | Dining - family space | 0.89186
NECB 2011Space FunctionDining - other | NECB 2011 | Space Function | Dining - other | 0.65032
NECB 2011Space FunctionDress./fitt. - performance arts | NECB 2011 | Space Function | Dress./fitt. - performance arts | 0.39948
NECB 2011Space FunctionElectrical/Mechanical | NECB 2011 | Space Function | Electrical/Mechanical | 1.2356
NECB 2011Space FunctionFood preparation | NECB 2011 | Space Function | Food preparation | 0.99405
NECB 2011Space FunctionLab - classrooms | NECB 2011 | Space Function | Lab - classrooms | 1.5979
NECB 2011Space FunctionLab - research | NECB 2011 | Space Function | Lab - research | 2.1925
NECB 2011Space FunctionLobby - elevator | NECB 2011 | Space Function | Lobby - elevator | 0.64103
NECB 2011Space FunctionLobby - performance arts | NECB 2011 | Space Function | Lobby - performance arts | 1.9974
NECB 2011Space FunctionLobby - motion picture | NECB 2011 | Space Function | Lobby - motion picture | 0.52025
NECB 2011Space FunctionLobby - other | NECB 2011 | Space Function | Lobby - other | 0.90115
NECB 2011Space FunctionLocker room | NECB 2011 | Space Function | Locker room | 0.91044
NECB 2011Space FunctionLounge/recreation | NECB 2011 | Space Function | Lounge/recreation | 0.87328
NECB 2011Space FunctionOffice - enclosed | NECB 2011 | Space Function | Office - enclosed | 1.1055
NECB 2011Space FunctionOffice - open plan | NECB 2011 | Space Function | Office - open plan | 1.0219
NECB 2011Space FunctionSales area | NECB 2011 | Space Function | Sales area | 1.6815
NECB 2011Space FunctionStairway | NECB 2011 | Space Function | Stairway | 0.68748
NECB 2011Space FunctionStorage area | NECB 2011 | Space Function | Storage area | 0.63174
NECB 2011Space FunctionWashroom | NECB 2011 | Space Function | Washroom | 0.97547
NECB 2011Space FunctionWorkshop space | NECB 2011 | Space Function | Workshop space | 1.5886
NECB 2011Space FunctionAutomotive - repair | NECB 2011 | Space Function | Automotive - repair | 0.6689
NECB 2011Space FunctionBank - banking and offices | NECB 2011 | Space Function | Bank - banking and offices | 1.3842
NECB 2011Space FunctionConvention centre - audience | NECB 2011 | Space Function | Convention centre - audience | 0.81754
NECB 2011Space FunctionConvention centre - exhibit | NECB 2011 | Space Function | Convention centre - exhibit | 1.4493
NECB 2011Space FunctionCourthouse - courtroom | NECB 2011 | Space Function | Courthouse - courtroom | 1.7187
NECB 2011Space FunctionCourthouse - cell | NECB 2011 | Space Function | Courthouse - cell | 1.3657
NECB 2011Space FunctionCourthouse - chambers | NECB 2011 | Space Function | Courthouse - chambers | 1.1706
NECB 2011Space FunctionPenitentiary - audience | NECB 2011 | Space Function | Penitentiary - audience | 0.42735
NECB 2011Space FunctionPenitentiary - classroom | NECB 2011 | Space Function | Penitentiary - classroom | 1.3378
NECB 2011Space FunctionPenitentiary - dining | NECB 2011 | Space Function | Penitentiary - dining | 1.0684
NECB 2011Space FunctionDormitory - living quarters | NECB 2011 | Space Function | Dormitory - living quarters | 0.3809
NECB 2011Space FunctionFire station - engine room | NECB 2011 | Space Function | Fire station - engine room | 0.55741
NECB 2011Space FunctionFire station - quarters | NECB 2011 | Space Function | Fire station - quarters | 0.31587
NECB 2011Space FunctionGym - fitness | NECB 2011 | Space Function | Gym - fitness | 0.91044
NECB 2011Space FunctionGym - audience | NECB 2011 | Space Function | Gym - audience | 0.42735
NECB 2011Space FunctionGym - play | NECB 2011 | Space Function | Gym - play | 1.1984
NECB 2011Space FunctionHospital corr. >= 2.4m | NECB 2011 | Space Function | Hospital corr. >= 2.4m | 0.89186
NECB 2011Space FunctionHospital corr. < 2.4m | NECB 2011 | Space Function | Hospital corr. < 2.4m | 1.087
NECB 2011Space FunctionHospital - emergency | NECB 2011 | Space Function | Hospital - emergency | 2.2575
NECB 2011Space FunctionHospital - exam | NECB 2011 | Space Function | Hospital - exam | 1.663
NECB 2011Space FunctionHospital - laundry/washing | NECB 2011 | Space Function | Hospital - laundry/washing | 0.74322
NECB 2011Space FunctionHospital - lounge/recreation | NECB 2011 | Space Function | Hospital - lounge/recreation | 1.0684
NECB 2011Space FunctionHospital - medical supply | NECB 2011 | Space Function | Hospital - medical supply | 1.2728
NECB 2011Space FunctionHospital - nursery | NECB 2011 | Space Function | Hospital - nursery | 0.88257
NECB 2011Space FunctionHospital - nurses' station | NECB 2011 | Space Function | Hospital - nurses' station | 0.87328
NECB 2011Space FunctionHospital - operating room | NECB 2011 | Space Function | Hospital - operating room | 1.8859
NECB 2011Space FunctionHospital - patient room | NECB 2011 | Space Function | Hospital - patient room | 0.62245
NECB 2011Space FunctionHospital - pharmacy | NECB 2011 | Space Function | Hospital - pharmacy | 1.1427
NECB 2011Space FunctionHospital - physical therapy | NECB 2011 | Space Function | Hospital - physical therapy | 0.91044
NECB 2011Space FunctionHospital - radiology/imaging | NECB 2011 | Space Function | Hospital - radiology/imaging | 1.3192
NECB 2011Space FunctionHospital - recovery | NECB 2011 | Space Function | Hospital - recovery | 1.152
NECB 2011Space FunctionHotel/Motel - dining | NECB 2011 | Space Function | Hotel/Motel - dining | 0.81754
NECB 2011Space FunctionHotel/Motel - rooms | NECB 2011 | Space Function | Hotel/Motel - rooms | 1.1055
NECB 2011Space FunctionHotel/Motel - lobby | NECB 2011 | Space Function | Hotel/Motel - lobby | 1.0591
NECB 2011Space FunctionHway lodging - dining | NECB 2011 | Space Function | Hway lodging - dining | 0.88257
NECB 2011Space FunctionHway lodging - rooms | NECB 2011 | Space Function | Hway lodging - rooms | 0.75251
NECB 2011Space FunctionLibrary - cataloging | NECB 2011 | Space Function | Library - cataloging | 0.72464
NECB 2011Space FunctionLibrary - reading | NECB 2011 | Space Function | Library - reading | 0.92902
NECB 2011Space FunctionLibrary - stacks | NECB 2011 | Space Function | Library - stacks | 2.1275
NECB 2011Space FunctionMfg - corr. >= 2.4m | NECB 2011 | Space Function | Mfg - corr. >= 2.4m | 0.40877
NECB 2011Space FunctionMfg - corr. < 2.4m | NECB 2011 | Space Function | Mfg - corr. < 2.4m | 0.51096
NECB 2011Space FunctionMfg - detailed | NECB 2011 | Space Function | Mfg - detailed | 1.2913
NECB 2011Space FunctionMfg - equipment | NECB 2011 | Space Function | Mfg - equipment | 1.2356
NECB 2011Space FunctionMfg - bay H > 15m | NECB 2011 | Space Function | Mfg - bay H > 15m | 1.0498
NECB 2011Space FunctionMfg - 7.5 <= bay H <= 15m | NECB 2011 | Space Function | Mfg - 7.5 <= bay H <= 15m | 1.2263
NECB 2011Space FunctionMfg - bay H < 7.5m | NECB 2011 | Space Function | Mfg - bay H < 7.5m | 1.1891
NECB 2011Space FunctionMuseum - exhibition | NECB 2011 | Space Function | Museum - exhibition | 1.0498
NECB 2011Space FunctionMuseum - restoration | NECB 2011 | Space Function | Museum - restoration | 1.0219
NECB 2011Space FunctionParking garage space | NECB 2011 | Space Function | Parking garage space | 0.1858
NECB 2011Space FunctionPost office sorting | NECB 2011 | Space Function | Post office sorting | 0.93831
NECB 2011Space FunctionReligious - audience | NECB 2011 | Space Function | Religious - audience | 1.6908
NECB 2011Space FunctionReligious - fellowship hall | NECB 2011 | Space Function | Religious - fellowship hall | 0.64103
NECB 2011Space FunctionReligious - pulpit/choir | NECB 2011 | Space Function | Religious - pulpit/choir | 1.6908
NECB 2011Space FunctionRetail - dressing/fitting | NECB 2011 | Space Function | Retail - dressing/fitting | 0.87328
NECB 2011Space FunctionRetail - mall concourse | NECB 2011 | Space Function | Retail - mall concourse | 1.0962
NECB 2011Space FunctionRetail - sales | NECB 2011 | Space Function | Retail - sales | 1.6815
NECB 2011Space FunctionSports arena - audience | NECB 2011 | Space Function | Sports arena - audience | 0.42735
NECB 2011Space FunctionSports arena - court c4 | NECB 2011 | Space Function | Sports arena - court c4 | 0.72464
NECB 2011Space FunctionSports arena - court c3 | NECB 2011 | Space Function | Sports arena - court c3 | 1.1984
NECB 2011Space FunctionSports arena - court c2 | NECB 2011 | Space Function | Sports arena - court c2 | 1.9231
NECB 2011Space FunctionSports arena - court c1 | NECB 2011 | Space Function | Sports arena - court c1 | 3.01
NECB 2011Space FunctionSports arena - ring | NECB 2011 | Space Function | Sports arena - ring | 2.6756
NECB 2011Space FunctionTransp. baggage | NECB 2011 | Space Function | Transp. baggage | 0.7618
NECB 2011Space FunctionTransp. seating | NECB 2011 | Space Function | Transp. seating | 0.53883
NECB 2011Space FunctionTransp. concourse | NECB 2011 | Space Function | Transp. concourse | 0.36232
NECB 2011Space FunctionTransp. counter | NECB 2011 | Space Function | Transp. counter | 1.0777
NECB 2011Space FunctionWarehouse - fine | NECB 2011 | Space Function | Warehouse - fine | 0.9476
NECB 2011Space FunctionWarehouse - med/blk | NECB 2011 | Space Function | Warehouse - med/blk | 0.59457
NECB 2011Space FunctionWarehouse - med/blk2 | NECB 2011 | Space Function | Warehouse - med/blk2 | 0.9476
ASHRAE 90.1-2013AtriumFirst Twenty Feet in Height | ASHRAE 90.1-2013 | Atrium | First Twenty Feet in Height | 9999
ASHRAE 90.1-2013AtriumFirst Forty Feet in Height | ASHRAE 90.1-2013 | Atrium | First Forty Feet in Height | 9999
ASHRAE 90.1-2013AtriumHeight Above Forty Feet | ASHRAE 90.1-2013 | Atrium | Height Above Forty Feet | 9999
ASHRAE 90.1-2013Audience/Seating AreaFor Auditorium | ASHRAE 90.1-2013 | Audience/Seating Area | For Auditorium | 0.63
ASHRAE 90.1-2013Audience/Seating AreaFor Convention Center | ASHRAE 90.1-2013 | Audience/Seating Area | For Convention Center | 0.82
ASHRAE 90.1-2013Audience/Seating AreaFor Gymnasium | ASHRAE 90.1-2013 | Audience/Seating Area | For Gymnasium | 0.65
ASHRAE 90.1-2013Audience/Seating AreaFor Motion Picture Theater | ASHRAE 90.1-2013 | Audience/Seating Area | For Motion Picture Theater | 1.14
ASHRAE 90.1-2013Audience/Seating AreaFor Penitentiary | ASHRAE 90.1-2013 | Audience/Seating Area | For Penitentiary | 0.28
ASHRAE 90.1-2013Audience/Seating AreaFor Performaing Arts Theater | ASHRAE 90.1-2013 | Audience/Seating Area | For Performaing Arts Theater | 2.43
ASHRAE 90.1-2013Audience/Seating AreaFor Religious Buildings | ASHRAE 90.1-2013 | Audience/Seating Area | For Religious Buildings | 1.53
ASHRAE 90.1-2013Audience/Seating AreaIn Sports Arena | ASHRAE 90.1-2013 | Audience/Seating Area | In Sports Arena | 0.43
ASHRAE 90.1-2013Audience/Seating AreaGeneral | ASHRAE 90.1-2013 | Audience/Seating Area | General | 0.43
ASHRAE 90.1-2013Banking Activity AreaGeneral | ASHRAE 90.1-2013 | Banking Activity Area | General | 1.01
ASHRAE 90.1-2013Classroom/Lecture/TrainingFor Penitentiary | ASHRAE 90.1-2013 | Classroom/Lecture/Training | For Penitentiary | 1.34
ASHRAE 90.1-2013Classroom/Lecture/TrainingGeneral | ASHRAE 90.1-2013 | Classroom/Lecture/Training | General | 1.24
ASHRAE 90.1-2013Computer RoomGeneral | ASHRAE 90.1-2013 | Computer Room | General | 1.71
ASHRAE 90.1-2013Conference/Meeting/MultipurposeGeneral | ASHRAE 90.1-2013 | Conference/Meeting/Multipurpose | General | 1.23
ASHRAE 90.1-2013Confinement CellsGeneral | ASHRAE 90.1-2013 | Confinement Cells | General | 0.81
ASHRAE 90.1-2013Convention CenterExhibit Space | ASHRAE 90.1-2013 | Convention Center | Exhibit Space | 1.45
ASHRAE 90.1-2013Copy/Print RoomGeneral | ASHRAE 90.1-2013 | Copy/Print Room | General | 0.72
ASHRAE 90.1-2013CorridorFor Visually Impaired | ASHRAE 90.1-2013 | Corridor | For Visually Impaired | 0.92
ASHRAE 90.1-2013CorridorFor Hospital | ASHRAE 90.1-2013 | Corridor | For Hospital | 0.99
ASHRAE 90.1-2013CorridorFor Manufacturing Facility | ASHRAE 90.1-2013 | Corridor | For Manufacturing Facility | 0.41
ASHRAE 90.1-2013CorridorGeneral | ASHRAE 90.1-2013 | Corridor | General | 0.66
ASHRAE 90.1-2013CourtroomGeneral | ASHRAE 90.1-2013 | Courtroom | General | 1.72
ASHRAE 90.1-2013Dining AreaFor Penitentiary | ASHRAE 90.1-2013 | Dining Area | For Penitentiary | 0.96
ASHRAE 90.1-2013Dining AreaFor Visually Impaired | ASHRAE 90.1-2013 | Dining Area | For Visually Impaired | 2.65
ASHRAE 90.1-2013Dining AreaFor Bar Lounge/Leisure Dining | ASHRAE 90.1-2013 | Dining Area | For Bar Lounge/Leisure Dining | 1.07
ASHRAE 90.1-2013Dining AreaFor Cafeteria/Fast Food Dining | ASHRAE 90.1-2013 | Dining Area | For Cafeteria/Fast Food Dining | 0.65
ASHRAE 90.1-2013Dining AreaFor Family Dining | ASHRAE 90.1-2013 | Dining Area | For Family Dining | 0.89
ASHRAE 90.1-2013Dining AreaGeneral | ASHRAE 90.1-2013 | Dining Area | General | 0.65
ASHRAE 90.1-2013DormitoryLiving Quarters | ASHRAE 90.1-2013 | Dormitory | Living Quarters | 0.38
ASHRAE 90.1-2013Dressing/Fitting RoomFor Performing Arts Theater | ASHRAE 90.1-2013 | Dressing/Fitting Room | For Performing Arts Theater | 0.61
ASHRAE 90.1-2013Dressing/Fitting RoomFor Retail | ASHRAE 90.1-2013 | Dressing/Fitting Room | For Retail | 0.71
ASHRAE 90.1-2013Electrical/MechanicalGeneral | ASHRAE 90.1-2013 | Electrical/Mechanical | General | 0.42
ASHRAE 90.1-2013Emergyency Vehicle GarageGeneral | ASHRAE 90.1-2013 | Emergyency Vehicle Garage | General | 0.56
ASHRAE 90.1-2013Fire StationSleeping Quarters | ASHRAE 90.1-2013 | Fire Station | Sleeping Quarters | 0.22
ASHRAE 90.1-2013Food PreparationGeneral | ASHRAE 90.1-2013 | Food Preparation | General | 1.21
ASHRAE 90.1-2013Guest RoomGeneral | ASHRAE 90.1-2013 | Guest Room | General | 0.91
ASHRAE 90.1-2013Guest RoomFor Hotel | ASHRAE 90.1-2013 | Guest Room | For Hotel | 0.91
ASHRAE 90.1-2013Gymnasium/Fitness CenterPlaying Area | ASHRAE 90.1-2013 | Gymnasium/Fitness Center | Playing Area | 0.72
ASHRAE 90.1-2013Gymnasium/Fitness CenterExercise Area | ASHRAE 90.1-2013 | Gymnasium/Fitness Center | Exercise Area | 1.2
ASHRAE 90.1-2013Healthcare FacilityExam/Treatment | ASHRAE 90.1-2013 | Healthcare Facility | Exam/Treatment | 1.66
ASHRAE 90.1-2013Healthcare FacilityRadiology/Imaging | ASHRAE 90.1-2013 | Healthcare Facility | Radiology/Imaging | 1.51
ASHRAE 90.1-2013Healthcare FacilityMedical Supply | ASHRAE 90.1-2013 | Healthcare Facility | Medical Supply | 0.74
ASHRAE 90.1-2013Healthcare FacilityNursery | ASHRAE 90.1-2013 | Healthcare Facility | Nursery | 0.88
ASHRAE 90.1-2013Healthcare FacilityNurse Station | ASHRAE 90.1-2013 | Healthcare Facility | Nurse Station | 0.71
ASHRAE 90.1-2013Healthcare FacilityOperating Room | ASHRAE 90.1-2013 | Healthcare Facility | Operating Room | 2.48
ASHRAE 90.1-2013Healthcare FacilityPatient Room | ASHRAE 90.1-2013 | Healthcare Facility | Patient Room | 0.62
ASHRAE 90.1-2013Healthcare FacilityPhysical Therapy | ASHRAE 90.1-2013 | Healthcare Facility | Physical Therapy | 0.91
ASHRAE 90.1-2013Healthcare FacilityRecovery | ASHRAE 90.1-2013 | Healthcare Facility | Recovery | 1.15
ASHRAE 90.1-2013LaboratoryFor Classrooms | ASHRAE 90.1-2013 | Laboratory | For Classrooms | 1.43
ASHRAE 90.1-2013LaboratoryGeneral | ASHRAE 90.1-2013 | Laboratory | General | 1.81
ASHRAE 90.1-2013Laundry/Washing AreaGeneral | ASHRAE 90.1-2013 | Laundry/Washing Area | General | 0.6
ASHRAE 90.1-2013LibraryReading Area | ASHRAE 90.1-2013 | Library | Reading Area | 1.06
ASHRAE 90.1-2013LibraryStacks | ASHRAE 90.1-2013 | Library | Stacks | 1.71
ASHRAE 90.1-2013Loading DockGeneral | ASHRAE 90.1-2013 | Loading Dock | General | 0.47
ASHRAE 90.1-2013LobbyFor Visually Impaired | ASHRAE 90.1-2013 | Lobby | For Visually Impaired | 1.8
ASHRAE 90.1-2013LobbyFor Elevator | ASHRAE 90.1-2013 | Lobby | For Elevator | 0.64
ASHRAE 90.1-2013LobbyFor Hotel | ASHRAE 90.1-2013 | Lobby | For Hotel | 1.06
ASHRAE 90.1-2013LobbyFor Motion Picture Theater | ASHRAE 90.1-2013 | Lobby | For Motion Picture Theater | 0.59
ASHRAE 90.1-2013LobbyFor Performaing Arts Theater | ASHRAE 90.1-2013 | Lobby | For Performaing Arts Theater | 2
ASHRAE 90.1-2013LobbyGeneral | ASHRAE 90.1-2013 | Lobby | General | 0.9
ASHRAE 90.1-2013Locker RoomGeneral | ASHRAE 90.1-2013 | Locker Room | General | 0.75
ASHRAE 90.1-2013Lounge/RecreationFor Healthcare Facility | ASHRAE 90.1-2013 | Lounge/Recreation | For Healthcare Facility | 0.92
ASHRAE 90.1-2013Lounge/RecreationGeneral | ASHRAE 90.1-2013 | Lounge/Recreation | General | 0.73
ASHRAE 90.1-2013ManufacturingLow Bay (<25 ft Floor to Ceiling Height) | ASHRAE 90.1-2013 | Manufacturing | Low Bay (<25 ft Floor to Ceiling Height) | 1.19
ASHRAE 90.1-2013ManufacturingHigh Bay (25-50 ft Floor to Ceiling Height) | ASHRAE 90.1-2013 | Manufacturing | High Bay (25-50 ft Floor to Ceiling Height) | 1.23
ASHRAE 90.1-2013ManufacturingExtra High Bay (>50 ft Floor to Ceiling Height) | ASHRAE 90.1-2013 | Manufacturing | Extra High Bay (>50 ft Floor to Ceiling Height) | 1.05
ASHRAE 90.1-2013ManufacturingDetailed Manufacturing | ASHRAE 90.1-2013 | Manufacturing | Detailed Manufacturing | 1.29
ASHRAE 90.1-2013ManufacturingEquipment Room | ASHRAE 90.1-2013 | Manufacturing | Equipment Room | 0.74
ASHRAE 90.1-2013MuseumGeneral Exhibition | ASHRAE 90.1-2013 | Museum | General Exhibition | 1.05
ASHRAE 90.1-2013MuseumRestoration | ASHRAE 90.1-2013 | Museum | Restoration | 1.02
ASHRAE 90.1-2013Office-EnclosedGeneral | ASHRAE 90.1-2013 | Office-Enclosed | General | 1.11
ASHRAE 90.1-2013Office-Open PlanGeneral | ASHRAE 90.1-2013 | Office-Open Plan | General | 0.98
ASHRAE 90.1-2013Parking GarageGarage Area | ASHRAE 90.1-2013 | Parking Garage | Garage Area | 0.19
ASHRAE 90.1-2013PharmacyGeneral | ASHRAE 90.1-2013 | Pharmacy | General | 1.68
ASHRAE 90.1-2013Post OfficeSorting Area | ASHRAE 90.1-2013 | Post Office | Sorting Area | 0.94
ASHRAE 90.1-2013Religious BuildingsWorship Pulpit, Choir | ASHRAE 90.1-2013 | Religious Buildings | Worship Pulpit, Choir | 1.53
ASHRAE 90.1-2013Religious BuildingsFellowship Hall | ASHRAE 90.1-2013 | Religious Buildings | Fellowship Hall | 0.64
ASHRAE 90.1-2013RestroomsFor Visually Impaired | ASHRAE 90.1-2013 | Restrooms | For Visually Impaired | 1.21
ASHRAE 90.1-2013RestroomsGeneral | ASHRAE 90.1-2013 | Restrooms | General | 0.98
ASHRAE 90.1-2013RetailMall Concourse | ASHRAE 90.1-2013 | Retail | Mall Concourse | 1.1
ASHRAE 90.1-2013Sales AreaGeneral | ASHRAE 90.1-2013 | Sales Area | General | 1.44
ASHRAE 90.1-2013Seating AreaGeneral | ASHRAE 90.1-2013 | Seating Area | General | 0.54
ASHRAE 90.1-2013Sports Arena - Playing AreaCourt Sports Arena - Class 4 | ASHRAE 90.1-2013 | Sports Arena - Playing Area | Court Sports Arena - Class 4 | 1.2
ASHRAE 90.1-2013Sports Arena - Playing AreaCourt Sports Arena - Class 3 | ASHRAE 90.1-2013 | Sports Arena - Playing Area | Court Sports Arena - Class 3 | 1.8
ASHRAE 90.1-2013Sports Arena - Playing AreaCourt Sports Arena - Class 2 | ASHRAE 90.1-2013 | Sports Arena - Playing Area | Court Sports Arena - Class 2 | 2.4
ASHRAE 90.1-2013Sports Arena - Playing AreaCourt Sports Arena - Class 1 | ASHRAE 90.1-2013 | Sports Arena - Playing Area | Court Sports Arena - Class 1 | 3.68
ASHRAE 90.1-2013StairwayGeneral | ASHRAE 90.1-2013 | Stairway | General | 0.69
ASHRAE 90.1-2013StorageLess than Fifty Feet | ASHRAE 90.1-2013 | Storage | Less than Fifty Feet | 1.24
ASHRAE 90.1-2013StorageGeneral | ASHRAE 90.1-2013 | Storage | General | 0.63
ASHRAE 90.1-2013TransportationAirport-Concourse | ASHRAE 90.1-2013 | Transportation | Airport-Concourse | 0.36
ASHRAE 90.1-2013TransportationAir/Train/Bus-Baggage Area | ASHRAE 90.1-2013 | Transportation | Air/Train/Bus-Baggage Area | 0.53
ASHRAE 90.1-2013TransportationTerminal-Ticket Counter | ASHRAE 90.1-2013 | Transportation | Terminal-Ticket Counter | 0.8
ASHRAE 90.1-2013Vehicular Maintenance AreaGeneral | ASHRAE 90.1-2013 | Vehicular Maintenance Area | General | 0.67
ASHRAE 90.1-2013Visually ImpairedFor Chapel | ASHRAE 90.1-2013 | Visually Impaired | For Chapel | 2.21
ASHRAE 90.1-2013Visually ImpairedGeneral | ASHRAE 90.1-2013 | Visually Impaired | General | 2.41
ASHRAE 90.1-2013WarehouseFine Material Storage | ASHRAE 90.1-2013 | Warehouse | Fine Material Storage | 0.95
ASHRAE 90.1-2013WarehouseMedium/Bulky Material Storage | ASHRAE 90.1-2013 | Warehouse | Medium/Bulky Material Storage | 0.58
ASHRAE 90.1-2013Whole BuildingAutomotive Facility | ASHRAE 90.1-2013 | Whole Building | Automotive Facility | 0.8
ASHRAE 90.1-2013Whole BuildingConvention Center | ASHRAE 90.1-2013 | Whole Building | Convention Center | 1.01
ASHRAE 90.1-2013Whole BuildingCourt House | ASHRAE 90.1-2013 | Whole Building | Court House | 1.01
ASHRAE 90.1-2013Whole BuildingDining: Bar Lounge/Leisure | ASHRAE 90.1-2013 | Whole Building | Dining: Bar Lounge/Leisure | 1.01
ASHRAE 90.1-2013Whole BuildingDining: Cafeteria/Fast Food | ASHRAE 90.1-2013 | Whole Building | Dining: Cafeteria/Fast Food | 0.9
ASHRAE 90.1-2013Whole BuildingDining: Family | ASHRAE 90.1-2013 | Whole Building | Dining: Family | 0.95
ASHRAE 90.1-2013Whole BuildingDormitory | ASHRAE 90.1-2013 | Whole Building | Dormitory | 0.57
ASHRAE 90.1-2013Whole BuildingExercise Center | ASHRAE 90.1-2013 | Whole Building | Exercise Center | 0.84
ASHRAE 90.1-2013Whole BuildingFire Station | ASHRAE 90.1-2013 | Whole Building | Fire Station | 0.671
ASHRAE 90.1-2013Whole BuildingGymnasium | ASHRAE 90.1-2013 | Whole Building | Gymnasium | 0.94
ASHRAE 90.1-2013Whole BuildingHealth Care-Clinic | ASHRAE 90.1-2013 | Whole Building | Health Care-Clinic | 0.9
ASHRAE 90.1-2013Whole BuildingHospital | ASHRAE 90.1-2013 | Whole Building | Hospital | 1.05
ASHRAE 90.1-2013Whole BuildingHotel | ASHRAE 90.1-2013 | Whole Building | Hotel | 0.87
ASHRAE 90.1-2013Whole BuildingLibrary | ASHRAE 90.1-2013 | Whole Building | Library | 1.19
ASHRAE 90.1-2013Whole BuildingManufacturing Facility | ASHRAE 90.1-2013 | Whole Building | Manufacturing Facility | 1.17
ASHRAE 90.1-2013Whole BuildingMotel | ASHRAE 90.1-2013 | Whole Building | Motel | 0.87
ASHRAE 90.1-2013Whole BuildingMotion Picture Theater | ASHRAE 90.1-2013 | Whole Building | Motion Picture Theater | 0.76
ASHRAE 90.1-2013Whole BuildingMulti-Family | ASHRAE 90.1-2013 | Whole Building | Multi-Family | 0.51
ASHRAE 90.1-2013Whole BuildingMuseum | ASHRAE 90.1-2013 | Whole Building | Museum | 1.02
ASHRAE 90.1-2013Whole BuildingOffice | ASHRAE 90.1-2013 | Whole Building | Office | 0.82
ASHRAE 90.1-2013Whole BuildingParking Garage | ASHRAE 90.1-2013 | Whole Building | Parking Garage | 0.21
ASHRAE 90.1-2013Whole BuildingPenitentiary | ASHRAE 90.1-2013 | Whole Building | Penitentiary | 0.81
ASHRAE 90.1-2013Whole BuildingPerforming Arts Theater | ASHRAE 90.1-2013 | Whole Building | Performing Arts Theater | 1.39
ASHRAE 90.1-2013Whole BuildingPolice Station | ASHRAE 90.1-2013 | Whole Building | Police Station | 0.87
ASHRAE 90.1-2013Whole BuildingPost Office | ASHRAE 90.1-2013 | Whole Building | Post Office | 0.87
ASHRAE 90.1-2013Whole BuildingReligious Building | ASHRAE 90.1-2013 | Whole Building | Religious Building | 1
ASHRAE 90.1-2013Whole BuildingRetail | ASHRAE 90.1-2013 | Whole Building | Retail | 1.26
ASHRAE 90.1-2013Whole BuildingSchool/University | ASHRAE 90.1-2013 | Whole Building | School/University | 0.87
ASHRAE 90.1-2013Whole BuildingSports Arena | ASHRAE 90.1-2013 | Whole Building | Sports Arena | 0.91
ASHRAE 90.1-2013Whole BuildingTown Hall | ASHRAE 90.1-2013 | Whole Building | Town Hall | 0.89
ASHRAE 90.1-2013Whole BuildingTransportation | ASHRAE 90.1-2013 | Whole Building | Transportation | 0.7
ASHRAE 90.1-2013Whole BuildingWarehouse | ASHRAE 90.1-2013 | Whole Building | Warehouse | 0.66
ASHRAE 90.1-2013Whole BuildingWorkshop | ASHRAE 90.1-2013 | Whole Building | Workshop | 1.19
ASHRAE 90.1-2013WorkshopGeneral | ASHRAE 90.1-2013 | Workshop | General | 1.59

## Space Types
A Space Type is a set of interior loads and their schedules to represent a specific use-type area in a building
|  |  | Color | Lighting | [6 empty] | based on 90.1 - 9.6.2 |  |  |  |  | Ventilation | [6 empty] | Occupancy |  |  | Infiltration |  |  |  | Gas Equipment |  |  |  |  | Electric Plug Loads |  |  |  |  | Thermostats - not currently part of a space type |  | Service Hot Water | [6 empty] | Exhaust - Not currently part of a space type |  |  | Exhaust Fan | [5 empty] | Residential or Nonresidential
Template | Building Type | Space Type | RGB | Lighting Standard | Lighting Primary Space Type | Lighting Secondary Space Type | LookupColumn | Lighting per Area (W/ft^2) | Lighting per Person (W/person) | Lighting per Length (W/ft) | Additional Lighting per Area (W/ft^2) | Lighting Fraction to Return Air | Lighting Fraction Radiant | Lighting Fraction Visible | Lighting Schedule | Ventilation Standard | Ventilation Primary Space Type | Ventilation Secondary Space Type | Lookup | Ventilation per Area (ft^3/min*ft^2) | Ventilation per Person (ft^3/min*person) | Ventilation Air Changes (ach) | Occupancy per Area (people/1000 ft^2) | Occupancy Schedule | Occupancy Activity Schedule | Infiltration per Exterior Area (ft^3/min*ft^2 ext) | Infiltration per Exterior Wall Area (ft^3/min*ft^2 ext) | Infiltration Air Changes (ach) | Infiltration Schedule | Gas Equipment per Area (Btu/hr*ft^2) | Gas Equipment Fraction Latent | Gas Equipment Fraction Radiant | Gas Equipment Fraction Lost | Gas Equipment Schedule | Electric Equipment per Area (W/ft^2) | Electric Equipment Fraction Latent | Electric Equipment Fraction Radiant | Electric Equipment Fraction Lost | Electric Equipment Schedule | Heating Setpoint Schedule | Cooling Setpoint Schedule | Service Water Heating Peak Flow Rate (gal/h) | Service Water Heating Area (ft^2) | Service Water Heating Peak Flow per Area (gal/h*ft^2) | Service Water Heating Target Temperature (C) | Service Water Heating Fraction Sensible | Service Water Heating Fraction Latent | Service Water Heating Schedule | Exhaust per Area (cfm/ft2) | Exhaust per Unit (cfm) | Exhaust Fan Power per Area (W/ft^2) | Exhaust Fan Efficiency | Exhaust Fan Power (W) | Exhaust Fan Pressure Rise (Pa) | Exhaust Fan Maximum Flow Rate (cfm) | Exhaust Schedule | Balanced Exhaust Fraction Schedule | Is Residential
189.1-2009 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral | 1.08 |  |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0446 |  |  | FullServiceRestaurant Infil Half On | 276.72 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant Gas Equip | 25.5 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp Kitchen | FullServiceRestaurant ClgSetp Kitchen | 133 | 1501 | 0.08860759494 | 49 | 0.2 | 0.05 | FullServiceRestaurant SWH | 0.7 | 4000 | 0.1215379059 | 0.338 | 694.5023 | 0.5 |  | FullServiceRestaurant Kitchen Exhaust
189.1-2009 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Family Dining | ASHRAE 189.1-2009Dining AreaFor Family Dining | 1.89 |  |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 |  | 67 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity | 0.0446 |  |  | FullServiceRestaurant Infil Half On | [5 empty] | 4.08 | 0.25 | 0.3 | 0 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp
90.1-2004 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral | 1.2 |  |  |  | 0 | 0.7 | 0.2 | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | RestaurantSitDown BLDG_OCC_SCH | RestaurantSitDown ACTIVITY_SCH |  | 0.2016 |  | RestaurantSitDown INFIL_HALF_ON_SCH | 205.81 | 0.1 | 0.2 | 0.7 | RestaurantSitDown Rest_GAS_EQUIP_SCH | 37.53 | 0.25 | 0.3 | 0.2 | RestaurantSitDown BLDG_EQUIP_SCH | RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_SETBACK | 133 | 1501 | 0.08860759494 | 49 | 0.2 | 0.05 | RestaurantSitDown BLDG_SWH_SCH | 0.7 | 4000 | 0.1215379059 | 0.338 | 694.5023 | 0.5 |  | RestaurantSitDown Kitchen_Exhaust_SCH
90.1-2004 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | For Family Dining | ASHRAE 90.1-2004Dining AreaFor Family Dining | 2.1 |  |  |  | 0 | 0.7 | 0.2 | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 |  | 70 | RestaurantSitDown BLDG_OCC_SCH | RestaurantSitDown ACTIVITY_SCH |  | 0.2016 |  | RestaurantSitDown INFIL_HALF_ON_SCH | [5 empty] | 6.032 | 0.25 | 0.3 | 0 | RestaurantSitDown BLDG_EQUIP_SCH | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_SETBACK
90.1-2004 | FullServiceRestaurant | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0 | [20 empty] | Always On
90.1-2007 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral | 1.2 |  |  |  | 0 | 0.7 | 0.2 | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 5 | RestaurantSitDown BLDG_OCC_SCH | RestaurantSitDown ACTIVITY_SCH |  | 0.2016 |  | RestaurantSitDown INFIL_HALF_ON_SCH | 205.81 | 0.1 | 0.2 | 0.7 | RestaurantSitDown Rest_GAS_EQUIP_SCH | 37.53 | 0.25 | 0.3 | 0.2 | RestaurantSitDown BLDG_EQUIP_SCH | RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_SETBACK | 133 | 1501 | 0.08860759494 | 49 | 0.2 | 0.05 | RestaurantSitDown BLDG_SWH_SCH | 0.7 | 4000 | 0.1215379059 | 0.338 | 694.5023 | 0.5 |  | RestaurantSitDown Kitchen_Exhaust_SCH
90.1-2007 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | For Family Dining | ASHRAE 90.1-2007Dining AreaFor Family Dining | 2.1 |  |  |  | 0 | 0.7 | 0.2 | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 | ASHRAE 62.1-2004 | Food and Beverage Service | Restaurant dining rooms | ASHRAE 62.1-2004Food and Beverage ServiceRestaurant dining rooms | 0.18 | 7.5 |  | 70 | RestaurantSitDown BLDG_OCC_SCH | RestaurantSitDown ACTIVITY_SCH |  | 0.2016 |  | RestaurantSitDown INFIL_HALF_ON_SCH | [5 empty] | 6.032 | 0.25 | 0.3 | 0 | RestaurantSitDown BLDG_EQUIP_SCH | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_SETBACK
90.1-2007 | FullServiceRestaurant | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0 | [20 empty] | Always On
90.1-2010 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral | 0.99 |  |  |  | 0 | 0.7 | 0.2 | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2010_2013 | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 5 | RestaurantSitDown BLDG_OCC_SCH | RestaurantSitDown ACTIVITY_SCH |  | 0.112 |  | RestaurantSitDown INFIL_HALF_ON_SCH | 205.81 | 0.1 | 0.2 | 0.7 | RestaurantSitDown Rest_GAS_EQUIP_SCH | 37.53 | 0.25 | 0.3 | 0.2 | RestaurantSitDown BLDG_EQUIP_SCH | RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_SETBACK | 133 | 1501 | 0.08860759494 | 49 | 0.2 | 0.05 | RestaurantSitDown BLDG_SWH_SCH | 0.7 | 4000 | 0.12154 | 0.338 | 694.5023 | 0.5 |  | RestaurantSitDown Kitchen_Exhaust_SCH
90.1-2010 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | For Family Dining | ASHRAE 90.1-2010Dining AreaFor Family Dining | 0.89 |  |  |  | 0 | 0.7 | 0.2 | RestaurantSitDown BLDG_LIGHT_DINING_SCH_2010 | ASHRAE 62.1-2007 | Food and Beverage Service | Restaurant dining rooms | ASHRAE 62.1-2007Food and Beverage ServiceRestaurant dining rooms | 0.18 | 7.5 |  | 70 | RestaurantSitDown BLDG_OCC_SCH | RestaurantSitDown ACTIVITY_SCH |  | 0.112 |  | RestaurantSitDown INFIL_HALF_ON_SCH | [5 empty] | 6.032 | 0.25 | 0.3 | 0 | RestaurantSitDown BLDG_EQUIP_SCH | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_SETBACK
90.1-2010 | FullServiceRestaurant | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0 | [20 empty] | Always On
DOE Ref 1980-2004 | FullServiceRestaurant | Kitchen | 78_222_133 | DOE Ref 1980-2004 | FullServiceRestaurant | Kitchen | DOE Ref 1980-2004FullServiceRestaurantKitchen | 1.52 |  |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity |  | 0.223 |  | FullServiceRestaurant Infil Half On | 378.75 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant Gas Equip | 35 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp Kitchen | FullServiceRestaurant ClgSetp Kitchen | 133 | 1501 | 0.08860759494 | 49 | 0.2 | 0.05 | FullServiceRestaurant SWH | 0.7 | 4000 | 0.1215379059 | 0.338 | 694.5023 | 0.5 |  | FullServiceRestaurant Kitchen Exhaust
DOE Ref 1980-2004 | FullServiceRestaurant | Dining | 31_169_34 | DOE Ref 1980-2004 | FullServiceRestaurant | Dining | DOE Ref 1980-2004FullServiceRestaurantDining | 2.54 |  |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 |  | 67 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity |  | 0.223 |  | FullServiceRestaurant Infil Half On | [5 empty] | 5.6 | 0.25 | 0.3 | 0 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp
DOE Ref 1980-2004 | FullServiceRestaurant | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0 | [19 empty] | 1 | Always On
DOE Ref Pre-1980 | FullServiceRestaurant | Kitchen | 78_222_133 | DOE Ref Pre-1980 | FullServiceRestaurant | Kitchen | DOE Ref Pre-1980FullServiceRestaurantKitchen | 1.52 |  |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity |  | 0.223 |  | FullServiceRestaurant Infil Half On | 378.75 | 0.1 | 0.2 | 0.7 | FullServiceRestaurant Gas Equip | 35 | 0.25 | 0.3 | 0.2 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp Kitchen | FullServiceRestaurant ClgSetp Kitchen | 133 | 1501 | 0.08860759494 | 49 | 0.2 | 0.05 | FullServiceRestaurant SWH | 0.7 | 4000 | 0.1215379059 | 0.338 | 694.5023 | 0.5 |  | FullServiceRestaurant Kitchen Exhaust
DOE Ref Pre-1980 | FullServiceRestaurant | Dining | 31_169_34 | DOE Ref Pre-1980 | FullServiceRestaurant | Dining | DOE Ref Pre-1980FullServiceRestaurantDining | 2.54 |  |  |  | 0 | 0.7 | 0.2 | FullServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 |  | 67 | FullServiceRestaurant Bldg Occ | FullServiceRestaurant Activity |  | 0.223 |  | FullServiceRestaurant Infil Half On | [5 empty] | 5.6 | 0.25 | 0.3 | 0 | FullServiceRestaurant Bldg Equip | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp
189.1-2009 | Hospital | Radiology | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology | 0.36 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 |  | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 7.28 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5250 | 0.0001904761905 | 49 | 0.2 | 0.05 | Hospital SWH Extd
189.1-2009 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 189.1-2009 | Hospital | Physical Therapy | ASHRAE 189.1-2009HospitalPhysical Therapy | 0.81 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 |  | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5280 | 0.0001893939394 | 49 | 0.2 | 0.05 | Hospital SWH
189.1-2009 | Hospital | PatRoom | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room | 0.63 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room |  |  | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 1 | 280 | 0.003571428571 | 49 | 0.2 | 0.05 | Hospital SWH Extd
189.1-2009 | Hospital | PatCorridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | Hospital Critical Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp
189.1-2009 | Hospital | OR | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room | 1.98 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 2 | 600 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital SWH
189.1-2009 | Hospital | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral | 0.99 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 6.99 | Hospital Bldg Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
189.1-2009 | Hospital | NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 |  | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 0.76 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
189.1-2009 | Hospital | Lobby | 31_162_169 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral | 1.17 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 7.14 | Hospital Bldg Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
189.1-2009 | Hospital | Lab | 204_120_230 | ASHRAE 189.1-2009 | Laboratory | General | ASHRAE 189.1-2009LaboratoryGeneral | 1.26 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 |  | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 3.22 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 2 | 2850 | 0.000701754386 | 49 | 0.2 | 0.05 | Hospital SWH
189.1-2009 | Hospital | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral | 1.08 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | Hospital Bldg Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | 70.46 | 0.1 | 0.2 | 0.7 | Hospital Kitchen Gas | 5.47 | 0.2 | 0.5 | 0.1 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital SWH Extd | 0.7 | 5300 | 0.1221241016 | 0.338 | 924.6539123 | 0.5024115756 |  | Hospital Kitchen Exhaust
189.1-2009 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room | 0.63 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
189.1-2009 | Hospital | ICU_Open | 78_167_222 | ASHRAE 189.1-2009 | Hospital | Recovery | ASHRAE 189.1-2009HospitalRecovery | 0.72 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
189.1-2009 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 5 | Hospital Critical Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
189.1-2009 | Hospital | ER_Triage | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency | 2.43 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 1.97 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
189.1-2009 | Hospital | ER_Trauma | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency | 2.43 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
189.1-2009 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 6.25 | Hospital Critical Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 0.99 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
189.1-2009 | Hospital | ER_Exam | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency | 2.43 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital Critical Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
189.1-2009 | Hospital | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral | 0.81 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 |  | 10 | Hospital Critical Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
189.1-2009 | Hospital | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | Hospital Critical Occ | Hospital Activity | 0.0446 |  |  | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
90.1-2004 | Hospital | Radiology | 136_78_222 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology | 0.4 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_RADIOLOGY_SCH | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 10 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 5250 | 0.0001904761905 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2004 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 90.1-2004 | Hospital | Physical Therapy | ASHRAE 90.1-2004HospitalPhysical Therapy | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 5280 | 0.0001893939394 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2004 | Hospital | PatRoom | 78_167_222 | ASHRAE 90.1-2004 | Hospital | Patient Room | ASHRAE 90.1-2004HospitalPatient Room | 0.7 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room |  |  | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 280 | 0.003571428571 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2004 | Hospital | PatCorridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | ASHRAE 90.1-2004Corridor/TransitionFor Hospital | 1 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2004 | Hospital | OR | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Operating Room | ASHRAE 90.1-2004HospitalOperating Room | 2.2 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 5 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 2 | 600 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2004 | Hospital | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 6.99 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2004 | Hospital | NurseStn | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station | 1 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_NURSEFLR234_SCH | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 |  | 7.14 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.04 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2004 | Hospital | Lobby | 31_162_169 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral | 1.3 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 7.14 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.1 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2004 | Hospital | Lab | 204_120_230 | ASHRAE 90.1-2004 | Laboratory | General | ASHRAE 90.1-2004LaboratoryGeneral | 1.4 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 2 | 2850 | 0.000701754386 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2004 | Hospital | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral | 1.2 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | 96.7 | 0.1 | 0.2 | 0.7 | Hospital BLDG_EQUIP_SCH | 7.5 | 0.2 | 0.5 | 0.1 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH | 0.7 | 5300 | 0.1221241016 | 0.338 | 924.6539123 | 0.5024115756 |  | Hospital Kitchen_Exhaust_SCH
90.1-2004 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 90.1-2004 | Hospital | Patient Room | ASHRAE 90.1-2004HospitalPatient Room | 0.7 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2004 | Hospital | ICU_Open | 78_167_222 | ASHRAE 90.1-2004 | Hospital | Recovery | ASHRAE 90.1-2004HospitalRecovery | 0.8 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2004 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station | 1 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2004 | Hospital | ER_Triage | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency | 2.7 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2004 | Hospital | ER_Trauma | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency | 2.7 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2004 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station | 1 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_NURSEFLR1_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 6.25 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.36 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2004 | Hospital | ER_Exam | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency | 2.7 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2004 | Hospital | Dining | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 |  | 10 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2004 | Hospital | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | ASHRAE 90.1-2004Corridor/TransitionFor Hospital | 1 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0595 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | Hospital | Radiology | 136_78_222 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology | 0.4 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_RADIOLOGY_SCH | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesMedical procedure |  | 15 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 7.28 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 5250 | 0.0001904761905 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2007 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 90.1-2007 | Hospital | Physical Therapy | ASHRAE 90.1-2007HospitalPhysical Therapy | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPhysical therapy |  | 15 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 5280 | 0.0001893939394 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2007 | Hospital | PatRoom | 78_167_222 | ASHRAE 90.1-2007 | Hospital | Patient Room | ASHRAE 90.1-2007HospitalPatient Room | 0.7 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room |  |  | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 280 | 0.003571428571 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2007 | Hospital | PatCorridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | ASHRAE 90.1-2007Corridor/TransitionFor Hospital | 1 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 1 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | Hospital | OR | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Operating Room | ASHRAE 90.1-2007HospitalOperating Room | 2.2 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 2 | 600 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2007 | Hospital | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 |  | 6.99 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | Hospital | NurseStn | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station | 1 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_NURSEFLR234_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 |  | 7.14 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.76 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | Hospital | Lobby | 31_162_169 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral | 1.3 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2004Office BuildingsMain entry lobbies | 0.06 | 5 |  | 7.14 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.07 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | Hospital | Lab | 204_120_230 | ASHRAE 90.1-2007 | Laboratory | General | ASHRAE 90.1-2007LaboratoryGeneral | 1.4 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Educational Facilities | Science laboratories | ASHRAE 62.1-2004Educational FacilitiesScience laboratories | 0.18 | 10 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 3.22 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 2 | 2850 | 0.000701754386 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2007 | Hospital | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral | 1.2 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | 70.46 | 0.1 | 0.2 | 0.7 | Hospital BLDG_EQUIP_SCH | 5.47 | 0.2 | 0.5 | 0.1 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH | 0.7 | 5300 | 0.1221241016 | 0.338 | 924.6539123 | 0.5024115756 |  | Hospital Kitchen_Exhaust_SCH
90.1-2007 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 90.1-2007 | Hospital | Patient Room | ASHRAE 90.1-2007HospitalPatient Room | 0.7 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | Hospital | ICU_Open | 78_167_222 | ASHRAE 90.1-2007 | Hospital | Recovery | ASHRAE 90.1-2007HospitalRecovery | 0.8 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station | 1 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | Hospital | ER_Triage | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency | 2.7 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.97 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2007 | Hospital | ER_Trauma | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency | 2.7 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2007 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station | 1 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_NURSEFLR1_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 6.25 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.99 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | Hospital | ER_Exam | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency | 2.7 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2007 | Hospital | Dining | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 10 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2007 | Hospital | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | ASHRAE 90.1-2007Corridor/TransitionFor Hospital | 1 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 1 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | Hospital | Radiology | 136_78_222 | ASHRAE 90.1-2010 | Hospital | Radiology/Imaging | ASHRAE 90.1-2010HospitalRadiology/Imaging | 1.32 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_RADIOLOGY_SCH | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesMedical procedure |  | 15 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 7.28 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 5250 | 0.0001904761905 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2010 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 90.1-2010 | Hospital | Physical Therapy | ASHRAE 90.1-2010HospitalPhysical Therapy | 0.91 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy |  | 15 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 5280 | 0.0001893939394 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2010 | Hospital | PatRoom | 78_167_222 | ASHRAE 90.1-2010 | Hospital | Patient Room | ASHRAE 90.1-2010HospitalPatient Room | 0.62 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room |  |  | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 280 | 0.003571428571 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2010 | Hospital | PatCorridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | For Hospital | ASHRAE 90.1-2010Corridor/TransitionFor Hospital | 0.89 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 1 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | Hospital | OR | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Operating Room | ASHRAE 90.1-2010HospitalOperating Room | 1.89 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 2 | 600 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2010 | Hospital | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 6.99 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | Hospital | NurseStn | 31_162_169 | ASHRAE 90.1-2010 | Hospital | Nurse Station | ASHRAE 90.1-2010HospitalNurse Station | 0.87 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_NURSEFLR234_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 7.14 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.76 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | Hospital | Lobby | 31_162_169 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2007Office BuildingsMain entry lobbies | 0.06 | 5 |  | 7.14 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.07 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | Hospital | Lab | 204_120_230 | ASHRAE 90.1-2010 | Laboratory | For Medical/Industrial/Research | ASHRAE 90.1-2010LaboratoryFor Medical/Industrial/Research | 1.81 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Educational Facilities | Science laboratories | ASHRAE 62.1-2007Educational FacilitiesScience laboratories | 0.18 | 10 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 3.22 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 2 | 2850 | 0.000701754386 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2010 | Hospital | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral | 0.99 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | 70.46 | 0.1 | 0.2 | 0.7 | Hospital BLDG_EQUIP_SCH | 5.47 | 0.2 | 0.5 | 0.1 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH | 0.7 | 5300 | 0.12212 | 0.338 | 924.6539 | 0.50241 |  | Hospital Kitchen_Exhaust_SCH
90.1-2010 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 90.1-2010 | Hospital | Patient Room | ASHRAE 90.1-2010HospitalPatient Room | 0.62 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | Hospital | ICU_Open | 78_167_222 | ASHRAE 90.1-2010 | Hospital | Recovery | ASHRAE 90.1-2010HospitalRecovery | 1.15 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 90.1-2010 | Hospital | Nurse Station | ASHRAE 90.1-2010HospitalNurse Station | 0.87 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | Hospital | ER_Triage | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Emergency | ASHRAE 90.1-2010HospitalEmergency | 2.26 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.97 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2010 | Hospital | ER_Trauma | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Emergency | ASHRAE 90.1-2010HospitalEmergency | 2.26 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2010 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 90.1-2010 | Hospital | Nurse Station | ASHRAE 90.1-2010HospitalNurse Station | 0.87 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_NURSEFLR1_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 6.25 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.99 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | Hospital | ER_Exam | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Emergency | ASHRAE 90.1-2010HospitalEmergency | 2.26 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2010 | Hospital | Dining | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | General | ASHRAE 90.1-2010Dining AreaGeneral | 0.65 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 10 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2010 | Hospital | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | For Hospital | ASHRAE 90.1-2010Corridor/TransitionFor Hospital | 0.89 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 1 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2013 | Hospital | Radiology | 136_78_222 | ASHRAE 90.1-2013 | Healthcare Facility | Radiology/Imaging | ASHRAE 90.1-2013Healthcare FacilityRadiology/Imaging | 1.51 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_RADIOLOGY_SCH | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesMedical procedure |  | 15 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 7.28 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 5250 | 0.0001904761905 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2013 | Hospital | PhysTherapy | 154_230_120 | ASHRAE 90.1-2013 | Healthcare Facility | Physical Therapy | ASHRAE 90.1-2013Healthcare FacilityPhysical Therapy | 0.91 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy |  | 15 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 5280 | 0.0001893939394 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2013 | Hospital | PatRoom | 78_167_222 | ASHRAE 90.1-2013 | Healthcare Facility | Patient Room | ASHRAE 90.1-2013Healthcare FacilityPatient Room | 0.62 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room |  |  | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 280 | 0.003571428571 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2013 | Hospital | PatCorridor | 169_31_31 | ASHRAE 90.1-2013 | Corridor | For Hospital | ASHRAE 90.1-2013CorridorFor Hospital | 0.99 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 1 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2013 | Hospital | OR | 169_31_159 | ASHRAE 90.1-2013 | Healthcare Facility | Operating Room | ASHRAE 90.1-2013Healthcare FacilityOperating Room | 2.48 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 2 | 600 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2013 | Hospital | Office | 120_230_199 | ASHRAE 90.1-2013 | Office-Enclosed | General | ASHRAE 90.1-2013Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 6.99 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2013 | Hospital | NurseStn | 31_162_169 | ASHRAE 90.1-2013 | Healthcare Facility | Nurse Station | ASHRAE 90.1-2013Healthcare FacilityNurse Station | 0.71 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_NURSEFLR234_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 7.14 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.76 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2013 | Hospital | Lobby | 31_162_169 | ASHRAE 90.1-2013 | Lobby | General | ASHRAE 90.1-2013LobbyGeneral | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2007Office BuildingsMain entry lobbies | 0.06 | 5 |  | 7.14 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.07 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2013 | Hospital | Lab | 204_120_230 | ASHRAE 90.1-2013 | Laboratory | General | ASHRAE 90.1-2013LaboratoryGeneral | 1.81 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Educational Facilities | Science laboratories | ASHRAE 62.1-2007Educational FacilitiesScience laboratories | 0.18 | 10 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 3.22 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 2 | 2850 | 0.000701754386 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_SCH
90.1-2013 | Hospital | Kitchen | 78_222_133 | ASHRAE 90.1-2013 | Food Preparation | General | ASHRAE 90.1-2013Food PreparationGeneral | 1.21 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 5 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | 70.46 | 0.1 | 0.2 | 0.7 | Hospital BLDG_EQUIP_SCH | 5.47 | 0.2 | 0.5 | 0.1 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH | 0.7 | 5300 | 0.12212 | 0.338 | 924.6539 | 0.50241 |  | Hospital Kitchen_Exhaust_SCH
90.1-2013 | Hospital | ICU_PatRm | 78_167_222 | ASHRAE 90.1-2013 | Healthcare Facility | Patient Room | ASHRAE 90.1-2013Healthcare FacilityPatient Room | 0.62 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2013 | Hospital | ICU_Open | 78_167_222 | ASHRAE 90.1-2013 | Healthcare Facility | Recovery | ASHRAE 90.1-2013Healthcare FacilityRecovery | 1.15 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.19 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2013 | Hospital | ICU_NurseStn | 31_162_169 | ASHRAE 90.1-2013 | Healthcare Facility | Nurse Station | ASHRAE 90.1-2013Healthcare FacilityNurse Station | 0.71 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 5 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.46 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2013 | Hospital | ER_Triage | 169_31_159 | ASHRAE 90.1-2013 | Healthcare Facility | Operating Room | ASHRAE 90.1-2013Healthcare FacilityOperating Room | 2.48 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.97 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2013 | Hospital | ER_Trauma | 169_31_159 | ASHRAE 90.1-2013 | Healthcare Facility | Operating Room | ASHRAE 90.1-2013Healthcare FacilityOperating Room | 2.48 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 2.92 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2013 | Hospital | ER_NurseStn | 31_162_169 | ASHRAE 90.1-2013 | Healthcare Facility | Nurse Station | ASHRAE 90.1-2013Healthcare FacilityNurse Station | 0.71 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_NURSEFLR1_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 6.25 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.99 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2013 | Hospital | ER_Exam | 169_31_159 | ASHRAE 90.1-2013 | Healthcare Facility | Exam/Treatment | ASHRAE 90.1-2013Healthcare FacilityExam/Treatment | 1.66 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_EXTD_SCH | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital BLDG_OCC_EXTD_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 1.09 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_EXTD_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital BLDG_SWH_EXTD_SCH
90.1-2013 | Hospital | Dining | 31_169_34 | ASHRAE 90.1-2013 | Dining Area | General | ASHRAE 90.1-2013Dining AreaGeneral | 0.65 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 10 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0.73 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
90.1-2013 | Hospital | Corridor | 169_31_31 | ASHRAE 90.1-2013 | Corridor | For Hospital | ASHRAE 90.1-2013CorridorFor Hospital | 0.99 |  |  |  | 0 | 0.7 | 0.2 | Hospital BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 1 | Hospital BLDG_OCC_SCH | Hospital ACTIVITY_SCH | 0.0446 |  |  | Hospital INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital BLDG_EQUIP_SCH | Hospital HTGSETP_SCH | Hospital CLGSETP_SCH
DOE Ref 1980-2004 | Hospital | Radiology | 136_78_222 | DOE Ref 1980-2004 | Hospital | Radiology | DOE Ref 1980-2004HospitalRadiology | 2.21 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 |  | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 10 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5250 | 0.0001904761905 | 49 | 0.2 | 0.05 | Hospital SWH Extd
DOE Ref 1980-2004 | Hospital | PhysTherapy | 154_230_120 | DOE Ref 1980-2004 | Hospital | PhysTherapy | DOE Ref 1980-2004HospitalPhysTherapy | 2.5 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 |  | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5280 | 0.0001893939394 | 49 | 0.2 | 0.05 | Hospital SWH
DOE Ref 1980-2004 | Hospital | PatRoom | 78_167_222 | DOE Ref 1980-2004 | Hospital | PatRoom | DOE Ref 1980-2004HospitalPatRoom | 2.19 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room |  |  | 2 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 1 | 280 | 0.003571428571 | 49 | 0.2 | 0.05 | Hospital SWH Extd
DOE Ref 1980-2004 | Hospital | PatCorridor | 169_31_31 | DOE Ref 1980-2004 | Hospital | PatCorridor | DOE Ref 1980-2004HospitalPatCorridor | 1.36 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp
DOE Ref 1980-2004 | Hospital | OR | 169_31_159 | DOE Ref 1980-2004 | Hospital | OR | DOE Ref 1980-2004HospitalOR | 9.75 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 2 | 600 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital SWH
DOE Ref 1980-2004 | Hospital | Office | 120_230_199 | DOE Ref 1980-2004 | Hospital | Office | DOE Ref 1980-2004HospitalOffice | 2.4 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 6.99 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
DOE Ref 1980-2004 | Hospital | NurseStn | 31_162_169 | DOE Ref 1980-2004 | Hospital | NurseStn | DOE Ref 1980-2004HospitalNurseStn | 1.46 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 |  | 7.14 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 1.04 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
DOE Ref 1980-2004 | Hospital | Lobby | 31_162_169 | DOE Ref 1980-2004 | Hospital | Lobby | DOE Ref 1980-2004HospitalLobby | 1.46 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 7.14 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 0.1 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
DOE Ref 1980-2004 | Hospital | Lab | 204_120_230 | DOE Ref 1980-2004 | Hospital | Lab | DOE Ref 1980-2004HospitalLab | 2.1 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 |  | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 2 | 2850 | 0.000701754386 | 49 | 0.2 | 0.05 | Hospital SWH
DOE Ref 1980-2004 | Hospital | Kitchen | 78_222_133 | DOE Ref 1980-2004 | Hospital | Kitchen | DOE Ref 1980-2004HospitalKitchen | 1.42 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | 96.7 | 0.1 | 0.2 | 0.7 | Hospital Kitchen Gas | 7.5 | 0.2 | 0.5 | 0.1 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital SWH Extd | 0.7 | 5300 | 0.1221241016 | 0.338 | 924.6539123 | 0.5024115756 |  | Hospital Kitchen Exhaust
DOE Ref 1980-2004 | Hospital | ICU_PatRm | 78_167_222 | DOE Ref 1980-2004 | Hospital | ICU_PatRm | DOE Ref 1980-2004HospitalICU_PatRm | 3.84 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
DOE Ref 1980-2004 | Hospital | ICU_Open | 78_167_222 | DOE Ref 1980-2004 | Hospital | ICU_Open | DOE Ref 1980-2004HospitalICU_Open | 3.84 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
DOE Ref 1980-2004 | Hospital | ICU_NurseStn | 31_162_169 | DOE Ref 1980-2004 | Hospital | ICU_NurseStn | DOE Ref 1980-2004HospitalICU_NurseStn | 1.71 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
DOE Ref 1980-2004 | Hospital | ER_Triage | 169_31_159 | DOE Ref 1980-2004 | Hospital | ER_Triage | DOE Ref 1980-2004HospitalER_Triage | 3.84 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
DOE Ref 1980-2004 | Hospital | ER_Trauma | 169_31_159 | DOE Ref 1980-2004 | Hospital | ER_Trauma | DOE Ref 1980-2004HospitalER_Trauma | 3.84 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
DOE Ref 1980-2004 | Hospital | ER_NurseStn | 31_162_169 | DOE Ref 1980-2004 | Hospital | ER_NurseStn | DOE Ref 1980-2004HospitalER_NurseStn | 1.66 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 6.25 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 1.36 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
DOE Ref 1980-2004 | Hospital | ER_Exam | 169_31_159 | DOE Ref 1980-2004 | Hospital | ER_Exam | DOE Ref 1980-2004HospitalER_Exam | 3.84 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
DOE Ref 1980-2004 | Hospital | Dining | 31_169_34 | DOE Ref 1980-2004 | Hospital | Dining | DOE Ref 1980-2004HospitalDining | 2.58 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 |  | 10 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
DOE Ref 1980-2004 | Hospital | Corridor | 169_31_31 | DOE Ref 1980-2004 | Hospital | Corridor | DOE Ref 1980-2004HospitalCorridor | 1.36 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
189.1-2009 | LargeHotel | Banquet | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral | 1.17 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 |  | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  |  | LargeHotel Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | LargeHotel | Cafe | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Hotel | ASHRAE 189.1-2009Dining AreaFor Hotel | 1.17 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 67 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  |  | LargeHotel Infil Quarter On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | LargeHotel | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral | 0.45 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  |  | LargeHotel Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel Corridor HtgSetp | LargeHotel Corridor ClgSetp
189.1-2009 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | ASHRAE 189.1-2009Hotel/MotelGuest Rooms | 0.99 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity | 0.0446 |  |  | LargeHotel Infil Quarter On | [5 empty] | 0.68 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
189.1-2009 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral | 1.08 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  |  | LargeHotel Infil Quarter On | 373.8 | 0.1 | 0.2 | 0.7 | LargeHotel Kitchen Gas | 24.16 | 0.2 | 0.5 | 0.1 | LargeHotel Kitchen Equip | LargeHotel Kitchen HtgSetp | LargeHotel Kitchen ClgSetp | 133 | 1112 | 0.1196043165 | 49 | 0.2 | 0.05 | LargeHotel SWH Kitchen | 0.7 | 4000 | 0.1221241016 | 0.338 | 697.852 | 0.50241 |  | LargeHotel Kitchen Exhaust
189.1-2009 | LargeHotel | Laundry | 120_149_230 | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | ASHRAE 189.1-2009HospitalLaundry-Washing | 0.54 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 |  | 4 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  |  | LargeHotel Infil Quarter On | 123.8 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Gas | 2.93 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Equip | LargeHotel HtgSetp | LargeHotel ClgSetp | 156.6 | 840 | 0.1864285714 | 60 | 0.2 | 0.05 | LargeHotel SWH Laundry | 0.59523 | 500 | 0.103845201 | 0.338 | 87.23150116 | 0.5024115756 |  | LargeHotel Laundry Exhaust_Always On
189.1-2009 | LargeHotel | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | For Hotel | ASHRAE 189.1-2009LobbyFor Hotel | 0.99 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 30 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  |  | LargeHotel Infil Quarter On | [5 empty] | 0.38 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral | 1.35 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  |  | LargeHotel Infil Quarter On | [5 empty] | 0.26 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | LargeHotel | Retail | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area | 1.53 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  |  | LargeHotel Infil Quarter On | [5 empty] | 0.51 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | LargeHotel | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral | 0.72 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 |  | 2 | LargeHotel Bldg Occ | LargeHotel Activity | 0.0446 |  |  | LargeHotel Infil Quarter On | [5 empty] | 0.13 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
90.1-2004 | LargeHotel | Banquet | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral | 1.3 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 |  | 67 | HotelLarge MeetingRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0595 |  |  | HotelLarge INFIL_SCH | [5 empty] | 6.301 | 0 | 0.5 | 0 | HotelLarge Kitchen_Elec_Equip_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2007 | LargeHotel | Banquet | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral | 1.3 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | 0.06 | 5 |  | 67 | HotelLarge MeetingRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0446 |  |  | HotelLarge INFIL_SCH | [5 empty] | 6.301 | 0 | 0.5 | 0 | HotelLarge Kitchen_Elec_Equip_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | LargeHotel | Banquet | 230_196_120 | ASHRAE 90.1-2010 | Dining Area | For Hotel | ASHRAE 90.1-2010Dining AreaFor Hotel | 0.89 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | 0.06 | 5 |  | 70 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.025458 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 6.301 | 0 | 0.5 | 0 | HotelLarge Kitchen_Elec_Equip_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | [10 empty] | 1 |  | 0 | 1017.4311 | HotelLarge Kitchen_Exhaust_SCH
90.1-2013 | LargeHotel | Banquet | 230_196_120 | ASHRAE 90.1-2013 | Dining Area | General | ASHRAE 90.1-2013Dining AreaGeneral | 0.65 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | 0.06 | 5 |  | 70 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.025458 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 6.301 | 0 | 0.5 | 0 | HotelLarge Kitchen_Elec_Equip_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | [10 empty] | 1 |  | 0 | 2000 | HotelLarge Kitchen_Exhaust_SCH
DOE Ref 1980-2004 | LargeHotel | Banquet | 230_196_120 | DOE Ref 1980-2004 | LargeHotel | Banquet | DOE Ref 1980-2004LargeHotelBanquet | 2.56 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dining rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDining rooms | 0 | 21.2 |  | 67 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 6.3 | 0 | 0.5 | 0 | LargeHotel Kitchen_Elec_Equip_SCH | LargeHotel HtgSetp | LargeHotel ClgSetp | [10 empty] | 1 |  | 1e-05 | 2000 | Always On
DOE Ref Pre-1980 | LargeHotel | Banquet | 230_196_120 | DOE Ref Pre-1980 | LargeHotel | Banquet | DOE Ref Pre-1980LargeHotelBanquet | 2.56 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dining rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDining rooms | 0 | 21.2 |  | 67 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 6.3 | 0 | 0.5 | 0 | LargeHotel Kitchen_Elec_Equip_SCH | LargeHotel HtgSetp | LargeHotel ClgSetp | [10 empty] | 1 |  | 1e-05 | 2000 | Always On
90.1-2004 | LargeHotel | Basement | 120_149_230 | ASHRAE 90.1-2004 | Basement | For Hotel | ASHRAE 90.1-2004BasementFor Hotel | 0.9 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | 0.06 | 5 |  | 5 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.5 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2007 | LargeHotel | Basement | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | 0.06 | 5 |  | 5 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.5 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | LargeHotel | Basement | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH_2010 | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | 0.06 | 5 |  | 5 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.5 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH_2010 | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2013 | LargeHotel | Basement | 120_149_230 | ASHRAE 90.1-2013 | Storage | General | ASHRAE 90.1-2013StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH_2010 | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Multipurpose assembly | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesMultipurpose assembly | 0.06 | 5 |  | 5 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.5 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH_2010 | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
DOE Ref 1980-2004 | LargeHotel | Basement | 120_149_230 | DOE Ref 1980-2004 | LargeHotel | Basement | DOE Ref 1980-2004LargeHotelBasement | 0.7 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 2.5 | LargeHotel Common Occ | LargeHotel Activity | [9 empty] | 0.5 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
DOE Ref Pre-1980 | LargeHotel | Basement | 120_149_230 | DOE Ref Pre-1980 | LargeHotel | Basement | DOE Ref Pre-1980LargeHotelBasement | 0.7 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 2.5 | LargeHotel Common Occ | LargeHotel Activity | [9 empty] | 0.5 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
90.1-2004 | LargeHotel | Cafe | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | For Hotel | ASHRAE 90.1-2004Dining AreaFor Hotel | 1.3 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 67 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0595 |  |  | HotelLarge INFIL_SCH | [5 empty] | 0.5 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2007 | LargeHotel | Cafe | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | For Hotel | ASHRAE 90.1-2007Dining AreaFor Hotel | 1.3 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 67 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  |  | HotelLarge INFIL_SCH | [5 empty] | 0.5 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | LargeHotel | Cafe | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | For Hotel | ASHRAE 90.1-2010Dining AreaFor Hotel | 0.89 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 70 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.5 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2013 | LargeHotel | Cafe | 31_169_34 | ASHRAE 90.1-2013 | Dining Area | General | ASHRAE 90.1-2013Dining AreaGeneral | 0.65 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 70 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.5 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
DOE Ref 1980-2004 | LargeHotel | Cafe | 31_169_34 | DOE Ref 1980-2004 | LargeHotel | Cafe | DOE Ref 1980-2004LargeHotelCafe | 1.46 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 67 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 0.5 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
DOE Ref Pre-1980 | LargeHotel | Cafe | 31_169_34 | DOE Ref Pre-1980 | LargeHotel | Cafe | DOE Ref Pre-1980LargeHotelCafe | 2.56 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 67 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 0.5 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
90.1-2004 | LargeHotel | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral | 0.5 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0595 |  |  | HotelLarge INFIL_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2007 | LargeHotel | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral | 0.5 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 1 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  |  | HotelLarge INFIL_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | LargeHotel | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral | 0.66 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_CORRIDOR_SCH_2010 | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.019242 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2013 | LargeHotel | Corridor | 169_31_31 | ASHRAE 90.1-2013 | Corridor | General | ASHRAE 90.1-2013CorridorGeneral | 0.66 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_CORRIDOR_SCH_2010 | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.019242 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
DOE Ref 1980-2004 | LargeHotel | Corridor | 169_31_31 | DOE Ref 1980-2004 | LargeHotel | Corridor | DOE Ref 1980-2004LargeHotelCorridor | 1.22 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel Corridor HtgSetp | LargeHotel Corridor ClgSetp
DOE Ref Pre-1980 | LargeHotel | Corridor | 169_31_31 | DOE Ref Pre-1980 | Hospital | Corridor | DOE Ref Pre-1980HospitalCorridor | 1.22 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel Corridor HtgSetp | LargeHotel Corridor ClgSetp
90.1-2004 | LargeHotel | Corridor2 | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral | 0.66 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2007 | LargeHotel | Corridor2 | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral | 0.66 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | LargeHotel | Corridor2 | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral | 0.66 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_CORRIDOR_SCH_2010 | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2013 | LargeHotel | Corridor2 | 169_31_31 | ASHRAE 90.1-2013 | Corridor | General | ASHRAE 90.1-2013CorridorGeneral | 0.66 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_CORRIDOR_SCH_2010 | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
DOE Ref 1980-2004 | LargeHotel | Corridor2 | 169_31_31 | DOE Ref 1980-2004 | LargeHotel | Corridor | DOE Ref 1980-2004LargeHotelCorridor | 1.22 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel Corridor HtgSetp | LargeHotel Corridor ClgSetp
DOE Ref Pre-1980 | LargeHotel | Corridor2 | 169_31_31 | DOE Ref Pre-1980 | Hospital | Corridor | DOE Ref Pre-1980HospitalCorridor | 1.22 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel Corridor HtgSetp | LargeHotel Corridor ClgSetp
90.1-2004 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2004 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2004Hotel/MotelGuest Rooms | 1.1 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 3.57 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0595 |  |  | HotelLarge INFIL_SCH | [5 empty] | 0.627 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Base | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
90.1-2007 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2007 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2007Hotel/MotelGuest Rooms | 1.1 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 3.57 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0446 |  |  | HotelLarge INFIL_SCH | [5 empty] | 0.627 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Base | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
90.1-2010 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Hotel | ASHRAE 90.1-2010Guest RoomFor Hotel | 1.11 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 3.57 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.627 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Base | HotelLarge Adva_OccGuestRoom_HtgSP_Sch | HotelLarge Adva_OccGuestRoom_ClgSP_Sch | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
90.1-2013 | LargeHotel | GuestRoom | 78_167_222 | ASHRAE 90.1-2013 | Guest Room | General | ASHRAE 90.1-2013Guest RoomGeneral | 0.91 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 3.57 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.627 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Adva | HotelLarge Adva_OccGuestRoom_HtgSP_Sch | HotelLarge Adva_OccGuestRoom_ClgSP_Sch | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
DOE Ref 1980-2004 | LargeHotel | GuestRoom | 78_167_222 | DOE Ref 1980-2004 | LargeHotel | GuestRoom | DOE Ref 1980-2004LargeHotelGuestRoom | 1.77 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel GuestRoom_Ltg_Sch_Base | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
DOE Ref Pre-1980 | LargeHotel | GuestRoom | 78_167_222 | DOE Ref Pre-1980 | LargeHotel | GuestRoom | DOE Ref Pre-1980LargeHotelGuestRoom | 1.77 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel GuestRoom_Ltg_Sch_Base | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
90.1-2004 | LargeHotel | GuestRoom2 | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Hotel | ASHRAE 90.1-2010Guest RoomFor Hotel | 1.11 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 5.68 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.977 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Base | HotelLarge Adva_OccGuestRoom_HtgSP_Sch | HotelLarge Adva_OccGuestRoom_ClgSP_Sch | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
90.1-2007 | LargeHotel | GuestRoom2 | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Hotel | ASHRAE 90.1-2010Guest RoomFor Hotel | 1.11 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 5.68 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.977 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Base | HotelLarge Adva_OccGuestRoom_HtgSP_Sch | HotelLarge Adva_OccGuestRoom_ClgSP_Sch | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
90.1-2010 | LargeHotel | GuestRoom2 | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Hotel | ASHRAE 90.1-2010Guest RoomFor Hotel | 1.11 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 5.68 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.977 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Base | HotelLarge Adva_OccGuestRoom_HtgSP_Sch | HotelLarge Adva_OccGuestRoom_ClgSP_Sch | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
90.1-2013 | LargeHotel | GuestRoom2 | 78_167_222 | ASHRAE 90.1-2013 | Guest Room | General | ASHRAE 90.1-2013Guest RoomGeneral | 0.91 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 5.68 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.977 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Adva | HotelLarge Adva_OccGuestRoom_HtgSP_Sch | HotelLarge Adva_OccGuestRoom_ClgSP_Sch | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
DOE Ref 1980-2004 | LargeHotel | GuestRoom2 | 78_167_222 | DOE Ref 1980-2004 | LargeHotel | GuestRoom | DOE Ref 1980-2004LargeHotelGuestRoom | 1.77 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel GuestRoom_Ltg_Sch_Base | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 5.68 | LargeHotel GuestRoom Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
DOE Ref Pre-1980 | LargeHotel | GuestRoom2 | 78_167_222 | DOE Ref Pre-1980 | LargeHotel | GuestRoom | DOE Ref Pre-1980LargeHotelGuestRoom | 1.77 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel GuestRoom_Ltg_Sch_Base | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 5.68 | LargeHotel GuestRoom Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
90.1-2004 | LargeHotel | GuestRoom3 | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Hotel | ASHRAE 90.1-2010Guest RoomFor Hotel | 1.11 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 3.57 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.056661 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.627 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Base | HotelLarge Adva_OccGuestRoom_HtgSP_Sch | HotelLarge Adva_OccGuestRoom_ClgSP_Sch | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
90.1-2007 | LargeHotel | GuestRoom3 | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Hotel | ASHRAE 90.1-2010Guest RoomFor Hotel | 1.11 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 3.57 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.056661 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.627 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Base | HotelLarge Adva_OccGuestRoom_HtgSP_Sch | HotelLarge Adva_OccGuestRoom_ClgSP_Sch | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
90.1-2010 | LargeHotel | GuestRoom3 | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Hotel | ASHRAE 90.1-2010Guest RoomFor Hotel | 1.11 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 3.57 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.056661 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.627 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Base | HotelLarge Adva_OccGuestRoom_HtgSP_Sch | HotelLarge Adva_OccGuestRoom_ClgSP_Sch | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
90.1-2013 | LargeHotel | GuestRoom3 | 78_167_222 | ASHRAE 90.1-2013 | Guest Room | General | ASHRAE 90.1-2013Guest RoomGeneral | 0.91 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 3.57 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.056661 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.627 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Adva | HotelLarge Adva_OccGuestRoom_HtgSP_Sch | HotelLarge Adva_OccGuestRoom_ClgSP_Sch | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
DOE Ref 1980-2004 | LargeHotel | GuestRoom3 | 78_167_222 | DOE Ref 1980-2004 | LargeHotel | GuestRoom | DOE Ref 1980-2004LargeHotelGuestRoom | 1.77 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel GuestRoom_Ltg_Sch_Base | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
DOE Ref Pre-1980 | LargeHotel | GuestRoom3 | 78_167_222 | DOE Ref Pre-1980 | LargeHotel | GuestRoom | DOE Ref Pre-1980LargeHotelGuestRoom | 1.77 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel GuestRoom_Ltg_Sch_Base | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 3.57 | LargeHotel GuestRoom Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
90.1-2004 | LargeHotel | GuestRoom4 | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Hotel | ASHRAE 90.1-2010Guest RoomFor Hotel | 1.11 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 5.68 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.050904 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.977 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Base | HotelLarge Adva_OccGuestRoom_HtgSP_Sch | HotelLarge Adva_OccGuestRoom_ClgSP_Sch | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
90.1-2007 | LargeHotel | GuestRoom4 | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Hotel | ASHRAE 90.1-2010Guest RoomFor Hotel | 1.11 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 5.68 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.050904 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.977 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Base | HotelLarge Adva_OccGuestRoom_HtgSP_Sch | HotelLarge Adva_OccGuestRoom_ClgSP_Sch | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
90.1-2010 | LargeHotel | GuestRoom4 | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Hotel | ASHRAE 90.1-2010Guest RoomFor Hotel | 1.11 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 5.68 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.050904 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.977 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Base | HotelLarge Adva_OccGuestRoom_HtgSP_Sch | HotelLarge Adva_OccGuestRoom_ClgSP_Sch | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
90.1-2013 | LargeHotel | GuestRoom4 | 78_167_222 | ASHRAE 90.1-2013 | Guest Room | General | ASHRAE 90.1-2013Guest RoomGeneral | 0.91 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 5.68 | HotelLarge GuestRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.050904 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.977 | 0 | 0.5 | 0 | HotelLarge GuestRoom_Eqp_Sch_Adva | HotelLarge Adva_OccGuestRoom_HtgSP_Sch | HotelLarge Adva_OccGuestRoom_ClgSP_Sch | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | HotelLarge GuestRoom_SWH_Sch
DOE Ref 1980-2004 | LargeHotel | GuestRoom4 | 78_167_222 | DOE Ref 1980-2004 | LargeHotel | GuestRoom | DOE Ref 1980-2004LargeHotelGuestRoom | 1.77 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel GuestRoom_Ltg_Sch_Base | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 5.68 | LargeHotel GuestRoom Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
DOE Ref Pre-1980 | LargeHotel | GuestRoom4 | 78_167_222 | DOE Ref Pre-1980 | LargeHotel | GuestRoom | DOE Ref Pre-1980LargeHotelGuestRoom | 1.77 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel GuestRoom_Ltg_Sch_Base | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 5.68 | LargeHotel GuestRoom Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 1.33 | 0 | 0.5 | 0 | LargeHotel GuestRoom Equip | LargeHotel GuestRoom HtgSetp | LargeHotel GuestRoom ClgSetp | 1.25 | 420 | 0.002976190476 | 43.3 | 0.2 | 0.05 | LargeHotel SWH GuestRoom
90.1-2004 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral | 1.2 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0595 |  |  | HotelLarge INFIL_SCH | 767 | 0.1 | 0.2 | 0.7 | HotelLarge Kitchen_Gas_Equip_SCH | 47.2 | 0.2 | 0.5 | 0.1 | HotelLarge Kitchen_Elec_Equip_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 133 | 1112 | 0.1196043165 | 49 | 0.2 | 0.05 | HotelLarge BLDG_SWH_SCH |  |  |  | 0.16 |  | 125 | 4000 | HotelLarge Kitchen_Exhaust_SCH
90.1-2007 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral | 1.2 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 5 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  |  | HotelLarge INFIL_SCH | 767 | 0.1 | 0.2 | 0.7 | HotelLarge Kitchen_Gas_Equip_SCH | 47.2 | 0.2 | 0.5 | 0.1 | HotelLarge Kitchen_Elec_Equip_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 133 | 1112 | 0.1196043165 | 49 | 0.2 | 0.05 | HotelLarge BLDG_SWH_SCH |  |  |  | 0.16 |  | 125 | 4000 | HotelLarge Kitchen_Exhaust_SCH
90.1-2010 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral | 0.99 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 20 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0513 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | 767 | 0.1 | 0.2 | 0.7 | HotelLarge Kitchen_Gas_Equip_SCH | 47.2 | 0.2 | 0.5 | 0.1 | HotelLarge Kitchen_Elec_Equip_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 133 | 1112 | 0.1196043165 | 49 | 0.2 | 0.05 | HotelLarge BLDG_SWH_SCH |  |  |  | 0.16 |  | 125 | 4000 | HotelLarge Kitchen_Exhaust_SCH | HotelLarge Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule
90.1-2013 | LargeHotel | Kitchen | 78_222_133 | ASHRAE 90.1-2013 | Food Preparation | General | ASHRAE 90.1-2013Food PreparationGeneral | 1.21 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 20 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0513 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | 767 | 0.1 | 0.2 | 0.7 | HotelLarge Kitchen_Gas_Equip_SCH | 47.2 | 0.2 | 0.5 | 0.1 | HotelLarge Kitchen_Elec_Equip_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 133 | 1112 | 0.1196043165 | 49 | 0.2 | 0.05 | HotelLarge BLDG_SWH_SCH |  |  |  | 0.385 |  | 125 | 4000 | HotelLarge Kitchen_Exhaust_SCH | HotelLarge Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule
DOE Ref 1980-2004 | LargeHotel | Kitchen | 78_222_133 | DOE Ref 1980-2004 | LargeHotel | Kitchen | DOE Ref 1980-2004LargeHotelKitchen | 1.56 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | 511 | 0.1 | 0.2 | 0.7 | LargeHotel Kitchen Gas | 47.1989 | 0.2 | 0.5 | 0.1 | LargeHotel Kitchen_Elec_Equip_SCH | LargeHotel Kitchen HtgSetp | LargeHotel Kitchen ClgSetp | 133 | 1112 | 0.1196043165 | 49 | 0.2 | 0.05 | LargeHotel SWH Kitchen |  |  |  | 1 | 689 | 1e-05 | 94.2478 | HotelLarge Kitchen_Exhaust_SCH
DOE Ref Pre-1980 | LargeHotel | Kitchen | 78_222_133 | DOE Ref Pre-1980 | LargeHotel | Kitchen | DOE Ref Pre-1980LargeHotelKitchen | 1.56 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | 511 | 0.1 | 0.2 | 0.7 | LargeHotel Kitchen Gas | 47.1989 | 0.2 | 0.5 | 0.1 | LargeHotel Kitchen_Elec_Equip_SCH | LargeHotel Kitchen HtgSetp | LargeHotel Kitchen ClgSetp | 133 | 1112 | 0.1196043165 | 49 | 0.2 | 0.05 | LargeHotel SWH Kitchen | 0.7 | 4000 | 0.12215 | 1 | 698 | 1e-05 | 94.2478 | HotelLarge Kitchen_Exhaust_SCH
90.1-2004 | LargeHotel | Laundry | 120_149_230 | ASHRAE 90.1-2004 | Hospital | Laundry-Washing | ASHRAE 90.1-2004HospitalLaundry-Washing | 0.6 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 |  | 4 | HotelLarge LaundryRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0595 |  |  | HotelLarge INFIL_SCH | 170 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | 5.73 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 156.6 | 840 | 0.1864285714 | 60 | 0.2 | 0.05 | HotelLarge LaundryRoom_SWH_Sch |  |  |  | 0.16 |  | 125 | 500 | HotelLarge Hours_of_operation
90.1-2007 | LargeHotel | Laundry | 120_149_230 | ASHRAE 90.1-2007 | Hospital | Laundry-Washing | ASHRAE 90.1-2007HospitalLaundry-Washing | 0.6 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Retail | Coinoperated laundries | ASHRAE 62.1-2004RetailCoinoperated laundries | 0.06 | 7.5 |  | 4 | HotelLarge LaundryRoom_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0446 |  |  | HotelLarge INFIL_SCH | 170 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | 5.73 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 156.6 | 840 | 0.1864285714 | 60 | 0.2 | 0.05 | HotelLarge LaundryRoom_SWH_Sch |  |  |  | 0.16 |  | 125 | 500 | HotelLarge Hours_of_operation
90.1-2010 | LargeHotel | Laundry | 120_149_230 | ASHRAE 90.1-2010 | Hospital | Laundry-Washing | ASHRAE 90.1-2010HospitalLaundry-Washing | 0.6 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | ASHRAE 62.1-2007RetailCoinoperated laundries | 0.06 | 7.5 |  | 10 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | 170 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | 5.73 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 156.6 | 840 | 0.1864285714 | 60 | 0.2 | 0.05 | HotelLarge LaundryRoom_SWH_Sch |  |  |  | 0.16 |  | 125 | 500 | HotelLarge Hours_of_operation
90.1-2013 | LargeHotel | Laundry | 120_149_230 | ASHRAE 90.1-2010 | Hospital | Laundry-Washing | ASHRAE 90.1-2010HospitalLaundry-Washing | 0.6 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | ASHRAE 62.1-2007RetailCoinoperated laundries | 0.06 | 7.5 |  | 10 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | 170 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | 5.73 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH | 156.6 | 840 | 0.1864285714 | 60 | 0.2 | 0.05 | HotelLarge LaundryRoom_SWH_Sch |  |  |  | 0.385 |  | 125 | 500 | HotelLarge Hours_of_operation
DOE Ref 1980-2004 | LargeHotel | Laundry | 120_149_230 | DOE Ref 1980-2004 | LargeHotel | Laundry | DOE Ref 1980-2004LargeHotelLaundry | 1.14 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 |  | 4 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | 170 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Gas | 5.73 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Equip | LargeHotel HtgSetp | LargeHotel ClgSetp | 156.6 | 840 | 0.1864285714 | 60 | 0.2 | 0.05 | LargeHotel SWH Laundry |  |  |  | 0.34 | 87 | 125 | 500 | Always On
DOE Ref Pre-1980 | LargeHotel | Laundry | 120_149_230 | DOE Ref Pre-1980 | LargeHotel | Laundry | DOE Ref Pre-1980LargeHotelLaundry | 1.14 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 |  | 4 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | 170 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Gas | 5.73 | 0 | 0.5 | 0 | LargeHotel LaundryRoom Equip | LargeHotel HtgSetp | LargeHotel ClgSetp | 156.6 | 840 | 0.1864285714 | 60 | 0.2 | 0.05 | LargeHotel SWH Laundry | 0.59523 | 500 | 0.1035696092 | 0.34 | 87 | 125 | 500.0557 | Always On
90.1-2004 | LargeHotel | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | For Hotel | ASHRAE 90.1-2004LobbyFor Hotel | 1.1 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 30 | HotelLarge Lobby_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0595 |  |  | HotelLarge INFIL_SCH | [5 empty] | 0.75 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2007 | LargeHotel | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | For Hotel | ASHRAE 90.1-2007LobbyFor Hotel | 1.1 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 |  | 30 | HotelLarge Lobby_Occ_Sch | HotelLarge ACTIVITY_SCH | 0.0446 |  |  | HotelLarge INFIL_SCH | [5 empty] | 0.75 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | LargeHotel | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | For Hotel | ASHRAE 90.1-2010LobbyFor Hotel | 1.06 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 |  | 30 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.75 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2013 | LargeHotel | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | For Hotel | ASHRAE 90.1-2010LobbyFor Hotel | 1.06 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 |  | 30 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.75 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
DOE Ref 1980-2004 | LargeHotel | Lobby | 230_157_120 | DOE Ref 1980-2004 | LargeHotel | Lobby | DOE Ref 1980-2004LargeHotelLobby | 1.88 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 30 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 0.75 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
DOE Ref Pre-1980 | LargeHotel | Lobby | 230_157_120 | DOE Ref Pre-1980 | LargeHotel | Lobby | DOE Ref Pre-1980LargeHotelLobby | 1.88 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 30 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 0.75 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
90.1-2004 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral | 1.5 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0595 |  |  | HotelLarge INFIL_SCH | [5 empty] | 0.5 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2007 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral | 1.5 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 0 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  |  | HotelLarge INFIL_SCH | [5 empty] | 0.5 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral | 0.95 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.5 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2013 | LargeHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral | 0.95 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.5 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
DOE Ref 1980-2004 | LargeHotel | Mechanical | 41_31_169 | DOE Ref 1980-2004 | LargeHotel | Mechanical | DOE Ref 1980-2004LargeHotelMechanical | 0.8 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 0.5 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
DOE Ref Pre-1980 | LargeHotel | Mechanical | 41_31_169 | DOE Ref Pre-1980 | LargeHotel | Mechanical | DOE Ref Pre-1980LargeHotelMechanical | 0.8 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 0.5 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
90.1-2004 | LargeHotel | Retail | 171_222_78 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area | 1.7 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0595 |  |  | HotelLarge INFIL_SCH | [5 empty] | 1 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2007 | LargeHotel | Retail | 171_222_78 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area | 1.7 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Retail | General Sales | ASHRAE 62.1-2004RetailGeneral Sales | 0.12 | 7.5 |  | 15 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  |  | HotelLarge INFIL_SCH | [5 empty] | 1 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | LargeHotel | Retail | 171_222_78 | ASHRAE 90.1-2010 | Retail | For Hotel | ASHRAE 90.1-2010RetailFor Hotel | 1.4 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 |  | 15 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 1 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2013 | LargeHotel | Retail | 171_222_78 | ASHRAE 90.1-2010 | Retail | For Hotel | ASHRAE 90.1-2010RetailFor Hotel | 1.4 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 |  | 15 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 1 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
DOE Ref 1980-2004 | LargeHotel | Retail | 171_222_78 | DOE Ref 1980-2004 | LargeHotel | Retail | DOE Ref 1980-2004LargeHotelRetail | 3.54 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
DOE Ref Pre-1980 | LargeHotel | Retail | 171_222_78 | DOE Ref Pre-1980 | LargeHotel | Retail | DOE Ref Pre-1980LargeHotelRetail | 3.54 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
90.1-2004 | LargeHotel | Retail2 | 171_222_78 | ASHRAE 90.1-2010 | Retail | For Hotel | ASHRAE 90.1-2010RetailFor Hotel | 1.4 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 |  | 15 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 1 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2007 | LargeHotel | Retail2 | 171_222_78 | ASHRAE 90.1-2010 | Retail | For Hotel | ASHRAE 90.1-2010RetailFor Hotel | 1.4 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 |  | 15 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 1 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | LargeHotel | Retail2 | 171_222_78 | ASHRAE 90.1-2010 | Retail | For Hotel | ASHRAE 90.1-2010RetailFor Hotel | 1.4 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 |  | 15 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 1 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2013 | LargeHotel | Retail2 | 171_222_78 | ASHRAE 90.1-2010 | Retail | For Hotel | ASHRAE 90.1-2010RetailFor Hotel | 1.4 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 |  | 15 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 1 | 0 | 0.5 | 0 | HotelLarge BLDG_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
DOE Ref 1980-2004 | LargeHotel | Retail2 | 171_222_78 | DOE Ref 1980-2004 | LargeHotel | Retail | DOE Ref 1980-2004LargeHotelRetail | 3.54 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
DOE Ref Pre-1980 | LargeHotel | Retail2 | 171_222_78 | DOE Ref Pre-1980 | LargeHotel | Retail | DOE Ref Pre-1980LargeHotelRetail | 3.54 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
90.1-2004 | LargeHotel | Storage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral | 0.8 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 |  | 2 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0595 |  |  | HotelLarge INFIL_SCH | [5 empty] | 0.25 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2007 | LargeHotel | Storage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral | 0.8 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 2 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.0446 |  |  | HotelLarge INFIL_SCH | [5 empty] | 0.25 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2010 | LargeHotel | Storage | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_STORAGE_SCH_2010 | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.25 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
90.1-2013 | LargeHotel | Storage | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | HotelLarge BLDG_LIGHT_STORAGE_SCH_2010 | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | HotelLarge BLDG_OCC_SCH | HotelLarge ACTIVITY_SCH | 0.112 |  |  | HotelLarge INFIL_QUARTER_ON_SCH | [5 empty] | 0.25 | 0 | 0.5 | 0 | HotelLarge BASEMENT_EQUIP_SCH | HotelLarge HTGSETP_SCH | HotelLarge CLGSETP_SCH
DOE Ref 1980-2004 | LargeHotel | Storage | 120_149_230 | DOE Ref 1980-2004 | LargeHotel | Storage | DOE Ref 1980-2004LargeHotelStorage | 0.37 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 |  | 2 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 0.25 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
DOE Ref Pre-1980 | LargeHotel | Storage | 120_149_230 | DOE Ref Pre-1980 | LargeHotel | Storage | DOE Ref Pre-1980LargeHotelStorage | 0.37 |  |  |  | 0 | 0.7 | 0.2 | LargeHotel Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 |  | 2 | LargeHotel Common Occ | LargeHotel Activity |  | 0.2232 |  | LargeHotel Infil Quarter On | [5 empty] | 0.25 | 0 | 0.5 | 0 | LargeHotel Bldg Equip | LargeHotel HtgSetp | LargeHotel ClgSetp
189.1-2009 | MidriseApartment | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral | 0.99 |  |  |  | 0 | 0.7 | 0.2 | MidriseApartment Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 2.11 | MidriseApartment Office Occ | MidriseApartment Activity | 0.0446 |  |  | MidriseApartment Infil | [5 empty] | 0.87 | 0 | 0.5 | 0 | MidriseApartment Office Equip | MidriseApartment Office HtgSetp | MidriseApartment Office ClgSetp
189.1-2009 | MidriseApartment | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral | 0.45 |  |  |  | 0 | 0.7 | 0.2 | MidriseApartment Corridor Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 |  |  | 0.0446 |  |  | MidriseApartment Infil | [5 empty] | 0 | 0 | 0.5 | 0 |  | MidriseApartment Corridor HtgSetp | MidriseApartment Corridor ClgSetp
189.1-2009 | MidriseApartment | Apartment | 78_167_222 | ASHRAE 189.1-2009 | Dormitory | Living Quarters | ASHRAE 189.1-2009DormitoryLiving Quarters | 0.99 |  |  |  | 0 | 0.7 | 0.2 | MidriseApartment Apartment Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 2.63 | MidriseApartment Apartment Occ | MidriseApartment Activity | 0.0446 |  |  | MidriseApartment Infil | [5 empty] | 0.61966 | 0 | 0.5 | 0 | MidriseApartment Apartment Equip | MidriseApartment Apartment HtgSetp | MidriseApartment Apartment ClgSetp | 3.5 | 950 | 0.003684210526 | 43.3 | 0.2 | 0.05 | MidriseApartment DHW
DOE Ref Pre-1980 | Hospital | Radiology | 136_78_222 | DOE Ref Pre-1980 | Hospital | Radiology | DOE Ref Pre-1980HospitalRadiology | 3.3 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Medical procedure | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesMedical procedure | 0 | 15 |  | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 10 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5250 | 0.0001904761905 | 49 | 0.2 | 0.05 | Hospital SWH Extd
DOE Ref Pre-1980 | Hospital | PhysTherapy | 154_230_120 | DOE Ref Pre-1980 | Hospital | PhysTherapy | DOE Ref Pre-1980HospitalPhysTherapy | 2.51 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 |  | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 1 | 5280 | 0.0001893939394 | 49 | 0.2 | 0.05 | Hospital SWH
DOE Ref Pre-1980 | Hospital | PatRoom | 78_167_222 | DOE Ref Pre-1980 | Hospital | PatRoom | DOE Ref Pre-1980HospitalPatRoom | 1.85 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Nursing | Patient Room | AIA 2001NursingPatient Room |  |  | 2 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 1 | 280 | 0.003571428571 | 49 | 0.2 | 0.05 | Hospital SWH Extd
DOE Ref Pre-1980 | Hospital | PatCorridor | 169_31_31 | DOE Ref Pre-1980 | Hospital | PatCorridor | DOE Ref Pre-1980HospitalPatCorridor | 1.32 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp
DOE Ref Pre-1980 | Hospital | OR | 169_31_159 | DOE Ref Pre-1980 | Hospital | OR | DOE Ref Pre-1980HospitalOR | 10 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical ClgSetp | 2 | 600 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital SWH
DOE Ref Pre-1980 | Hospital | Office | 120_230_199 | DOE Ref Pre-1980 | Hospital | Office | DOE Ref Pre-1980HospitalOffice | 1.9 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 6.99 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
DOE Ref Pre-1980 | Hospital | NurseStn | 31_162_169 | DOE Ref Pre-1980 | Hospital | NurseStn | DOE Ref Pre-1980HospitalNurseStn | 1.53 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 |  | 7.14 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 1.04 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
DOE Ref Pre-1980 | Hospital | Lobby | 31_162_169 | DOE Ref Pre-1980 | Hospital | Lobby | DOE Ref Pre-1980HospitalLobby | 1.49 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 7.14 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 0.1 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
DOE Ref Pre-1980 | Hospital | Lab | 204_120_230 | DOE Ref Pre-1980 | Hospital | Lab | DOE Ref Pre-1980HospitalLab | 1.9 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Education | Laboratories | ASHRAE 62.1-1999EducationLaboratories | 0 | 20 |  | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 2 | 2850 | 0.000701754386 | 49 | 0.2 | 0.05 | Hospital SWH
DOE Ref Pre-1980 | Hospital | Kitchen | 78_222_133 | DOE Ref Pre-1980 | Hospital | Kitchen | DOE Ref Pre-1980HospitalKitchen | 2.24 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | Hospital Bldg Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | 96.7 | 0.1 | 0.2 | 0.7 | Hospital Kitchen Gas | 7.5 | 0.2 | 0.5 | 0.1 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | 150 | 10000 | 0.015 | 49 | 0.2 | 0.05 | Hospital SWH Extd | 0.7 | 5300 | 0.1221241016 | 0.338 | 924.6539123 | 0.5024115756 |  | Hospital Kitchen Exhaust
DOE Ref Pre-1980 | Hospital | ICU_PatRm | 78_167_222 | DOE Ref Pre-1980 | Hospital | ICU_PatRm | DOE Ref Pre-1980HospitalICU_PatRm | 4.22 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
DOE Ref Pre-1980 | Hospital | ICU_Open | 78_167_222 | DOE Ref Pre-1980 | Hospital | ICU_Open | DOE Ref Pre-1980HospitalICU_Open | 4.22 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 3 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
DOE Ref Pre-1980 | Hospital | ICU_NurseStn | 31_162_169 | DOE Ref Pre-1980 | Hospital | ICU_NurseStn | DOE Ref Pre-1980HospitalICU_NurseStn | 1.64 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | Critical and Intensive Care | AIA 2001Surgery and Critical CareCritical and Intensive Care |  |  | 2 | 5 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
DOE Ref Pre-1980 | Hospital | ER_Triage | 169_31_159 | DOE Ref Pre-1980 | Hospital | ER_Triage | DOE Ref Pre-1980HospitalER_Triage | 5 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
DOE Ref Pre-1980 | Hospital | ER_Trauma | 169_31_159 | DOE Ref Pre-1980 | Hospital | ER_Trauma | DOE Ref Pre-1980HospitalER_Trauma | 5 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 4 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
DOE Ref Pre-1980 | Hospital | ER_NurseStn | 31_162_169 | DOE Ref Pre-1980 | Hospital | ER_NurseStn | DOE Ref Pre-1980HospitalER_NurseStn | 1.64 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 6.25 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 1.36 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp
DOE Ref Pre-1980 | Hospital | ER_Exam | 169_31_159 | DOE Ref Pre-1980 | Hospital | ER_Exam | DOE Ref Pre-1980HospitalER_Exam | 5 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | AIA 2001 | Surgery and Critical Care | ER Waiting Room | AIA 2001Surgery and Critical CareER Waiting Room |  |  | 2 | 20 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 1.5 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Critical HtgSetp | Hospital Critical HtgSetp | 1 | 300 | 0.003333333333 | 49 | 0.2 | 0.05 | Hospital SWH Extd
DOE Ref Pre-1980 | Hospital | Dining | 31_169_34 | DOE Ref Pre-1980 | Hospital | Dining | DOE Ref Pre-1980HospitalDining | 2.77 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Dining Rooms | ASHRAE 62.1-1999Food and Beverage ServiceDining Rooms | 0 | 20 |  | 10 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
DOE Ref Pre-1980 | Hospital | Corridor | 169_31_31 | DOE Ref Pre-1980 | Hospital | Corridor | DOE Ref Pre-1980HospitalCorridor | 1.32 |  |  |  | 0 | 0.7 | 0.2 | Hospital Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | Hospital Critical Occ | Hospital Activity |  | 0.2232 |  | Hospital Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Hospital Bldg Equip | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp
NECB 2011 | Hospital | WholeBuilding | 255_255_255 | NECB 2011 | Hospital | WholeBuilding | NECB 2011HospitalWholeBuilding | 1.2077 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Hospital | WholeBuilding | NECB 2011HospitalWholeBuilding |  |  | 0.002287331 | 4.65 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.69677 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
90.1-2004 | MidriseApartment | Office | 120_230_199 | ASHRAE 90.1-2004 | MidriseApartment | Office | ASHRAE 90.1-2004MidriseApartmentOffice | 1.11 |  |  | 1.1 | 0 | 0 | 0 | ApartmentMidRise LTG_OFF_SCH_2004_2007 | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Bedrooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBedrooms | 0.1 | 0 |  | 2.11 | ApartmentMidRise OCC_OFF_SCH | ApartmentMidRise Activity Schedule | 0.2016 |  |  | ApartmentMidRise INF_OFF_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_OFF_SCH_2004_2007 | ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | ApartmentMidRise CLGSETP_OFF_SCH_No_Setback
90.1-2004 | MidriseApartment | Corridor | 169_31_31 | ASHRAE 90.1-2004 | MidriseApartment | Corridor | ASHRAE 90.1-2004MidriseApartmentCorridor | 0.5 |  |  |  | 0 | 0 | 0 | ApartmentMidRise LTG_COR_SCH_2004_2007 | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 | ApartmentMidRise All Off |  | 0.2016 |  |  | ApartmentMidRise INF_COR_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH
90.1-2004 | MidriseApartment | Corridor_topfloor | 169_31_31 | ASHRAE 90.1-2004 | MidriseApartment | Corridor | ASHRAE 90.1-2004MidriseApartmentCorridor | 0.5 |  |  |  | 0 | 0 | 0 | ApartmentMidRise LTG_COR_SCH_2004_2007 | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 | ApartmentMidRise All Off |  | 0.023446 |  |  | ApartmentMidRise INF_COR_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH
90.1-2004 | MidriseApartment | Apartment | 78_167_222 | ASHRAE 90.1-2004 | MidriseApartment | Apartment | ASHRAE 90.1-2004MidriseApartmentApartment | 0.36 |  |  | 0.09 | 0 | 0 | 0 | ApartmentMidRise LTG_APT_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Apartment | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesApartment | 0 | 0 | 0.35 | 2.63 | ApartmentMidRise OCC_APT_SCH | ApartmentMidRise Activity Schedule | 0.2016 |  |  | ApartmentMidRise INF_APT_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH | 3.48 | 950 | 0.003663157895 | 60 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
189.1-2009 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5 | Small Office Bldg Occ | Small Office Activity | 0.0446 |  |  | Small Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Small Office Bldg Equip | Small Office HtgSetp | Small Office ClgSetp | 3 | 5502 | 0.0005452562704 | 43.3 | 0.2 | 0.05 | Office SWH
189.1-2009 | Office | WholeBuilding - Md Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice | 0.9 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5 | Medium Office Bldg Occ | Medium Office Activity | 0.0446 |  |  | Medium Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp | 27.7 | 53628 | 0.0005165212203 | 43.3 | 0.2 | 0.05 | Medium Office Bldg Swh
189.1-2009 | Office | WholeBuilding - Lg Office | 120_230_199 | ASHRAE 189.1-2009 | Whole Building | Office | ASHRAE 189.1-2009Whole BuildingOffice | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Large Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5 | Large Office Bldg Occ | Large Office Activity | 0.0446 |  |  | Large Office Infil Quarter On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Large Office Bldg Equip | Large Office HtgSetp | Large Office ClgSetp | 63.9 | 498588 | 0.0001281619293 | 43.3 | 0.2 | 0.05 | Office SWH
189.1-2009 | Office | Vending | 230_157_120 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral | 0.45 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | Office Misc Occ | Office Activity | 0.0446 |  |  | Office Infil Quarter On | [5 empty] | 3.85 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | Office | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral | 0.72 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 |  | Office Activity | 0.0446 |  |  | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | Office | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral | 0.54 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 |  | Office Activity | 0.0446 |  |  | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | Office | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral | 0.81 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 10 | Office Misc Occ | Office Activity | 0.0446 |  |  | Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp |  |  |  | 43.3 | 0.2 | 0.05 | Medium Office Bldg Occ
189.1-2009 | Office | PrintRoom | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral | 0.99 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 10 | Office Misc Occ | Office Activity | 0.0446 |  |  | Office Infil Quarter On | [5 empty] | 2.79 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | Office | OpenOffice | 120_230_199 | ASHRAE 189.1-2009 | Office-Open Plan | General | ASHRAE 189.1-2009Office-Open PlanGeneral | 0.99 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5.25 | Office Work Occ | Office Activity | 0.0446 |  |  | Office Infil Quarter On | [5 empty] | 0.71 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | Office | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral | 1.17 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 |  | 10 | Office Misc Occ | Office Activity | 0.0446 |  |  | Office Infil Quarter On | [5 empty] | 0.07 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | Office | IT_Room | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral | 0.99 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 5 | Office Misc Occ | Office Activity | 0.0446 |  |  | Office Infil Quarter On | [5 empty] | 1.56 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral | 1.35 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 0 |  | Office Activity | 0.0446 |  |  | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | Office | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral | 0.45 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | Office Work Occ | Office Activity | 0.0446 |  |  | Office Infil Quarter On | [5 empty] | 0.16 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | Office | Conference | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral | 1.17 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 |  | 50 | Office Misc Occ | Office Activity | 0.0446 |  |  | Office Infil Quarter On | [5 empty] | 0.37 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | Office | ClosedOffice | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral | 0.99 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 4.75 | Office Work Occ | Office Activity | 0.0446 |  |  | Office Infil Quarter On | [5 empty] | 0.64 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | Office | BreakRoom | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral | 1.08 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 |  | 50 | Office Misc Occ | Office Activity | 0.0446 |  |  | Office Infil Quarter On | [5 empty] | 4.46 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
189.1-2009 | Office | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0 | [11 empty] | #N/A | #N/A | #N/A |  |  |  | 0.0446 |  |  | Small Office Infil Quarter On
90.1-2004 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 90.1-2004 | Whole Building | Office | ASHRAE 90.1-2004Whole BuildingOffice | 1 |  |  |  | 0 | 0.7 | 0.2 | OfficeSmall BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Office Buildings | Whole Building | ASHRAE 62.1-1999Office BuildingsWhole Building | 0.1 |  |  | 5.6 | OfficeSmall BLDG_OCC_SCH | OfficeSmall ACTIVITY_SCH | 0.0595 |  |  | OfficeSmall INFIL_QUARTER_ON_SCH | [5 empty] | 0.63 | 0 | 0.5 | 0 | OfficeSmall BLDG_EQUIP_SCH | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_OPTIMUM | 3 | 5502 | 0.0005452562704 | 43.3 | 0.2 | 0.05 | OfficeSmall BLDG_SWH_SCH
90.1-2004 | Office | WholeBuilding - Md Office | 120_230_199 | ASHRAE 90.1-2004 | Whole Building | Office | ASHRAE 90.1-2004Whole BuildingOffice | 1 |  |  |  | 0 | 0.7 | 0.2 | OfficeMedium BLDG_LIGHT_SCH_2004 | ASHRAE 62.1-1999 | Office Buildings | Whole Building | ASHRAE 62.1-1999Office BuildingsWhole Building | 0.1 |  |  | 5 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.75 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH_2004 | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM | 27.7 | 53628 | 0.0005165212203 | 43.3 | 0.2 | 0.05 | OfficeMedium BLDG_SWH_SCH
90.1-2004 | Office | WholeBuilding - Lg Office | 120_230_199 | ASHRAE 90.1-2004 | Whole Building | Office | ASHRAE 90.1-2004Whole BuildingOffice | 1 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeLarge BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Office Buildings | Whole Building | ASHRAE 62.1-1999Office BuildingsWhole Building | 0.1 |  |  | 5 | OfficeLarge BLDG_OCC_SCH | OfficeLarge ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | OfficeLarge BLDG_EQUIP_SCH | OfficeLarge HTGSETP_DC_SCH | OfficeLarge CLGSETP_DC_SCH | 27.7 | 53628 | 0.0005165212203 | 43.3 | 0.2 | 0.05 | OfficeLarge BLDG_SWH_SCH
90.1-2004 | Office | Vending | 230_157_120 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral | 0.5 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 3.85 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Office | Storage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral | 0.8 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Office | Stair | 230_157_120 | ASHRAE 90.1-2004 | Stairs-Active | General | ASHRAE 90.1-2004Stairs-ActiveGeneral | 0.6 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Office | Restroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral | 0.9 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM |  |  |  | 43.3 | 0.2 | 0.05 | OfficeMedium BLDG_SWH_SCH
90.1-2004 | Office | PrintRoom | 41_31_169 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral | 1.1 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 5.4 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Office | OpenOffice | 120_230_199 | ASHRAE 90.1-2004 | Office-Open Plan | General | ASHRAE 90.1-2004Office-Open PlanGeneral | 1.1 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5.25 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.96 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Office | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral | 1.3 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 |  | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Office | IT_Room | 41_31_169 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral | 1.1 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 5 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 2 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral | 1.5 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Office | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral | 0.5 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.29 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Office | Conference | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral | 1.3 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 |  | 50 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Office | ClosedOffice | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral | 1.1 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 4.75 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.87 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Office | BreakRoom | 230_157_120 | ASHRAE 90.1-2004 | Lounge/Recreation | General | ASHRAE 90.1-2004Lounge/RecreationGeneral | 1.2 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 |  | 50 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 5.58 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Office | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0 | [17 empty] | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL
90.1-2007 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 90.1-2004 | Whole Building | Office | ASHRAE 90.1-2004Whole BuildingOffice | 1 |  |  |  | 0 | 0.7 | 0.2 | OfficeSmall BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Office Buildings | Whole Building | ASHRAE 62.1-1999Office BuildingsWhole Building | 0.1 |  |  | 5.6 | OfficeSmall BLDG_OCC_SCH | OfficeSmall ACTIVITY_SCH | 0.0595 |  |  | OfficeSmall INFIL_QUARTER_ON_SCH | [5 empty] | 0.63 | 0 | 0.5 | 0 | OfficeSmall BLDG_EQUIP_SCH | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_OPTIMUM | 3 | 5502 | 0.0005452562704 | 43.3 | 0.2 | 0.05 | OfficeSmall BLDG_SWH_SCH
90.1-2007 | Office | WholeBuilding - Md Office | 120_230_199 | ASHRAE 90.1-2007 | Whole Building | Office | ASHRAE 90.1-2007Whole BuildingOffice | 1 |  |  |  | 0 | 0.7 | 0.2 | OfficeMedium BLDG_LIGHT_SCH_2004 | ASHRAE 62.1-2004 | Office Buildings | Whole Building | ASHRAE 62.1-2004Office BuildingsWhole Building | 0.085 |  |  | 5 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.75 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH_2004 | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM | 27.7 | 53628 | 0.0005165212203 | 43.3 | 0.2 | 0.05 | OfficeMedium BLDG_SWH_SCH
90.1-2007 | Office | WholeBuilding - Lg Office | 120_230_199 | ASHRAE 90.1-2007 | Whole Building | Office | ASHRAE 90.1-2007Whole BuildingOffice | 1 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Whole Building | ASHRAE 62.1-2004Office BuildingsWhole Building | 0.085 |  |  | 5 | OfficeLarge BLDG_OCC_SCH | OfficeLarge ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | OfficeLarge BLDG_EQUIP_SCH | OfficeLarge HTGSETP_DC_SCH | OfficeLarge CLGSETP_DC_SCH | 27.7 | 53628 | 0.0005165212203 | 43.3 | 0.2 | 0.05 | OfficeLarge BLDG_SWH_SCH
90.1-2007 | Office | Vending | 230_157_120 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral | 0.5 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 1 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 3.85 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Office | Storage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral | 0.8 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Office | Stair | 230_157_120 | ASHRAE 90.1-2007 | Stairs-Active | General | ASHRAE 90.1-2007Stairs-ActiveGeneral | 0.6 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Office | Restroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral | 0.9 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.07 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM |  |  |  | 43.3 | 0.2 | 0.05 | OfficeMedium BLDG_SWH_SCH
90.1-2007 | Office | PrintRoom | 41_31_169 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral | 1.1 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 2.79 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Office | OpenOffice | 120_230_199 | ASHRAE 90.1-2007 | Office-Open Plan | General | ASHRAE 90.1-2007Office-Open PlanGeneral | 1.1 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 |  | 5.25 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.71 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Office | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral | 1.3 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2004Office BuildingsMain entry lobbies | 0.06 | 5 |  | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.07 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Office | IT_Room | 41_31_169 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral | 1.1 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Telephone/data entry | ASHRAE 62.1-2004Office BuildingsTelephone/data entry | 0.06 | 5 |  | 5 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 1.56 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral | 1.5 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Office | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral | 0.5 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 1 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.16 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Office | Conference | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral | 1.3 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Conference/meeting | ASHRAE 62.1-2004GeneralConference/meeting | 0.06 | 5 |  | 50 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Office | ClosedOffice | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral | 1.1 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 |  | 4.75 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.64 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Office | BreakRoom | 230_157_120 | ASHRAE 90.1-2007 | Lounge/Recreation | General | ASHRAE 90.1-2007Lounge/RecreationGeneral | 1.2 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Conference/meeting | ASHRAE 62.1-2004GeneralConference/meeting | 0.06 | 5 |  | 50 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 4.46 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Office | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0 | [17 empty] | 0.112 |  |  | OfficeMedium INFIL_SCH_PNNL
90.1-2010 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 90.1-2010 | Whole Building | Office | ASHRAE 90.1-2010Whole BuildingOffice | 0.9 |  |  |  | 0 | 0.7 | 0.2 | OfficeSmall BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Whole Building | ASHRAE 62.1-2007Office BuildingsWhole Building | 0.085 |  |  | 5.6 | OfficeSmall BLDG_OCC_SCH | OfficeSmall ACTIVITY_SCH | 0.112 |  |  | OfficeSmall INFIL_QUARTER_ON_SCH | [5 empty] | 0.63 | 0 | 0.5 | 0 | OfficeSmall BLDG_EQUIP_SCH | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_OPTIMUM | 3 | 5502 | 0.0005452562704 | 43.3 | 0.2 | 0.05 | OfficeSmall BLDG_SWH_SCH
90.1-2010 | Office | WholeBuilding - Md Office | 120_230_199 | ASHRAE 90.1-2010 | Whole Building | Office | ASHRAE 90.1-2010Whole BuildingOffice | 0.9 |  |  |  | 0 | 0.7 | 0.2 | OfficeMedium BLDG_LIGHT_SCH_2010 | ASHRAE 62.1-2007 | Office Buildings | Whole Building | ASHRAE 62.1-2007Office BuildingsWhole Building | 0.085 |  |  | 5 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.75 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH_2010 | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM | 27.7 | 53628 | 0.0005165212203 | 43.3 | 0.2 | 0.05 | OfficeMedium BLDG_SWH_SCH
90.1-2010 | Office | WholeBuilding - Lg Office | 120_230_199 | ASHRAE 90.1-2010 | Whole Building | Office | ASHRAE 90.1-2010Whole BuildingOffice | 0.9 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Whole Building | ASHRAE 62.1-2007Office BuildingsWhole Building | 0.085 |  |  | 5 | OfficeLarge BLDG_OCC_SCH | OfficeLarge ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | OfficeLarge BLDG_EQUIP_SCH | OfficeLarge HTGSETP_DC_SCH | OfficeLarge CLGSETP_DC_SCH | 27.7 | 53628 | 0.0005165212203 | 43.3 | 0.2 | 0.05 | OfficeLarge BLDG_SWH_SCH
90.1-2010 | Office | Vending | 230_157_120 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral | 0.66 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 1 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 3.85 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Office | Storage | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral | 0.63 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Office | Stair | 230_157_120 | ASHRAE 90.1-2010 | Stairway | General | ASHRAE 90.1-2010StairwayGeneral | 0.69 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Office | Restroom | 169_169_31 | ASHRAE 90.1-2010 | Restrooms | General | ASHRAE 90.1-2010RestroomsGeneral | 0.98 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.07 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM |  |  |  | 43.3 | 0.2 | 0.05 | OfficeMedium BLDG_SWH_SCH
90.1-2010 | Office | PrintRoom | 41_31_169 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral | 1.11 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 2.79 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Office | OpenOffice | 120_230_199 | ASHRAE 90.1-2010 | Office-Open Plan | General | ASHRAE 90.1-2010Office-Open PlanGeneral | 0.98 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 5.25 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.71 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Office | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral | 0.9 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2007Office BuildingsMain entry lobbies | 0.06 | 5 |  | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.07 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Office | IT_Room | 41_31_169 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral | 1.11 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | ASHRAE 62.1-2007Office BuildingsTelephone/data entry | 0.06 | 5 |  | 5 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 1.56 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral | 0.95 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Office | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral | 0.66 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 1 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.16 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Office | Conference | 230_196_120 | ASHRAE 90.1-2010 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2010Conference/Meeting/MultipurposeGeneral | 1.23 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 |  | 50 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Office | ClosedOffice | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral | 1.11 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 4.75 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.64 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Office | BreakRoom | 230_157_120 | ASHRAE 90.1-2010 | Lounge/Recreation | General | ASHRAE 90.1-2010Lounge/RecreationGeneral | 0.73 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 |  | 50 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 4.46 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Office | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0 | [17 empty] | 0.112 |  |  | OfficeMedium INFIL_SCH_PNNL
90.1-2013 | Office | WholeBuilding - Sm Office | 120_230_199 | ASHRAE 90.1-2013 | Whole Building | Office | ASHRAE 90.1-2013Whole BuildingOffice | 0.82 |  |  |  | 0 | 0.7 | 0.2 | OfficeSmall BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Whole Building | ASHRAE 62.1-2007Office BuildingsWhole Building | 0.085 |  |  | 5.6 | OfficeSmall BLDG_OCC_SCH | OfficeSmall ACTIVITY_SCH | 0.112 |  |  | OfficeSmall INFIL_QUARTER_ON_SCH | [5 empty] | 0.63 | 0 | 0.5 | 0 | OfficeSmall BLDG_EQUIP_SCH | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_OPTIMUM | 3 | 5502 | 0.0005452562704 | 43.3 | 0.2 | 0.05 | OfficeSmall BLDG_SWH_SCH
90.1-2013 | Office | WholeBuilding - Md Office | 120_230_199 | ASHRAE 90.1-2013 | Whole Building | Office | ASHRAE 90.1-2013Whole BuildingOffice | 0.82 |  |  |  | 0 | 0.7 | 0.2 | OfficeMedium BLDG_LIGHT_SCH_2013 | ASHRAE 62.1-2007 | Office Buildings | Whole Building | ASHRAE 62.1-2007Office BuildingsWhole Building | 0.085 |  |  | 5 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.75 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH_2013 | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM | 27.7 | 53628 | 0.0005165212203 | 43.3 | 0.2 | 0.05 | OfficeMedium BLDG_SWH_SCH
90.1-2013 | Office | WholeBuilding - Lg Office | 120_230_199 | ASHRAE 90.1-2013 | Whole Building | Office | ASHRAE 90.1-2013Whole BuildingOffice | 0.82 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeLarge BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Whole Building | ASHRAE 62.1-2007Office BuildingsWhole Building | 0.085 |  |  | 5 | OfficeLarge BLDG_OCC_SCH | OfficeLarge ACTIVITY_SCH | 0.0595 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | OfficeLarge BLDG_EQUIP_SCH | OfficeLarge HTGSETP_DC_SCH | OfficeLarge CLGSETP_DC_SCH | 27.7 | 53628 | 0.0005165212203 | 43.3 | 0.2 | 0.05 | OfficeLarge BLDG_SWH_SCH
90.1-2013 | Office | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0 | [17 empty] | 0.112 |  |  | OfficeMedium INFIL_SCH_PNNL
DOE Ref 1980-2004 | Office | WholeBuilding - Sm Office | 120_230_199 | DOE Ref 1980-2004 | Office | WholeBuilding - Sm Office | DOE Ref 1980-2004OfficeWholeBuilding - Sm Office | 1.81 |  |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5 | Small Office Bldg Occ | Small Office Activity |  | 0.2232 |  | Small Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Small Office Bldg Equip | Small Office HtgSetp | Small Office ClgSetp | 3 | 5502 | 0.0005452562704 | 43.3 | 0.2 | 0.05 | Office SWH
DOE Ref 1980-2004 | Office | WholeBuilding - Md Office | 120_230_199 | DOE Ref 1980-2004 | Office | WholeBuilding - Md Office | DOE Ref 1980-2004OfficeWholeBuilding - Md Office | 1.57 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5 | Medium Office Bldg Occ | Medium Office Activity |  | 0.2232 |  | Medium Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp | 27.7 | 53628 | 0.0005165212203 | 43.3 | 0.2 | 0.05 | Medium Office Bldg Swh
DOE Ref 1980-2004 | Office | WholeBuilding - Lg Office | 120_230_199 | DOE Ref 1980-2004 | Office | WholeBuilding - Lg Office | DOE Ref 1980-2004OfficeWholeBuilding - Lg Office | 1 |  |  |  | 0 | 0.7 | 0.2 | Large Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5 | Large Office Bldg Occ | Large Office Activity |  | 0.2232 |  | Large Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Large Office Bldg Equip | Large Office HtgSetp | Large Office ClgSetp | 63.9 | 498588 | 0.0001281619293 | 43.3 | 0.2 | 0.05 | Office SWH
DOE Ref 1980-2004 | Office | Vending | 230_157_120 | DOE Ref 1980-2004 | Office | Vending | DOE Ref 1980-2004OfficeVending | 1.57 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | Office Misc Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 3.85 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref 1980-2004 | Office | Storage | 120_149_230 | DOE Ref 1980-2004 | Office | Storage | DOE Ref 1980-2004OfficeStorage | 1.27 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 |  | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref 1980-2004 | Office | Stair | 230_157_120 | DOE Ref 1980-2004 | Office | Stair | DOE Ref 1980-2004OfficeStair | 0.942 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 |  | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref 1980-2004 | Office | Restroom | 169_169_31 | DOE Ref 1980-2004 | Office | Restroom | DOE Ref 1980-2004OfficeRestroom | 1.41 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 10 | Office Misc Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp |  |  |  | 43.3 | 0.2 | 0.05 | Medium Office Bldg Occ
DOE Ref 1980-2004 | Office | PrintRoom | 41_31_169 | DOE Ref 1980-2004 | Office | PrintRoom | DOE Ref 1980-2004OfficePrintRoom | 1.55 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 10 | Office Misc Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 5.4 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref 1980-2004 | Office | OpenOffice | 120_230_199 | DOE Ref 1980-2004 | Office | OpenOffice | DOE Ref 1980-2004OfficeOpenOffice | 1.73 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5.25 | Office Work Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0.96 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref 1980-2004 | Office | Lobby | 230_157_120 | DOE Ref 1980-2004 | Office | Lobby | DOE Ref 1980-2004OfficeLobby | 2.04 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 |  | 10 | Office Misc Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref 1980-2004 | Office | IT_Room | 41_31_169 | DOE Ref 1980-2004 | Office | IT_Room | DOE Ref 1980-2004OfficeIT_Room | 1.55 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 5 | Office Misc Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref 1980-2004 | Office | Elec/MechRoom | 41_31_169 | DOE Ref 1980-2004 | Office | Elec/MechRoom | DOE Ref 1980-2004OfficeElec/MechRoom | 2.355 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 0 |  | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref 1980-2004 | Office | Corridor | 169_31_31 | DOE Ref 1980-2004 | Office | Corridor | DOE Ref 1980-2004OfficeCorridor | 0.785 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | Office Work Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0.29 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref 1980-2004 | Office | Conference | 230_196_120 | DOE Ref 1980-2004 | Office | Conference | DOE Ref 1980-2004OfficeConference | 1.84 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 |  | 50 | Office Misc Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref 1980-2004 | Office | ClosedOffice | 120_230_199 | DOE Ref 1980-2004 | Office | ClosedOffice | DOE Ref 1980-2004OfficeClosedOffice | 1.727 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 4.75 | Office Work Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0.87 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref 1980-2004 | Office | BreakRoom | 230_157_120 | DOE Ref 1980-2004 | Office | BreakRoom | DOE Ref 1980-2004OfficeBreakRoom | 1.884 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 |  | 50 | Office Misc Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 5.63 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref 1980-2004 | Office | Attic | 120_149_230 | [16 empty] | #N/A | #N/A | #N/A |  |  |  |  | 0.2232 |  | Small Office Infil Quarter On
DOE Ref Pre-1980 | Office | WholeBuilding - Sm Office | 120_230_199 | DOE Ref Pre-1980 | Office | WholeBuilding - Sm Office | DOE Ref Pre-1980OfficeWholeBuilding - Sm Office | 1.81 |  |  |  | 0 | 0.7 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5 | Small Office Bldg Occ | Small Office Activity |  | 0.2232 |  | Small Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Small Office Bldg Equip | Small Office HtgSetp | Small Office ClgSetp | 3 | 5502 | 0.0005452562704 | 43.3 | 0.2 | 0.05 | Office SWH
DOE Ref Pre-1980 | Office | WholeBuilding - Md Office | 120_230_199 | DOE Ref Pre-1980 | Office | WholeBuilding - Md Office | DOE Ref Pre-1980OfficeWholeBuilding - Md Office | 1.57 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5 | Medium Office Bldg Occ | Medium Office Activity |  | 0.2232 |  | Medium Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Medium Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp | 27.7 | 53628 | 0.0005165212203 | 43.3 | 0.2 | 0.05 | Medium Office Bldg Swh
DOE Ref Pre-1980 | Office | WholeBuilding - Lg Office | 120_230_199 | DOE Ref Pre-1980 | Office | WholeBuilding - Lg Office | DOE Ref Pre-1980OfficeWholeBuilding - Lg Office | 1.5 |  |  |  | 0 | 0.7 | 0.2 | Large Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5 | Large Office Bldg Occ | Large Office Activity |  | 0.2232 |  | Large Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Large Office Bldg Equip | Large Office HtgSetp | Large Office ClgSetp | 63.9 | 498588 | 0.0001281619293 | 43.3 | 0.2 | 0.05 | Office SWH
DOE Ref Pre-1980 | Office | Vending | 230_157_120 | DOE Ref Pre-1980 | Office | Vending | DOE Ref Pre-1980OfficeVending | 0.95 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | Office Misc Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 3.85 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | Office | Storage | 120_149_230 | DOE Ref Pre-1980 | Office | Storage | DOE Ref Pre-1980OfficeStorage | 1.539 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 |  | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | Office | Stair | 230_157_120 | DOE Ref Pre-1980 | Office | Stair | DOE Ref Pre-1980OfficeStair | 1.14 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 |  | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | Office | Restroom | 169_169_31 | DOE Ref Pre-1980 | Office | Restroom | DOE Ref Pre-1980OfficeRestroom | 1.71 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 10 | Office Misc Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp |  |  |  | 43.3 | 0.2 | 0.05 | Medium Office Bldg Occ
DOE Ref Pre-1980 | Office | PrintRoom | 41_31_169 | DOE Ref Pre-1980 | Office | PrintRoom | DOE Ref Pre-1980OfficePrintRoom | 1.881 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 10 | Office Misc Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 5.4 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | Office | OpenOffice | 120_230_199 | DOE Ref Pre-1980 | Office | OpenOffice | DOE Ref Pre-1980OfficeOpenOffice | 2.09 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5.25 | Office Work Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0.96 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | Office | Lobby | 230_157_120 | DOE Ref Pre-1980 | Office | Lobby | DOE Ref Pre-1980OfficeLobby | 2.47 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 |  | 10 | Office Misc Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | Office | IT_Room | 41_31_169 | DOE Ref Pre-1980 | Office | IT_Room | DOE Ref Pre-1980OfficeIT_Room | 2.09 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 5 | Office Misc Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 2 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | Office | Elec/MechRoom | 41_31_169 | DOE Ref Pre-1980 | Office | Elec/MechRoom | DOE Ref Pre-1980OfficeElec/MechRoom | 2.85 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 0 |  | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0.27 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | Office | Corridor | 169_31_31 | DOE Ref Pre-1980 | Office | Corridor | DOE Ref Pre-1980OfficeCorridor | 0.95 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 1 | Office Work Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0.29 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | Office | Conference | 230_196_120 | DOE Ref Pre-1980 | Office | Conference | DOE Ref Pre-1980OfficeConference | 2.47 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Conference rooms | ASHRAE 62.1-1999OfficesConference rooms | 0 | 20 |  | 50 | Office Misc Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 1 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | Office | ClosedOffice | 120_230_199 | DOE Ref Pre-1980 | Office | ClosedOffice | DOE Ref Pre-1980OfficeClosedOffice | 2.09 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 4.75 | Office Work Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 0.87 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | Office | BreakRoom | 230_157_120 | DOE Ref Pre-1980 | Office | BreakRoom | DOE Ref Pre-1980OfficeBreakRoom | 2.28 |  |  |  | 0.4 | 0.4 | 0.2 | Office Bldg Light | ASHRAE 62.1-1999 | Offices | Reception Areas | ASHRAE 62.1-1999OfficesReception Areas | 0 | 15 |  | 50 | Office Misc Occ | Office Activity |  | 0.2232 |  | Office Infil Quarter On | [5 empty] | 5.63 | 0 | 0.5 | 0 | Office Bldg Equip | Medium Office HtgSetp | Medium Office ClgSetp
DOE Ref Pre-1980 | Office | Attic | 120_149_230 | [16 empty] | #N/A | #N/A | #N/A |  |  |  |  | 0.2232 |  | Small Office Infil Quarter On
189.1-2009 | Outpatient | Xray | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology | 0.36 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 0.95 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 900 | 0.001111111111 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | Outpatient | Toilet | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral | 0.81 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 0.29 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 90 | 0.6310269118 | 0.31 | 34.0754 | 1 |  | Outpatient_FirstFlr_Exhaust
189.1-2009 | Outpatient | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral | 0.54 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | Soil Work | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Medical Supply | ASHRAE 189.1-2009HospitalMedical Supply | 1.26 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 210 | 0.6310269118 | 0.31 | 79.5093 | 1 |  | Outpatient_FirstFlr_Exhaust
189.1-2009 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Emergency | ASHRAE 189.1-2009HospitalEmergency | 2.43 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 285 | 0.00350877193 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | Outpatient | PreOp | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Patient Room | ASHRAE 189.1-2009HospitalPatient Room | 0.63 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 |  |  | 9.29 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 263.5 | 0.003795066414 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 189.1-2009 | Hospital | Physical Therapy | ASHRAE 189.1-2009HospitalPhysical Therapy | 0.81 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 1.09 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 946 | 0.001057082452 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | Outpatient | PACU | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Recovery | ASHRAE 189.1-2009HospitalRecovery | 0.72 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.009259259259 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | Outpatient | OR | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room | 1.98 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | 17.4 | 0 | 0 | 0.5 | Outpatient Bldg Equip | 2.92 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient OR HtgSetp | Outpatient OR ClgSetp | 6 | 470 | 0.01276595745 | 43.3 | 0.2 | 0.05 | Outpatient SWH
189.1-2009 | Outpatient | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral | 0.99 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | NurseStation | 31_162_169 | ASHRAE 189.1-2009 | Hospital | Nurse Station | ASHRAE 189.1-2009HospitalNurse Station | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology | 0.36 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 168 | 0.005952380952 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 168 | 0.3786161471 | 0.31 | 63.6075 | 1 |  | Outpatient_FirstFlr_Exhaust
189.1-2009 | Outpatient | MRI | 169_31_159 | ASHRAE 189.1-2009 | Hospital | Radiology | ASHRAE 189.1-2009HospitalRadiology | 0.36 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 38.63 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 440 | 0.002272727273 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 440 | 0.3786161471 | 0.31 | 166.5909 | 1 |  | Outpatient_FirstFlr_Exhaust
189.1-2009 | Outpatient | MedGas | 204_120_230 | ASHRAE 189.1-2009 | Active Storage | For Hospital | ASHRAE 189.1-2009Active StorageFor Hospital | 0.81 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 |  | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | Lounge | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | For Hospital | ASHRAE 189.1-2009Lounge/RecreationFor Hospital | 0.72 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral | 0.54 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 |  |  | 13.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 2.19 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral | 1.17 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 27.87 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | Janitor | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral | 0.72 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 |  |  | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | IT_Room | 41_31_169 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral | 0.99 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | 0 | 20 |  | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | Hall | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | For Hospital | ASHRAE 189.1-2009Corridor/TransitionFor Hospital | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 0.29 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | Exam | 136_78_222 | ASHRAE 189.1-2009 | Hospital | Exam/Treatment | ASHRAE 189.1-2009HospitalExam/Treatment | 1.35 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral | 1.35 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 |  |  | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 3.64 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 189.1-2009 | Dressing/Locker/Fitting Room | General | ASHRAE 189.1-2009Dressing/Locker/Fitting RoomGeneral | 0.54 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 4.65 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 0.8 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | Conference | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral | 1.17 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 |  | 46.45 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | CleanWork | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Medical Supply | ASHRAE 189.1-2009HospitalMedical Supply | 1.26 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | Cafe | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral | 0.81 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 92.94 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | BioHazard | 204_120_230 | ASHRAE 189.1-2009 | Active Storage | For Hospital | ASHRAE 189.1-2009Active StorageFor Hospital | 0.81 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 |  |  | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 0.07 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
189.1-2009 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 189.1-2009 | Hospital | Operating Room | ASHRAE 189.1-2009HospitalOperating Room | 1.98 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 |  |  | 0 | Outpatient Bldg Occ | Outpatient Activity | 0.0446 |  |  | Outpatient Infil | [5 empty] | 1.46 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.009259259259 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1.3333 | 144 | 0.5048215295 | 0.31 | 54.5207 | 1 |  | Outpatient_FirstFlr_Exhaust
90.1-2004 | Outpatient | Xray | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology | 0.4 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.3 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 900 | 0.001111111111 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2004 | Outpatient | Toilet | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral | 0.9 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.4 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | [7 empty] | 1.6667 | 90 | 0.6310269118 | 0.31 | 34.0754 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2004 | Outpatient | Stair | 230_157_120 | ASHRAE 90.1-2004 | Stairs-Active | General | ASHRAE 90.1-2004Stairs-ActiveGeneral | 0.6 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | Soil Work | 204_120_230 | ASHRAE 90.1-2004 | Hospital | Medical Supply | ASHRAE 90.1-2004HospitalMedical Supply | 1.4 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | [7 empty] | 1.6667 | 210 | 0.6310269118 | 0.31 | 79.5093 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2004 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Emergency | ASHRAE 90.1-2004HospitalEmergency | 2.7 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 3 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 285 | 0.00350877193 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2004 | Outpatient | PreOp | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Patient Room | ASHRAE 90.1-2004HospitalPatient Room | 0.7 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 |  |  | 9.29 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 263.5 | 0.003795066414 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2004 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 90.1-2004 | Hospital | Physical Therapy | ASHRAE 90.1-2004HospitalPhysical Therapy | 0.9 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.5 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 946 | 0.001057082452 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2004 | Outpatient | PACU | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Recovery | ASHRAE 90.1-2004HospitalRecovery | 0.8 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 3 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 108 | 0.009259259259 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2004 | Outpatient | OR | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Operating Room | ASHRAE 90.1-2004HospitalOperating Room | 2.2 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | 23.9 | 0 | 0 | 0.5 | OutPatientHealthCare BLDG_EQUIP_SCH | 4 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare OR_HTGSETP_SCH | OutPatientHealthCare OR_CLGSETP_SCH | 6 | 470 | 0.01276595745 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2004 | Outpatient | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | NurseStation | 31_162_169 | ASHRAE 90.1-2004 | Hospital | Nurse Station | ASHRAE 90.1-2004HospitalNurse Station | 1 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology | 0.4 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 168 | 0.005952380952 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1 | 168 | 0.3786161471 | 0.31 | 63.6075 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2004 | Outpatient | MRI | 169_31_159 | ASHRAE 90.1-2004 | Hospital | Radiology | ASHRAE 90.1-2004HospitalRadiology | 0.4 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 53.06 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 440 | 0.002272727273 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1 | 440 | 0.3786161471 | 0.31 | 166.5909 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2004 | Outpatient | MedGas | 204_120_230 | ASHRAE 90.1-2004 | Active Storage | For Hospital | ASHRAE 90.1-2004Active StorageFor Hospital | 0.9 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | Lounge | 230_157_120 | ASHRAE 90.1-2004 | Lounge/Recreation | For Hospital | ASHRAE 90.1-2004Lounge/RecreationFor Hospital | 0.8 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 13.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 3 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 90.1-2004 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2004Dressing/Locker/Fitting RoomGeneral | 0.6 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 |  |  | 13.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 3 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral | 1.3 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 27.87 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | Janitor | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral | 0.8 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | IT_Room | 41_31_169 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | 0 | 20 |  | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | Hall | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | For Hospital | ASHRAE 90.1-2004Corridor/TransitionFor Hospital | 1 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.4 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | Exam | 136_78_222 | ASHRAE 90.1-2004 | Hospital | Exam/Treatment | ASHRAE 90.1-2004HospitalExam/Treatment | 1.5 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral | 1.5 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 5 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 90.1-2004 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2004Dressing/Locker/Fitting RoomGeneral | 0.6 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | Conference | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral | 1.3 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 |  | 46.45 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | CleanWork | 204_120_230 | ASHRAE 90.1-2004 | Hospital | Medical Supply | ASHRAE 90.1-2004HospitalMedical Supply | 1.4 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | Cafe | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral | 0.9 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 92.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | BioHazard | 204_120_230 | ASHRAE 90.1-2004 | Active Storage | For Hospital | ASHRAE 90.1-2004Active StorageFor Hospital | 0.9 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.1 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 90.1-2004 | Hospital | Operating Room | ASHRAE 90.1-2004HospitalOperating Room | 2.2 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0595 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 108 | 0.009259259259 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1.3333 | 144 | 0.5048215295 | 0.31 | 54.5207 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2007 | Outpatient | Xray | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology | 0.4 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.95 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 900 | 0.001111111111 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2007 | Outpatient | Toilet | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral | 0.9 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.29 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | [7 empty] | 1.6667 | 90 | 0.6310269118 | 0.31 | 34.0754 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2007 | Outpatient | Stair | 230_157_120 | ASHRAE 90.1-2007 | Stairs-Active | General | ASHRAE 90.1-2007Stairs-ActiveGeneral | 0.6 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | Soil Work | 204_120_230 | ASHRAE 90.1-2007 | Hospital | Medical Supply | ASHRAE 90.1-2007HospitalMedical Supply | 1.4 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | [7 empty] | 1.6667 | 210 | 0.6310269118 | 0.31 | 79.5093 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2007 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Emergency | ASHRAE 90.1-2007HospitalEmergency | 2.7 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 285 | 0.00350877193 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2007 | Outpatient | PreOp | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Patient Room | ASHRAE 90.1-2007HospitalPatient Room | 0.7 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 |  |  | 9.29 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 263.5 | 0.003795066414 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2007 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 90.1-2007 | Hospital | Physical Therapy | ASHRAE 90.1-2007HospitalPhysical Therapy | 0.9 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPhysical therapy |  | 15 |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.09 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 946 | 0.001057082452 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2007 | Outpatient | PACU | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Recovery | ASHRAE 90.1-2007HospitalRecovery | 0.8 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 108 | 0.009259259259 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2007 | Outpatient | OR | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Operating Room | ASHRAE 90.1-2007HospitalOperating Room | 2.2 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | 17.4 | 0 | 0 | 0.5 | OutPatientHealthCare BLDG_EQUIP_SCH | 2.92 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare OR_HTGSETP_SCH | OutPatientHealthCare OR_CLGSETP_SCH | 6 | 470 | 0.01276595745 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2007 | Outpatient | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 |  | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | NurseStation | 31_162_169 | ASHRAE 90.1-2007 | Hospital | Nurse Station | ASHRAE 90.1-2007HospitalNurse Station | 1 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology | 0.4 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 168 | 0.005952380952 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1 | 168 | 0.3786161471 | 0.31 | 63.6075 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2007 | Outpatient | MRI | 169_31_159 | ASHRAE 90.1-2007 | Hospital | Radiology | ASHRAE 90.1-2007HospitalRadiology | 0.4 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 38.63 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 440 | 0.002272727273 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1 | 440 | 0.3786161471 | 0.31 | 166.5909 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2007 | Outpatient | MedGas | 204_120_230 | ASHRAE 90.1-2007 | Active Storage | For Hospital | ASHRAE 90.1-2007Active StorageFor Hospital | 0.9 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.07 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | Lounge | 230_157_120 | ASHRAE 90.1-2007 | Lounge/Recreation | For Hospital | ASHRAE 90.1-2007Lounge/RecreationFor Hospital | 0.8 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 |  | 13.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 90.1-2007 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2007Dressing/Locker/Fitting RoomGeneral | 0.6 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 |  |  | 13.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral | 1.3 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2004Office BuildingsMain entry lobbies | 0.06 | 5 |  | 27.87 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | Janitor | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral | 0.8 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | IT_Room | 41_31_169 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Telephone/data entry | ASHRAE 62.1-2004Office BuildingsTelephone/data entry | 0.06 | 5 |  | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | Hall | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | For Hospital | ASHRAE 90.1-2007Corridor/TransitionFor Hospital | 1 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.29 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | Exam | 136_78_222 | ASHRAE 90.1-2007 | Hospital | Exam/Treatment | ASHRAE 90.1-2007HospitalExam/Treatment | 1.5 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral | 1.5 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 3.64 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 90.1-2007 | Dressing/Locker/Fitting Room | General | ASHRAE 90.1-2007Dressing/Locker/Fitting RoomGeneral | 0.6 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Hospitals, Nursing and Convalescent Homes | Patient rooms | ASHRAE 62.1-2004Hospitals, Nursing and Convalescent HomesPatient rooms |  | 25 |  | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | Conference | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral | 1.3 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Conference/meeting | ASHRAE 62.1-2004GeneralConference/meeting | 0.06 | 5 |  | 46.45 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.73 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | CleanWork | 204_120_230 | ASHRAE 90.1-2007 | Hospital | Medical Supply | ASHRAE 90.1-2007HospitalMedical Supply | 1.4 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | Cafe | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral | 0.9 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 92.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.73 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | BioHazard | 204_120_230 | ASHRAE 90.1-2007 | Active Storage | For Hospital | ASHRAE 90.1-2007Active StorageFor Hospital | 0.9 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.07 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 90.1-2007 | Hospital | Operating Room | ASHRAE 90.1-2007HospitalOperating Room | 2.2 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 108 | 0.009259259259 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1.3333 | 144 | 0.5048215295 | 0.31 | 54.5207 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2010 | Outpatient | Xray | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Radiology/Imaging | ASHRAE 90.1-2010HospitalRadiology/Imaging | 1.32 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.95 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 900 | 0.001111111111 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2010 | Outpatient | Toilet | 169_169_31 | ASHRAE 90.1-2010 | Restrooms | General | ASHRAE 90.1-2010RestroomsGeneral | 0.98 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.29 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | [7 empty] | 1.6667 | 90 | 0.63103 | 0.31 | 34.0754 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2010 | Outpatient | Stair | 230_157_120 | ASHRAE 90.1-2010 | Stairway | General | ASHRAE 90.1-2010StairwayGeneral | 0.69 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | Soil Work | 204_120_230 | ASHRAE 90.1-2010 | Hospital | Medical Supply | ASHRAE 90.1-2010HospitalMedical Supply | 1.27 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | [7 empty] | 1.6667 | 210 | 0.63103 | 0.31 | 79.5093 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2010 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Emergency | ASHRAE 90.1-2010HospitalEmergency | 2.26 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 285 | 0.00350877193 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2010 | Outpatient | PreOp | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Patient Room | ASHRAE 90.1-2010HospitalPatient Room | 0.62 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 |  |  | 9.29 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 263.5 | 0.003795066414 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2010 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 90.1-2010 | Hospital | Physical Therapy | ASHRAE 90.1-2010HospitalPhysical Therapy | 0.91 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy |  | 15 |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.09 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 946 | 0.001057082452 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2010 | Outpatient | PACU | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Recovery | ASHRAE 90.1-2010HospitalRecovery | 1.15 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 108 | 0.009259259259 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2010 | Outpatient | OR | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Operating Room | ASHRAE 90.1-2010HospitalOperating Room | 1.89 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | 17.4 | 0 | 0 | 0.5 | OutPatientHealthCare BLDG_EQUIP_SCH | 2.92 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare OR_HTGSETP_SCH | OutPatientHealthCare OR_CLGSETP_SCH | 6 | 470 | 0.01276595745 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2010 | Outpatient | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | NurseStation | 31_162_169 | ASHRAE 90.1-2010 | Hospital | Nurse Station | ASHRAE 90.1-2010HospitalNurse Station | 0.87 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 90.1-2010 | Hospital | Radiology/Imaging | ASHRAE 90.1-2010HospitalRadiology/Imaging | 1.32 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 168 | 0.005952380952 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1 | 168 | 0.37862 | 0.31 | 63.6075 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2010 | Outpatient | MRI | 169_31_159 | ASHRAE 90.1-2010 | Hospital | Radiology/Imaging | ASHRAE 90.1-2010HospitalRadiology/Imaging | 1.32 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 38.63 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 440 | 0.002272727273 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1 | 440 | 0.37862 | 0.31 | 166.5909 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2010 | Outpatient | MedGas | 204_120_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.07 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | Lounge | 230_157_120 | ASHRAE 90.1-2010 | Lounge/Recreation | For Hospital | ASHRAE 90.1-2010Lounge/RecreationFor Hospital | 1.07 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 |  | 13.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 90.1-2010 | Locker Room | General | ASHRAE 90.1-2010Locker RoomGeneral | 0.75 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 |  |  | 13.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral | 0.9 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2007Office BuildingsMain entry lobbies | 0.06 | 5 |  | 27.87 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | Janitor | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | IT_Room | 41_31_169 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | ASHRAE 62.1-2007Office BuildingsTelephone/data entry | 0.06 | 5 |  | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | Hall | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | For Hospital | ASHRAE 90.1-2010Corridor/TransitionFor Hospital | 0.89 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.29 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | Exam | 136_78_222 | ASHRAE 90.1-2010 | Hospital | Exam/Treatment | ASHRAE 90.1-2010HospitalExam/Treatment | 1.66 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral | 0.95 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 3.64 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 90.1-2010 | Dressing/Fitting Room | For Retail | ASHRAE 90.1-2010Dressing/Fitting RoomFor Retail | 0.87 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Patient rooms | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPatient rooms |  | 25 |  | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | Conference | 230_196_120 | ASHRAE 90.1-2010 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2010Conference/Meeting/MultipurposeGeneral | 1.23 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 |  | 46.45 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.73 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | CleanWork | 204_120_230 | ASHRAE 90.1-2010 | Hospital | Medical Supply | ASHRAE 90.1-2010HospitalMedical Supply | 1.27 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | Cafe | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | General | ASHRAE 90.1-2010Dining AreaGeneral | 0.65 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 92.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.73 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | BioHazard | 204_120_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.07 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 90.1-2010 | Hospital | Operating Room | ASHRAE 90.1-2010HospitalOperating Room | 1.89 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 108 | 0.009259259259 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1.3333 | 144 | 0.50482 | 0.31 | 54.5207 | 1 |  | OutPatientHealthCare Hours_of_operation
DOE Ref 1980-2004 | Outpatient | Xray | 169_31_159 | DOE Ref 1980-2004 | Outpatient | Xray | DOE Ref 1980-2004OutpatientXray | 2.1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 900 | 0.001111111111 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref 1980-2004 | Outpatient | Toilet | 169_169_31 | DOE Ref 1980-2004 | Outpatient | Toilet | DOE Ref 1980-2004OutpatientToilet | 0.8 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 0.4 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 90 | 0.6310269118 | 0.31 | 34.0754 | 1 |  | Outpatient_FirstFlr_Exhaust
DOE Ref 1980-2004 | Outpatient | Stair | 230_157_120 | DOE Ref 1980-2004 | Outpatient | Stair | DOE Ref 1980-2004OutpatientStair | 0.8 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | Soil Work | 204_120_230 | DOE Ref 1980-2004 | Outpatient | Soil Work | DOE Ref 1980-2004OutpatientSoil Work | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 210 | 0.6310269118 | 0.31 | 79.5093 | 1 |  | Outpatient_FirstFlr_Exhaust
DOE Ref 1980-2004 | Outpatient | ProcedureRoom | 169_31_159 | DOE Ref 1980-2004 | Outpatient | ProcedureRoom | DOE Ref 1980-2004OutpatientProcedureRoom | 1.6 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 285 | 0.00350877193 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref 1980-2004 | Outpatient | PreOp | 169_31_159 | DOE Ref 1980-2004 | Outpatient | PreOp | DOE Ref 1980-2004OutpatientPreOp | 1.4 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 |  |  | 9.29 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 263.5 | 0.003795066414 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref 1980-2004 | Outpatient | PhysicalTherapy | 154_230_120 | DOE Ref 1980-2004 | Outpatient | PhysicalTherapy | DOE Ref 1980-2004OutpatientPhysicalTherapy | 1.6 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.5 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 946 | 0.001057082452 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref 1980-2004 | Outpatient | PACU | 169_31_159 | DOE Ref 1980-2004 | Outpatient | PACU | DOE Ref 1980-2004OutpatientPACU | 2.3 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.009259259259 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref 1980-2004 | Outpatient | OR | 169_31_159 | DOE Ref 1980-2004 | Outpatient | OR | DOE Ref 1980-2004OutpatientOR | 7 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | 23.9 | 0 | 0 | 0.5 | Outpatient Bldg Equip | 4 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient OR HtgSetp | Outpatient OR ClgSetp | 6 | 470 | 0.01276595745 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref 1980-2004 | Outpatient | Office | 120_230_199 | DOE Ref 1980-2004 | Outpatient | Office | DOE Ref 1980-2004OutpatientOffice | 1.8 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 4.65 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | NurseStation | 31_162_169 | DOE Ref 1980-2004 | Outpatient | NurseStation | DOE Ref 1980-2004OutpatientNurseStation | 2.1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | MRI_Control | 136_78_222 | DOE Ref 1980-2004 | Outpatient | MRI_Control | DOE Ref 1980-2004OutpatientMRI_Control | 2.1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 168 | 0.005952380952 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 168 | 0.3786161471 | 0.31 | 63.6075 | 1 |  | Outpatient_FirstFlr_Exhaust
DOE Ref 1980-2004 | Outpatient | MRI | 169_31_159 | DOE Ref 1980-2004 | Outpatient | MRI | DOE Ref 1980-2004OutpatientMRI | 2.1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 53.06 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 440 | 0.002272727273 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 440 | 0.3786161471 | 0.31 | 166.5909 | 1 |  | Outpatient_FirstFlr_Exhaust
DOE Ref 1980-2004 | Outpatient | MedGas | 204_120_230 | DOE Ref 1980-2004 | Outpatient | MedGas | DOE Ref 1980-2004OutpatientMedGas | 1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 0.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | Lounge | 230_157_120 | DOE Ref 1980-2004 | Outpatient | Lounge | DOE Ref 1980-2004OutpatientLounge | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 13.94 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | LockerRoom | 169_169_31 | DOE Ref 1980-2004 | Outpatient | LockerRoom | DOE Ref 1980-2004OutpatientLockerRoom | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 |  |  | 13.94 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | Lobby | 230_157_120 | DOE Ref 1980-2004 | Outpatient | Lobby | DOE Ref 1980-2004OutpatientLobby | 1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 27.87 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | Janitor | 120_149_230 | DOE Ref 1980-2004 | Outpatient | Janitor | DOE Ref 1980-2004OutpatientJanitor | 1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 |  |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | IT_Room | 41_31_169 | DOE Ref 1980-2004 | Outpatient | IT_Room | DOE Ref 1980-2004OutpatientIT_Room | 1.8 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | 0 | 20 |  | 4.65 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | Hall | 169_31_31 | DOE Ref 1980-2004 | Outpatient | Hall | DOE Ref 1980-2004OutpatientHall | 0.8 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 0.4 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | Exam | 136_78_222 | DOE Ref 1980-2004 | Outpatient | Exam | DOE Ref 1980-2004OutpatientExam | 1.6 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | Elec/MechRoom | 41_31_169 | DOE Ref 1980-2004 | Outpatient | Elec/MechRoom | DOE Ref 1980-2004OutpatientElec/MechRoom | 0.7 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 |  |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 5 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | DressingRoom | 136_78_222 | DOE Ref 1980-2004 | Outpatient | DressingRoom | DOE Ref 1980-2004OutpatientDressingRoom | 1.8 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 4.65 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | Conference | 230_196_120 | DOE Ref 1980-2004 | Outpatient | Conference | DOE Ref 1980-2004OutpatientConference | 1.8 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 |  | 46.45 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | CleanWork | 204_120_230 | DOE Ref 1980-2004 | Outpatient | CleanWork | DOE Ref 1980-2004OutpatientCleanWork | 1.3 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | Cafe | 31_169_34 | DOE Ref 1980-2004 | Outpatient | Cafe | DOE Ref 1980-2004OutpatientCafe | 1.3 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 92.94 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | BioHazard | 204_120_230 | DOE Ref 1980-2004 | Outpatient | BioHazard | DOE Ref 1980-2004OutpatientBioHazard | 1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 |  |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 0.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref 1980-2004 | Outpatient | Anesthesia | 204_120_230 | DOE Ref 1980-2004 | Outpatient | Anesthesia | DOE Ref 1980-2004OutpatientAnesthesia | 2.1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 |  |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.009259259259 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1.3333 | 144 | 0.5048215295 | 0.31 | 54.5207 | 1 |  | Outpatient_FirstFlr_Exhaust
DOE Ref Pre-1980 | Outpatient | Xray | 169_31_159 | DOE Ref Pre-1980 | Outpatient | Xray | DOE Ref Pre-1980OutpatientXray | 2.1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 900 | 0.001111111111 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref Pre-1980 | Outpatient | Toilet | 169_169_31 | DOE Ref Pre-1980 | Outpatient | Toilet | DOE Ref Pre-1980OutpatientToilet | 0.8 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 0.4 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 90 | 0.6310269118 | 0.31 | 34.0754 | 1 |  | Outpatient_FirstFlr_Exhaust
DOE Ref Pre-1980 | Outpatient | Stair | 230_157_120 | DOE Ref Pre-1980 | Outpatient | Stair | DOE Ref Pre-1980OutpatientStair | 0.8 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 0 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | Soil Work | 204_120_230 | DOE Ref Pre-1980 | Outpatient | Soil Work | DOE Ref Pre-1980OutpatientSoil Work | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | [7 empty] | 1.6667 | 210 | 0.6310269118 | 0.31 | 79.5093 | 1 |  | Outpatient_FirstFlr_Exhaust
DOE Ref Pre-1980 | Outpatient | ProcedureRoom | 169_31_159 | DOE Ref Pre-1980 | Outpatient | ProcedureRoom | DOE Ref Pre-1980OutpatientProcedureRoom | 1.6 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 285 | 0.00350877193 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref Pre-1980 | Outpatient | PreOp | 169_31_159 | DOE Ref Pre-1980 | Outpatient | PreOp | DOE Ref Pre-1980OutpatientPreOp | 1.4 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 |  |  | 9.29 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 263.5 | 0.003795066414 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref Pre-1980 | Outpatient | PhysicalTherapy | 154_230_120 | DOE Ref Pre-1980 | Outpatient | PhysicalTherapy | DOE Ref Pre-1980OutpatientPhysicalTherapy | 1.6 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-1999Hospitals, Nursing and Convalescent HomesPhysical therapy | 0 | 15 |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.5 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 946 | 0.001057082452 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref Pre-1980 | Outpatient | PACU | 169_31_159 | DOE Ref Pre-1980 | Outpatient | PACU | DOE Ref Pre-1980OutpatientPACU | 2.3 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.009259259259 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref Pre-1980 | Outpatient | OR | 169_31_159 | DOE Ref Pre-1980 | Outpatient | OR | DOE Ref Pre-1980OutpatientOR | 7 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | 23.9 | 0 | 0 | 0.5 | Outpatient Bldg Equip | 4 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient OR HtgSetp | Outpatient OR ClgSetp | 6 | 470 | 0.01276595745 | 43.3 | 0.2 | 0.05 | Outpatient SWH
DOE Ref Pre-1980 | Outpatient | Office | 120_230_199 | DOE Ref Pre-1980 | Outpatient | Office | DOE Ref Pre-1980OutpatientOffice | 1.8 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 4.65 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | NurseStation | 31_162_169 | DOE Ref Pre-1980 | Outpatient | NurseStation | DOE Ref Pre-1980OutpatientNurseStation | 2.1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | MRI_Control | 136_78_222 | DOE Ref Pre-1980 | Outpatient | MRI_Control | DOE Ref Pre-1980OutpatientMRI_Control | 2.1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 168 | 0.005952380952 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 168 | 0.3786161471 | 0.31 | 63.6075 | 1 |  | Outpatient_FirstFlr_Exhaust
DOE Ref Pre-1980 | Outpatient | MRI | 169_31_159 | DOE Ref Pre-1980 | Outpatient | MRI | DOE Ref Pre-1980OutpatientMRI | 2.1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 53.06 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 440 | 0.002272727273 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1 | 440 | 0.3786161471 | 0.31 | 166.5909 | 1 |  | Outpatient_FirstFlr_Exhaust
DOE Ref Pre-1980 | Outpatient | MedGas | 204_120_230 | DOE Ref Pre-1980 | Outpatient | MedGas | DOE Ref Pre-1980OutpatientMedGas | 1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 0.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | Lounge | 230_157_120 | DOE Ref Pre-1980 | Outpatient | Lounge | DOE Ref Pre-1980OutpatientLounge | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 13.94 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | LockerRoom | 169_169_31 | DOE Ref Pre-1980 | Outpatient | LockerRoom | DOE Ref Pre-1980OutpatientLockerRoom | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 |  |  | 13.94 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 3 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | Lobby | 230_157_120 | DOE Ref Pre-1980 | Outpatient | Lobby | DOE Ref Pre-1980OutpatientLobby | 1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 27.87 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | Janitor | 120_149_230 | DOE Ref Pre-1980 | Outpatient | Janitor | DOE Ref Pre-1980OutpatientJanitor | 1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 |  |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 0 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | IT_Room | 41_31_169 | DOE Ref Pre-1980 | Outpatient | IT_Room | DOE Ref Pre-1980OutpatientIT_Room | 1.8 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Offices | Telecommunication centers and data entry areas | ASHRAE 62.1-1999OfficesTelecommunication centers and data entry areas | 0 | 20 |  | 4.65 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | Hall | 169_31_31 | DOE Ref Pre-1980 | Outpatient | Hall | DOE Ref Pre-1980OutpatientHall | 0.8 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 0.4 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | Exam | 136_78_222 | DOE Ref Pre-1980 | Outpatient | Exam | DOE Ref Pre-1980OutpatientExam | 1.6 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | Elec/MechRoom | 41_31_169 | DOE Ref Pre-1980 | Outpatient | Elec/MechRoom | DOE Ref Pre-1980OutpatientElec/MechRoom | 0.7 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 |  |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 5 | 0 | 0.3 | 0.7 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | DressingRoom | 136_78_222 | DOE Ref Pre-1980 | Outpatient | DressingRoom | DOE Ref Pre-1980OutpatientDressingRoom | 1.8 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 4.65 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | Conference | 230_196_120 | DOE Ref Pre-1980 | Outpatient | Conference | DOE Ref Pre-1980OutpatientConference | 1.8 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 |  | 46.45 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | CleanWork | 204_120_230 | DOE Ref Pre-1980 | Outpatient | CleanWork | DOE Ref Pre-1980OutpatientCleanWork | 1.3 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 |  |  | 18.58 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | Cafe | 31_169_34 | DOE Ref Pre-1980 | Outpatient | Cafe | DOE Ref Pre-1980OutpatientCafe | 1.3 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 92.94 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | BioHazard | 204_120_230 | DOE Ref Pre-1980 | Outpatient | BioHazard | DOE Ref Pre-1980OutpatientBioHazard | 1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 |  |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 0.1 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp
DOE Ref Pre-1980 | Outpatient | Anesthesia | 204_120_230 | DOE Ref Pre-1980 | Outpatient | Anesthesia | DOE Ref Pre-1980OutpatientAnesthesia | 2.1 |  |  |  | 0 | 0.7 | 0.2 | Outpatient Bldg Light | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 |  |  | 0 | Outpatient Bldg Occ | Outpatient Activity |  | 0.2232 |  | Outpatient Infil | [5 empty] | 2 | 0 | 0.5 | 0 | Outpatient Bldg Equip | Outpatient HtgSetp | Outpatient ClgSetp | 1 | 108 | 0.009259259259 | 43.3 | 0.2 | 0.05 | Outpatient SWH | 1.3333 | 144 | 0.5048215295 | 0.31 | 54.5207 | 1 |  | Outpatient_FirstFlr_Exhaust
189.1-2009 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral | 0.81 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  |  | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 56.5 | 2045 | 0.02762836186 | 43.3 | 0.2 | 0.05 | PrimarySchool SWH | 0.29338 | 600 | 0.05093797833 | 0.338 | 104.1753 | 0.5
189.1-2009 | PrimarySchool | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral | 0.99 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 4.65 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  |  | PrimarySchool Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral | 1.35 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  |  | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
189.1-2009 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral | 1.17 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 0 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  |  | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | PrimarySchool | Library | 230_196_120 | ASHRAE 189.1-2009 | Whole Building | Library | ASHRAE 189.1-2009Whole BuildingLibrary | 1.17 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 |  | 21.36 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  |  | PrimarySchool Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral | 1.08 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 13.93 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  |  | PrimarySchool Infil | 220.5 | 0.1 | 0.2 | 0.7 | PrimarySchool Kitchen Gas | 13.13 | 0.25 | 0.3 | 0.2 | PrimarySchool Kitchen Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 100 | 1808 | 0.05530973451 | 49 | 0.2 | 0.05 | PrimarySchool SWH | 0.7 | 3300 | 0.1215379059 | 0.338 | 572.9644 | 0.5 |  | PrimarySchool Kitchen Exhaust
189.1-2009 | PrimarySchool | Gym | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterExercise Area | 0.81 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 |  | 27.9 | PrimarySchool Gym Occ | PrimarySchool Activity | 0.0446 |  |  | PrimarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral | 0.45 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  |  | PrimarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
189.1-2009 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral | 1.26 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 |  | 23.22 | PrimarySchool Bldg Occ | PrimarySchool Activity | 0.0446 |  |  | PrimarySchool Infil | [5 empty] | 1.02 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
189.1-2009 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral | 0.81 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 66.67 | PrimarySchool Cafeteria Occ | PrimarySchool Activity | 0.0446 |  |  | PrimarySchool Infil | [5 empty] | 1.72 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
90.1-2004 | MidriseApartment | Apartment_topfloor_WE | 78_167_222 | ASHRAE 90.1-2004 | MidriseApartment | Apartment | ASHRAE 90.1-2004MidriseApartmentApartment | 0.36 |  |  | 0.09 | 0 | 0 | 0 | ApartmentMidRise LTG_APT_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Apartment | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesApartment | 0 | 0 | 0.35 | 2.63 | ApartmentMidRise OCC_APT_SCH | ApartmentMidRise Activity Schedule | 0.080378 |  |  | ApartmentMidRise INF_APT_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH | 3.48 | 950 | 0.003663157895 | 60 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
90.1-2004 | MidriseApartment | Apartment_topfloor_NS | 78_167_222 | ASHRAE 90.1-2004 | MidriseApartment | Apartment | ASHRAE 90.1-2004MidriseApartmentApartment | 0.36 |  |  | 0.09 | 0 | 0 | 0 | ApartmentMidRise LTG_APT_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Apartment | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesApartment | 0 | 0 | 0.35 | 2.63 | ApartmentMidRise OCC_APT_SCH | ApartmentMidRise Activity Schedule | 0.057597 |  |  | ApartmentMidRise INF_APT_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH | 3.48 | 950 | 0.003663157895 | 60 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
90.1-2007 | MidriseApartment | Office | 120_230_199 | ASHRAE 90.1-2004 | MidriseApartment | Office | ASHRAE 90.1-2004MidriseApartmentOffice | 1.11 |  |  | 1.1 | 0 | 0 | 0 | ApartmentMidRise LTG_OFF_SCH_2004_2007 | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Living rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLiving rooms | 0.085 | 0 |  | 2.11 | ApartmentMidRise OCC_OFF_SCH | ApartmentMidRise Activity Schedule | 0.2016 |  |  | ApartmentMidRise INF_OFF_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_OFF_SCH_2004_2007 | ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | ApartmentMidRise CLGSETP_OFF_SCH_No_Setback
90.1-2007 | MidriseApartment | Corridor | 169_31_31 | ASHRAE 90.1-2004 | MidriseApartment | Corridor | ASHRAE 90.1-2004MidriseApartmentCorridor | 0.5 |  |  |  | 0 | 0 | 0 | ApartmentMidRise LTG_COR_SCH_2004_2007 | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 | ApartmentMidRise All Off |  | 0.2016 |  |  | ApartmentMidRise INF_COR_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH
90.1-2007 | MidriseApartment | Corridor_topfloor | 169_31_31 | ASHRAE 90.1-2004 | MidriseApartment | Corridor | ASHRAE 90.1-2004MidriseApartmentCorridor | 0.5 |  |  |  | 0 | 0 | 0 | ApartmentMidRise LTG_COR_SCH_2004_2007 | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 | ApartmentMidRise All Off |  | 0.023446 |  |  | ApartmentMidRise INF_COR_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH
90.1-2007 | MidriseApartment | Apartment | 78_167_222 | ASHRAE 90.1-2004 | MidriseApartment | Apartment | ASHRAE 90.1-2004MidriseApartmentApartment | 0.36 |  |  | 0.09 | 0 | 0 | 0 | ApartmentMidRise LTG_APT_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Apartment | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesApartment | 0 | 0 | 0.35 | 2.63 | ApartmentMidRise OCC_APT_SCH | ApartmentMidRise Activity Schedule | 0.2016 |  |  | ApartmentMidRise INF_APT_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH | 3.48 | 950 | 0.003663157895 | 60 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
90.1-2007 | MidriseApartment | Apartment_topfloor_WE | 78_167_222 | ASHRAE 90.1-2004 | MidriseApartment | Apartment | ASHRAE 90.1-2004MidriseApartmentApartment | 0.36 |  |  | 0.09 | 0 | 0 | 0 | ApartmentMidRise LTG_APT_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Apartment | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesApartment | 0 | 0 | 0.35 | 2.63 | ApartmentMidRise OCC_APT_SCH | ApartmentMidRise Activity Schedule | 0.080378 |  |  | ApartmentMidRise INF_APT_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH | 3.48 | 950 | 0.003663157895 | 60 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
90.1-2007 | MidriseApartment | Apartment_topfloor_NS | 78_167_222 | ASHRAE 90.1-2004 | MidriseApartment | Apartment | ASHRAE 90.1-2004MidriseApartmentApartment | 0.36 |  |  | 0.09 | 0 | 0 | 0 | ApartmentMidRise LTG_APT_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Apartment | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesApartment | 0 | 0 | 0.35 | 2.63 | ApartmentMidRise OCC_APT_SCH | ApartmentMidRise Activity Schedule | 0.057597 |  |  | ApartmentMidRise INF_APT_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH | 3.48 | 950 | 0.003663157895 | 60 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
90.1-2010 | MidriseApartment | Office | 120_230_199 | ASHRAE 90.1-2004 | MidriseApartment | Office | ASHRAE 90.1-2004MidriseApartmentOffice | 1.11 |  |  | 1.11 | 0 | 0 | 0 | ApartmentMidRise LTG_OFF_SCH_2010_2013 | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Living rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLiving rooms | 0.085 | 0 |  | 2.11 | ApartmentMidRise OCC_OFF_SCH | ApartmentMidRise Activity Schedule | 0.112 |  |  | ApartmentMidRise INF_OFF_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_OFF_SCH_2010_2013 | ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | ApartmentMidRise CLGSETP_OFF_SCH_No_Setback
90.1-2010 | MidriseApartment | Corridor | 169_31_31 | ASHRAE 90.1-2010 | MidriseApartment | Corridor | ASHRAE 90.1-2010MidriseApartmentCorridor | 0.792 |  |  |  | 0 | 0 | 0 | ApartmentMidRise LTG_COR_SCH_2010 | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 | ApartmentMidRise All Off |  | 0.112 |  |  | ApartmentMidRise INF_COR_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH
90.1-2010 | MidriseApartment | Corridor_topfloor | 169_31_31 | ASHRAE 90.1-2010 | MidriseApartment | Corridor | ASHRAE 90.1-2010MidriseApartmentCorridor | 0.792 |  |  |  | 0 | 0 | 0 | ApartmentMidRise LTG_COR_SCH_2010 | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 | ApartmentMidRise All Off |  | 0.013026 |  |  | ApartmentMidRise INF_COR_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH
90.1-2010 | MidriseApartment | Apartment | 78_167_222 | ASHRAE 90.1-2004 | MidriseApartment | Apartment | ASHRAE 90.1-2004MidriseApartmentApartment | 0.36 |  |  | 0.09 | 0 | 0 | 0 | ApartmentMidRise LTG_APT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Apartment | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesApartment | 0 | 0 | 0.35 | 2.63 | ApartmentMidRise OCC_APT_SCH | ApartmentMidRise Activity Schedule | 0.112 |  |  | ApartmentMidRise INF_APT_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH | 3.48 | 950 | 0.003663157895 | 60 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
90.1-2010 | MidriseApartment | Apartment_topfloor_WE | 78_167_222 | ASHRAE 90.1-2004 | MidriseApartment | Apartment | ASHRAE 90.1-2004MidriseApartmentApartment | 0.36 |  |  | 0.09 | 0 | 0 | 0 | ApartmentMidRise LTG_APT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Apartment | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesApartment | 0 | 0 | 0.35 | 2.63 | ApartmentMidRise OCC_APT_SCH | ApartmentMidRise Activity Schedule | 0.044654 |  |  | ApartmentMidRise INF_APT_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH | 3.48 | 950 | 0.003663157895 | 60 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
90.1-2010 | MidriseApartment | Apartment_topfloor_NS | 78_167_222 | ASHRAE 90.1-2004 | MidriseApartment | Apartment | ASHRAE 90.1-2004MidriseApartmentApartment | 0.36 |  |  | 0.09 | 0 | 0 | 0 | ApartmentMidRise LTG_APT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Apartment | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesApartment | 0 | 0 | 0.35 | 2.63 | ApartmentMidRise OCC_APT_SCH | ApartmentMidRise Activity Schedule | 0.031998 |  |  | ApartmentMidRise INF_APT_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH | 3.48 | 950 | 0.003663157895 | 60 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
90.1-2013 | MidriseApartment | Office | 120_230_199 | ASHRAE 90.1-2004 | MidriseApartment | Office | ASHRAE 90.1-2004MidriseApartmentOffice | 1.11 |  |  | 1.11 | 0 | 0 | 0 | ApartmentMidRise LTG_OFF_SCH_2010_2013 | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Living rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLiving rooms | 0.085 | 0 |  | 2.11 | ApartmentMidRise OCC_OFF_SCH | ApartmentMidRise Activity Schedule | 0.112 |  |  | ApartmentMidRise INF_OFF_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_OFF_SCH_2010_2013 | ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | ApartmentMidRise CLGSETP_OFF_SCH_NO_OPTIMUM
90.1-2013 | MidriseApartment | Corridor | 169_31_31 | ASHRAE 90.1-2010 | MidriseApartment | Corridor | ASHRAE 90.1-2010MidriseApartmentCorridor | 0.792 |  |  |  | 0 | 0 | 0 | ApartmentMidRise LTG_COR_SCH_2013 | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 | ApartmentMidRise All Off |  | 0.112 |  |  | ApartmentMidRise INF_COR_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH
90.1-2013 | MidriseApartment | Corridor_topfloor | 169_31_31 | ASHRAE 90.1-2010 | MidriseApartment | Corridor | ASHRAE 90.1-2010MidriseApartmentCorridor | 0.792 |  |  |  | 0 | 0 | 0 | ApartmentMidRise LTG_COR_SCH_2013 | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 | ApartmentMidRise All Off |  | 0.013026 |  |  | ApartmentMidRise INF_COR_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH
90.1-2013 | MidriseApartment | Apartment | 78_167_222 | ASHRAE 90.1-2004 | MidriseApartment | Apartment | ASHRAE 90.1-2004MidriseApartmentApartment | 0.36 |  |  | 0.09 | 0 | 0 | 0 | ApartmentMidRise LTG_APT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Apartment | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesApartment | 0 | 0 | 0.35 | 2.63 | ApartmentMidRise OCC_APT_SCH | ApartmentMidRise Activity Schedule | 0.112 |  |  | ApartmentMidRise INF_APT_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH | 3.48 | 950 | 0.003663157895 | 60 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
90.1-2013 | MidriseApartment | Apartment_topfloor_WE | 78_167_222 | ASHRAE 90.1-2004 | MidriseApartment | Apartment | ASHRAE 90.1-2004MidriseApartmentApartment | 0.36 |  |  | 0.09 | 0 | 0 | 0 | ApartmentMidRise LTG_APT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Apartment | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesApartment | 0 | 0 | 0.35 | 2.63 | ApartmentMidRise OCC_APT_SCH | ApartmentMidRise Activity Schedule | 0.044654 |  |  | ApartmentMidRise INF_APT_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH | 3.48 | 950 | 0.003663157895 | 60 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
90.1-2013 | MidriseApartment | Apartment_topfloor_NS | 78_167_222 | ASHRAE 90.1-2004 | MidriseApartment | Apartment | ASHRAE 90.1-2004MidriseApartmentApartment | 0.36 |  |  | 0.09 | 0 | 0 | 0 | ApartmentMidRise LTG_APT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Apartment | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesApartment | 0 | 0 | 0.35 | 2.63 | ApartmentMidRise OCC_APT_SCH | ApartmentMidRise Activity Schedule | 0.031998 |  |  | ApartmentMidRise INF_APT_SCH | [5 empty] | 0.61966 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | ApartmentMidRise HTGSETP_APT_SCH | ApartmentMidRise CLGSETP_APT_SCH | 3.48 | 950 | 0.003663157895 | 60 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
DOE Ref 1980-2004 | MidriseApartment | Office | 120_230_199 | DOE Ref Pre-1980 | MidriseApartment | Office | DOE Ref Pre-1980MidriseApartmentOffice | 2.04 |  |  |  | 0 | 0 | 0 | MidriseApartment Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 2.11 | MidriseApartment Office Occ | MidriseApartment Activity |  | 0.223 |  | MidriseApartment OFFICE Infil | [5 empty] | 1.2 | 0 | 0.5 | 0 | ApartmentMidRise EQP_OFF_SCH_Pre2004 | MidriseApartment Office HtgSetp | MidriseApartment Office ClgSetp
DOE Ref 1980-2004 | MidriseApartment | Corridor | 169_31_31 | DOE Ref Pre-1980 | MidriseApartment | Corridor | DOE Ref Pre-1980MidriseApartmentCorridor | 0.92 |  |  |  | 0 | 0 | 0 | MidriseApartment Corridor Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 |  |  |  | 0.223 |  | MidriseApartment Infil | [5 empty] | 0 | 0 | 0.5 | 0 | ApartmentMidRise BLDG_ELEVATORS Pre2004 | MidriseApartment UnitHeater HtgSP Sch | MidriseApartment UnitHeater ClgSP Sch
DOE Ref 1980-2004 | MidriseApartment | Apartment | 78_167_222 | DOE Ref Pre-1980 | MidriseApartment | Apartment | DOE Ref Pre-1980MidriseApartmentApartment | 0.36 |  |  |  | 0 | 0 | 0 | MidriseApartment Apartment Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Apartment | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesApartment | 0 | 36 |  | 2.63 | MidriseApartment Apartment Occ | MidriseApartment Activity |  | 0.223 |  | MidriseApartment Infil | [5 empty] | 0.5 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | MidriseApartment Apartment HtgSetp | MidriseApartment Apartment ClgSetp | 3.48 | 950 | 0.003663157895 | 43.3 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
DOE Ref Pre-1980 | MidriseApartment | Office | 120_230_199 | DOE Ref Pre-1980 | MidriseApartment | Office | DOE Ref Pre-1980MidriseApartmentOffice | 2.04 |  |  |  | 0 | 0 | 0 | MidriseApartment Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 2.11 | MidriseApartment Office Occ | MidriseApartment Activity |  | 0.223 |  | MidriseApartment OFFICE Infil | [5 empty] | 1.2 | 0 | 0.5 | 0 | ApartmentMidRise EQP_OFF_SCH_Pre2004 | MidriseApartment Office HtgSetp | MidriseApartment Office ClgSetp
DOE Ref Pre-1980 | MidriseApartment | Corridor | 169_31_31 | DOE Ref Pre-1980 | MidriseApartment | Corridor | DOE Ref Pre-1980MidriseApartmentCorridor | 0.92 |  |  |  | 0 | 0 | 0 | MidriseApartment Corridor Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 |  |  |  | 0.223 |  | MidriseApartment Infil | [5 empty] | 0 | 0 | 0.5 | 0 | ApartmentMidRise BLDG_ELEVATORS Pre2004 | MidriseApartment UnitHeater HtgSP Sch | MidriseApartment UnitHeater ClgSP Sch
DOE Ref Pre-1980 | MidriseApartment | Apartment | 78_167_222 | DOE Ref Pre-1980 | MidriseApartment | Apartment | DOE Ref Pre-1980MidriseApartmentApartment | 0.36 |  |  |  | 0 | 0 | 0 | MidriseApartment Apartment Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Apartment | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesApartment | 0 | 36 |  | 2.63 | MidriseApartment Apartment Occ | MidriseApartment Activity |  | 0.223 |  | MidriseApartment Infil | [5 empty] | 0.5 | 0 | 0.5 | 0 | ApartmentMidRise EQP_APT_SCH | MidriseApartment Apartment HtgSetp | MidriseApartment Apartment ClgSetp | 3.48 | 950 | 0.003663157895 | 43.3 | 0.2 | 0.05 | ApartmentMidRise APT_DHW_SCH
90.1-2004 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_BATH_SCH | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | 56.5 | 2045 | 0.02762836186 | 43.3 | 0.2 | 0.05 | SchoolPrimary BLDG_SWH_SCH | 0.29338 | 600 | 0.05093797833 | 0.338 | 104.1753 | 0.5
90.1-2004 | PrimarySchool | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5 | SchoolPrimary BLDG_OCC_SCH_Offices | SchoolPrimary ACTIVITY_SCH | 0.0595 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral | 1.5 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral | 1.3 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | PrimarySchool | Library | 230_196_120 | ASHRAE 90.1-2004 | Whole Building | Library | ASHRAE 90.1-2004Whole BuildingLibrary | 1.3 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 |  | 10 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  |  | SchoolPrimary INFIL_SCH_PNNL | 0 |  |  |  |  | 1.39 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral | 1.2 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 13.93 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  |  | SchoolPrimary INFIL_SCH_PNNL | 453.7 | 0.1 | 0.2 | 0.7 | SchoolPrimary KITCHEN_GAS_EQUIP_SCH | 17.7 | 0.25 | 0.3 | 0.2 | SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | 100 | 1808 | 0.05530973451 | 49 | 0.2 | 0.05 | SchoolPrimary BLDG_SWH_SCH | 0.7 | 3300 | 0.1215379059 | 0.338 | 572.9644 | 0.5 |  | SchoolPrimary Kitchen_Exhaust_SCH
90.1-2004 | PrimarySchool | Gym | 154_230_120 | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 90.1-2004Gymnasium/Exercise CenterExercise Area | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_GYM_SCH | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 |  | 30 | SchoolPrimary BLDG_OCC_SCH_Gym | SchoolPrimary ACTIVITY_SCH | 0.0595 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.46 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral | 0.5 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2004 | Classroom/Lecture/Training | General | ASHRAE 90.1-2004Classroom/Lecture/TrainingGeneral | 1.4 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 |  | 25 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0595 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1.39 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2004 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 100 | SchoolPrimary BLDG_OCC_SCH_Cafeteria | SchoolPrimary ACTIVITY_SCH | 0.0595 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 2.36 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_BATH_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | 56.5 | 2045 | 0.02762836186 | 43.3 | 0.2 | 0.05 | SchoolPrimary BLDG_SWH_SCH | 0.29338 | 600 | 0.05093797833 | 0.338 | 104.1753 | 0.5
90.1-2007 | PrimarySchool | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 |  | 5 | SchoolPrimary BLDG_OCC_SCH_Offices | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral | 1.5 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral | 1.3 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | PrimarySchool | Library | 230_196_120 | ASHRAE 90.1-2007 | Whole Building | Library | ASHRAE 90.1-2007Whole BuildingLibrary | 1.3 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | ASHRAE 62.1-2004 | Educational Facilities | Media center | ASHRAE 62.1-2004Educational FacilitiesMedia center | 0.12 | 10 |  | 10 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1.39 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral | 1.2 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 13.93 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | 453.7 | 0.1 | 0.2 | 0.7 | SchoolPrimary KITCHEN_GAS_EQUIP_SCH | 17.7 | 0.25 | 0.3 | 0.2 | SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | 100 | 1808 | 0.05530973451 | 49 | 0.2 | 0.05 | SchoolPrimary BLDG_SWH_SCH | 0.7 | 3300 | 0.1215379059 | 0.338 | 572.9644 | 0.5 |  | SchoolPrimary Kitchen_Exhaust_SCH
90.1-2007 | PrimarySchool | Gym | 154_230_120 | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 90.1-2007Gymnasium/Exercise CenterExercise Area | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_GYM_SCH | ASHRAE 62.1-2004 | Sports and Entertainment | Gym, stadium (play area) | ASHRAE 62.1-2004Sports and EntertainmentGym, stadium (play area) | 0.3 |  |  | 30 | SchoolPrimary BLDG_OCC_SCH_Gym | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.46 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral | 0.5 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2007 | Classroom/Lecture/Training | General | ASHRAE 90.1-2007Classroom/Lecture/TrainingGeneral | 1.4 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (ages 5-8) | ASHRAE 62.1-2004Educational FacilitiesClassrooms (ages 5-8) | 0.12 | 10 |  | 25 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1.39 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 100 | SchoolPrimary BLDG_OCC_SCH_Cafeteria | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 2.36 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2010 | Restrooms | General | ASHRAE 90.1-2010RestroomsGeneral | 0.98 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_BATH_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | 56.5 | 2045 | 0.02762836186 | 43.3 | 0.2 | 0.05 | SchoolPrimary BLDG_SWH_SCH | 0.29338 | 600 | 0.050938 | 0.338 | 104.1753 | 0.5
90.1-2010 | PrimarySchool | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 5 | SchoolPrimary BLDG_OCC_SCH_Offices | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral | 0.95 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
189.1-2009 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral | 1.08 |  |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0446 |  |  | QuickServiceRestaurant Infil Half On | 298.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant Gas Equip | 20.4 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp Kitchen | QuickServiceRestaurant ClgSetp Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant SWH | 0.7 | 3300 | 0.1221241016 | 0.338 | 575.7279 | 0.50241 |  | QuickServiceRestaurant Kitchen Exhaust
189.1-2009 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | For Family Dining | ASHRAE 189.1-2009Dining AreaFor Family Dining | 1.89 |  |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 67 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity | 0.0446 |  |  | QuickServiceRestaurant Infil Half On | [5 empty] | 8.74 | 0.25 | 0.3 | 0 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp
90.1-2004 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral | 1.2 |  |  |  | 0 | 0.7 | 0.2 | RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2004_2007 | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | RestaurantFastFood BLDG_OCC_SCH | RestaurantFastFood ACTIVITY_SCH |  | 0.2016 |  | RestaurantFastFood INFIL_SCH_PNNL | 250.86 | 0.1 | 0.2 | 0.7 | RestaurantFastFood FF_GAS_EQUIP_SCH | 25.166 | 0.25 | 0.3 | 0.3 | RestaurantFastFood BLDG_EQUIP_SCH | RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_SETBACK | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | RestaurantFastFood BLDG_SWH_SCH | 0.7 | 3300 | 0.1221241016 | 0.338 | 575.7279 | 0.50241 |  | RestaurantFastFood Hours_of_operation
90.1-2004 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | For Family Dining | ASHRAE 90.1-2004Dining AreaFor Family Dining | 2.1 |  |  |  | 0 | 0.37 | 0.2 | RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 70 | RestaurantFastFood BLDG_OCC_SCH | RestaurantFastFood ACTIVITY_SCH |  | 0.2016 |  | RestaurantFastFood INFIL_SCH_PNNL | [5 empty] | 10.85 | 0.25 | 0.3 | 0 | RestaurantFastFood BLDG_EQUIP_SCH | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_SETBACK
90.1-2004 | QuickServiceRestaurant | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0 | [20 empty] | Always On
90.1-2007 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral | 1.2 |  |  |  | 0 | 0.7 | 0.2 | RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2004_2007 | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 5 | RestaurantFastFood BLDG_OCC_SCH | RestaurantFastFood ACTIVITY_SCH |  | 0.2016 |  | RestaurantFastFood INFIL_SCH_PNNL | 250.86 | 0.1 | 0.2 | 0.7 | RestaurantFastFood FF_GAS_EQUIP_SCH | 25.166 | 0.25 | 0.3 | 0.3 | RestaurantFastFood BLDG_EQUIP_SCH | RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_SETBACK | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | RestaurantFastFood BLDG_SWH_SCH | 0.7 | 3300 | 0.1221241016 | 0.338 | 575.7279 | 0.50241 |  | RestaurantFastFood Hours_of_operation
90.1-2007 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | For Family Dining | ASHRAE 90.1-2007Dining AreaFor Family Dining | 2.1 |  |  |  | 0 | 0.37 | 0.2 | RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 70 | RestaurantFastFood BLDG_OCC_SCH | RestaurantFastFood ACTIVITY_SCH |  | 0.2016 |  | RestaurantFastFood INFIL_SCH_PNNL | [5 empty] | 10.85 | 0.25 | 0.3 | 0 | RestaurantFastFood BLDG_EQUIP_SCH | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_SETBACK
90.1-2007 | QuickServiceRestaurant | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0 | [20 empty] | Always On
90.1-2010 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral | 0.99 |  |  |  | 0 | 0.7 | 0.2 | RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2010_2013 | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 5 | RestaurantFastFood BLDG_OCC_SCH | RestaurantFastFood ACTIVITY_SCH |  | 0.112 |  | RestaurantFastFood INFIL_SCH_PNNL | 250.86 | 0.1 | 0.2 | 0.7 | RestaurantFastFood FF_GAS_EQUIP_SCH | 25.166 | 0.25 | 0.3 | 0.3 | RestaurantFastFood BLDG_EQUIP_SCH | RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_SETBACK | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | RestaurantFastFood BLDG_SWH_SCH | 0.7 | 3300 | 0.12212 | 0.338 | 575.7279 | 0.50241 |  | RestaurantFastFood Hours_of_operation
90.1-2010 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | For Family Dining | ASHRAE 90.1-2010Dining AreaFor Family Dining | 0.89 |  |  |  | 0 | 0.7 | 0.2 | RestaurantFastFood BLDG_LIGHT_DINING_SCH_2010 | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 70 | RestaurantFastFood BLDG_OCC_SCH | RestaurantFastFood ACTIVITY_SCH |  | 0.112 |  | RestaurantFastFood INFIL_SCH_PNNL | [5 empty] | 10.85 | 0.25 | 0.3 | 0 | RestaurantFastFood BLDG_EQUIP_SCH | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_SETBACK
90.1-2010 | QuickServiceRestaurant | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0 | [20 empty] | Always On
DOE Ref 1980-2004 | QuickServiceRestaurant | Kitchen | 78_222_133 | DOE Ref 1980-2004 | QuickServiceRestaurant | Kitchen | DOE Ref 1980-2004QuickServiceRestaurantKitchen | 1.55 |  |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity |  | 0.223 |  | QuickServiceRestaurant Infil Half On | 409.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant Gas Equip | 28 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp Kitchen | QuickServiceRestaurant ClgSetp Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant SWH | 0.7 | 3300 | 0.1221241016 | 0.338 | 575.7279 | 0.50241 |  | QuickServiceRestaurant Kitchen Exhaust
DOE Ref 1980-2004 | QuickServiceRestaurant | Dining | 31_169_34 | DOE Ref 1980-2004 | QuickServiceRestaurant | Dining | DOE Ref 1980-2004QuickServiceRestaurantDining | 1.44 |  |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 70 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity |  | 0.223 |  | QuickServiceRestaurant Infil Half On | [5 empty] | 12 | 0.25 | 0.3 | 0 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp
DOE Ref 1980-2004 | QuickServiceRestaurant | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0 | [19 empty] | 1 | Always On
DOE Ref Pre-1980 | QuickServiceRestaurant | Kitchen | 78_222_133 | DOE Ref Pre-1980 | QuickServiceRestaurant | Kitchen | DOE Ref Pre-1980QuickServiceRestaurantKitchen | 2.24 |  |  |  | 0 | 0.7 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 5 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity |  | 0.223 |  | QuickServiceRestaurant Infil Half On | 409.6 | 0.1 | 0.2 | 0.7 | QuickServiceRestaurant Gas Equip | 28 | 0.25 | 0.3 | 0.3 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp Kitchen | QuickServiceRestaurant ClgSetp Kitchen | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | QuickServiceRestaurant SWH | 0.7 | 3300 | 0.1221241016 | 0.338 | 575.7279 | 0.50241 |  | QuickServiceRestaurant Kitchen Exhaust
DOE Ref Pre-1980 | QuickServiceRestaurant | Dining | 31_169_34 | DOE Ref Pre-1980 | QuickServiceRestaurant | Dining | DOE Ref Pre-1980QuickServiceRestaurantDining | 3.7 |  |  |  | 0 | 0.37 | 0.2 | QuickServiceRestaurant Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 70 | QuickServiceRestaurant Bldg Occ | QuickServiceRestaurant Activity |  | 0.223 |  | QuickServiceRestaurant Infil Half On | [5 empty] | 12 | 0.25 | 0.3 | 0 | QuickServiceRestaurant Bldg Equip | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp
189.1-2009 | Retail | Retail | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area | 1.53 |  |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | 0.3 | 0 |  | 15 | Retail Bldg Occ | Retail Activity | 0.0446 |  |  | Retail Infil Half On | [5 empty] | 0.22 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
189.1-2009 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area | 1.53 |  |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | Retail Bldg Occ | Retail Activity | 0.0446 |  |  | Retail Infil Half On | [5 empty] | 1.45 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
189.1-2009 | Retail | Entry | 169_31_31 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Mall Concourse | ASHRAE 189.1-2009Retail (not including accent lighting)Mall Concourse | 1.53 |  |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | Retail Bldg Occ | Retail Activity | 0.0446 |  |  | Retail Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
189.1-2009 | Retail | Back_Space | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral | 0.72 |  |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 |  | 3.33 | Retail Bldg Occ | Retail Activity | 0.0446 |  |  | Retail Infil Half On | [5 empty] | 0.546 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
90.1-2004 | Retail | Back_Space | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral | 0.8 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_BACK_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 |  | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0595 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 0.75 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK
90.1-2004 | Retail | Entry | 169_31_31 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral | 1.3 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_ENTRY_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0595 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 0.3 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone FRONT_ENTRY_COOLING
90.1-2004 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area | 1.7 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_FRONT_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0595 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 2 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK
90.1-2004 | Retail | Retail | 171_222_78 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area | 1.7 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | 0.3 | 0 |  | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0595 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 0.3 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK
90.1-2007 | Retail | Back_Space | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral | 0.8 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_BACK_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0446 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 0.75 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK
90.1-2007 | Retail | Entry | 169_31_31 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral | 1.3 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_ENTRY_SCH | ASHRAE 62.1-2004 | Retail | General Sales | ASHRAE 62.1-2004RetailGeneral Sales | 0.12 | 7.5 |  | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0446 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 0.3 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone FRONT_ENTRY_COOLING
90.1-2007 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area | 1.7 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_FRONT_SCH | ASHRAE 62.1-2004 | Retail | General Sales | ASHRAE 62.1-2004RetailGeneral Sales | 0.12 | 7.5 |  | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0446 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 2 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK
90.1-2007 | Retail | Retail | 171_222_78 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area | 1.7 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Retail | General Sales | ASHRAE 62.1-2004RetailGeneral Sales | 0.12 | 7.5 |  | 15 | RetailStandalone BLDG_OCC_SCH | RetailStandalone ACTIVITY_SCH | 0.0446 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 0.3 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK
90.1-2010 | Retail | Back_Space | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_BACK_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 15 | RetailStandalone BLDG_OCC_SCH_2010 | RetailStandalone ACTIVITY_SCH | 0.0446 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 0.75 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK
90.1-2010 | Retail | Entry | 169_31_31 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral | 0.9 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_ENTRY_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 |  | 15 | RetailStandalone BLDG_OCC_SCH_2010 | RetailStandalone ACTIVITY_SCH | 0.0446 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 0.3 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone FRONT_ENTRY_COOLING
90.1-2010 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 90.1-2010 | Sales Area | General | ASHRAE 90.1-2010Sales AreaGeneral | 1.68 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_FRONT_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 |  | 15 | RetailStandalone BLDG_OCC_SCH_2010 | RetailStandalone ACTIVITY_SCH | 0.0446 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 2 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK
90.1-2010 | Retail | Retail | 171_222_78 | ASHRAE 90.1-2010 | Sales Area | General | ASHRAE 90.1-2010Sales AreaGeneral | 1.68 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 |  | 15 | RetailStandalone BLDG_OCC_SCH_2010 | RetailStandalone ACTIVITY_SCH | 0.0446 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 0.3 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK
DOE Ref 1980-2004 | Retail | Retail | 171_222_78 | DOE Ref 1980-2004 | Retail | Retail | DOE Ref 1980-2004RetailRetail | 3.3677 |  |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | 0.3 | 0 |  | 15 | Retail Bldg Occ | Retail Activity | 0.2232 |  |  | Retail Infil Half On | [5 empty] | 0.3 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
DOE Ref 1980-2004 | Retail | Point_of_Sale | 171_222_78 | DOE Ref 1980-2004 | Retail | Point_of_Sale | DOE Ref 1980-2004RetailPoint_of_Sale | 3.3677 |  |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | Retail Bldg Occ | Retail Activity | 0.2232 |  |  | Retail Infil Half On | [5 empty] | 2 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
DOE Ref 1980-2004 | Retail | Entry | 169_31_31 | DOE Ref 1980-2004 | Retail | Entry | DOE Ref 1980-2004RetailEntry | 3.3677 |  |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | Retail Bldg Occ | Retail Activity | 0.2232 |  |  | Retail Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail FRONT ENTRY COOLING
DOE Ref 1980-2004 | Retail | Back_Space | 120_149_230 | DOE Ref 1980-2004 | Retail | Back_Space | DOE Ref 1980-2004RetailBack_Space | 1.1659 |  |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 |  | 3.33 | Retail Bldg Occ | Retail Activity | 0.2232 |  |  | Retail Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
DOE Ref Pre-1980 | Retail | Retail | 171_222_78 | DOE Ref Pre-1980 | Retail | Retail | DOE Ref Pre-1980RetailRetail | 3.3677 |  |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Clothiers, furniture | ASHRAE 62.1-1999Specialty ShopsClothiers, furniture | 0.3 | 0 |  | 15 | Retail Bldg Occ | Retail Activity | 0.2232 |  |  | Retail Infil Half On | [5 empty] | 0.3 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
DOE Ref Pre-1980 | Retail | Point_of_Sale | 171_222_78 | DOE Ref Pre-1980 | Retail | Point_of_Sale | DOE Ref Pre-1980RetailPoint_of_Sale | 3.3677 |  |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | Retail Bldg Occ | Retail Activity | 0.2232 |  |  | Retail Infil Half On | [5 empty] | 2 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
DOE Ref Pre-1980 | Retail | Entry | 169_31_31 | DOE Ref Pre-1980 | Retail | Entry | DOE Ref Pre-1980RetailEntry | 3.3677 |  |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | Retail Bldg Occ | Retail Activity | 0.2232 |  |  | Retail Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail FRONT ENTRY COOLING
DOE Ref Pre-1980 | Retail | Back_Space | 120_149_230 | DOE Ref Pre-1980 | Retail | Back_Space | DOE Ref Pre-1980RetailBack_Space | 1.1659 |  |  |  | 0 | 0.7 | 0.2 | Retail Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 |  | 3.33 | Retail Bldg Occ | Retail Activity | 0.2232 |  |  | Retail Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | Retail Bldg Equip | Retail HtgSetp | Retail ClgSetp
189.1-2009 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral | 0.81 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 9.29 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  |  | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 52.2 | 2260 | 0.02309734513 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH | 0.28122 | 635.6646 | 0.04882618419 | 0.338 | 110.3676 | 0.5
189.1-2009 | SecondarySchool | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral | 0.99 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 4.65 | SecondarySchool Office Occ | SecondarySchool Activity | 0.0446 |  |  | SecondarySchool Infil | [5 empty] | 0.73 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral | 1.35 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0.93 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  |  | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
189.1-2009 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 189.1-2009 | Lobby | General | ASHRAE 189.1-2009LobbyGeneral | 1.17 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 0 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  |  | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | SecondarySchool | Library | 230_196_120 | ASHRAE 189.1-2009 | Whole Building | Library | ASHRAE 189.1-2009Whole BuildingLibrary | 1.17 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 |  | 21.34 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  |  | SecondarySchool Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 189.1-2009 | Food Preparation | General | ASHRAE 189.1-2009Food PreparationGeneral | 1.08 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 15.48 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  |  | SecondarySchool Infil | 258.6 | 0.1 | 0.2 | 0.7 | SecondarySchool Kitchen Gas | 15.05 | 0.25 | 0.3 | 0.2 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 133 | 2325 | 0.05720430108 | 49 | 0.2 | 0.05 | SecondarySchool SWH | 0.7 | 4000 | 0.1215379059 | 0.338 | 694.5023 | 0.5 |  | SecondarySchool Kitchen Exhaust
189.1-2009 | SecondarySchool | Gym | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterExercise Area | 0.81 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 |  | 92.94 | SecondarySchool Gym Occ | SecondarySchool Activity | 0.0446 |  |  | SecondarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.007499177206 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
189.1-2009 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral | 0.45 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 9.31 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  |  | SecondarySchool Infil | [5 empty] | 0.27 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
189.1-2009 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 189.1-2009 | Classroom/Lecture/Training | General | ASHRAE 189.1-2009Classroom/Lecture/TrainingGeneral | 1.26 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 |  | 23.22 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  |  | SecondarySchool Infil | [5 empty] | 0.68 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 189.1-2009 | Dining Area | General | ASHRAE 189.1-2009Dining AreaGeneral | 0.81 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 66.84 | SecondarySchool Bldg Occ | SecondarySchool Activity | 0.0446 |  |  | SecondarySchool Infil | [5 empty] | 1.3 | 0 | 0.5 | 0 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 189.1-2009 | Audience/Seating Area | General | ASHRAE 189.1-2009Audience/Seating AreaGeneral | 0.81 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Auditorium | ASHRAE 62.1-1999EducationAuditorium | 0 | 15 |  | 92.94 | SecondarySchool Auditorium Occ | SecondarySchool Activity | 0.0446 |  |  | SecondarySchool Infil | [5 empty] | 0.34 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
90.1-2004 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 90.1-2004 | Audience/Seating Area | General | ASHRAE 90.1-2004Audience/Seating AreaGeneral | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Education | Auditorium | ASHRAE 62.1-1999EducationAuditorium | 0 | 15 |  | 150 | SchoolSecondary BLDG_OCC_SCH_Auditorium | SchoolSecondary ACTIVITY_SCH | 0.0595 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.46 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2004 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2004 | Dining Area | General | ASHRAE 90.1-2004Dining AreaGeneral | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 100 | SchoolSecondary BLDG_OCC_SCH_Cafeteria | SchoolSecondary ACTIVITY_SCH | 0.0595 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 7.15 | 0 | 0.5 | 0 | SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2004 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2004 | Classroom/Lecture/Training | General | ASHRAE 90.1-2004Classroom/Lecture/TrainingGeneral | 1.4 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 |  | 35 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0595 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.929 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2004 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral | 0.5 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0595 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2004 | SecondarySchool | Gym | 154_230_120 | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Playing Area | ASHRAE 90.1-2004Gymnasium/Exercise CenterPlaying Area | 1.4 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_GYM_SCH | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 |  | 30 | SchoolSecondary BLDG_OCC_SCH_Gym | SchoolSecondary ACTIVITY_SCH | 0.0595 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.46 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_SETBACK | 159.5 | 21269 | 0.007499177206 | 43.3 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH
90.1-2004 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2004 | Food Preparation | General | ASHRAE 90.1-2004Food PreparationGeneral | 1.2 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 15.23 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0595 |  |  | SchoolSecondary INFIL_SCH_PNNL | 532.1 | 0.1 | 0.2 | 0.7 | SchoolSecondary KITCHEN_GAS_EQUIP_SCH | 20.65 | 0.25 | 0.3 | 0.2 | SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_SETBACK | 133 | 2325 | 0.05720430108 | 49 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH | 0.7 | 4000 | 0.1215379059 | 0.338 | 694.5023 | 0.5 |  | SchoolSecondary Kitchen_Exhaust_SCH
90.1-2004 | SecondarySchool | Library | 230_196_120 | ASHRAE 90.1-2004 | Whole Building | Library | ASHRAE 90.1-2004Whole BuildingLibrary | 1.3 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 |  | 10 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0595 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.93 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2004 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2004 | Lobby | General | ASHRAE 90.1-2004LobbyGeneral | 1.3 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0595 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2004 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral | 1.5 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0595 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_Setback | SchoolSecondary CLGSETP_SCH_Setback
90.1-2004 | SecondarySchool | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5 | SchoolSecondary BLDG_OCC_SCH_Offices | SchoolSecondary ACTIVITY_SCH | 0.0595 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2004 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_BATH_SCH | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0595 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_Setback | SchoolSecondary CLGSETP_SCH_Setback | 52.2 | 2260 | 0.02309734513 | 43.3 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH | 0.28122 | 635.6646 | 0.04882618419 | 0.338 | 110.3676 | 0.5
90.1-2007 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 90.1-2007 | Audience/Seating Area | General | ASHRAE 90.1-2007Audience/Seating AreaGeneral | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Public Assembly Spaces | Auditorium seating area | ASHRAE 62.1-2004Public Assembly SpacesAuditorium seating area | 0.06 | 5 |  | 150 | SchoolSecondary BLDG_OCC_SCH_Auditorium | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.46 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2007 | Dining Area | General | ASHRAE 90.1-2007Dining AreaGeneral | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 100 | SchoolSecondary BLDG_OCC_SCH_Cafeteria | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 7.15 | 0 | 0.5 | 0 | SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2007 | Classroom/Lecture/Training | General | ASHRAE 90.1-2007Classroom/Lecture/TrainingGeneral | 1.4 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | ASHRAE 62.1-2004 | Educational Facilities | Classrooms (age 9 plus) | ASHRAE 62.1-2004Educational FacilitiesClassrooms (age 9 plus) | 0.12 | 10 |  | 35 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.929 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral | 0.5 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | SecondarySchool | Gym | 154_230_120 | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Playing Area | ASHRAE 90.1-2007Gymnasium/Exercise CenterPlaying Area | 1.4 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_GYM_SCH | ASHRAE 62.1-2004 | Sports and Entertainment | Gym, stadium (play area) | ASHRAE 62.1-2004Sports and EntertainmentGym, stadium (play area) | 0.3 |  |  | 30 | SchoolSecondary BLDG_OCC_SCH_Gym | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.46 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | 159.5 | 21269 | 0.007499177206 | 43.3 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH
90.1-2007 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2007 | Food Preparation | General | ASHRAE 90.1-2007Food PreparationGeneral | 1.2 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2004Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 15.23 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | 532.1 | 0.1 | 0.2 | 0.7 | SchoolSecondary KITCHEN_GAS_EQUIP_SCH | 20.65 | 0.25 | 0.3 | 0.2 | SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | 133 | 2325 | 0.05720430108 | 49 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH | 0.7 | 4000 | 0.1215379059 | 0.338 | 694.5023 | 0.5 |  | SchoolSecondary Kitchen_Exhaust_SCH
90.1-2007 | SecondarySchool | Library | 230_196_120 | ASHRAE 90.1-2007 | Whole Building | Library | ASHRAE 90.1-2007Whole BuildingLibrary | 1.3 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | ASHRAE 62.1-2004 | Educational Facilities | Media center | ASHRAE 62.1-2004Educational FacilitiesMedia center | 0.12 | 10 |  | 10 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.93 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2007 | Lobby | General | ASHRAE 90.1-2007LobbyGeneral | 1.3 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral | 1.5 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_Setback | SchoolSecondary CLGSETP_SCH_Setback
90.1-2007 | SecondarySchool | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 |  | 5 | SchoolSecondary BLDG_OCC_SCH_Offices | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_OPTIMUM
90.1-2007 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_BATH_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_Setback | SchoolSecondary CLGSETP_SCH_Setback | 52.2 | 2260 | 0.02309734513 | 43.3 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH | 0.28122 | 635.6646 | 0.04882618419 | 0.338 | 110.3676 | 0.5
90.1-2010 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 90.1-2010 | Audience/Seating Area | For Auditorium | ASHRAE 90.1-2010Audience/Seating AreaFor Auditorium | 0.79 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Public Assembly Spaces | Auditorium seating area | ASHRAE 62.1-2007Public Assembly SpacesAuditorium seating area | 0.06 | 5 |  | 150 | SchoolSecondary BLDG_OCC_SCH_Auditorium | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.46 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2010 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | General | ASHRAE 90.1-2010Dining AreaGeneral | 0.65 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 100 | SchoolSecondary BLDG_OCC_SCH_Cafeteria | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 7.15 | 0 | 0.5 | 0 | SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2010 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2010 | Classroom/Lecture/Training | General | ASHRAE 90.1-2010Classroom/Lecture/TrainingGeneral | 1.24 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (age 9 plus) | ASHRAE 62.1-2007Educational FacilitiesClassrooms (age 9 plus) | 0.12 | 10 |  | 35 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.929 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2010 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral | 0.66 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2010 | SecondarySchool | Gym | 154_230_120 | ASHRAE 90.1-2010 | Gymnasium/Fitness Center | Fitness Area | ASHRAE 90.1-2010Gymnasium/Fitness CenterFitness Area | 0.72 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_GYM_SCH | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) | ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | 0.3 |  |  | 30 | SchoolSecondary BLDG_OCC_SCH_Gym | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.46 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_SETBACK | 159.5 | 21269 | 0.007499177206 | 43.3 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH
90.1-2010 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral | 0.99 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 15.23 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | 532.1 | 0.1 | 0.2 | 0.7 | SchoolSecondary KITCHEN_GAS_EQUIP_SCH | 20.65 | 0.25 | 0.3 | 0.2 | SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_SETBACK | 133 | 2325 | 0.05720430108 | 49 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH | 0.7 | 4000 | 0.12154 | 0.338 | 694.5023 | 0.5 |  | SchoolSecondary Kitchen_Exhaust_SCH
90.1-2010 | SecondarySchool | Library | 230_196_120 | ASHRAE 90.1-2010 | Whole Building | Library | ASHRAE 90.1-2010Whole BuildingLibrary | 1.18 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | ASHRAE 62.1-2007 | Educational Facilities | Media center | ASHRAE 62.1-2007Educational FacilitiesMedia center | 0.12 | 10 |  | 10 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.93 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2010 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2010 | Lobby | General | ASHRAE 90.1-2010LobbyGeneral | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2010 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral | 0.95 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_Setback | SchoolSecondary CLGSETP_SCH_Setback
90.1-2010 | SecondarySchool | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 5 | SchoolSecondary BLDG_OCC_SCH_Offices | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2010 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2010 | Restrooms | General | ASHRAE 90.1-2010RestroomsGeneral | 0.98 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_BATH_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_Setback | SchoolSecondary CLGSETP_SCH_Setback | 52.2 | 2260 | 0.02309734513 | 43.3 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH | 0.28122 | 635.6646 | 0.048826 | 0.338 | 110.3676 | 0.5
DOE Ref 1980-2004 | SecondarySchool | Restroom | 169_169_31 | DOE Ref 1980-2004 | SecondarySchool | Restroom | DOE Ref 1980-2004SecondarySchoolRestroom | 0.89 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 9.29 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 52.2 | 2260 | 0.02309734513 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH | 0.28122 | 635.6646 | 0.04882618419 | 0.338 | 110.3676 | 0.5
DOE Ref 1980-2004 | SecondarySchool | Office | 120_230_199 | DOE Ref 1980-2004 | SecondarySchool | Office | DOE Ref 1980-2004SecondarySchoolOffice | 1.87 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 4.65 | SecondarySchool Office Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 1 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref 1980-2004 | SecondarySchool | Mechanical | 41_31_169 | DOE Ref 1980-2004 | SecondarySchool | Mechanical | DOE Ref 1980-2004SecondarySchoolMechanical | 0.75 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0.93 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
DOE Ref 1980-2004 | SecondarySchool | Lobby | 230_157_120 | DOE Ref 1980-2004 | SecondarySchool | Lobby | DOE Ref 1980-2004SecondarySchoolLobby | 1.11 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 0 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref 1980-2004 | SecondarySchool | Library | 230_196_120 | DOE Ref 1980-2004 | SecondarySchool | Library | DOE Ref 1980-2004SecondarySchoolLibrary | 1.52 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 |  | 21.34 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.93 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref 1980-2004 | SecondarySchool | Kitchen | 78_222_133 | DOE Ref 1980-2004 | SecondarySchool | Kitchen | DOE Ref 1980-2004SecondarySchoolKitchen | 1.56 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 15.48 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | 354.9 | 0.1 | 0.2 | 0.7 | SecondarySchool Kitchen Gas | 20.65 | 0.25 | 0.3 | 0.2 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 133 | 2325 | 0.05720430108 | 49 | 0.2 | 0.05 | SecondarySchool SWH | 0.7 | 4000 | 0.1215379059 | 0.338 | 694.5023 | 0.5 |  | SecondarySchool Kitchen Exhaust
DOE Ref 1980-2004 | SecondarySchool | Gym | 154_230_120 | DOE Ref 1980-2004 | SecondarySchool | Gym | DOE Ref 1980-2004SecondarySchoolGym | 1.06 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 |  | 92.94 | SecondarySchool Gym Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.007499177206 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
DOE Ref 1980-2004 | SecondarySchool | Gym - audience | 154_230_120 | DOE Ref 1980-2004 | SecondarySchool | Gym | DOE Ref 1980-2004SecondarySchoolGym | 1.06 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 |  | 27.9 | SecondarySchool Gym Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.007499177206 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
DOE Ref 1980-2004 | SecondarySchool | Corridor | 169_31_31 | DOE Ref 1980-2004 | SecondarySchool | Corridor | DOE Ref 1980-2004SecondarySchoolCorridor | 0.86 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 9.31 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
DOE Ref 1980-2004 | SecondarySchool | Classroom | 120_230_199 | DOE Ref 1980-2004 | SecondarySchool | Classroom | DOE Ref 1980-2004SecondarySchoolClassroom | 2 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 |  | 23.22 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.93 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref 1980-2004 | SecondarySchool | Cafeteria | 31_169_34 | DOE Ref 1980-2004 | SecondarySchool | Cafeteria | DOE Ref 1980-2004SecondarySchoolCafeteria | 1.34 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 66.84 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 1.79 | 0 | 0.5 | 0 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref 1980-2004 | SecondarySchool | Auditorium | 230_196_120 | DOE Ref 1980-2004 | SecondarySchool | Auditorium | DOE Ref 1980-2004SecondarySchoolAuditorium | 1.12 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Auditorium | ASHRAE 62.1-1999EducationAuditorium | 0 | 15 |  | 92.94 | SecondarySchool Auditorium Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref Pre-1980 | SecondarySchool | Restroom | 169_169_31 | DOE Ref Pre-1980 | SecondarySchool | Restroom | DOE Ref Pre-1980SecondarySchoolRestroom | 0.89 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 9.29 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 52.2 | 2260 | 0.02309734513 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH | 0.28122 | 635.6646 | 0.04882618419 | 0.338 | 110.3676 | 0.5
DOE Ref Pre-1980 | SecondarySchool | Office | 120_230_199 | DOE Ref Pre-1980 | SecondarySchool | Office | DOE Ref Pre-1980SecondarySchoolOffice | 1.87 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 4.65 | SecondarySchool Office Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 1 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref Pre-1980 | SecondarySchool | Mechanical | 41_31_169 | DOE Ref Pre-1980 | SecondarySchool | Mechanical | DOE Ref Pre-1980SecondarySchoolMechanical | 0.75 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0.93 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
DOE Ref Pre-1980 | SecondarySchool | Lobby | 230_157_120 | DOE Ref Pre-1980 | SecondarySchool | Lobby | DOE Ref Pre-1980SecondarySchoolLobby | 1.11 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 0 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref Pre-1980 | SecondarySchool | Library | 230_196_120 | DOE Ref Pre-1980 | SecondarySchool | Library | DOE Ref Pre-1980SecondarySchoolLibrary | 1.52 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 |  | 21.34 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.93 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref Pre-1980 | SecondarySchool | Kitchen | 78_222_133 | DOE Ref Pre-1980 | SecondarySchool | Kitchen | DOE Ref Pre-1980SecondarySchoolKitchen | 1.56 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 15.48 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | 354.9 | 0.1 | 0.2 | 0.7 | SecondarySchool Kitchen Gas | 20.65 | 0.25 | 0.3 | 0.2 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen | 133 | 2325 | 0.05720430108 | 49 | 0.2 | 0.05 | SecondarySchool SWH | 0.7 | 4000 | 0.1215379059 | 0.338 | 694.5023 | 0.5 |  | SecondarySchool Kitchen Exhaust
DOE Ref Pre-1980 | SecondarySchool | Gym | 154_230_120 | DOE Ref Pre-1980 | SecondarySchool | Gym | DOE Ref Pre-1980SecondarySchoolGym | 1.06 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 |  | 92.94 | SecondarySchool Gym Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.007499177206 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
DOE Ref Pre-1980 | SecondarySchool | Gym - audience | 154_230_120 | DOE Ref Pre-1980 | SecondarySchool | Gym | DOE Ref Pre-1980SecondarySchoolGym | 1.06 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 |  | 27.9 | SecondarySchool Gym Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp | 159.5 | 21269 | 0.007499177206 | 43.3 | 0.2 | 0.05 | SecondarySchool SWH Showers
DOE Ref Pre-1980 | SecondarySchool | Corridor | 169_31_31 | DOE Ref Pre-1980 | SecondarySchool | Corridor | DOE Ref Pre-1980SecondarySchoolCorridor | 0.86 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 9.31 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp BathCorrMechKitchen | SecondarySchool ClgSetp BathCorrMechKitchen
DOE Ref Pre-1980 | SecondarySchool | Classroom | 120_230_199 | DOE Ref Pre-1980 | SecondarySchool | Classroom | DOE Ref Pre-1980SecondarySchoolClassroom | 2 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 |  | 23.22 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.93 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref Pre-1980 | SecondarySchool | Cafeteria | 31_169_34 | DOE Ref Pre-1980 | SecondarySchool | Cafeteria | DOE Ref Pre-1980SecondarySchoolCafeteria | 1.34 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 66.84 | SecondarySchool Bldg Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 1.79 | 0 | 0.5 | 0 | SecondarySchool Kitchen Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
DOE Ref Pre-1980 | SecondarySchool | Auditorium | 230_196_120 | DOE Ref Pre-1980 | SecondarySchool | Auditorium | DOE Ref Pre-1980SecondarySchoolAuditorium | 1.12 |  |  |  | 0 | 0.37 | 0.2 | SecondarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Auditorium | ASHRAE 62.1-1999EducationAuditorium | 0 | 15 |  | 92.94 | SecondarySchool Auditorium Occ | SecondarySchool Activity |  | 0.2232 |  | SecondarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | SecondarySchool Bldg Equip | SecondarySchool HtgSetp | SecondarySchool ClgSetp
189.1-2009 | SmallHotel | Storage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral | 0.72 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 |  | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 |  |  | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel UnitHeater HtgSP Sch | SmallHotel UnitHeater ClgSP Sch
189.1-2009 | SmallHotel | Stair | 230_157_120 | ASHRAE 189.1-2009 | Stairs-Active | General | ASHRAE 189.1-2009Stairs-ActiveGeneral | 0.54 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 |  |  | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel UnitHeater HtgSP Sch | SmallHotel UnitHeater ClgSP Sch
189.1-2009 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral | 1.08 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 31.34 | SmallHotel StaffLounge Occ | SmallHotel Activity | 0.0446 |  |  | SmallHotel Infil Half On | [5 empty] | 3.67 | 0 | 0.5 | 0 | SmallHotel StaffLounge Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 189.1-2009 | Restrooms | General | ASHRAE 189.1-2009RestroomsGeneral | 0.81 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 2.85 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 |  |  | SmallHotel Infil Half On | [5 empty] | 0.51 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | [7 empty] | 1.1396 | 400 | 0.1978578326 | 0.338 | 69.4502 | 0.5
189.1-2009 | SmallHotel | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral | 0.99 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 7.14 | SmallHotel Office Occ | SmallHotel Activity | 0.0446 |  |  | SmallHotel Infil Half On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel Office Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | SmallHotel | Meeting | 230_196_120 | ASHRAE 189.1-2009 | Conference/Meeting/Multipurpose | General | ASHRAE 189.1-2009Conference/Meeting/MultipurposeGeneral | 1.17 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Meeting Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 |  | 50 | SmallHotel Meeting Occ | SmallHotel Activity | 0.0446 |  |  | SmallHotel Infil Half On | [5 empty] | 0.61 | 0 | 0.5 | 0 | SmallHotel Meeting Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 189.1-2009 | Electrical/Mechanical | General | ASHRAE 189.1-2009Electrical/MechanicalGeneral | 1.35 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 |  |  | SmallHotel Infil Half On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | SmallHotel | Laundry | 120_149_230 | ASHRAE 189.1-2009 | Hospital | Laundry-Washing | ASHRAE 189.1-2009HospitalLaundry-Washing | 0.54 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Laundry Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 |  | 10 | SmallHotel Laundry Occ | SmallHotel Activity | 0.0446 |  |  | SmallHotel Infil Half On | 42.6 |  |  |  | SmallHotel Laundry Gas | 1.04 | 0 | 0.5 | 0 | SmallHotel Laundry Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 67.5 | 1053 | 0.0641025641 | 60 | 0.2 | 0.05 | SmallHotel SWH Laundry
189.1-2009 | SmallHotel | GuestRoom | 78_167_222 | ASHRAE 189.1-2009 | Hotel/Motel | Guest Rooms | ASHRAE 189.1-2009Hotel/MotelGuest Rooms | 0.99 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Dormitory sleeping areas | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesDormitory sleeping areas | 0 | 15 |  | 3.97 | SmallHotel GuestRoom Occ | SmallHotel Activity | 0.0446 |  |  | SmallHotel Infil Half On | [5 empty] | 0.68 | 0 | 0.5 | 0 | SmallHotel GuestRoom Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 1.75 | 351 | 0.004985754986 | 43.3 | 0.2 | 0.05 | SmallHotel SWH GuestRoom
189.1-2009 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 189.1-2009 | Lounge/Recreation | General | ASHRAE 189.1-2009Lounge/RecreationGeneral | 1.08 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 30 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 |  |  | SmallHotel Infil Half On | [5 empty] | 0.73 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | SmallHotel | Exercise | 154_230_120 | ASHRAE 189.1-2009 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 189.1-2009Gymnasium/Exercise CenterExercise Area | 0.81 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Exercise Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 |  | 30 | SmallHotel Exercise Occ | SmallHotel Activity | 0.0446 |  |  | SmallHotel Infil Half On | [5 empty] | 0.55 | 0 | 0.5 | 0 | SmallHotel Exercise Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | SmallHotel | Elec/MechRoom | 41_31_171 |  |  |  |  | #N/A | [7 empty] | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 |  |  | 0.223 |  |  | SmallHotel Infil Half On | [5 empty] | 198.2 | 0 | 0.5 | 0 | SmallHotel BLDG ELEVATORS
189.1-2009 | SmallHotel | Corridor | 169_31_31 | ASHRAE 189.1-2009 | Corridor/Transition | General | ASHRAE 189.1-2009Corridor/TransitionGeneral | 0.45 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | SmallHotel Bldg Occ | SmallHotel Activity | 0.0446 |  |  | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
189.1-2009 | SmallHotel | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0 | [11 empty] | #N/A | #N/A | #N/A |  |  |  | 0.0751 |  |  | Always On
90.1-2004 | SmallHotel | Storage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral | 0.8 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.2016 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2004 | SmallHotel | Storage4Front | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral | 0.8 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0504 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2004 | SmallHotel | Storage4Rear | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral | 0.8 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Storage rooms | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsStorage rooms | 0.15 | 0 |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.1196 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2004 | SmallHotel | Stair | 230_157_120 | ASHRAE 90.1-2004 | Stairs-Active | General | ASHRAE 90.1-2004Stairs-ActiveGeneral | 0.6 |  |  |  | 0 | 0.7 | 0.2 | Always On | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.2016 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2004 | SmallHotel | Stair4 | 230_157_120 | ASHRAE 90.1-2004 | Stairs-Active | General | ASHRAE 90.1-2004Stairs-ActiveGeneral | 0.6 |  |  |  | 0 | 0.7 | 0.2 | Always On | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.1196 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2004 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 90.1-2004 | Lounge/Recreation | General | ASHRAE 90.1-2004Lounge/RecreationGeneral | 1.2 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 |  | 51.28 | HotelSmall EmployeeLounge_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 2 | 0 | 0.5 | 0 | HotelSmall EmployeeLounge_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2004 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 90.1-2004 | Restrooms | General | ASHRAE 90.1-2004RestroomsGeneral | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Always On | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 2.85 | HotelSmall Lobby_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [7 empty] | 1.1396 | 400 | 0.1978578326 | 0.338 | 69.4502 | 0.5 |  |  |  | No
90.1-2004 | SmallHotel | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 7.14 | HotelSmall Office_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 1.28 | 0 | 0.5 | 0 | HotelSmall OFF_EQUIP_SCH | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2004 | SmallHotel | Meeting | 230_196_120 | ASHRAE 90.1-2004 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2004Conference/Meeting/MultipurposeGeneral | 1.3 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 |  | 50 | HotelSmall MeetingRoom_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0.574 | 0 | 0.5 | 0 | HotelSmall MeetingRoom_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2004 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2004 | Electrical/Mechanical | General | ASHRAE 90.1-2004Electrical/MechanicalGeneral | 1.5 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_MECHROOM_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2004 | SmallHotel | Laundry | 120_149_230 | ASHRAE 90.1-2004 | Hospital | Laundry-Washing | ASHRAE 90.1-2004HospitalLaundry-Washing | 0.6 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_LAUNDRY_SCH | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 |  | 10 | HotelSmall LaundryRoom_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch | 129.9 | 0 | 0.2 | 0 | HotelSmall LaundryRoom_Eqp_Gas_Sch | 2.57 | 0 | 0.2 | 0 | HotelSmall LaundryRoom_Eqp_Elec_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | 123 | 1053 | 0.1168091168 | 82.2 | 0.2 | 0.05 | HotelSmall LaundryRoom_SHW_Sch | [9 empty] | No
90.1-2004 | SmallHotel | GuestRoom123Occ | 78_167_222 | ASHRAE 90.1-2004 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2004Hotel/MotelGuest Rooms | 1.1 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Bedrooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBedrooms | 0.1 | 0 |  | 4.27 | HotelSmall GuestRoom_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall GuestRoom_Eqp_Sch_Base | HotelSmall Base_OccGuestRoom_HtgSP_Sch | HotelSmall Base_OccGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall GuestRoom_SHW_Sch | [9 empty] | Yes
90.1-2004 | SmallHotel | GuestRoom4Occ | 78_167_222 | ASHRAE 90.1-2004 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2004Hotel/MotelGuest Rooms | 1.1 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Bedrooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBedrooms | 0.1 | 0 |  | 4.27 | HotelSmall GuestRoom_Occ_Sch | HotelSmall Activity_Sch | 0.0504 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall GuestRoom_Eqp_Sch_Base | HotelSmall Base_OccGuestRoom_HtgSP_Sch | HotelSmall Base_OccGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall GuestRoom_SHW_Sch | [9 empty] | Yes
90.1-2004 | SmallHotel | GuestRoom123Vac | 78_167_222 | ASHRAE 90.1-2004 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2004Hotel/MotelGuest Rooms | 1.1 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall AlwaysOff | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Bedrooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBedrooms | 0.1 | 0 |  | 4.27 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall VacGuestRoom_HtgSP_Sch | HotelSmall VacGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall AlwaysOff | [9 empty] | Yes
90.1-2004 | SmallHotel | GuestRoom4Vac | 78_167_222 | ASHRAE 90.1-2004 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2004Hotel/MotelGuest Rooms | 1.1 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall AlwaysOff | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Bedrooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesBedrooms | 0.1 | 0 |  | 4.27 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0504 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall VacGuestRoom_HtgSP_Sch | HotelSmall VacGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall AlwaysOff | [9 empty] | Yes
90.1-2004 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 90.1-2004 | Lounge/Recreation | General | ASHRAE 90.1-2004Lounge/RecreationGeneral | 1.2 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 30 | HotelSmall Lobby_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 2.42 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2004 | SmallHotel | Exercise | 154_230_120 | ASHRAE 90.1-2004 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 90.1-2004Gymnasium/Exercise CenterExercise Area | 0.9 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_EXERCENTER_SCH | ASHRAE 62.1-1999 | Sports and Amusement | Spectator areas | ASHRAE 62.1-1999Sports and AmusementSpectator areas | 0 | 15 |  | 19.94 | HotelSmall ExerciseCenter_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 1.73 | 0 | 0.5 | 0 | HotelSmall ExerciseCenter_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2004 | SmallHotel | Elec/MechRoom | 41_31_174 | DOE Ref 1980-2004 | SmallHotel | Elec/MechRoom | DOE Ref 1980-2004SmallHotelElec/MechRoom | 0 | [7 empty] | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 |  |  | 0.2016 |  |  | Always On | [5 empty] | 198.2 | 0 | 0.5 | 0 | HotelSmall BLDG_ELEVATORS | [18 empty] | No
90.1-2004 | SmallHotel | ElevatorCore | 41_31_174 | DOE Ref 1980-2004 | SmallHotel | ElevatorCore | DOE Ref 1980-2004SmallHotelElevatorCore | 0 | [7 empty] | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 |  |  | 0.2016 |  |  | Always On | [6 empty] | 0 | 0.5 | 0 | HotelSmall BLDG_ELEVATORS | [18 empty] | No
90.1-2004 | SmallHotel | ElevatorCore4 | 41_31_174 | DOE Ref 1980-2004 | SmallHotel | ElevatorCore | DOE Ref 1980-2004SmallHotelElevatorCore | 0 | [7 empty] | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 |  |  | 0.05042 |  |  | Always On | [6 empty] | 0 | 0.5 | 0 | HotelSmall BLDG_ELEVATORS | [18 empty] | No
90.1-2004 | SmallHotel | Corridor | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral | 0.5 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.2016 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2004 | SmallHotel | Corridor4 | 169_31_31 | ASHRAE 90.1-2004 | Corridor/Transition | General | ASHRAE 90.1-2004Corridor/TransitionGeneral | 0.5 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0258 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2007 | SmallHotel | Storage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral | 0.8 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.2016 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2007 | SmallHotel | Storage4Front | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral | 0.8 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0504 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2007 | SmallHotel | Storage4Rear | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral | 0.8 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.1196 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2007 | SmallHotel | Stair | 230_157_120 | ASHRAE 90.1-2007 | Stairs-Active | General | ASHRAE 90.1-2007Stairs-ActiveGeneral | 0.6 |  |  |  | 0 | 0.7 | 0.2 | Always On | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.2016 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2007 | SmallHotel | Stair4 | 230_157_120 | ASHRAE 90.1-2007 | Stairs-Active | General | ASHRAE 90.1-2007Stairs-ActiveGeneral | 0.6 |  |  |  | 0 | 0.7 | 0.2 | Always On | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.1196 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2007 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 90.1-2007 | Lounge/Recreation | General | ASHRAE 90.1-2007Lounge/RecreationGeneral | 1.2 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 |  | 51.28 | HotelSmall EmployeeLounge_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 2 | 0 | 0.5 | 0 | HotelSmall EmployeeLounge_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2007 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 90.1-2007 | Restrooms | General | ASHRAE 90.1-2007RestroomsGeneral | 0.9 |  |  |  | 0 | 0.7 | 0.2 | Always On | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 2.85 | HotelSmall Lobby_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [7 empty] | 1.1396 | 400 | 0.1978578326 | 0.338 | 69.4502 | 0.5 |  |  |  | No
90.1-2007 | SmallHotel | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Office Light | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 |  | 7.14 | HotelSmall Office_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 1.28 | 0 | 0.5 | 0 | HotelSmall OFF_EQUIP_SCH | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2007 | SmallHotel | Meeting | 230_196_120 | ASHRAE 90.1-2007 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2007Conference/Meeting/MultipurposeGeneral | 1.3 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | ASHRAE 62.1-2004 | General | Conference/meeting | ASHRAE 62.1-2004GeneralConference/meeting | 0.06 | 5 |  | 50 | HotelSmall MeetingRoom_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0.574 | 0 | 0.5 | 0 | HotelSmall MeetingRoom_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2007 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2007 | Electrical/Mechanical | General | ASHRAE 90.1-2007Electrical/MechanicalGeneral | 1.5 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_MECHROOM_SCH | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2007 | SmallHotel | Laundry | 120_149_230 | ASHRAE 90.1-2007 | Hospital | Laundry-Washing | ASHRAE 90.1-2007HospitalLaundry-Washing | 0.6 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_LAUNDRY_SCH | ASHRAE 62.1-2004 | Retail | Coinoperated laundries | ASHRAE 62.1-2004RetailCoinoperated laundries | 0.06 | 7.5 |  | 10 | HotelSmall LaundryRoom_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch | 129.9 | 0 | 0.2 | 0 | HotelSmall LaundryRoom_Eqp_Gas_Sch | 2.57 | 0 | 0.2 | 0 | HotelSmall LaundryRoom_Eqp_Elec_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | 123 | 1053 | 0.1168091168 | 82.2 | 0.2 | 0.05 | HotelSmall LaundryRoom_SHW_Sch | [9 empty] | No
90.1-2007 | SmallHotel | GuestRoom123Occ | 78_167_222 | ASHRAE 90.1-2007 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2007Hotel/MotelGuest Rooms | 1.1 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 4.27 | HotelSmall GuestRoom_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall GuestRoom_Eqp_Sch_Base | HotelSmall Base_OccGuestRoom_HtgSP_Sch | HotelSmall Base_OccGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall GuestRoom_SHW_Sch | [9 empty] | Yes
90.1-2007 | SmallHotel | GuestRoom4Occ | 78_167_222 | ASHRAE 90.1-2007 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2007Hotel/MotelGuest Rooms | 1.1 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 4.27 | HotelSmall GuestRoom_Occ_Sch | HotelSmall Activity_Sch | 0.0504 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall GuestRoom_Eqp_Sch_Base | HotelSmall Base_OccGuestRoom_HtgSP_Sch | HotelSmall Base_OccGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall GuestRoom_SHW_Sch | [9 empty] | Yes
90.1-2007 | SmallHotel | GuestRoom123Vac | 78_167_222 | ASHRAE 90.1-2007 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2007Hotel/MotelGuest Rooms | 1.1 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall AlwaysOff | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 4.27 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall VacGuestRoom_HtgSP_Sch | HotelSmall VacGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall AlwaysOff | [9 empty] | Yes
90.1-2007 | SmallHotel | GuestRoom4Vac | 78_167_222 | ASHRAE 90.1-2007 | Hotel/Motel | Guest Rooms | ASHRAE 90.1-2007Hotel/MotelGuest Rooms | 1.1 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall AlwaysOff | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 4.27 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0504 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall VacGuestRoom_HtgSP_Sch | HotelSmall VacGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall AlwaysOff | [9 empty] | Yes
90.1-2007 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 90.1-2007 | Lounge/Recreation | General | ASHRAE 90.1-2007Lounge/RecreationGeneral | 1.2 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | ASHRAE 62.1-2004 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2004Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 |  | 30 | HotelSmall Lobby_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 2.42 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2007 | SmallHotel | Exercise | 154_230_120 | ASHRAE 90.1-2007 | Gymnasium/Exercise Center | Exercise Area | ASHRAE 90.1-2007Gymnasium/Exercise CenterExercise Area | 0.9 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_EXERCENTER_SCH | ASHRAE 62.1-2004 | Sports and Entertainment | Health club/weight rooms | ASHRAE 62.1-2004Sports and EntertainmentHealth club/weight rooms | 0.06 | 20 |  | 19.94 | HotelSmall ExerciseCenter_Occ_Sch | HotelSmall Activity_Sch | 0.2016 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 1.73 | 0 | 0.5 | 0 | HotelSmall ExerciseCenter_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2007 | SmallHotel | Elec/MechRoom | 41_31_173 | DOE Ref 1980-2004 | SmallHotel | Elec/MechRoom | DOE Ref 1980-2004SmallHotelElec/MechRoom | 0 | [7 empty] | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 0 |  |  | 0.2016 |  |  | Always On | [5 empty] | 198.2 | 0 | 0.5 | 0 | HotelSmall BLDG_ELEVATORS | [18 empty] | No
90.1-2007 | SmallHotel | ElevatorCore | 41_31_173 | DOE Ref 1980-2004 | SmallHotel | ElevatorCore | DOE Ref 1980-2004SmallHotelElevatorCore | 0 | [7 empty] | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 0 |  |  | 0.2016 |  |  | Always On | [6 empty] | 0 | 0.5 | 0 | HotelSmall BLDG_ELEVATORS | [18 empty] | No
90.1-2007 | SmallHotel | ElevatorCore4 | 41_31_173 | DOE Ref 1980-2004 | SmallHotel | ElevatorCore | DOE Ref 1980-2004SmallHotelElevatorCore | 0 | [7 empty] | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 0 |  |  | 0.05042 |  |  | Always On | [6 empty] | 0 | 0.5 | 0 | HotelSmall BLDG_ELEVATORS | [18 empty] | No
90.1-2007 | SmallHotel | Corridor | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral | 0.5 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.2016 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2007 | SmallHotel | Corridor4 | 169_31_31 | ASHRAE 90.1-2007 | Corridor/Transition | General | ASHRAE 90.1-2007Corridor/TransitionGeneral | 0.5 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2004 | General | Corridors | ASHRAE 62.1-2004GeneralCorridors | 0.06 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0258 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2010 | SmallHotel | Storage | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.112 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2010 | SmallHotel | Storage4Front | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.028 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2010 | SmallHotel | Storage4Rear | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.06644 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2010 | SmallHotel | Stair | 230_157_120 | ASHRAE 90.1-2010 | Stairway | General | ASHRAE 90.1-2010StairwayGeneral | 0.69 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STAIR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.112 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2010 | SmallHotel | Stair4 | 230_157_120 | ASHRAE 90.1-2010 | Stairway | General | ASHRAE 90.1-2010StairwayGeneral | 0.69 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STAIR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0664 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2010 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 90.1-2010 | Lounge/Recreation | General | ASHRAE 90.1-2010Lounge/RecreationGeneral | 0.73 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 |  | 51.28 | HotelSmall EmployeeLounge_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 2 | 0 | 0.5 | 0 | HotelSmall EmployeeLounge_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2010 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 90.1-2010 | Restrooms | General | ASHRAE 90.1-2010RestroomsGeneral | 0.98 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_RESTROOM_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 2.85 | HotelSmall Lobby_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [7 empty] | 1.1396 | 400 | 0.19786 | 0.338 | 69.4502 | 0.5 |  |  |  | No
90.1-2010 | SmallHotel | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 7.14 | HotelSmall Office_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 1.28 | 0 | 0.5 | 0 | HotelSmall OFF_EQUIP_SCH | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2010 | SmallHotel | Meeting | 230_196_120 | ASHRAE 90.1-2010 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2010Conference/Meeting/MultipurposeGeneral | 1.23 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 |  | 50 | HotelSmall MeetingRoom_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0.574 | 0 | 0.5 | 0 | HotelSmall MeetingRoom_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2010 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2010 | Electrical/Mechanical | General | ASHRAE 90.1-2010Electrical/MechanicalGeneral | 0.95 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_MECHROOM_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2010 | SmallHotel | Laundry | 120_149_230 | ASHRAE 90.1-2010 | Hospital | Laundry-Washing | ASHRAE 90.1-2010HospitalLaundry-Washing | 0.6 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_LAUNDRY_SCH | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | ASHRAE 62.1-2007RetailCoinoperated laundries | 0.06 | 7.5 |  | 10 | HotelSmall LaundryRoom_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch | 129.9 | 0 | 0.2 | 0 | HotelSmall LaundryRoom_Eqp_Gas_Sch | 2.57 | 0 | 0.2 | 0 | HotelSmall LaundryRoom_Eqp_Elec_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | 123 | 1053 | 0.1168091168 | 82.2 | 0.2 | 0.05 | HotelSmall LaundryRoom_SHW_Sch | [9 empty] | No
90.1-2010 | SmallHotel | GuestRoom123Occ | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Highway Lodging | ASHRAE 90.1-2010Guest RoomFor Highway Lodging | 0.75 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2010 | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 4.27 | HotelSmall GuestRoom_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall GuestRoom_Eqp_Sch_Base | HotelSmall Adva_OccGuestRoom_HtgSP_Sch | HotelSmall Adva_OccGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall GuestRoom_SHW_Sch | [9 empty] | Yes
90.1-2010 | SmallHotel | GuestRoom4Occ | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Highway Lodging | ASHRAE 90.1-2010Guest RoomFor Highway Lodging | 0.75 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2010 | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 4.27 | HotelSmall GuestRoom_Occ_Sch | HotelSmall Activity_Sch | 0.028 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall GuestRoom_Eqp_Sch_Base | HotelSmall Adva_OccGuestRoom_HtgSP_Sch | HotelSmall Adva_OccGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall GuestRoom_SHW_Sch | [9 empty] | Yes
90.1-2010 | SmallHotel | GuestRoom123Vac | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Highway Lodging | ASHRAE 90.1-2010Guest RoomFor Highway Lodging | 0.75 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall AlwaysOff | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 4.27 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall VacGuestRoom_HtgSP_Sch | HotelSmall VacGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall AlwaysOff | [9 empty] | Yes
90.1-2010 | SmallHotel | GuestRoom4Vac | 78_167_222 | ASHRAE 90.1-2010 | Guest Room | For Highway Lodging | ASHRAE 90.1-2010Guest RoomFor Highway Lodging | 0.75 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall AlwaysOff | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 4.27 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.028 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall VacGuestRoom_HtgSP_Sch | HotelSmall VacGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall AlwaysOff | [9 empty] | Yes
90.1-2010 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 90.1-2010 | Lounge/Recreation | General | ASHRAE 90.1-2010Lounge/RecreationGeneral | 0.73 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 |  | 30 | HotelSmall Lobby_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 2.42 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2010 | SmallHotel | Exercise | 154_230_120 | ASHRAE 90.1-2010 | Gymnasium/Fitness Center | Fitness Area | ASHRAE 90.1-2010Gymnasium/Fitness CenterFitness Area | 0.72 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_EXERCENTER_SCH | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/weight rooms | ASHRAE 62.1-2007Sports and EntertainmentHealth club/weight rooms | 0.06 | 20 |  | 19.94 | HotelSmall ExerciseCenter_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 1.73 | 0 | 0.5 | 0 | HotelSmall ExerciseCenter_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2010 | SmallHotel | Elec/MechRoom | 41_31_175 | DOE Ref 1980-2004 | SmallHotel | Elec/MechRoom | DOE Ref 1980-2004SmallHotelElec/MechRoom | 0 | [7 empty] | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 |  |  | 0.112 |  |  | Always On | [5 empty] | 198.2 | 0 | 0.5 | 0 | HotelSmall BLDG_ELEVATORS | [18 empty] | No
90.1-2010 | SmallHotel | ElevatorCore | 41_31_175 | DOE Ref 1980-2004 | SmallHotel | ElevatorCore | DOE Ref 1980-2004SmallHotelElevatorCore | 0 | [7 empty] | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 |  |  | 0.112 |  |  | Always On | [6 empty] | 0 | 0.5 | 0 | HotelSmall BLDG_ELEVATORS | [18 empty] | No
90.1-2010 | SmallHotel | ElevatorCore4 | 41_31_175 | DOE Ref 1980-2004 | SmallHotel | ElevatorCore | DOE Ref 1980-2004SmallHotelElevatorCore | 0 | [7 empty] | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 |  |  | 0.02801 |  |  | Always On | [6 empty] | 0 | 0.5 | 0 | HotelSmall BLDG_ELEVATORS | [18 empty] | No
90.1-2010 | SmallHotel | Corridor | 169_31_31 | ASHRAE 90.1-2013 | Corridor | General | ASHRAE 90.1-2013CorridorGeneral | 0.66 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.112 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2010 | SmallHotel | Corridor4 | 169_31_31 | ASHRAE 90.1-2013 | Corridor | General | ASHRAE 90.1-2013CorridorGeneral | 0.66 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0143 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2013 | SmallHotel | Storage | 120_149_230 | ASHRAE 90.1-2013 | Storage | General | ASHRAE 90.1-2013StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.112 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2013 | SmallHotel | Storage4Front | 120_149_230 | ASHRAE 90.1-2013 | Storage | General | ASHRAE 90.1-2013StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.028 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2013 | SmallHotel | Storage4Rear | 120_149_230 | ASHRAE 90.1-2013 | Storage | General | ASHRAE 90.1-2013StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.06644 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2013 | SmallHotel | Stair | 230_157_120 | ASHRAE 90.1-2013 | Stairway | General | ASHRAE 90.1-2013StairwayGeneral | 0.69 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STAIR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.112 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2013 | SmallHotel | Stair4 | 230_157_120 | ASHRAE 90.1-2013 | Stairway | General | ASHRAE 90.1-2013StairwayGeneral | 0.69 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_STAIR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0664 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2013 | SmallHotel | StaffLounge | 31_169_34 | ASHRAE 90.1-2013 | Lounge/Recreation | General | ASHRAE 90.1-2013Lounge/RecreationGeneral | 0.73 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 |  | 51.28 | HotelSmall EmployeeLounge_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 2 | 0 | 0.5 | 0 | HotelSmall EmployeeLounge_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2013 | SmallHotel | PublicRestroom | 169_169_31 | ASHRAE 90.1-2013 | Restrooms | General | ASHRAE 90.1-2013RestroomsGeneral | 0.98 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_RESTROOM_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 2.85 | HotelSmall Lobby_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [7 empty] | 1.1396 | 400 | 0.19786 | 0.338 | 69.4502 | 0.5 |  |  |  | No
90.1-2013 | SmallHotel | Office | 120_230_199 | ASHRAE 90.1-2013 | Office-Enclosed | General | ASHRAE 90.1-2013Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 7.14 | HotelSmall Office_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 1.28 | 0 | 0.5 | 0 | HotelSmall OFF_EQUIP_SCH | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2013 | SmallHotel | Meeting | 230_196_120 | ASHRAE 90.1-2013 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2013Conference/Meeting/MultipurposeGeneral | 1.23 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 |  | 50 | HotelSmall MeetingRoom_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 0.574 | 0 | 0.5 | 0 | HotelSmall MeetingRoom_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2013 | SmallHotel | Mechanical | 41_31_169 | ASHRAE 90.1-2013 | Electrical/Mechanical | General | ASHRAE 90.1-2013Electrical/MechanicalGeneral | 0.42 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_MECHROOM_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | HotelSmall AlwaysOff | HotelSmall SemiHeated_HtgSP_Sch | SmallHotel UnitHeater ClgSP Sch | [16 empty] | No
90.1-2013 | SmallHotel | Laundry | 120_149_230 | ASHRAE 90.1-2013 | Laundry/Washing Area | General | ASHRAE 90.1-2013Laundry/Washing AreaGeneral | 0.6 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_LAUNDRY_SCH | ASHRAE 62.1-2007 | Retail | Coinoperated laundries | ASHRAE 62.1-2007RetailCoinoperated laundries | 0.06 | 7.5 |  | 10 | HotelSmall LaundryRoom_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch | 129.9 | 0 | 0.2 | 0 | HotelSmall LaundryRoom_Eqp_Gas_Sch | 2.57 | 0 | 0.2 | 0 | HotelSmall LaundryRoom_Eqp_Elec_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | 123 | 1053 | 0.1168091168 | 82.2 | 0.2 | 0.05 | HotelSmall LaundryRoom_SHW_Sch | [9 empty] | No
90.1-2013 | SmallHotel | GuestRoom123Occ | 78_167_222 | ASHRAE 90.1-2013 | Guest Room | For Hotel | ASHRAE 90.1-2013Guest RoomFor Hotel | 0.91 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2013 | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 4.27 | HotelSmall GuestRoom_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall GuestRoom_Eqp_Sch_Base | HotelSmall Adva_OccGuestRoom_HtgSP_Sch | HotelSmall Adva_OccGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall GuestRoom_SHW_Sch | [9 empty] | Yes
90.1-2013 | SmallHotel | GuestRoom4Occ | 78_167_222 | ASHRAE 90.1-2013 | Guest Room | For Hotel | ASHRAE 90.1-2013Guest RoomFor Hotel | 0.91 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2013 | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 4.27 | HotelSmall GuestRoom_Occ_Sch | HotelSmall Activity_Sch | 0.028 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall GuestRoom_Eqp_Sch_Base | HotelSmall Adva_OccGuestRoom_HtgSP_Sch | HotelSmall Adva_OccGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall GuestRoom_SHW_Sch | [9 empty] | Yes
90.1-2013 | SmallHotel | GuestRoom123Vac | 78_167_222 | ASHRAE 90.1-2013 | Guest Room | For Hotel | ASHRAE 90.1-2013Guest RoomFor Hotel | 0.91 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall AlwaysOff | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 4.27 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall VacGuestRoom_HtgSP_Sch | HotelSmall VacGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall AlwaysOff | [9 empty] | Yes
90.1-2013 | SmallHotel | GuestRoom4Vac | 78_167_222 | ASHRAE 90.1-2013 | Guest Room | For Hotel | ASHRAE 90.1-2013Guest RoomFor Hotel | 0.91 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall AlwaysOff | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Bedroom/living Room | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesBedroom/living Room | 0.06 | 5 |  | 4.27 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.028 |  |  | HotelSmall GuestRoom_Infil_Sch | [5 empty] | 1.1 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall VacGuestRoom_HtgSP_Sch | HotelSmall VacGuestRoom_ClgSP_Sch | 2.22 | 351 | 0.006324786325 | 60 | 0.2 | 0.05 | HotelSmall AlwaysOff | [9 empty] | Yes
90.1-2013 | SmallHotel | GuestLounge | 230_157_120 | ASHRAE 90.1-2013 | Lounge/Recreation | General | ASHRAE 90.1-2013Lounge/RecreationGeneral | 0.73 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 |  | 30 | HotelSmall Lobby_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 2.42 | 0 | 0.5 | 0 | HotelSmall Lobby_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2013 | SmallHotel | Exercise | 154_230_120 | ASHRAE 90.1-2013 | Gymnasium/Fitness Center | Fitness Area | ASHRAE 90.1-2013Gymnasium/Fitness CenterFitness Area | #N/A |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_EXERCENTER_SCH | ASHRAE 62.1-2007 | Sports and Entertainment | Health club/weight rooms | ASHRAE 62.1-2007Sports and EntertainmentHealth club/weight rooms | 0.06 | 20 |  | 19.94 | HotelSmall ExerciseCenter_Occ_Sch | HotelSmall Activity_Sch | 0.112 |  |  | HotelSmall CommonArea_Infil_Sch | [5 empty] | 1.73 | 0 | 0.5 | 0 | HotelSmall ExerciseCenter_Eqp_Sch | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2013 | SmallHotel | Elec/MechRoom | 41_31_175 | ASHRAE 90.1-2013 | Electrical/Mechanical | General | ASHRAE 90.1-2013Electrical/MechanicalGeneral | 0.42 | [7 empty] | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 |  |  | 0.112 |  |  | Always On | [5 empty] | 198.2 | 0 | 0.5 | 0 | HotelSmall BLDG_ELEVATORS | [18 empty] | No
90.1-2013 | SmallHotel | ElevatorCore | 41_31_175 | DOE Ref 1980-2004 | SmallHotel | ElevatorCore | DOE Ref 1980-2004SmallHotelElevatorCore | 0 | [7 empty] | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 |  |  | 0.112 |  |  | Always On | [6 empty] | 0 | 0.5 | 0 | HotelSmall BLDG_ELEVATORS | [18 empty] | No
90.1-2013 | SmallHotel | ElevatorCore4 | 41_31_175 | DOE Ref 1980-2004 | SmallHotel | ElevatorCore | DOE Ref 1980-2004SmallHotelElevatorCore | 0 | [7 empty] | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 |  |  | 0.02801 |  |  | Always On | [6 empty] | 0 | 0.5 | 0 | HotelSmall BLDG_ELEVATORS | [18 empty] | No
90.1-2013 | SmallHotel | Corridor | 169_31_31 | ASHRAE 90.1-2013 | Corridor | General | ASHRAE 90.1-2013CorridorGeneral | 0.66 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_CORRIDOR_SCH_2013 | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.112 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
90.1-2013 | SmallHotel | Corridor4 | 169_31_31 | ASHRAE 90.1-2013 | Corridor | General | ASHRAE 90.1-2013CorridorGeneral | 0.66 |  |  |  | 0 | 0.7 | 0.2 | HotelSmall BLDG_LIGHT_CORRIDOR_SCH_2013 | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | HotelSmall AlwaysOff | HotelSmall Activity_Sch | 0.0143 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | HotelSmall AlwaysOff | HotelSmall CommonArea_HtgSP_Sch | HotelSmall CommonArea_ClgSP_Sch | [16 empty] | No
DOE Ref 1980-2004 | SmallHotel | Storage | 120_149_230 | DOE Ref 1980-2004 | SmallHotel | Storage | DOE Ref 1980-2004SmallHotelStorage | 0.45 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel UnitHeater HtgSP Sch | SmallHotel UnitHeater ClgSP Sch
DOE Ref 1980-2004 | SmallHotel | Stair | 230_157_120 | DOE Ref 1980-2004 | SmallHotel | Stair | DOE Ref 1980-2004SmallHotelStair | 0.82 |  |  |  | 0 | 0.7 | 0.2 | Always On | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel UnitHeater HtgSP Sch | SmallHotel UnitHeater ClgSP Sch
DOE Ref 1980-2004 | SmallHotel | StaffLounge | 31_169_34 | DOE Ref 1980-2004 | SmallHotel | StaffLounge | DOE Ref 1980-2004SmallHotelStaffLounge | 1.65 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 31.34 | SmallHotel StaffLounge Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 7.17 | 0 | 0.5 | 0 | SmallHotel StaffLounge Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref 1980-2004 | SmallHotel | PublicRestroom | 169_169_31 | DOE Ref 1980-2004 | SmallHotel | PublicRestroom | DOE Ref 1980-2004SmallHotelPublicRestroom | 1.1 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 2.85 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 1 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | [7 empty] | 1.1396 | 400 | 0.1978578326 | 0.338 | 69.4502 | 0.5
DOE Ref 1980-2004 | SmallHotel | Office | 120_230_199 | DOE Ref 1980-2004 | SmallHotel | Office | DOE Ref 1980-2004SmallHotelOffice | 2.01 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 7.14 | SmallHotel Office Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 1.2 | 0 | 0.5 | 0 | SmallHotel Office Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref 1980-2004 | SmallHotel | Meeting | 230_196_120 | DOE Ref 1980-2004 | SmallHotel | Meeting | DOE Ref 1980-2004SmallHotelMeeting | 2.13 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Meeting Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 |  | 50 | SmallHotel Meeting Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 1.2 | 0 | 0.5 | 0 | SmallHotel Meeting Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref 1980-2004 | SmallHotel | Mechanical | 41_31_169 | DOE Ref 1980-2004 | SmallHotel | Mechanical | DOE Ref 1980-2004SmallHotelMechanical | 0.96 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref 1980-2004 | SmallHotel | Laundry | 120_149_230 | DOE Ref 1980-2004 | SmallHotel | Laundry | DOE Ref 1980-2004SmallHotelLaundry | 1.04 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Laundry Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 |  | 10 | SmallHotel Laundry Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | 58.4 | 0 | 0.2 | 0.5 | SmallHotel Laundry Gas | 2.03 | 0 | 0.5 | 0 | SmallHotel Laundry Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 67.5 | 1053 | 0.0641025641 | 60 | 0.2 | 0.05 | HotelSmall LaundryRoom_SHW_Sch
DOE Ref 1980-2004 | SmallHotel | GuestRoom | 78_167_222 | DOE Ref 1980-2004 | SmallHotel | GuestRoom | DOE Ref 1980-2004SmallHotelGuestRoom | 1.74 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Living rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLiving rooms | 0.085 | 0 |  | 3.97 | SmallHotel GuestRoom Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 1.33 | 0 | 0.5 | 0 | SmallHotel GuestRoom Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 1.75 | 351 | 0.004985754986 | 43.3 | 0.2 | 0.05 | HotelSmall GuestRoom_SHW_Sch
DOE Ref 1980-2004 | SmallHotel | GuestLounge | 230_157_120 | DOE Ref 1980-2004 | SmallHotel | GuestLounge | DOE Ref 1980-2004SmallHotelGuestLounge | 1.31 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 30 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 1.43 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref 1980-2004 | SmallHotel | Exercise | 154_230_120 | DOE Ref 1980-2004 | SmallHotel | Exercise | DOE Ref 1980-2004SmallHotelExercise | 1.37 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Exercise Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 |  | 31.33 | SmallHotel Exercise Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 1.07 | 0 | 0.5 | 0 | SmallHotel Exercise Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref 1980-2004 | SmallHotel | Elec/MechRoom | 41_31_169 | DOE Ref 1980-2004 | SmallHotel | Elec/MechRoom | DOE Ref 1980-2004SmallHotelElec/MechRoom | 0 | [7 empty] | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 |  |  |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 198.2 | 0 | 0.5 | 0 | SmallHotel BLDG ELEVATORS
DOE Ref 1980-2004 | SmallHotel | ElevatorCore | 41_31_169 | DOE Ref 1980-2004 | SmallHotel | ElevatorCore | DOE Ref 1980-2004SmallHotelElevatorCore | 0 | [7 empty] | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 |  |  |  | 0.2232 |  | SmallHotel Infil Half On | [6 empty] | 0 | 0.5 | 0 | SmallHotel BLDG ELEVATORS
DOE Ref 1980-2004 | SmallHotel | Corridor | 169_31_31 | DOE Ref 1980-2004 | SmallHotel | Corridor | DOE Ref 1980-2004SmallHotelCorridor | 0.86 |  |  |  | 0 | 0.7 | 0.2 | Always On | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref 1980-2004 | SmallHotel | Attic | 120_149_230 | DOE Ref 1980-2004 | SmallHotel | Attic | DOE Ref 1980-2004SmallHotelAttic | 0 | [18 empty] | 0.2232 |  | Always On
DOE Ref Pre-1980 | SmallHotel | Storage | 120_149_230 | DOE Ref Pre-1980 | SmallHotel | Storage | DOE Ref Pre-1980SmallHotelStorage | 0.45 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Storage Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel UnitHeater HtgSP Sch | SmallHotel UnitHeater ClgSP Sch
DOE Ref Pre-1980 | SmallHotel | Stair | 230_157_120 | DOE Ref Pre-1980 | SmallHotel | Stair | DOE Ref Pre-1980SmallHotelStair | 0.82 |  |  |  | 0 | 0.7 | 0.2 | Always On | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel UnitHeater HtgSP Sch | SmallHotel UnitHeater ClgSP Sch
DOE Ref Pre-1980 | SmallHotel | StaffLounge | 31_169_34 | DOE Ref Pre-1980 | SmallHotel | StaffLounge | DOE Ref Pre-1980SmallHotelStaffLounge | 1.65 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 31.34 | SmallHotel StaffLounge Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 7.17 | 0 | 0.5 | 0 | SmallHotel StaffLounge Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | SmallHotel | PublicRestroom | 169_169_31 | DOE Ref Pre-1980 | SmallHotel | PublicRestroom | DOE Ref Pre-1980SmallHotelPublicRestroom | 1.1 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 2.85 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 1 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | [7 empty] | 1.1396 | 400 | 0.1978578326 | 0.338 | 69.4502 | 0.5
DOE Ref Pre-1980 | SmallHotel | Office | 120_230_199 | DOE Ref Pre-1980 | SmallHotel | Office | DOE Ref Pre-1980SmallHotelOffice | 2.01 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Office Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 7.14 | SmallHotel Office Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 1.2 | 0 | 0.5 | 0 | SmallHotel Office Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | SmallHotel | Meeting | 230_196_120 | DOE Ref Pre-1980 | SmallHotel | Meeting | DOE Ref Pre-1980SmallHotelMeeting | 2.13 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Meeting Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Conference rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesConference rooms | 0 | 20 |  | 50 | SmallHotel Meeting Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 1.2 | 0 | 0.5 | 0 | SmallHotel Meeting Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | SmallHotel | Mechanical | 41_31_169 | DOE Ref Pre-1980 | SmallHotel | Mechanical | DOE Ref Pre-1980SmallHotelMechanical | 0.96 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On |  | 0 | 0.2 | 0.5 |  | 0 | 0 | 0.2 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | SmallHotel | Laundry | 120_149_230 | DOE Ref Pre-1980 | SmallHotel | Laundry | DOE Ref Pre-1980SmallHotelLaundry | 1.04 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Laundry Light | ASHRAE 62.1-1999 | Dry Cleaners, Laundries | Commercial Laundry | ASHRAE 62.1-1999Dry Cleaners, LaundriesCommercial Laundry | 0 | 25 |  | 10 | SmallHotel Laundry Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | 58.4 | 0 | 0.2 | 0.5 | SmallHotel Laundry Gas | 2.03 | 0 | 0.5 | 0 | SmallHotel Laundry Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 67.5 | 1053 | 0.0641025641 | 60 | 0.2 | 0.05 | HotelSmall LaundryRoom_SHW_Sch
DOE Ref Pre-1980 | SmallHotel | GuestRoom | 78_167_222 | DOE Ref Pre-1980 | SmallHotel | GuestRoom | DOE Ref Pre-1980SmallHotelGuestRoom | 1.74 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel GuestRoom Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Living rooms | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLiving rooms | 0.085 | 0 |  | 3.97 | SmallHotel GuestRoom Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 1.33 | 0 | 0.5 | 0 | SmallHotel GuestRoom Equip | SmallHotel HtgSetp | SmallHotel ClgSetp | 1.75 | 351 | 0.004985754986 | 43.3 | 0.2 | 0.05 | HotelSmall GuestRoom_SHW_Sch
DOE Ref Pre-1980 | SmallHotel | GuestLounge | 230_157_120 | DOE Ref Pre-1980 | SmallHotel | GuestLounge | DOE Ref Pre-1980SmallHotelGuestLounge | 1.31 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel StaffLounge Light | ASHRAE 62.1-1999 | Hotels, Motels, Resorts, Dormitories | Lobbies | ASHRAE 62.1-1999Hotels, Motels, Resorts, DormitoriesLobbies | 0 | 15 |  | 30 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 1.43 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | SmallHotel | Exercise | 154_230_120 | DOE Ref Pre-1980 | SmallHotel | Exercise | DOE Ref Pre-1980SmallHotelExercise | 1.37 |  |  |  | 0 | 0.7 | 0.2 | SmallHotel Exercise Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 |  | 31.33 | SmallHotel Exercise Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 1.07 | 0 | 0.5 | 0 | SmallHotel Exercise Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | SmallHotel | Elec/MechRoom | 41_31_172 | DOE Ref Pre-1980 | SmallHotel | Elec/MechRoom | DOE Ref Pre-1980SmallHotelElec/MechRoom | 0 | [7 empty] | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 |  |  |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 198.2 | 0 | 0.5 | 0 | SmallHotel BLDG ELEVATORS
DOE Ref Pre-1980 | SmallHotel | ElevatorCore | 41_31_172 | DOE Ref Pre-1980 | SmallHotel | ElevatorCore | DOE Ref Pre-1980SmallHotelElevatorCore | 0 | [7 empty] | ASHRAE 62.1-1999 | Public Spaces | Public restrooms | ASHRAE 62.1-1999Public SpacesPublic restrooms | 0 | 0 |  | 0 |  |  |  | 0.2232 |  | SmallHotel Infil Half On | [6 empty] | 0 | 0.5 | 0 | SmallHotel BLDG ELEVATORS
DOE Ref Pre-1980 | SmallHotel | Corridor | 169_31_31 | DOE Ref Pre-1980 | SmallHotel | Corridor | DOE Ref Pre-1980SmallHotelCorridor | 0.86 |  |  |  | 0 | 0.7 | 0.2 | Always On | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0 | SmallHotel Bldg Occ | SmallHotel Activity |  | 0.2232 |  | SmallHotel Infil Half On | [5 empty] | 0 | 0 | 0.5 | 0 | SmallHotel Bldg Equip | SmallHotel HtgSetp | SmallHotel ClgSetp
DOE Ref Pre-1980 | SmallHotel | Attic | 120_149_230 | DOE Ref 1980-2004 | SmallHotel | Attic | DOE Ref 1980-2004SmallHotelAttic | 0 | [18 empty] | 0.2232 |  | Always On
189.1-2009 | StripMall | WholeBuilding | 171_222_78 | ASHRAE 189.1-2009 | Whole Building | Retail | ASHRAE 189.1-2009Whole BuildingRetail | 1.35 |  |  |  | 0 | 0.7 | 0.2 | StripMall Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | StripMall Bldg Occ | StripMall Activity | 0.0446 |  |  | StripMall Infil Half On | [5 empty] | 0.29 | 0 | 0.5 | 0 | StripMall Bldg Equip | StripMall HtgSetp | StripMall ClgSetp
90.1-2013 | QuickServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2013 | Food Preparation | General | ASHRAE 90.1-2013Food PreparationGeneral | 1.21 |  |  |  | 0 | 0.7 | 0.2 | RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2010_2013 | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 5 | RestaurantFastFood BLDG_OCC_SCH | RestaurantFastFood ACTIVITY_SCH |  | 0.112 |  | RestaurantFastFood INFIL_SCH_PNNL | 250.86 | 0.1 | 0.2 | 0.7 | RestaurantFastFood FF_GAS_EQUIP_SCH | 25.166 | 0.25 | 0.3 | 0.3 | RestaurantFastFood BLDG_EQUIP_SCH | RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | 40 | 1250 | 0.032 | 49 | 0.2 | 0.05 | RestaurantFastFood BLDG_SWH_SCH | 0.7 | 3300 | 0.12212 | 0.338 | 575.7279 | 0.50241 |  | RestaurantFastFood Hours_of_operation
90.1-2013 | QuickServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2013 | Dining Area | For Family Dining | ASHRAE 90.1-2013Dining AreaFor Family Dining | 0.89 |  |  |  | 0 | 0.37 | 0.2 | RestaurantFastFood BLDG_LIGHT_DINING_SCH_2013 | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 70 | RestaurantFastFood BLDG_OCC_SCH | RestaurantFastFood ACTIVITY_SCH |  | 0.112 |  | RestaurantFastFood INFIL_SCH_PNNL | [5 empty] | 10.85 | 0.25 | 0.3 | 0 | RestaurantFastFood BLDG_EQUIP_SCH | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | QuickServiceRestaurant | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0
90.1-2013 | StripMall | Strip mall - type 1 | 171_222_78 | ASHRAE 90.1-2013 | Whole Building | Retail | ASHRAE 90.1-2013Whole BuildingRetail | 1.26 |  |  | 0.38346 | 0 | 0.7 | 0.2 | RetailStripmall Type1_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales combined by area | ASHRAE 62.1-2007RetailGeneral Sales combined by area | 0.2325 | 0 |  | 8 | RetailStripmall Type1_OCC_SCH | HotelSmall Activity_Sch | 0.049538 |  |  | RetailStripmall Type1_Infil_SCH | [5 empty] | 0.4 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | 1.8 | [5 empty] | RetailStripmall Type1_SWH_SCH
90.1-2013 | StripMall | Strip mall - type 2 | 171_222_78 | ASHRAE 90.1-2013 | Whole Building | Retail | ASHRAE 90.1-2013Whole BuildingRetail | 1.26 |  |  | 0.18346 | 0 | 0.7 | 0.2 | RetailStripmall Type2_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales combined by area | ASHRAE 62.1-2007RetailGeneral Sales combined by area | 0.2325 | 0 |  | 8 | RetailStripmall Type2_OCC_SCH | HotelSmall Activity_Sch | 0.034933 |  |  | RetailStripmall Type2_Infil_SCH | [5 empty] | 0.4 | 0 | 0.5 | 0 | RetailStripmall Type2_EQUIP_SCH | RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | 1.8 | [5 empty] | RetailStripmall Type2_SWH_SCH
90.1-2013 | StripMall | Strip mall - type 3 | 171_222_78 | ASHRAE 90.1-2013 | Whole Building | Retail | ASHRAE 90.1-2013Whole BuildingRetail | 1.26 |  |  | 0.0336 | 0 | 0.7 | 0.2 | RetailStripmall Type3_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales combined by area | ASHRAE 62.1-2007RetailGeneral Sales combined by area | 0.2325 | 0 |  | 8 | RetailStripmall Type3_OCC_SCH | HotelSmall Activity_Sch | 0.034933 |  |  | RetailStripmall Type3_Infil_SCH | [5 empty] | 0.4 | 0 | 0.5 | 0 | RetailStripmall Type3_EQUIP_SCH | RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | 1.8 | [5 empty] | RetailStripmall Type3_SWH_SCH
90.1-2010 | StripMall | Strip mall - type 1 | 171_222_78 | ASHRAE 90.1-2010 | Whole Building | Retail | ASHRAE 90.1-2010Whole BuildingRetail | 1.4 |  |  | 0.42 | 0 | 0.7 | 0.2 | RetailStripmall Type1_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales combined by area | ASHRAE 62.1-2007RetailGeneral Sales combined by area | 0.2325 | 0 |  | 8 | RetailStripmall Type1_OCC_SCH | HotelSmall Activity_Sch | 0.049538 |  |  | RetailStripmall Type1_Infil_SCH | [5 empty] | 0.4 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | 1.8 | [5 empty] | RetailStripmall Type1_SWH_SCH
90.1-2010 | StripMall | Strip mall - type 2 | 171_222_78 | ASHRAE 90.1-2010 | Whole Building | Retail | ASHRAE 90.1-2010Whole BuildingRetail | 1.4 |  |  | 0.22 | 0 | 0.7 | 0.2 | RetailStripmall Type2_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales combined by area | ASHRAE 62.1-2007RetailGeneral Sales combined by area | 0.2325 | 0 |  | 8 | RetailStripmall Type2_OCC_SCH | HotelSmall Activity_Sch | 0.034933 |  |  | RetailStripmall Type2_Infil_SCH | [5 empty] | 0.4 | 0 | 0.5 | 0 | RetailStripmall Type2_EQUIP_SCH | RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type2_CLGSETP_SCH_NO_SETBACK | 1.8 | [5 empty] | RetailStripmall Type2_SWH_SCH
90.1-2010 | StripMall | Strip mall - type 3 | 171_222_78 | ASHRAE 90.1-2010 | Whole Building | Retail | ASHRAE 90.1-2010Whole BuildingRetail | 1.4 |  |  | 0.07 | 0 | 0.7 | 0.2 | RetailStripmall Type3_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales combined by area | ASHRAE 62.1-2007RetailGeneral Sales combined by area | 0.2325 | 0 |  | 8 | RetailStripmall Type3_OCC_SCH | HotelSmall Activity_Sch | 0.034933 |  |  | RetailStripmall Type3_Infil_SCH | [5 empty] | 0.4 | 0 | 0.5 | 0 | RetailStripmall Type3_EQUIP_SCH | RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type3_CLGSETP_SCH_NO_SETBACK | 1.8 | [5 empty] | RetailStripmall Type3_SWH_SCH
90.1-2007 | StripMall | Strip mall - type 1 | 171_222_78 | ASHRAE 90.1-2007 | Whole Building | Retail | ASHRAE 90.1-2007Whole BuildingRetail | 1.5 |  |  | 0.72 | 0 | 0.7 | 0.2 | RetailStripmall Type1_LIGHT_SCH | ASHRAE 62.1-2004 | Retail | General Sales combined by area | ASHRAE 62.1-2004RetailGeneral Sales combined by area | 0.2325 | 0 |  | 8 | RetailStripmall Type1_OCC_SCH | HotelSmall Activity_Sch | 0.089168 |  |  | RetailStripmall Type1_Infil_SCH | [5 empty] | 0.4 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | 1.8 | [5 empty] | RetailStripmall Type1_SWH_SCH
189.1-2009 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area | 1.53 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 |  | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | [5 empty] | 0.36 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
189.1-2009 | SuperMarket | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral | 0.99 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
189.1-2009 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 189.1-2009 | Active Storage | General | ASHRAE 189.1-2009Active StorageGeneral | 0.72 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 |  | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
189.1-2009 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 189.1-2009 | Retail (not including accent lighting) | Sales Area | ASHRAE 189.1-2009Retail (not including accent lighting)Sales Area | 1.53 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 |  | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | 6.25 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 3.64 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.00214178625 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.215339442 | 0.338 | 520.8767 | 0.5 |  | SuperMarket_Deli_Exhaust
90.1-2004 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area | 1.7 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 |  | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 |  |  | SuperMarket Infil Half On | [5 empty] | 0.5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2004 | SuperMarket | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 |  |  | SuperMarket Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2004 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 90.1-2004 | Active Storage | General | ASHRAE 90.1-2004Active StorageGeneral | 0.8 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 |  | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 |  |  | SuperMarket Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2004 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 90.1-2004 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2004Retail (not including accent lighting)Sales Area | 1.7 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 |  | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0595 |  |  | SuperMarket Infil Half On | 8.53 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.00214178625 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.215339442 | 0.338 | 520.8767 | 0.5 |  | SuperMarket_Deli_Exhaust
90.1-2007 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area | 1.7 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2004 | Retail | Supermarket | ASHRAE 62.1-2004RetailSupermarket | 0.06 | 7.5 |  | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | [5 empty] | 0.36 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2007 | SuperMarket | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 |  | 5 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2007 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 90.1-2007 | Active Storage | General | ASHRAE 90.1-2007Active StorageGeneral | 0.8 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2004 | General | Storage rooms | ASHRAE 62.1-2004GeneralStorage rooms | 0.12 |  |  | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2007 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 90.1-2007 | Retail (not including accent lighting) | Sales Area | ASHRAE 90.1-2007Retail (not including accent lighting)Sales Area | 1.7 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2004 | Retail | Supermarket | ASHRAE 62.1-2004RetailSupermarket | 0.06 | 7.5 |  | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | 6.25 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 3.64 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.00214178625 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.215339442 | 0.338 | 520.8767 | 0.5 |  | SuperMarket_Deli_Exhaust
90.1-2010 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 90.1-2010 | Sales Area | General | ASHRAE 90.1-2010Sales AreaGeneral | 1.68 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | Retail | Supermarket | ASHRAE 62.1-2007RetailSupermarket | 0.06 | 7.5 |  | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | [5 empty] | 0.36 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2010 | SuperMarket | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 5 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2010 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 90.1-2010 | Storage | General | ASHRAE 90.1-2010StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2010 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 90.1-2010 | Sales Area | General | ASHRAE 90.1-2010Sales AreaGeneral | 1.68 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | Retail | Supermarket | ASHRAE 62.1-2007RetailSupermarket | 0.06 | 7.5 |  | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | 6.25 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 3.64 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.00214178625 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.21534 | 0.338 | 520.8767 | 0.5 |  | SuperMarket_Deli_Exhaust
DOE Ref 1980-2004 | SuperMarket | Sales/Produce | 230_196_120 | DOE Ref 1980-2004 | SuperMarket | Sales/Produce | DOE Ref 1980-2004SuperMarketSales/Produce | 2.78 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 |  | 8 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 |  | SuperMarket Infil Half On | [5 empty] | 0.5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
DOE Ref 1980-2004 | SuperMarket | Office | 120_230_199 | DOE Ref 1980-2004 | SuperMarket | Office | DOE Ref 1980-2004SuperMarketOffice | 1.98 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 |  | SuperMarket Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
DOE Ref 1980-2004 | SuperMarket | DryStorage | 120_149_230 | DOE Ref 1980-2004 | SuperMarket | DryStorage | DOE Ref 1980-2004SuperMarketDryStorage | 1.1 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 |  | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 |  | SuperMarket Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
DOE Ref 1980-2004 | SuperMarket | Deli/Bakery | 31_169_34 | DOE Ref 1980-2004 | SuperMarket | Deli/Bakery | DOE Ref 1980-2004SuperMarketDeli/Bakery | 2.78 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 |  | 8 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 |  | SuperMarket Infil Half On | 8.53 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.00214178625 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.215339442 | 0.338 | 520.8767 | 0.5 |  | SuperMarket_Deli_Exhaust
DOE Ref Pre-1980 | SuperMarket | Sales/Produce | 230_196_120 | DOE Ref Pre-1980 | SuperMarket | Sales/Produce | DOE Ref Pre-1980SuperMarketSales/Produce | 5.04 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 |  | 8 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 |  | SuperMarket Infil Half On | [5 empty] | 0.5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
DOE Ref Pre-1980 | SuperMarket | Office | 120_230_199 | DOE Ref Pre-1980 | SuperMarket | Office | DOE Ref Pre-1980SuperMarketOffice | 2.9 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 5 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 |  | SuperMarket Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
DOE Ref Pre-1980 | SuperMarket | DryStorage | 120_149_230 | DOE Ref Pre-1980 | SuperMarket | DryStorage | DOE Ref Pre-1980SuperMarketDryStorage | 0.77 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Shipping and receiving | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsShipping and receiving | 0.15 | 0 |  | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 |  | SuperMarket Infil Half On | [5 empty] | 0.75 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
DOE Ref Pre-1980 | SuperMarket | Deli/Bakery | 31_169_34 | DOE Ref Pre-1980 | SuperMarket | Deli/Bakery | DOE Ref Pre-1980SuperMarketDeli/Bakery | 5.04 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-1999 | Specialty Shops | Supermarket | ASHRAE 62.1-1999Specialty ShopsSupermarket | 0 | 15 |  | 8 | SuperMarket Bldg Occ | SuperMarket Activity |  | 0.2232 |  | SuperMarket Infil Half On | 8.53 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 5 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.00214178625 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.215339442 | 0.338 | 520.8767 | 0.5 |  | SuperMarket_Deli_Exhaust
189.1-2009 | Warehouse | Office | 120_230_199 | ASHRAE 189.1-2009 | Office-Enclosed | General | ASHRAE 189.1-2009Office-EnclosedGeneral | 0.99 |  |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 1.96 | Warehouse Bldg Occ | Warehouse Activity | 0.0446 |  |  | Always On | [5 empty] | 0.54 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp | Warehouse ClgSetp
189.1-2009 | Warehouse | Fine | 120_149_230 | ASHRAE 189.1-2009 | Warehouse | Fine Material Storage | ASHRAE 189.1-2009WarehouseFine Material Storage | 1.26 |  |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 |  | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0446 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp FineStorage | Warehouse ClgSetp FineStorage
189.1-2009 | Warehouse | Bulk | 41_31_169 | ASHRAE 189.1-2009 | Warehouse | Medium/Bulky Material Storage | ASHRAE 189.1-2009WarehouseMedium/Bulky Material Storage | 0.81 |  |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 |  | 0 | Warehouse Bldg Occ | Warehouse Activity | 0.0446 |  |  | Always On | [5 empty] | 0.17 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp BulkStorage | Warehouse ClgSetp
90.1-2004 | Warehouse | Office | 120_230_199 | ASHRAE 90.1-2004 | Office-Enclosed | General | ASHRAE 90.1-2004Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 1.96 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0595 |  |  | Warehouse ALWAYS_ON | [5 empty] | 0.75 | 0 | 0.5 | 0 | Warehouse Office_Plug_SCH | Warehouse HtgSetp | Warehouse ClgSetp
90.1-2004 | Warehouse | Fine | 120_149_230 | ASHRAE 90.1-2004 | Warehouse | Fine Material Storage | ASHRAE 90.1-2004WarehouseFine Material Storage | 1.4 |  |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 |  | 0 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0595 |  |  | Warehouse ALWAYS_ON | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse ALWAYS_OFF | Warehouse Fine Storage Heating Setpoint Schedule | Warehouse Fine Storage Cooling Setpoint Schedule
90.1-2004 | Warehouse | Bulk | 41_31_169 | ASHRAE 90.1-2004 | Warehouse | Medium/Bulky Material Storage | ASHRAE 90.1-2004WarehouseMedium/Bulky Material Storage | 0.9 |  |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 |  | 0 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0595 |  |  | Warehouse ALWAYS_ON | [5 empty] | 0.25 | 0 | 0.5 | 0 | Warehouse ALWAYS_OFF | Warehouse Bulk Storage Heating Setpoint Schedule | Warehouse ClgSetp
90.1-2007 | Warehouse | Office | 120_230_199 | ASHRAE 90.1-2007 | Office-Enclosed | General | ASHRAE 90.1-2007Office-EnclosedGeneral | 1.1 |  |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2004 | Office Buildings | Office space | ASHRAE 62.1-2004Office BuildingsOffice space | 0.06 | 5 |  | 1.96 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0446 |  |  | Warehouse ALWAYS_ON | [5 empty] | 0.54 | 0 | 0.5 | 0 | Warehouse Office_Plug_SCH | Warehouse HtgSetp | Warehouse ClgSetp
90.1-2007 | Warehouse | Fine | 120_149_230 | ASHRAE 90.1-2007 | Warehouse | Fine Material Storage | ASHRAE 90.1-2007WarehouseFine Material Storage | 1.4 |  |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2004 | Miscellaneous Spaces | Warehouses | ASHRAE 62.1-2004Miscellaneous SpacesWarehouses | 0.06 |  |  | 0 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0446 |  |  | Warehouse ALWAYS_ON | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse ALWAYS_OFF | Warehouse Fine Storage Heating Setpoint Schedule | Warehouse Fine Storage Cooling Setpoint Schedule
90.1-2007 | Warehouse | Bulk | 41_31_169 | ASHRAE 90.1-2007 | Warehouse | Medium/Bulky Material Storage | ASHRAE 90.1-2007WarehouseMedium/Bulky Material Storage | 0.9 |  |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2004 | Miscellaneous Spaces | Warehouses | ASHRAE 62.1-2004Miscellaneous SpacesWarehouses | 0.06 |  |  | 0 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0446 |  |  | Warehouse ALWAYS_ON | [5 empty] | 0.17 | 0 | 0.5 | 0 | Warehouse ALWAYS_OFF | Warehouse Bulk Storage Heating Setpoint Schedule | Warehouse ClgSetp
90.1-2010 | Warehouse | Office | 120_230_199 | ASHRAE 90.1-2010 | Office-Enclosed | General | ASHRAE 90.1-2010Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 1.96 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0446 |  |  | Warehouse ALWAYS_ON | [5 empty] | 0.54 | 0 | 0.5 | 0 | Warehouse Office_Plug_SCH | Warehouse HtgSetp | Warehouse ClgSetp
90.1-2010 | Warehouse | Fine | 120_149_230 | ASHRAE 90.1-2010 | Warehouse | Fine Material Storage | ASHRAE 90.1-2010WarehouseFine Material Storage | 0.95 |  |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses | ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | 0.06 |  |  | 0 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0446 |  |  | Warehouse ALWAYS_ON | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse ALWAYS_OFF | Warehouse Fine Storage Heating Setpoint Schedule | Warehouse Fine Storage Cooling Setpoint Schedule
90.1-2010 | Warehouse | Bulk | 41_31_169 | ASHRAE 90.1-2010 | Warehouse | Medium/Bulky Material Storage | ASHRAE 90.1-2010WarehouseMedium/Bulky Material Storage | 0.58 |  |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses | ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | 0.06 |  |  | 0 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0446 |  |  | Warehouse ALWAYS_ON | [5 empty] | 0.17 | 0 | 0.5 | 0 | Warehouse ALWAYS_OFF | Warehouse Bulk Storage Heating Setpoint Schedule | Warehouse ClgSetp
DOE Ref 1980-2004 | Warehouse | Office | 120_230_199 | DOE Ref 1980-2004 | Warehouse | Office | DOE Ref 1980-2004WarehouseOffice | 2.02 |  |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 1.96 | Warehouse Bldg Occ | Warehouse Activity |  | 0.2232 |  | Always On | [5 empty] | 0.75 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp | Warehouse ClgSetp
DOE Ref 1980-2004 | Warehouse | Fine | 120_149_230 | DOE Ref 1980-2004 | Warehouse | Fine | DOE Ref 1980-2004WarehouseFine | 1.08 |  |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 |  | 0 | Warehouse Bldg Occ | Warehouse Activity |  | 0.2232 |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp FineStorage | Warehouse ClgSetp FineStorage
DOE Ref 1980-2004 | Warehouse | Bulk | 41_31_169 | DOE Ref 1980-2004 | Warehouse | Bulk | DOE Ref 1980-2004WarehouseBulk | 0.31 |  |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 |  | 0 | Warehouse Bldg Occ | Warehouse Activity |  | 0.2232 |  | Always On | [5 empty] | 0.25 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp BulkStorage | Warehouse ClgSetp
DOE Ref Pre-1980 | Warehouse | Office | 120_230_199 | DOE Ref Pre-1980 | Warehouse | Office | DOE Ref Pre-1980WarehouseOffice | 2.9 |  |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 1.96 | Warehouse Bldg Occ | Warehouse Activity |  | 0.2232 |  | Always On | [5 empty] | 0.75 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp | Warehouse ClgSetp
DOE Ref Pre-1980 | Warehouse | Fine | 120_149_230 | DOE Ref Pre-1980 | Warehouse | Fine | DOE Ref Pre-1980WarehouseFine | 1.08 |  |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 |  | 0 | Warehouse Bldg Occ | Warehouse Activity |  | 0.2232 |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp FineStorage | Warehouse ClgSetp FineStorage
DOE Ref Pre-1980 | Warehouse | Bulk | 41_31_169 | DOE Ref Pre-1980 | Warehouse | Bulk | DOE Ref Pre-1980WarehouseBulk | 0.62 |  |  |  | 0 | 0.5 | 0.2 | Warehouse Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Warehouses | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsWarehouses | 0.05 | 0 |  | 0 | Warehouse Bldg Occ | Warehouse Activity |  | 0.2232 |  | Always On | [5 empty] | 0.25 | 0 | 0.5 | 0 | Warehouse Bldg Equip | Warehouse HtgSetp BulkStorage | Warehouse ClgSetp
NECB 2011 | Automotive facility | WholeBuilding | 255_255_255 | NECB 2011 | Automotive facility | WholeBuilding | NECB 2011Automotive facilityWholeBuilding | 0.81754 |  |  |  | 0 | 0.5 | 0.2 | NECB-E-Lighting | NECB 2011 | Automotive facility | WholeBuilding | NECB 2011Automotive facilityWholeBuilding |  |  | 0.001151044 | 4.65 | NECB-E-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.46451 | 0 | 0.5 | 0 | NECB-E-Electric-Equipment | NECB-E-Thermostat Setpoint-Heating | NECB-E-Thermostat Setpoint-Cooling | [6 empty] | NECB-E-Service Water Heating | [7 empty] | NECB-E-FAN
NECB 2011 | Convention centre | WholeBuilding | 255_255_255 | NECB 2011 | Convention centre | WholeBuilding | NECB 2011Convention centreWholeBuilding | 1.0777 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Convention centre | WholeBuilding | NECB 2011Convention centreWholeBuilding |  |  | 0.000747686 | 11.61 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Courthouse | WholeBuilding | 255_255_255 | NECB 2011 | Courthouse | WholeBuilding | NECB 2011CourthouseWholeBuilding | 1.0498 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Courthouse | WholeBuilding | NECB 2011CourthouseWholeBuilding |  |  | 0.000462385 | 6.19 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.46451 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Dining - bar/lounge | WholeBuilding | 255_255_255 | NECB 2011 | Dining - bar/lounge | WholeBuilding | NECB 2011Dining - bar/loungeWholeBuilding | 0.99405 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Dining - bar/lounge | WholeBuilding | NECB 2011Dining - bar/loungeWholeBuilding |  |  | 0.001269099 | 9.29 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Dining - cafeteria | WholeBuilding | 255_255_255 | NECB 2011 | Dining - cafeteria | WholeBuilding | NECB 2011Dining - cafeteriaWholeBuilding | 0.90115 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Dining - cafeteria | WholeBuilding | NECB 2011Dining - cafeteriaWholeBuilding |  |  | 0.001269099 | 9.29 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Dining - family | WholeBuilding | 255_255_255 | NECB 2011 | Dining - family | WholeBuilding | NECB 2011Dining - familyWholeBuilding | 0.89186 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Dining - family | WholeBuilding | NECB 2011Dining - familyWholeBuilding |  |  | 0.001269099 | 9.29 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Dormitory | WholeBuilding | 255_255_255 | NECB 2011 | Dormitory | WholeBuilding | NECB 2011DormitoryWholeBuilding | 0.61315 |  |  |  | 0 | 0.5 | 0.2 | NECB-G-Lighting | NECB 2011 | Dormitory | WholeBuilding | NECB 2011DormitoryWholeBuilding |  |  | 0.000383681 | 3.1 | NECB-G-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-G-Electric-Equipment | NECB-G-Thermostat Setpoint-Heating | NECB-G-Thermostat Setpoint-Cooling | [6 empty] | NECB-G-Service Water Heating | [7 empty] | NECB-G-FAN
NECB 2011 | Exercise centre | WholeBuilding | 255_255_255 | NECB 2011 | Exercise centre | WholeBuilding | NECB 2011Exercise centreWholeBuilding | 0.88257 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Exercise centre | WholeBuilding | NECB 2011Exercise centreWholeBuilding |  |  | 0.001249422 | 9.29 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Fire station | WholeBuilding | 255_255_255 | NECB 2011 | Fire station | WholeBuilding | NECB 2011Fire stationWholeBuilding | 0.70606 |  |  |  | 0 | 0.5 | 0.2 | NECB-F-Lighting | NECB 2011 | Fire station | WholeBuilding | NECB 2011Fire stationWholeBuilding |  |  | 0.000751622 | 3.72 | NECB-F-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-F-Electric-Equipment | NECB-F-Thermostat Setpoint-Heating | NECB-F-Thermostat Setpoint-Cooling | [6 empty] | NECB-F-Service Water Heating | [7 empty] | NECB-F-FAN
NECB 2011 | Gymnasium | WholeBuilding | 255_255_255 | NECB 2011 | Gymnasium | WholeBuilding | NECB 2011GymnasiumWholeBuilding | 1.0033 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Gymnasium | WholeBuilding | NECB 2011GymnasiumWholeBuilding |  |  | 0.001249422 | 9.29 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Health-care clinic | WholeBuilding | 255_255_255 | NECB 2011 | Health-care clinic | WholeBuilding | NECB 2011Health-care clinicWholeBuilding | 0.87328 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Health-care clinic | WholeBuilding | NECB 2011Health-care clinicWholeBuilding |  |  | 0.002287331 | 4.65 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.69677 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
90.1-2010 | PrimarySchool | Library | 230_196_120 | ASHRAE 90.1-2010 | Whole Building | Library | ASHRAE 90.1-2010Whole BuildingLibrary | 1.18 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | ASHRAE 62.1-2007 | Educational Facilities | Media center | ASHRAE 62.1-2007Educational FacilitiesMedia center | 0.12 | 10 |  | 10 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1.39 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
NECB 2011 | Hotel | WholeBuilding | 255_255_255 | NECB 2011 | Hotel | WholeBuilding | NECB 2011HotelWholeBuilding | 1.0033 |  |  |  | 0 | 0.5 | 0.2 | NECB-F-Lighting | NECB 2011 | Hotel | WholeBuilding | NECB 2011HotelWholeBuilding |  |  | 0.000399422 | 3.72 | NECB-F-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-F-Electric-Equipment | NECB-F-Thermostat Setpoint-Heating | NECB-F-Thermostat Setpoint-Cooling | [6 empty] | NECB-F-Service Water Heating | [7 empty] | NECB-F-FAN
NECB 2011 | Library | WholeBuilding | 255_255_255 | NECB 2011 | Library | WholeBuilding | NECB 2011LibraryWholeBuilding | 1.1799 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Library | WholeBuilding | NECB 2011LibraryWholeBuilding |  |  | 0.00072801 | 4.65 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Manufacturing facility | WholeBuilding | 255_255_255 | NECB 2011 | Manufacturing facility | WholeBuilding | NECB 2011Manufacturing facilityWholeBuilding | 1.1055 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Manufacturing facility | WholeBuilding | NECB 2011Manufacturing facilityWholeBuilding |  |  | 0.00107234 | 3.1 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Motel | WholeBuilding | 255_255_255 | NECB 2011 | Motel | WholeBuilding | NECB 2011MotelWholeBuilding | 0.88257 |  |  |  | 0 | 0.5 | 0.2 | NECB-F-Lighting | NECB 2011 | Motel | WholeBuilding | NECB 2011MotelWholeBuilding |  |  | 0.000399422 | 3.72 | NECB-F-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-F-Electric-Equipment | NECB-F-Thermostat Setpoint-Heating | NECB-F-Thermostat Setpoint-Cooling | [6 empty] | NECB-F-Service Water Heating | [7 empty] | NECB-F-FAN
NECB 2011 | Motion picture theatre | WholeBuilding | 255_255_255 | NECB 2011 | Motion picture theatre | WholeBuilding | NECB 2011Motion picture theatreWholeBuilding | 0.82683 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Motion picture theatre | WholeBuilding | NECB 2011Motion picture theatreWholeBuilding |  |  | 0.000600116 | 11.61 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Multi-unit residential | WholeBuilding | 255_255_255 | NECB 2011 | Multi-unit residential | WholeBuilding | NECB 2011Multi-unit residentialWholeBuilding | 0.60386 |  |  |  | 0 | 0.5 | 0.2 | NECB-G-Lighting | NECB 2011 | Multi-unit residential | WholeBuilding | NECB 2011Multi-unit residentialWholeBuilding |  |  | 0.000344329 | 1.55 | NECB-G-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.46451 | 0 | 0.5 | 0 | NECB-G-Electric-Equipment | NECB-G-Thermostat Setpoint-Heating | NECB-G-Thermostat Setpoint-Cooling | [6 empty] | NECB-G-Service Water Heating | [7 empty] | NECB-G-FAN
NECB 2011 | Museum | WholeBuilding | 255_255_255 | NECB 2011 | Museum | WholeBuilding | NECB 2011MuseumWholeBuilding | 1.0591 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Museum | WholeBuilding | NECB 2011MuseumWholeBuilding |  |  | 0.000482061 | 4.65 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Office | WholeBuilding | 255_255_255 | NECB 2011 | Office | WholeBuilding | NECB 2011OfficeWholeBuilding | 0.90115 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Office | WholeBuilding | NECB 2011OfficeWholeBuilding |  |  | 0.000399422 | 3.72 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.69677 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Parking garage | WholeBuilding | 255_255_255 | NECB 2011 | Parking garage | WholeBuilding | NECB 2011Parking garageWholeBuilding | 0.25084 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Parking garage | WholeBuilding | NECB 2011Parking garageWholeBuilding |  |  | 0.0003097 | 0.09 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Penitentiary | WholeBuilding | 255_255_255 | NECB 2011 | Penitentiary | WholeBuilding | NECB 2011PenitentiaryWholeBuilding | 0.96618 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Penitentiary | WholeBuilding | NECB 2011PenitentiaryWholeBuilding |  |  | 0.000383681 | 3.1 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Performing arts theatre | WholeBuilding | 255_255_255 | NECB 2011 | Performing arts theatre | WholeBuilding | NECB 2011Performing arts theatreWholeBuilding | 1.3935 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Performing arts theatre | WholeBuilding | NECB 2011Performing arts theatreWholeBuilding |  |  | 0.000600116 | 11.61 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Police station | WholeBuilding | 255_255_255 | NECB 2011 | Police station | WholeBuilding | NECB 2011Police stationWholeBuilding | 0.95689 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Police station | WholeBuilding | NECB 2011Police stationWholeBuilding |  |  | 0.000399422 | 3.72 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.69677 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Post office | WholeBuilding | 255_255_255 | NECB 2011 | Post office | WholeBuilding | NECB 2011Post officeWholeBuilding | 0.87328 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Post office | WholeBuilding | NECB 2011Post officeWholeBuilding |  |  | 0.000751622 | 3.72 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.69677 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Religious | WholeBuilding | 255_255_255 | NECB 2011 | Religious | WholeBuilding | NECB 2011ReligiousWholeBuilding | 1.0498 |  |  |  | 0 | 0.5 | 0.2 | NECB-I-Lighting | NECB 2011 | Religious | WholeBuilding | NECB 2011ReligiousWholeBuilding |  |  | 0.0007772 | 18.58 | NECB-I-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-I-Electric-Equipment | NECB-I-Thermostat Setpoint-Heating | NECB-I-Thermostat Setpoint-Cooling | [6 empty] | NECB-I-Service Water Heating | [7 empty] | NECB-I-FAN
NECB 2011 | Retail | WholeBuilding | 255_255_255 | NECB 2011 | Retail | WholeBuilding | NECB 2011RetailWholeBuilding | 1.4028 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Retail | WholeBuilding | NECB 2011RetailWholeBuilding |  |  | 0.000423033 | 3.1 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | School/university | WholeBuilding | 255_255_255 | NECB 2011 | School/university | WholeBuilding | NECB 2011School/universityWholeBuilding | 0.99405 |  |  |  | 0 | 0.5 | 0.2 | NECB-D-Lighting | NECB 2011 | School/university | WholeBuilding | NECB 2011School/universityWholeBuilding |  |  | 0.000747686 | 11.61 | NECB-D-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.46451 | 0 | 0.5 | 0 | NECB-D-Electric-Equipment | NECB-D-Thermostat Setpoint-Heating | NECB-D-Thermostat Setpoint-Cooling | [6 empty] | NECB-D-Service Water Heating | [7 empty] | NECB-D-FAN
NECB 2011 | Sports arena | WholeBuilding | 255_255_255 | NECB 2011 | Sports arena | WholeBuilding | NECB 2011Sports arenaWholeBuilding | 0.78038 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Sports arena | WholeBuilding | NECB 2011Sports arenaWholeBuilding |  |  | 0.000659144 | 9.29 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Town hall | WholeBuilding | 255_255_255 | NECB 2011 | Town hall | WholeBuilding | NECB 2011Town hallWholeBuilding | 0.91973 |  |  |  | 0 | 0.5 | 0.2 | NECB-D-Lighting | NECB 2011 | Town hall | WholeBuilding | NECB 2011Town hallWholeBuilding |  |  | 0.000399422 | 3.72 | NECB-D-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.69677 | 0 | 0.5 | 0 | NECB-D-Electric-Equipment | NECB-D-Thermostat Setpoint-Heating | NECB-D-Thermostat Setpoint-Cooling | [6 empty] | NECB-D-Service Water Heating | [7 empty] | NECB-D-FAN
NECB 2011 | Transportation | WholeBuilding | 255_255_255 | NECB 2011 | Transportation | WholeBuilding | NECB 2011TransportationWholeBuilding | 0.77109 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Transportation | WholeBuilding | NECB 2011TransportationWholeBuilding |  |  | 0.000541089 | 6.19 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Warehouse | WholeBuilding | 255_255_255 | NECB 2011 | Warehouse | WholeBuilding | NECB 2011WarehouseWholeBuilding | 0.65961 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Warehouse | WholeBuilding | NECB 2011WarehouseWholeBuilding |  |  | 0.000308126 | 0.06 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Workshop | WholeBuilding | 255_255_255 | NECB 2011 | Workshop | WholeBuilding | NECB 2011WorkshopWholeBuilding | 1.1984 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Workshop | WholeBuilding | NECB 2011WorkshopWholeBuilding |  |  | 0.00107234 | 3.1 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | - undefined - | 255_255_255 | NECB 2011 | Space Function | - undefined - | NECB 2011Space Function- undefined - | 0 |  |  |  | 0 | 0.5 | 0.2 | NECB-*-Lighting | NECB 2011 | Space Function | - undefined - | NECB 2011Space Function- undefined - | 0 | 0 | 0 | 0 | NECB-*-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-*-Electric-Equipment | NECB-*-Thermostat Setpoint-Heating | NECB-*-Thermostat Setpoint-Cooling | [6 empty] | NECB-*-Service Water Heating | [7 empty] | NECB-*-FAN
NECB 2011 | Space Function | Dwelling Unit(s) | 255_255_255 | NECB 2011 | Space Function | Dwelling Unit(s) | NECB 2011Space FunctionDwelling Unit(s) | 0.46451 |  |  |  | 0 | 0.5 | 0.2 | NECB-G-Lighting | NECB 2011 | Space Function | Dwelling Unit(s) | NECB 2011Space FunctionDwelling Unit(s) |  |  | 0.000344329 | 1.55 | NECB-G-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.46451 | 0 | 0.5 | 0 | NECB-G-Electric-Equipment | NECB-G-Thermostat Setpoint-Heating | NECB-G-Thermostat Setpoint-Cooling | [6 empty] | NECB-G-Service Water Heating | [7 empty] | NECB-G-FAN
NECB 2011 | Space Function | Atrium - H < 13m | 255_255_255 | NECB 2011 | Space Function | Atrium - H < 13m | NECB 2011Space FunctionAtrium - H < 13m | 0 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Atrium - H < 13m | NECB 2011Space FunctionAtrium - H < 13m |  |  | 0.000304977 | 9.29 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Atrium - H > 13m | 255_255_255 | NECB 2011 | Space Function | Atrium - H > 13m | NECB 2011Space FunctionAtrium - H > 13m | 0 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Atrium - H > 13m | NECB 2011Space FunctionAtrium - H > 13m |  |  | 0.000304977 | 9.29 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Audience - auditorium | 255_255_255 | NECB 2011 | Space Function | Audience - auditorium | NECB 2011Space FunctionAudience - auditorium | 0.78967 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Audience - auditorium | NECB 2011Space FunctionAudience - auditorium |  |  | 0.004117196 | 18.58 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Audience - performance arts | 255_255_255 | NECB 2011 | Space Function | Audience - performance arts | NECB 2011Space FunctionAudience - performance arts | 2.434 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Audience - performance arts | NECB 2011Space FunctionAudience - performance arts |  |  | 0.004117196 | 12.39 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Audience - motion picture | 255_255_255 | NECB 2011 | Space Function | Audience - motion picture | NECB 2011Space FunctionAudience - motion picture | 1.1427 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Audience - motion picture | NECB 2011Space FunctionAudience - motion picture |  |  | 0.004117196 | 18.58 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Classroom/lecture/training | 255_255_255 | NECB 2011 | Space Function | Classroom/lecture/training | NECB 2011Space FunctionClassroom/lecture/training | 1.2356 |  |  |  | 0 | 0.5 | 0.2 | NECB-D-Lighting | NECB 2011 | Space Function | Classroom/lecture/training | NECB 2011Space FunctionClassroom/lecture/training |  |  | 0.002782919 | 12.39 | NECB-D-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.46451 | 0 | 0.5 | 0 | NECB-D-Electric-Equipment | NECB-D-Thermostat Setpoint-Heating | NECB-D-Thermostat Setpoint-Cooling | [6 empty] | NECB-D-Service Water Heating | [7 empty] | NECB-D-FAN
NECB 2011 | Space Function | Conf./meet./multi-purpose | 255_255_255 | NECB 2011 | Space Function | Conf./meet./multi-purpose | NECB 2011Space FunctionConf./meet./multi-purpose | 1.2263 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Conf./meet./multi-purpose | NECB 2011Space FunctionConf./meet./multi-purpose |  |  | 0.001575717 | 18.58 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Corr. >= 2.4m wide | 255_255_255 | NECB 2011 | Space Function | Corr. >= 2.4m wide | NECB 2011Space FunctionCorr. >= 2.4m wide | 0.65961 |  |  |  | 0 | 0.5 | 0.2 | NECB-*-Lighting | NECB 2011 | Space Function | Corr. >= 2.4m wide | NECB 2011Space FunctionCorr. >= 2.4m wide |  |  | 0.000304977 | 0.93 | NECB-*-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-*-Electric-Equipment | NECB-*-Thermostat Setpoint-Heating | NECB-*-Thermostat Setpoint-Cooling | [6 empty] | NECB-*-Service Water Heating | [7 empty] | NECB-*-FAN
NECB 2011 | Space Function | Corr. < 2.4m wide | 255_255_255 | NECB 2011 | Space Function | Corr. < 2.4m wide | NECB 2011Space FunctionCorr. < 2.4m wide | 0.78038 |  |  |  | 0 | 0.5 | 0.2 | NECB-*-Lighting | NECB 2011 | Space Function | Corr. < 2.4m wide | NECB 2011Space FunctionCorr. < 2.4m wide |  |  | 0.000304977 | 0.93 | NECB-*-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-*-Electric-Equipment | NECB-*-Thermostat Setpoint-Heating | NECB-*-Thermostat Setpoint-Cooling | [6 empty] | NECB-*-Service Water Heating | [7 empty] | NECB-*-FAN
NECB 2011 | Space Function | Dining - bar lounge/leisure | 255_255_255 | NECB 2011 | Space Function | Dining - bar lounge/leisure | NECB 2011Space FunctionDining - bar lounge/leisure | 1.3099 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Dining - bar lounge/leisure | NECB 2011Space FunctionDining - bar lounge/leisure |  |  | 0.003583485 | 9.29 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Dining - family space | 255_255_255 | NECB 2011 | Space Function | Dining - family space | NECB 2011Space FunctionDining - family space | 0.89186 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Dining - family space | NECB 2011Space FunctionDining - family space |  |  | 0.003583485 | 9.29 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Dining - other | 255_255_255 | NECB 2011 | Space Function | Dining - other | NECB 2011Space FunctionDining - other | 0.65032 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Dining - other | NECB 2011Space FunctionDining - other |  |  | 0.003583485 | 9.29 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Dress./fitt. - performance arts | 255_255_255 | NECB 2011 | Space Function | Dress./fitt. - performance arts | NECB 2011Space FunctionDress./fitt. - performance arts | 0.39948 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Dress./fitt. - performance arts | NECB 2011Space FunctionDress./fitt. - performance arts |  |  | 0.001181788 | 3.1 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Electrical/Mechanical | 255_255_255 | NECB 2011 | Space Function | Electrical/Mechanical | NECB 2011Space FunctionElectrical/Mechanical | 1.2356 |  |  |  | 0 | 0.5 | 0.2 | NECB-*-Lighting | NECB 2011 | Space Function | Electrical/Mechanical | NECB 2011Space FunctionElectrical/Mechanical |  |  | 0.000304977 | 0.46 | NECB-*-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-*-Electric-Equipment | NECB-*-Thermostat Setpoint-Heating | NECB-*-Thermostat Setpoint-Cooling | [6 empty] | NECB-*-Service Water Heating | [7 empty] | NECB-*-FAN
NECB 2011 | Space Function | Food preparation | 255_255_255 | NECB 2011 | Space Function | Food preparation | NECB 2011Space FunctionFood preparation | 0.99405 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Food preparation | NECB 2011Space FunctionFood preparation |  |  | 0.001372399 | 4.65 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Lab - classrooms | 255_255_255 | NECB 2011 | Space Function | Lab - classrooms | NECB 2011Space FunctionLab - classrooms | 1.5979 |  |  |  | 0 | 0.5 | 0.2 | NECB-D-Lighting | NECB 2011 | Space Function | Lab - classrooms | NECB 2011Space FunctionLab - classrooms |  |  | 0.002185672 | 4.65 | NECB-D-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-D-Electric-Equipment | NECB-D-Thermostat Setpoint-Heating | NECB-D-Thermostat Setpoint-Cooling | [6 empty] | NECB-D-Service Water Heating | [7 empty] | NECB-D-FAN
NECB 2011 | Space Function | Lab - research | 255_255_255 | NECB 2011 | Space Function | Lab - research | NECB 2011Space FunctionLab - research | 2.1925 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Lab - research | NECB 2011Space FunctionLab - research |  |  | 0.002185672 | 4.65 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Lobby - elevator | 255_255_255 | NECB 2011 | Space Function | Lobby - elevator | NECB 2011Space FunctionLobby - elevator | 0.64103 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Lobby - elevator | NECB 2011Space FunctionLobby - elevator |  |  | 0.004117196 | 9.29 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Lobby - performance arts | 255_255_255 | NECB 2011 | Space Function | Lobby - performance arts | NECB 2011Space FunctionLobby - performance arts | 1.9974 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Lobby - performance arts | NECB 2011Space FunctionLobby - performance arts |  |  | 0.004117196 | 9.29 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Lobby - motion picture | 255_255_255 | NECB 2011 | Space Function | Lobby - motion picture | NECB 2011Space FunctionLobby - motion picture | 0.52025 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Lobby - motion picture | NECB 2011Space FunctionLobby - motion picture |  |  | 0.004117196 | 9.29 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Lobby - other | 255_255_255 | NECB 2011 | Space Function | Lobby - other | NECB 2011Space FunctionLobby - other | 0.90115 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Lobby - other | NECB 2011Space FunctionLobby - other |  |  | 0.004117196 | 9.29 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Locker room | 255_255_255 | NECB 2011 | Space Function | Locker room | NECB 2011Space FunctionLocker room | 0.91044 |  |  |  | 0 | 0.5 | 0.2 | NECB-*-Lighting | NECB 2011 | Space Function | Locker room | NECB 2011Space FunctionLocker room |  |  | 0.000940347 | 9.29 | NECB-*-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-*-Electric-Equipment | NECB-*-Thermostat Setpoint-Heating | NECB-*-Thermostat Setpoint-Cooling | [6 empty] | NECB-*-Service Water Heating | [7 empty] | NECB-*-FAN
NECB 2011 | Space Function | Lounge/recreation | 255_255_255 | NECB 2011 | Space Function | Lounge/recreation | NECB 2011Space FunctionLounge/recreation | 0.87328 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Lounge/recreation | NECB 2011Space FunctionLounge/recreation |  |  | 0.000940347 | 9.29 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Office - enclosed | 255_255_255 | NECB 2011 | Space Function | Office - enclosed | NECB 2011Space FunctionOffice - enclosed | 1.1055 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Office - enclosed | NECB 2011Space FunctionOffice - enclosed |  |  | 0.000432051 | 4.65 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.69677 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Office - open plan | 255_255_255 | NECB 2011 | Space Function | Office - open plan | NECB 2011Space FunctionOffice - open plan | 1.0219 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Office - open plan | NECB 2011Space FunctionOffice - open plan |  |  | 0.000432051 | 4.65 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.69677 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Sales area | 255_255_255 | NECB 2011 | Space Function | Sales area | NECB 2011Space FunctionSales area | 1.6815 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Sales area | NECB 2011Space FunctionSales area |  |  | 0.001181788 | 3.1 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Stairway | 255_255_255 | NECB 2011 | Space Function | Stairway | NECB 2011Space FunctionStairway | 0.68748 |  |  |  | 0 | 0.5 | 0.2 | NECB-*-Lighting | NECB 2011 | Space Function | Stairway | NECB 2011Space FunctionStairway |  |  | 0.000304977 | 0.46 | NECB-*-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-*-Electric-Equipment | NECB-*-Thermostat Setpoint-Heating | NECB-*-Thermostat Setpoint-Cooling | [6 empty] | NECB-*-Service Water Heating | [7 empty] | NECB-*-FAN
NECB 2011 | Space Function | Storage area | 255_255_255 | NECB 2011 | Space Function | Storage area | NECB 2011Space FunctionStorage area | 0.63174 |  |  |  | 0 | 0.5 | 0.2 | NECB-E-Lighting | NECB 2011 | Space Function | Storage area | NECB 2011Space FunctionStorage area |  |  | 0.000355807 | 0.93 | NECB-E-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-E-Electric-Equipment | NECB-E-Thermostat Setpoint-Heating | NECB-E-Thermostat Setpoint-Cooling | [6 empty] | NECB-E-Service Water Heating | [7 empty] | NECB-E-FAN
NECB 2011 | Space Function | Washroom | 255_255_255 | NECB 2011 | Space Function | Washroom | NECB 2011Space FunctionWashroom | 0.97547 |  |  |  | 0 | 0.5 | 0.2 | NECB-*-Lighting | NECB 2011 | Space Function | Washroom | NECB 2011Space FunctionWashroom |  |  | 0.000304977 | 3.1 | NECB-*-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-*-Electric-Equipment | NECB-*-Thermostat Setpoint-Heating | NECB-*-Thermostat Setpoint-Cooling | [6 empty] | NECB-*-Service Water Heating | [7 empty] | NECB-*-FAN
NECB 2011 | Space Function | Workshop space | 255_255_255 | NECB 2011 | Space Function | Workshop space | NECB 2011Space FunctionWorkshop space | 1.5886 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Workshop space | NECB 2011Space FunctionWorkshop space |  |  | 0.001931524 | 3.1 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Automotive - repair | 255_255_255 | NECB 2011 | Space Function | Automotive - repair | NECB 2011Space FunctionAutomotive - repair | 0.6689 |  |  |  | 0 | 0.5 | 0.2 | NECB-E-Lighting | NECB 2011 | Space Function | Automotive - repair | NECB 2011Space FunctionAutomotive - repair |  |  | 0.001270739 | 4.65 | NECB-E-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.46451 | 0 | 0.5 | 0 | NECB-E-Electric-Equipment | NECB-E-Thermostat Setpoint-Heating | NECB-E-Thermostat Setpoint-Cooling | [6 empty] | NECB-E-Service Water Heating | [7 empty] | NECB-E-FAN
NECB 2011 | Space Function | Bank - banking and offices | 255_255_255 | NECB 2011 | Space Function | Bank - banking and offices | NECB 2011Space FunctionBank - banking and offices | 1.3842 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Bank - banking and offices | NECB 2011Space FunctionBank - banking and offices |  |  | 0.00087681 | 3.72 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.46451 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Convention centre - audience | 255_255_255 | NECB 2011 | Space Function | Convention centre - audience | NECB 2011Space FunctionConvention centre - audience | 0.81754 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Convention centre - audience | NECB 2011Space FunctionConvention centre - audience |  |  | 0.004117196 | 18.58 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Convention centre - exhibit | 255_255_255 | NECB 2011 | Space Function | Convention centre - exhibit | NECB 2011Space FunctionConvention centre - exhibit | 1.4493 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Convention centre - exhibit | NECB 2011Space FunctionConvention centre - exhibit |  |  | 0.000864103 | 18.58 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Courthouse - courtroom | 255_255_255 | NECB 2011 | Space Function | Courthouse - courtroom | NECB 2011Space FunctionCourthouse - courtroom | 1.7187 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Courthouse - courtroom | NECB 2011Space FunctionCourthouse - courtroom |  |  | 0.002084013 | 18.58 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Courthouse - cell | 255_255_255 | NECB 2011 | Space Function | Courthouse - cell | NECB 2011Space FunctionCourthouse - cell | 1.3657 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Courthouse - cell | NECB 2011Space FunctionCourthouse - cell |  |  | 0.001245325 | 3.72 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Courthouse - chambers | 255_255_255 | NECB 2011 | Space Function | Courthouse - chambers | NECB 2011Space FunctionCourthouse - chambers | 1.1706 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Courthouse - chambers | NECB 2011Space FunctionCourthouse - chambers |  |  | 0.000432051 | 4.65 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.69677 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Penitentiary - audience | 255_255_255 | NECB 2011 | Space Function | Penitentiary - audience | NECB 2011Space FunctionPenitentiary - audience | 0.42735 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Penitentiary - audience | NECB 2011Space FunctionPenitentiary - audience |  |  | 0.002084013 | 18.58 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Penitentiary - classroom | 255_255_255 | NECB 2011 | Space Function | Penitentiary - classroom | NECB 2011Space FunctionPenitentiary - classroom | 1.3378 |  |  |  | 0 | 0.5 | 0.2 | NECB-D-Lighting | NECB 2011 | Space Function | Penitentiary - classroom | NECB 2011Space FunctionPenitentiary - classroom |  |  | 0.002782919 | 12.39 | NECB-D-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.46451 | 0 | 0.5 | 0 | NECB-D-Electric-Equipment | NECB-D-Thermostat Setpoint-Heating | NECB-D-Thermostat Setpoint-Cooling | [6 empty] | NECB-D-Service Water Heating | [7 empty] | NECB-D-FAN
NECB 2011 | Space Function | Penitentiary - dining | 255_255_255 | NECB 2011 | Space Function | Penitentiary - dining | NECB 2011Space FunctionPenitentiary - dining | 1.0684 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Penitentiary - dining | NECB 2011Space FunctionPenitentiary - dining |  |  | 0.003583485 | 9.29 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Dormitory - living quarters | 255_255_255 | NECB 2011 | Space Function | Dormitory - living quarters | NECB 2011Space FunctionDormitory - living quarters | 0.3809 |  |  |  | 0 | 0.5 | 0.2 | NECB-G-Lighting | NECB 2011 | Space Function | Dormitory - living quarters | NECB 2011Space FunctionDormitory - living quarters |  |  | 0.000559125 | 3.72 | NECB-G-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-G-Electric-Equipment | NECB-G-Thermostat Setpoint-Heating | NECB-G-Thermostat Setpoint-Cooling | [6 empty] | NECB-G-Service Water Heating | [7 empty] | NECB-G-FAN
NECB 2011 | Space Function | Fire station - engine room | 255_255_255 | NECB 2011 | Space Function | Fire station - engine room | NECB 2011Space FunctionFire station - engine room | 0.55741 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Fire station - engine room | NECB 2011Space FunctionFire station - engine room |  |  | 0.001270739 | 3.72 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Fire station - quarters | 255_255_255 | NECB 2011 | Space Function | Fire station - quarters | NECB 2011Space FunctionFire station - quarters | 0.31587 |  |  |  | 0 | 0.5 | 0.2 | NECB-G-Lighting | NECB 2011 | Space Function | Fire station - quarters | NECB 2011Space FunctionFire station - quarters |  |  | 0.000813273 | 3.72 | NECB-G-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-G-Electric-Equipment | NECB-G-Thermostat Setpoint-Heating | NECB-G-Thermostat Setpoint-Cooling | [6 empty] | NECB-G-Service Water Heating | [7 empty] | NECB-G-FAN
NECB 2011 | Space Function | Gym - fitness | 255_255_255 | NECB 2011 | Space Function | Gym - fitness | NECB 2011Space FunctionGym - fitness | 0.91044 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Gym - fitness | NECB 2011Space FunctionGym - fitness |  |  | 0.004371344 | 18.58 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Gym - audience | 255_255_255 | NECB 2011 | Space Function | Gym - audience | NECB 2011Space FunctionGym - audience | 0.42735 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Gym - audience | NECB 2011Space FunctionGym - audience |  |  | 0.004117196 | 18.58 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Gym - play | 255_255_255 | NECB 2011 | Space Function | Gym - play | NECB 2011Space FunctionGym - play | 1.1984 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Gym - play | NECB 2011Space FunctionGym - play |  |  | 0.001524887 | 18.58 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.13935 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Hospital corr. >= 2.4m | 255_255_255 | NECB 2011 | Space Function | Hospital corr. >= 2.4m | NECB 2011Space FunctionHospital corr. >= 2.4m | 0.89186 |  |  |  | 0 | 0.5 | 0.2 | NECB-*-Lighting | NECB 2011 | Space Function | Hospital corr. >= 2.4m | NECB 2011Space FunctionHospital corr. >= 2.4m |  |  | 0.000762444 | 0.93 | NECB-*-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-*-Electric-Equipment | NECB-*-Thermostat Setpoint-Heating | NECB-*-Thermostat Setpoint-Cooling | [6 empty] | NECB-*-Service Water Heating | [7 empty] | NECB-*-FAN
NECB 2011 | Space Function | Hospital corr. < 2.4m | 255_255_255 | NECB 2011 | Space Function | Hospital corr. < 2.4m | NECB 2011Space FunctionHospital corr. < 2.4m | 1.087 |  |  |  | 0 | 0.5 | 0.2 | NECB-*-Lighting | NECB 2011 | Space Function | Hospital corr. < 2.4m | NECB 2011Space FunctionHospital corr. < 2.4m |  |  | 0.000762444 | 0.93 | NECB-*-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-*-Electric-Equipment | NECB-*-Thermostat Setpoint-Heating | NECB-*-Thermostat Setpoint-Cooling | [6 empty] | NECB-*-Service Water Heating | [7 empty] | NECB-*-FAN
NECB 2011 | Space Function | Hospital - emergency | 255_255_255 | NECB 2011 | Space Function | Hospital - emergency | NECB 2011Space FunctionHospital - emergency | 2.2575 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Hospital - emergency | NECB 2011Space FunctionHospital - emergency |  |  | 0.003049775 | 4.65 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Hospital - exam | 255_255_255 | NECB 2011 | Space Function | Hospital - exam | NECB 2011Space FunctionHospital - exam | 1.663 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Hospital - exam | NECB 2011Space FunctionHospital - exam |  |  | 0.001524887 | 4.65 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Hospital - laundry/washing | 255_255_255 | NECB 2011 | Space Function | Hospital - laundry/washing | NECB 2011Space FunctionHospital - laundry/washing | 0.74322 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Hospital - laundry/washing | NECB 2011Space FunctionHospital - laundry/washing |  |  | 0.002287331 | 4.65 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 1.858 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Hospital - lounge/recreation | 255_255_255 | NECB 2011 | Space Function | Hospital - lounge/recreation | NECB 2011Space FunctionHospital - lounge/recreation | 1.0684 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Hospital - lounge/recreation | NECB 2011Space FunctionHospital - lounge/recreation |  |  | 0.001270739 | 9.29 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Hospital - medical supply | 255_255_255 | NECB 2011 | Space Function | Hospital - medical supply | NECB 2011Space FunctionHospital - medical supply | 1.2728 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Hospital - medical supply | NECB 2011Space FunctionHospital - medical supply |  |  | 0.001524887 | 4.65 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Hospital - nursery | 255_255_255 | NECB 2011 | Space Function | Hospital - nursery | NECB 2011Space FunctionHospital - nursery | 0.88257 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Hospital - nursery | NECB 2011Space FunctionHospital - nursery |  |  | 0.001524887 | 4.65 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Hospital - nurses' station | 255_255_255 | NECB 2011 | Space Function | Hospital - nurses' station | NECB 2011Space FunctionHospital - nurses' station | 0.87328 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Hospital - nurses' station | NECB 2011Space FunctionHospital - nurses' station |  |  | 0.001524887 | 4.65 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Hospital - operating room | 255_255_255 | NECB 2011 | Space Function | Hospital - operating room | NECB 2011Space FunctionHospital - operating room | 1.8859 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Hospital - operating room | NECB 2011Space FunctionHospital - operating room |  |  | 0.004574662 | 4.65 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Hospital - patient room | 255_255_255 | NECB 2011 | Space Function | Hospital - patient room | NECB 2011Space FunctionHospital - patient room | 0.62245 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Hospital - patient room | NECB 2011Space FunctionHospital - patient room |  |  | 0.001524887 | 4.65 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Hospital - pharmacy | 255_255_255 | NECB 2011 | Space Function | Hospital - pharmacy | NECB 2011Space FunctionHospital - pharmacy | 1.1427 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Hospital - pharmacy | NECB 2011Space FunctionHospital - pharmacy |  |  | 0.002287331 | 4.65 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Hospital - physical therapy | 255_255_255 | NECB 2011 | Space Function | Hospital - physical therapy | NECB 2011Space FunctionHospital - physical therapy | 0.91044 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Hospital - physical therapy | NECB 2011Space FunctionHospital - physical therapy |  |  | 0.002287331 | 4.65 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Hospital - radiology/imaging | 255_255_255 | NECB 2011 | Space Function | Hospital - radiology/imaging | NECB 2011Space FunctionHospital - radiology/imaging | 1.3192 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Hospital - radiology/imaging | NECB 2011Space FunctionHospital - radiology/imaging |  |  | 0.002287331 | 4.65 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Hospital - recovery | 255_255_255 | NECB 2011 | Space Function | Hospital - recovery | NECB 2011Space FunctionHospital - recovery | 1.152 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Hospital - recovery | NECB 2011Space FunctionHospital - recovery |  |  | 0.004574662 | 4.65 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Hotel/Motel - dining | 255_255_255 | NECB 2011 | Space Function | Hotel/Motel - dining | NECB 2011Space FunctionHotel/Motel - dining | 0.81754 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Hotel/Motel - dining | NECB 2011Space FunctionHotel/Motel - dining |  |  | 0.003583485 | 9.29 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Hotel/Motel - rooms | 255_255_255 | NECB 2011 | Space Function | Hotel/Motel - rooms | NECB 2011Space FunctionHotel/Motel - rooms | 1.1055 |  |  |  | 0 | 0.5 | 0.2 | NECB-F-Lighting | NECB 2011 | Space Function | Hotel/Motel - rooms | NECB 2011Space FunctionHotel/Motel - rooms |  |  | 0.000559125 | 3.72 | NECB-F-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-F-Electric-Equipment | NECB-F-Thermostat Setpoint-Heating | NECB-F-Thermostat Setpoint-Cooling | [6 empty] | NECB-F-Service Water Heating | [7 empty] | NECB-F-FAN
NECB 2011 | Space Function | Hotel/Motel - lobby | 255_255_255 | NECB 2011 | Space Function | Hotel/Motel - lobby | NECB 2011Space FunctionHotel/Motel - lobby | 1.0591 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Hotel/Motel - lobby | NECB 2011Space FunctionHotel/Motel - lobby |  |  | 0.001448643 | 9.29 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Hway lodging - dining | 255_255_255 | NECB 2011 | Space Function | Hway lodging - dining | NECB 2011Space FunctionHway lodging - dining | 0.88257 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Hway lodging - dining | NECB 2011Space FunctionHway lodging - dining |  |  | 0.003583485 | 9.29 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Hway lodging - rooms | 255_255_255 | NECB 2011 | Space Function | Hway lodging - rooms | NECB 2011Space FunctionHway lodging - rooms | 0.75251 |  |  |  | 0 | 0.5 | 0.2 | NECB-F-Lighting | NECB 2011 | Space Function | Hway lodging - rooms | NECB 2011Space FunctionHway lodging - rooms |  |  | 0.000559125 | 3.72 | NECB-F-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-F-Electric-Equipment | NECB-F-Thermostat Setpoint-Heating | NECB-F-Thermostat Setpoint-Cooling | [6 empty] | NECB-F-Service Water Heating | [7 empty] | NECB-F-FAN
NECB 2011 | Space Function | Library - cataloging | 255_255_255 | NECB 2011 | Space Function | Library - cataloging | NECB 2011Space FunctionLibrary - cataloging | 0.72464 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Library - cataloging | NECB 2011Space FunctionLibrary - cataloging |  |  | 0.000864103 | 4.65 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Library - reading | 255_255_255 | NECB 2011 | Space Function | Library - reading | NECB 2011Space FunctionLibrary - reading | 0.92902 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Library - reading | NECB 2011Space FunctionLibrary - reading |  |  | 0.000864103 | 4.65 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Library - stacks | 255_255_255 | NECB 2011 | Space Function | Library - stacks | NECB 2011Space FunctionLibrary - stacks | 2.1275 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Library - stacks | NECB 2011Space FunctionLibrary - stacks |  |  | 0.000864103 | 4.65 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Mfg - corr. >= 2.4m | 255_255_255 | NECB 2011 | Space Function | Mfg - corr. >= 2.4m | NECB 2011Space FunctionMfg - corr. >= 2.4m | 0.40877 |  |  |  | 0 | 0.5 | 0.2 | NECB-*-Lighting | NECB 2011 | Space Function | Mfg - corr. >= 2.4m | NECB 2011Space FunctionMfg - corr. >= 2.4m |  |  | 0.001270739 | 0.93 | NECB-*-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-*-Electric-Equipment | NECB-*-Thermostat Setpoint-Heating | NECB-*-Thermostat Setpoint-Cooling | [6 empty] | NECB-*-Service Water Heating | [7 empty] | NECB-*-FAN
NECB 2011 | Space Function | Mfg - corr. < 2.4m | 255_255_255 | NECB 2011 | Space Function | Mfg - corr. < 2.4m | NECB 2011Space FunctionMfg - corr. < 2.4m | 0.51096 |  |  |  | 0 | 0.5 | 0.2 | NECB-*-Lighting | NECB 2011 | Space Function | Mfg - corr. < 2.4m | NECB 2011Space FunctionMfg - corr. < 2.4m |  |  | 0.001270739 | 0.93 | NECB-*-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-*-Electric-Equipment | NECB-*-Thermostat Setpoint-Heating | NECB-*-Thermostat Setpoint-Cooling | [6 empty] | NECB-*-Service Water Heating | [7 empty] | NECB-*-FAN
NECB 2011 | Space Function | Mfg - detailed | 255_255_255 | NECB 2011 | Space Function | Mfg - detailed | NECB 2011Space FunctionMfg - detailed | 1.2913 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Mfg - detailed | NECB 2011Space FunctionMfg - detailed |  |  | 0.001270739 | 3.1 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Mfg - equipment | 255_255_255 | NECB 2011 | Space Function | Mfg - equipment | NECB 2011Space FunctionMfg - equipment | 1.2356 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Mfg - equipment | NECB 2011Space FunctionMfg - equipment |  |  | 0.001270739 | 3.1 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Mfg - bay H > 15m | 255_255_255 | NECB 2011 | Space Function | Mfg - bay H > 15m | NECB 2011Space FunctionMfg - bay H > 15m | 1.0498 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Mfg - bay H > 15m | NECB 2011Space FunctionMfg - bay H > 15m |  |  | 0.001270739 | 3.1 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Mfg - 7.5 <= bay H <= 15m | 255_255_255 | NECB 2011 | Space Function | Mfg - 7.5 <= bay H <= 15m | NECB 2011Space FunctionMfg - 7.5 <= bay H <= 15m | 1.2263 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Mfg - 7.5 <= bay H <= 15m | NECB 2011Space FunctionMfg - 7.5 <= bay H <= 15m |  |  | 0.001270739 | 3.1 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Mfg - bay H < 7.5m | 255_255_255 | NECB 2011 | Space Function | Mfg - bay H < 7.5m | NECB 2011Space FunctionMfg - bay H < 7.5m | 1.1891 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Mfg - bay H < 7.5m | NECB 2011Space FunctionMfg - bay H < 7.5m |  |  | 0.001270739 | 3.1 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.92902 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Museum - exhibition | 255_255_255 | NECB 2011 | Space Function | Museum - exhibition | NECB 2011Space FunctionMuseum - exhibition | 1.0498 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Museum - exhibition | NECB 2011Space FunctionMuseum - exhibition |  |  | 0.001829865 | 18.58 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Museum - restoration | 255_255_255 | NECB 2011 | Space Function | Museum - restoration | NECB 2011Space FunctionMuseum - restoration | 1.0219 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Museum - restoration | NECB 2011Space FunctionMuseum - restoration |  |  | 0.000864103 | 4.65 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.46451 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Parking garage space | 255_255_255 | NECB 2011 | Space Function | Parking garage space | NECB 2011Space FunctionParking garage space | 0.1858 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Parking garage space | NECB 2011Space FunctionParking garage space |  |  | 0.002541479 | 0.09 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Post office sorting | 255_255_255 | NECB 2011 | Space Function | Post office sorting | NECB 2011Space FunctionPost office sorting | 0.93831 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Post office sorting | NECB 2011Space FunctionPost office sorting |  |  | 0.00087681 | 4.65 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.69677 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Religious - audience | 255_255_255 | NECB 2011 | Space Function | Religious - audience | NECB 2011Space FunctionReligious - audience | 1.6908 |  |  |  | 0 | 0.5 | 0.2 | NECB-I-Lighting | NECB 2011 | Space Function | Religious - audience | NECB 2011Space FunctionReligious - audience |  |  | 0.003354752 | 18.58 | NECB-I-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-I-Electric-Equipment | NECB-I-Thermostat Setpoint-Heating | NECB-I-Thermostat Setpoint-Cooling | [6 empty] | NECB-I-Service Water Heating | [7 empty] | NECB-I-FAN
NECB 2011 | Space Function | Religious - fellowship hall | 255_255_255 | NECB 2011 | Space Function | Religious - fellowship hall | NECB 2011Space FunctionReligious - fellowship hall | 0.64103 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Religious - fellowship hall | NECB 2011Space FunctionReligious - fellowship hall |  |  | 0.003354752 | 18.58 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Religious - pulpit/choir | 255_255_255 | NECB 2011 | Space Function | Religious - pulpit/choir | NECB 2011Space FunctionReligious - pulpit/choir | 1.6908 |  |  |  | 0 | 0.5 | 0.2 | NECB-I-Lighting | NECB 2011 | Space Function | Religious - pulpit/choir | NECB 2011Space FunctionReligious - pulpit/choir |  |  | 0.003354752 | 18.58 | NECB-I-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-I-Electric-Equipment | NECB-I-Thermostat Setpoint-Heating | NECB-I-Thermostat Setpoint-Cooling | [6 empty] | NECB-I-Service Water Heating | [7 empty] | NECB-I-FAN
NECB 2011 | Space Function | Retail - dressing/fitting | 255_255_255 | NECB 2011 | Space Function | Retail - dressing/fitting | NECB 2011Space FunctionRetail - dressing/fitting | 0.87328 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Retail - dressing/fitting | NECB 2011Space FunctionRetail - dressing/fitting |  |  | 0.001181788 | 3.1 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Retail - mall concourse | 255_255_255 | NECB 2011 | Space Function | Retail - mall concourse | NECB 2011Space FunctionRetail - mall concourse | 1.0962 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Retail - mall concourse | NECB 2011Space FunctionRetail - mall concourse |  |  | 0.001829865 | 4.65 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Retail - sales | 255_255_255 | NECB 2011 | Space Function | Retail - sales | NECB 2011Space FunctionRetail - sales | 1.6815 |  |  |  | 0 | 0.5 | 0.2 | NECB-C-Lighting | NECB 2011 | Space Function | Retail - sales | NECB 2011Space FunctionRetail - sales |  |  | 0.001181788 | 3.1 | NECB-C-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-C-Electric-Equipment | NECB-C-Thermostat Setpoint-Heating | NECB-C-Thermostat Setpoint-Cooling | [6 empty] | NECB-C-Service Water Heating | [7 empty] | NECB-C-FAN
NECB 2011 | Space Function | Sports arena - audience | 255_255_255 | NECB 2011 | Space Function | Sports arena - audience | NECB 2011Space FunctionSports arena - audience | 0.42735 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Sports arena - audience | NECB 2011Space FunctionSports arena - audience |  |  | 0.006023305 | 18.58 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Sports arena - court c4 | 255_255_255 | NECB 2011 | Space Function | Sports arena - court c4 | NECB 2011Space FunctionSports arena - court c4 | 0.72464 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Sports arena - court c4 | NECB 2011Space FunctionSports arena - court c4 |  |  | 0.001524887 | 18.58 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.13935 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Sports arena - court c3 | 255_255_255 | NECB 2011 | Space Function | Sports arena - court c3 | NECB 2011Space FunctionSports arena - court c3 | 1.1984 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Sports arena - court c3 | NECB 2011Space FunctionSports arena - court c3 |  |  | 0.001524887 | 18.58 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.13935 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Sports arena - court c2 | 255_255_255 | NECB 2011 | Space Function | Sports arena - court c2 | NECB 2011Space FunctionSports arena - court c2 | 1.9231 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Sports arena - court c2 | NECB 2011Space FunctionSports arena - court c2 |  |  | 0.001524887 | 18.58 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.13935 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Sports arena - court c1 | 255_255_255 | NECB 2011 | Space Function | Sports arena - court c1 | NECB 2011Space FunctionSports arena - court c1 | 3.01 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Sports arena - court c1 | NECB 2011Space FunctionSports arena - court c1 |  |  | 0.001524887 | 18.58 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.13935 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Sports arena - ring | 255_255_255 | NECB 2011 | Space Function | Sports arena - ring | NECB 2011Space FunctionSports arena - ring | 2.6756 |  |  |  | 0 | 0.5 | 0.2 | NECB-B-Lighting | NECB 2011 | Space Function | Sports arena - ring | NECB 2011Space FunctionSports arena - ring |  |  | 0.001524887 | 18.58 | NECB-B-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.13935 | 0 | 0.5 | 0 | NECB-B-Electric-Equipment | NECB-B-Thermostat Setpoint-Heating | NECB-B-Thermostat Setpoint-Cooling | [6 empty] | NECB-B-Service Water Heating | [7 empty] | NECB-B-FAN
NECB 2011 | Space Function | Transp. baggage | 255_255_255 | NECB 2011 | Space Function | Transp. baggage | NECB 2011Space FunctionTransp. baggage | 0.7618 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Transp. baggage | NECB 2011Space FunctionTransp. baggage |  |  | 0.00087681 | 4.65 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Transp. seating | 255_255_255 | NECB 2011 | Space Function | Transp. seating | NECB 2011Space FunctionTransp. seating | 0.53883 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Transp. seating | NECB 2011Space FunctionTransp. seating |  |  | 0.004117196 | 9.29 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Transp. concourse | 255_255_255 | NECB 2011 | Space Function | Transp. concourse | NECB 2011Space FunctionTransp. concourse | 0.36232 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Transp. concourse | NECB 2011Space FunctionTransp. concourse |  |  | 0.004117196 | 4.65 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Transp. counter | 255_255_255 | NECB 2011 | Space Function | Transp. counter | NECB 2011Space FunctionTransp. counter | 1.0777 |  |  |  | 0 | 0.5 | 0.2 | NECB-H-Lighting | NECB 2011 | Space Function | Transp. counter | NECB 2011Space FunctionTransp. counter |  |  | 0.00087681 | 9.29 | NECB-H-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.23226 | 0 | 0.5 | 0 | NECB-H-Electric-Equipment | NECB-H-Thermostat Setpoint-Heating | NECB-H-Thermostat Setpoint-Cooling | [6 empty] | NECB-H-Service Water Heating | [7 empty] | NECB-H-FAN
NECB 2011 | Space Function | Warehouse - fine | 255_255_255 | NECB 2011 | Space Function | Warehouse - fine | NECB 2011Space FunctionWarehouse - fine | 0.9476 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Warehouse - fine | NECB 2011Space FunctionWarehouse - fine |  |  | 0.000304977 | 1.86 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Warehouse - med/blk | 255_255_255 | NECB 2011 | Space Function | Warehouse - med/blk | NECB 2011Space FunctionWarehouse - med/blk | 0.59457 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Warehouse - med/blk | NECB 2011Space FunctionWarehouse - med/blk |  |  | 0.000304977 | 0.93 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
NECB 2011 | Space Function | Warehouse - med/blk2 | 255_255_255 | NECB 2011 | Space Function | Warehouse - med/blk2 | NECB 2011Space FunctionWarehouse - med/blk2 | 0.9476 |  |  |  | 0 | 0.5 | 0.2 | NECB-A-Lighting | NECB 2011 | Space Function | Warehouse - med/blk2 | NECB 2011Space FunctionWarehouse - med/blk2 |  |  | 0.000304977 | 0.93 | NECB-A-Occupancy | NECB-Activity | 0.049225 |  |  | Always On | [5 empty] | 0.092902 | 0 | 0.5 | 0 | NECB-A-Electric-Equipment | NECB-A-Thermostat Setpoint-Heating | NECB-A-Thermostat Setpoint-Cooling | [6 empty] | NECB-A-Service Water Heating | [7 empty] | NECB-A-FAN
90.1-2013 | SecondarySchool | Auditorium | 230_196_120 | ASHRAE 90.1-2013 | Audience/Seating Area | For Auditorium | ASHRAE 90.1-2013Audience/Seating AreaFor Auditorium | 0.63 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Public Assembly Spaces | Auditorium seating area | ASHRAE 62.1-2007Public Assembly SpacesAuditorium seating area | 0.06 | 5 |  | 150 | SchoolSecondary BLDG_OCC_SCH_Auditorium | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.46 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2013 | SecondarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2013 | Dining Area | General | ASHRAE 90.1-2013Dining AreaGeneral | 0.65 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 100 | SchoolSecondary BLDG_OCC_SCH_Cafeteria | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 7.15 | 0 | 0.5 | 0 | SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2013 | SecondarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2013 | Classroom/Lecture/Training | General | ASHRAE 90.1-2013Classroom/Lecture/TrainingGeneral | 1.24 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (age 9 plus) | ASHRAE 62.1-2007Educational FacilitiesClassrooms (age 9 plus) | 0.12 | 10 |  | 35 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.929 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2013 | SecondarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2013 | Corridor | General | ASHRAE 90.1-2013CorridorGeneral | 0.66 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2013 | SecondarySchool | Gym | 154_230_120 | ASHRAE 90.1-2013 | Gymnasium/Fitness Center | Exercise Area | ASHRAE 90.1-2013Gymnasium/Fitness CenterExercise Area | 1.2 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_GYM_SCH | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) | ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | 0.3 |  |  | 30 | SchoolSecondary BLDG_OCC_SCH_Gym | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.46 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_SETBACK | 159.5 | 21269 | 0.007499177206 | 43.3 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH
90.1-2013 | SecondarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2013 | Food Preparation | General | ASHRAE 90.1-2013Food PreparationGeneral | 1.21 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 15.23 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | 532.1 | 0.1 | 0.2 | 0.7 | SchoolSecondary KITCHEN_GAS_EQUIP_SCH | 20.65 | 0.25 | 0.3 | 0.2 | SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_PSZ_AC | SchoolSecondary CLGSETP_SCH_NO_SETBACK | 133 | 2325 | 0.05720430108 | 49 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH | 0.7 | 4000 | 0.12154 | 0.338 | 694.5023 | 0.5 |  | SchoolSecondary Kitchen_Exhaust_SCH
90.1-2013 | SecondarySchool | Library | 230_196_120 | ASHRAE 90.1-2013 | Whole Building | Library | ASHRAE 90.1-2013Whole BuildingLibrary | 1.19 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | ASHRAE 62.1-2007 | Educational Facilities | Media center | ASHRAE 62.1-2007Educational FacilitiesMedia center | 0.12 | 10 |  | 10 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.93 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2013 | SecondarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2013 | Lobby | General | ASHRAE 90.1-2013LobbyGeneral | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2013 | SecondarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2013 | Electrical/Mechanical | General | ASHRAE 90.1-2013Electrical/MechanicalGeneral | 0.42 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_Setback | SchoolSecondary CLGSETP_SCH_Setback
90.1-2013 | SecondarySchool | Office | 120_230_199 | ASHRAE 90.1-2013 | Office-Enclosed | General | ASHRAE 90.1-2013Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 5 | SchoolSecondary BLDG_OCC_SCH_Offices | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | SchoolSecondary CLGSETP_SCH_NO_SETBACK
90.1-2013 | SecondarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2013 | Restrooms | General | ASHRAE 90.1-2013RestroomsGeneral | 0.98 |  |  |  | 0 | 0.37 | 0.2 | SchoolSecondary BLDG_LIGHT_BATH_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | SchoolSecondary BLDG_OCC_SCH | SchoolSecondary ACTIVITY_SCH | 0.0446 |  |  | SchoolSecondary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolSecondary BLDG_EQUIP_SCH | SchoolSecondary HTGSETP_SCH_Setback | SchoolSecondary CLGSETP_SCH_Setback | 52.2 | 2260 | 0.02309734513 | 43.3 | 0.2 | 0.05 | SchoolSecondary BLDG_SWH_SCH | 0.28122 | 635.6646 | 0.048826 | 0.338 | 110.3676 | 0.5
90.1-2010 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2010 | Food Preparation | General | ASHRAE 90.1-2010Food PreparationGeneral | 0.99 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 13.93 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | 453.7 | 0.1 | 0.2 | 0.7 | SchoolPrimary KITCHEN_GAS_EQUIP_SCH | 17.7 | 0.25 | 0.3 | 0.2 | SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | 100 | 1808 | 0.05530973451 | 49 | 0.2 | 0.05 | SchoolPrimary BLDG_SWH_SCH | 0.7 | 3300 | 0.12154 | 0.338 | 572.9644 | 0.5 |  | SchoolPrimary Kitchen_Exhaust_SCH
90.1-2010 | PrimarySchool | Gym | 154_230_120 | ASHRAE 90.1-2010 | Gymnasium/Fitness Center | Fitness Area | ASHRAE 90.1-2010Gymnasium/Fitness CenterFitness Area | 0.72 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_GYM_SCH | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) | ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | 0.3 |  |  | 30 | SchoolPrimary BLDG_OCC_SCH_Gym | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.46 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2010 | Corridor/Transition | General | ASHRAE 90.1-2010Corridor/TransitionGeneral | 0.66 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2010 | Classroom/Lecture/Training | General | ASHRAE 90.1-2010Classroom/Lecture/TrainingGeneral | 1.24 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (ages 5-8) | ASHRAE 62.1-2007Educational FacilitiesClassrooms (ages 5-8) | 0.12 | 10 |  | 25 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1.39 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2010 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2010 | Dining Area | General | ASHRAE 90.1-2010Dining AreaGeneral | 0.65 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 100 | SchoolPrimary BLDG_OCC_SCH_Cafeteria | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 2.36 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | PrimarySchool | Restroom | 169_169_31 | ASHRAE 90.1-2013 | Restrooms | General | ASHRAE 90.1-2013RestroomsGeneral | 0.98 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_BATH_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | 56.5 | 2045 | 0.02762836186 | 43.3 | 0.2 | 0.05 | SchoolPrimary BLDG_SWH_SCH | 0.29338 | 600 | 0.050938 | 0.338 | 104.1753 | 0.5
90.1-2013 | PrimarySchool | Office | 120_230_199 | ASHRAE 90.1-2013 | Office-Enclosed | General | ASHRAE 90.1-2013Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 5 | SchoolPrimary BLDG_OCC_SCH_Offices | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | PrimarySchool | Mechanical | 41_31_169 | ASHRAE 90.1-2013 | Electrical/Mechanical | General | ASHRAE 90.1-2013Electrical/MechanicalGeneral | 0.42 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | PrimarySchool | Lobby | 230_157_120 | ASHRAE 90.1-2013 | Lobby | General | ASHRAE 90.1-2013LobbyGeneral | 0.9 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | PrimarySchool | Library | 230_196_120 | ASHRAE 90.1-2013 | Whole Building | Library | ASHRAE 90.1-2013Whole BuildingLibrary | 1.19 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | ASHRAE 62.1-2007 | Educational Facilities | Media center | ASHRAE 62.1-2007Educational FacilitiesMedia center | 0.12 | 10 |  | 10 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1.39 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Retail | Back_Space | 120_149_230 | ASHRAE 90.1-2013 | Storage | General | ASHRAE 90.1-2013StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_BACK_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 15 | RetailStandalone BLDG_OCC_SCH_2010 | RetailStandalone ACTIVITY_SCH | 0.0446 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 0.75 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK
90.1-2013 | Retail | Entry | 169_31_31 | ASHRAE 90.1-2013 | Lobby | General | ASHRAE 90.1-2013LobbyGeneral | 0.9 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_ENTRY_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 |  | 15 | RetailStandalone BLDG_OCC_SCH_2010 | RetailStandalone ACTIVITY_SCH | 0.0446 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 0.3 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone FRONT_ENTRY_COOLING
90.1-2013 | Retail | Point_of_Sale | 171_222_78 | ASHRAE 90.1-2013 | Sales Area | General | ASHRAE 90.1-2013Sales AreaGeneral | 1.44 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_FRONT_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 |  | 15 | RetailStandalone BLDG_OCC_SCH_2010 | RetailStandalone ACTIVITY_SCH | 0.0446 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 2 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK
90.1-2013 | Retail | Retail | 171_222_78 | ASHRAE 90.1-2013 | Sales Area | General | ASHRAE 90.1-2013Sales AreaGeneral | 1.44 |  |  |  | 0 | 0.7 | 0.2 | RetailStandalone BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Retail | General Sales | ASHRAE 62.1-2007RetailGeneral Sales | 0.12 | 7.5 |  | 15 | RetailStandalone BLDG_OCC_SCH_2010 | RetailStandalone ACTIVITY_SCH | 0.0446 |  |  | RetailStandalone INFIL_SCH_PNNL | [5 empty] | 0.3 | 0 | 0.5 | 0 | RetailStandalone BLDG_EQUIP_SCH | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK
90.1-2013 | FullServiceRestaurant | Kitchen | 78_222_133 | ASHRAE 90.1-2013 | Food Preparation | General | ASHRAE 90.1-2013Food PreparationGeneral | 1.21 |  |  |  | 0 | 0.7 | 0.2 | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2010_2013 | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 5 | RestaurantSitDown BLDG_OCC_SCH | RestaurantSitDown ACTIVITY_SCH |  | 0.112 |  | RestaurantSitDown INFIL_HALF_ON_SCH | 205.81 | 0.1 | 0.2 | 0.7 | RestaurantSitDown Rest_GAS_EQUIP_SCH | 37.53 | 0.25 | 0.3 | 0.2 | RestaurantSitDown BLDG_EQUIP_SCH | RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | 133 | 1501 | 0.08860759494 | 49 | 0.2 | 0.05 | RestaurantSitDown BLDG_SWH_SCH | 0.7 | 4000 | 0.12154 | 0.338 | 694.5023 | 0.5 |  | RestaurantSitDown Kitchen_Exhaust_SCH
90.1-2013 | FullServiceRestaurant | Dining | 31_169_34 | ASHRAE 90.1-2013 | Dining Area | For Family Dining | ASHRAE 90.1-2013Dining AreaFor Family Dining | 0.89 |  |  |  | 0 | 0.7 | 0.2 | RestaurantSitDown BLDG_LIGHT_DINING_SCH_2013 | ASHRAE 62.1-2007 | Food and Beverage Service | Restaurant dining rooms | ASHRAE 62.1-2007Food and Beverage ServiceRestaurant dining rooms | 0.18 | 7.5 |  | 70 | RestaurantSitDown BLDG_OCC_SCH | RestaurantSitDown ACTIVITY_SCH |  | 0.112 |  | RestaurantSitDown INFIL_HALF_ON_SCH | [5 empty] | 6.032 | 0.25 | 0.3 | 0 | RestaurantSitDown BLDG_EQUIP_SCH | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | FullServiceRestaurant | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0
90.1-2007 | StripMall | Strip mall - type 2 | 171_222_78 | ASHRAE 90.1-2007 | Whole Building | Retail | ASHRAE 90.1-2007Whole BuildingRetail | 1.5 |  |  | 0.5 | 0 | 0.7 | 0.2 | RetailStripmall Type2_LIGHT_SCH | ASHRAE 62.1-2004 | Retail | General Sales combined by area | ASHRAE 62.1-2004RetailGeneral Sales combined by area | 0.2325 | 0 |  | 8 | RetailStripmall Type2_OCC_SCH | HotelSmall Activity_Sch | 0.062879 |  |  | RetailStripmall Type2_Infil_SCH | [5 empty] | 0.4 | 0 | 0.5 | 0 | RetailStripmall Type2_EQUIP_SCH | RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type2_CLGSETP_SCH_NO_SETBACK | 1.8 | [5 empty] | RetailStripmall Type2_SWH_SCH
90.1-2007 | StripMall | Strip mall - type 3 | 171_222_78 | ASHRAE 90.1-2007 | Whole Building | Retail | ASHRAE 90.1-2007Whole BuildingRetail | 1.5 |  |  | 0.07 | 0 | 0.7 | 0.2 | RetailStripmall Type3_LIGHT_SCH | ASHRAE 62.1-2004 | Retail | General Sales combined by area | ASHRAE 62.1-2004RetailGeneral Sales combined by area | 0.2325 | 0 |  | 8 | RetailStripmall Type3_OCC_SCH | HotelSmall Activity_Sch | 0.062879 |  |  | RetailStripmall Type3_Infil_SCH | [5 empty] | 0.4 | 0 | 0.5 | 0 | RetailStripmall Type3_EQUIP_SCH | RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type3_CLGSETP_SCH_NO_SETBACK | 1.8 | [5 empty] | RetailStripmall Type3_SWH_SCH
90.1-2004 | StripMall | Strip mall - type 1 | 171_222_78 | ASHRAE 90.1-2004 | Whole Building | Retail | ASHRAE 90.1-2004Whole BuildingRetail | 1.5 |  |  | 0.95 | 0 | 0.7 | 0.2 | RetailStripmall Type1_LIGHT_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 8 | RetailStripmall Type1_OCC_SCH | HotelSmall Activity_Sch | 0.089168 |  |  | RetailStripmall Type1_Infil_SCH | [5 empty] | 0.4 | 0 | 0.5 | 0 | RetailStripmall Type1_EQUIP_SCH | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | 1.8 | [5 empty] | RetailStripmall Type1_SWH_SCH
90.1-2004 | StripMall | Strip mall - type 2 | 171_222_78 | ASHRAE 90.1-2004 | Whole Building | Retail | ASHRAE 90.1-2004Whole BuildingRetail | 1.5 |  |  | 0.375 | 0 | 0.7 | 0.2 | RetailStripmall Type2_LIGHT_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 8 | RetailStripmall Type2_OCC_SCH | HotelSmall Activity_Sch | 0.062879 |  |  | RetailStripmall Type2_Infil_SCH | [5 empty] | 0.4 | 0 | 0.5 | 0 | RetailStripmall Type2_EQUIP_SCH | RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type2_CLGSETP_SCH_NO_SETBACK | 1.8 | [5 empty] | RetailStripmall Type2_SWH_SCH
90.1-2004 | StripMall | Strip mall - type 3 | 171_222_78 | ASHRAE 90.1-2004 | Whole Building | Retail | ASHRAE 90.1-2004Whole BuildingRetail | 1.5 |  |  |  | 0 | 0.7 | 0.2 | RetailStripmall Type3_LIGHT_SCH | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 8 | RetailStripmall Type3_OCC_SCH | HotelSmall Activity_Sch | 0.062879 |  |  | RetailStripmall Type3_Infil_SCH | [5 empty] | 0.4 | 0 | 0.5 | 0 | RetailStripmall Type3_EQUIP_SCH | RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type3_CLGSETP_SCH_NO_SETBACK | 1.8 | [5 empty] | RetailStripmall Type3_SWH_SCH
DOE Ref 1980-2004 | StripMall | Strip mall - type 1 | 171_222_78 | DOE Ref 1980-2004 | StripMall | WholeBuilding | DOE Ref 1980-2004StripMallWholeBuilding | 5.5983 |  |  |  | 0 | 0.7 | 0.2 | StripMall Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | StripMall Bldg Occ | StripMall Activity | 0.22303 |  |  | StripMall Infil Half On | [5 empty] | 0.4 | 0 | 0.5 | 0 | StripMall Bldg Equip | StripMall HtgSetp | StripMall ClgSetp | 1.8
DOE Ref 1980-2004 | StripMall | Strip mall - type 2 | 171_222_78 | DOE Ref 1980-2004 | StripMall | WholeBuilding | DOE Ref 1980-2004StripMallWholeBuilding | 3.299 |  |  |  | 0 | 0.7 | 0.2 | StripMall Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | StripMall Bldg Occ | StripMall Activity | 0.22303 |  |  | StripMall Infil Half On | [5 empty] | 0.4 | 0 | 0.5 | 0 | StripMall Bldg Equip | StripMall HtgSetp | StripMall ClgSetp | 1.8
DOE Ref 1980-2004 | StripMall | Strip mall - type 3 | 171_222_78 | DOE Ref 1980-2004 | StripMall | WholeBuilding | DOE Ref 1980-2004StripMallWholeBuilding | 2.6988 |  |  |  | 0 | 0.7 | 0.2 | StripMall Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | StripMall Bldg Occ | StripMall Activity | 0.22303 |  |  | StripMall Infil Half On | [5 empty] | 0.4 | 0 | 0.5 | 0 | StripMall Bldg Equip | StripMall HtgSetp | StripMall ClgSetp | 1.8
DOE Ref Pre-1980 | StripMall | Strip mall - type 1 | 171_222_78 | DOE Ref Pre-1980 | StripMall | WholeBuilding | DOE Ref Pre-1980StripMallWholeBuilding | 5.5983 |  |  |  | 0 | 0.7 | 0.2 | StripMall Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | StripMall Bldg Occ | StripMall Activity | 0.22303 |  |  | StripMall Infil Half On | [5 empty] | 0.4 | 0 | 0.5 | 0 | StripMall Bldg Equip | StripMall HtgSetp | StripMall ClgSetp | 1.8
DOE Ref Pre-1980 | StripMall | Strip mall - type 2 | 171_222_78 | DOE Ref Pre-1980 | StripMall | WholeBuilding | DOE Ref Pre-1980StripMallWholeBuilding | 3.299 |  |  |  | 0 | 0.7 | 0.2 | StripMall Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | StripMall Bldg Occ | StripMall Activity | 0.22303 |  |  | StripMall Infil Half On | [5 empty] | 0.4 | 0 | 0.5 | 0 | StripMall Bldg Equip | StripMall HtgSetp | StripMall ClgSetp | 1.8
DOE Ref Pre-1980 | StripMall | Strip mall - type 3 | 171_222_78 | DOE Ref Pre-1980 | StripMall | WholeBuilding | DOE Ref Pre-1980StripMallWholeBuilding | 2.6988 |  |  |  | 0 | 0.7 | 0.2 | StripMall Bldg Light | ASHRAE 62.1-1999 | Retail Stores, Sales Floors, and Show Room Floors | Basement and street | ASHRAE 62.1-1999Retail Stores, Sales Floors, and Show Room FloorsBasement and street | 0.3 | 0 |  | 15 | StripMall Bldg Occ | StripMall Activity | 0.22303 |  |  | StripMall Infil Half On | [5 empty] | 0.4 | 0 | 0.5 | 0 | StripMall Bldg Equip | StripMall HtgSetp | StripMall ClgSetp | 1.8
90.1-2013 | PrimarySchool | Kitchen | 78_222_133 | ASHRAE 90.1-2013 | Food Preparation | General | ASHRAE 90.1-2013Food PreparationGeneral | 1.21 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 13.93 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | 453.7 | 0.1 | 0.2 | 0.7 | SchoolPrimary KITCHEN_GAS_EQUIP_SCH | 17.7 | 0.25 | 0.3 | 0.2 | SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | 100 | 1808 | 0.05530973451 | 49 | 0.2 | 0.05 | SchoolPrimary BLDG_SWH_SCH | 0.7 | 3300 | 0.12154 | 0.338 | 572.9644 | 0.5 |  | SchoolPrimary Kitchen_Exhaust_SCH
90.1-2013 | PrimarySchool | Gym | 154_230_120 | ASHRAE 90.1-2013 | Gymnasium/Fitness Center | Exercise Area | ASHRAE 90.1-2013Gymnasium/Fitness CenterExercise Area | 1.2 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_GYM_SCH | ASHRAE 62.1-2007 | Sports and Entertainment | Gym, stadium (play area) | ASHRAE 62.1-2007Sports and EntertainmentGym, stadium (play area) | 0.3 |  |  | 30 | SchoolPrimary BLDG_OCC_SCH_Gym | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.46 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | PrimarySchool | Corridor | 169_31_31 | ASHRAE 90.1-2013 | Corridor | General | ASHRAE 90.1-2013CorridorGeneral | 0.66 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | PrimarySchool | Classroom | 120_230_199 | ASHRAE 90.1-2013 | Classroom/Lecture/Training | General | ASHRAE 90.1-2013Classroom/Lecture/TrainingGeneral | 1.24 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | ASHRAE 62.1-2007 | Educational Facilities | Classrooms (ages 5-8) | ASHRAE 62.1-2007Educational FacilitiesClassrooms (ages 5-8) | 0.12 | 10 |  | 25 | SchoolPrimary BLDG_OCC_SCH | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 1.39 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | PrimarySchool | Cafeteria | 31_169_34 | ASHRAE 90.1-2013 | Dining Area | General | ASHRAE 90.1-2013Dining AreaGeneral | 0.65 |  |  |  | 0 | 0.37 | 0.2 | SchoolPrimary BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 100 | SchoolPrimary BLDG_OCC_SCH_Cafeteria | SchoolPrimary ACTIVITY_SCH | 0.0446 |  |  | SchoolPrimary INFIL_SCH_PNNL | [5 empty] | 2.36 | 0 | 0.5 | 0 | SchoolPrimary BLDG_EQUIP_SCH | SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | SchoolPrimary CLGSETP_SCH_NO_OPTIMUM
DOE Ref 1980-2004 | PrimarySchool | Restroom | 169_169_31 | DOE Ref 1980-2004 | PrimarySchool | Restroom | DOE Ref 1980-2004PrimarySchoolRestroom | 0.9 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 56.5 | 2045 | 0.02762836186 | 43.3 | 0.2 | 0.05 | PrimarySchool SWH | 0.29338 | 600 | 0.05093797833 | 0.338 | 104.1753 | 0.5
DOE Ref 1980-2004 | PrimarySchool | Office | 120_230_199 | DOE Ref 1980-2004 | PrimarySchool | Office | DOE Ref 1980-2004PrimarySchoolOffice | 1.89 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 4.65 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 1 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref 1980-2004 | PrimarySchool | Mechanical | 41_31_169 | DOE Ref 1980-2004 | PrimarySchool | Mechanical | DOE Ref 1980-2004PrimarySchoolMechanical | 0.77 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0.93 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
DOE Ref 1980-2004 | PrimarySchool | Lobby | 230_157_120 | DOE Ref 1980-2004 | PrimarySchool | Lobby | DOE Ref 1980-2004PrimarySchoolLobby | 1.14 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 0 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref 1980-2004 | PrimarySchool | Library | 230_196_120 | DOE Ref 1980-2004 | PrimarySchool | Library | DOE Ref 1980-2004PrimarySchoolLibrary | 2.11 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 |  | 21.36 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 1.39 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref 1980-2004 | PrimarySchool | Kitchen | 78_222_133 | DOE Ref 1980-2004 | PrimarySchool | Kitchen | DOE Ref 1980-2004PrimarySchoolKitchen | 1.6 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 13.93 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | 302.6 | 0.1 | 0.2 | 0.7 | PrimarySchool Kitchen Gas | 17.7 | 0.25 | 0.3 | 0.2 | PrimarySchool Kitchen Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 100 | 1808 | 0.05530973451 | 49 | 0.2 | 0.05 | PrimarySchool SWH | 0.7 | 3300 | 0.1215379059 | 0.338 | 572.9644 | 0.5 |  | PrimarySchool Kitchen Exhaust
DOE Ref 1980-2004 | PrimarySchool | Gym | 154_230_120 | DOE Ref 1980-2004 | PrimarySchool | Gym | DOE Ref 1980-2004PrimarySchoolGym | 1.07 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 |  | 27.9 | PrimarySchool Gym Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref 1980-2004 | PrimarySchool | Corridor | 169_31_31 | DOE Ref 1980-2004 | PrimarySchool | Corridor | DOE Ref 1980-2004PrimarySchoolCorridor | 0.9 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
DOE Ref 1980-2004 | PrimarySchool | Classroom | 120_230_199 | DOE Ref 1980-2004 | PrimarySchool | Classroom | DOE Ref 1980-2004PrimarySchoolClassroom | 2 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 |  | 23.22 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 1.39 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref 1980-2004 | PrimarySchool | Cafeteria | 31_169_34 | DOE Ref 1980-2004 | PrimarySchool | Cafeteria | DOE Ref 1980-2004PrimarySchoolCafeteria | 1.4 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 66.67 | PrimarySchool Cafeteria Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 2.36 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref Pre-1980 | PrimarySchool | Restroom | 169_169_31 | DOE Ref Pre-1980 | PrimarySchool | Restroom | DOE Ref Pre-1980PrimarySchoolRestroom | 0.9 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Public restrooms (Assume 12 toilet/625 ft^2) | ASHRAE 62.1-1999Public SpacesPublic restrooms (Assume 12 toilet/625 ft^2) | 0.96 | 0 |  | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 56.5 | 2045 | 0.02762836186 | 43.3 | 0.2 | 0.05 | PrimarySchool SWH | 0.29338 | 600 | 0.05093797833 | 0.338 | 104.1753 | 0.5
DOE Ref Pre-1980 | PrimarySchool | Office | 120_230_199 | DOE Ref Pre-1980 | PrimarySchool | Office | DOE Ref Pre-1980PrimarySchoolOffice | 1.89 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Offices | Office Space | ASHRAE 62.1-1999OfficesOffice Space | 0 | 20 |  | 4.65 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 1 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref Pre-1980 | PrimarySchool | Mechanical | 41_31_169 | DOE Ref Pre-1980 | PrimarySchool | Mechanical | DOE Ref Pre-1980PrimarySchoolMechanical | 0.77 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Public Spaces | Corridors and utilities | ASHRAE 62.1-1999Public SpacesCorridors and utilities | 0.05 | 0 |  | 0.93 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
DOE Ref Pre-1980 | PrimarySchool | Lobby | 230_157_120 | DOE Ref Pre-1980 | PrimarySchool | Lobby | DOE Ref Pre-1980PrimarySchoolLobby | 1.14 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 0 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref Pre-1980 | PrimarySchool | Library | 230_196_120 | DOE Ref Pre-1980 | PrimarySchool | Library | DOE Ref Pre-1980PrimarySchoolLibrary | 2.11 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Libraries | ASHRAE 62.1-1999EducationLibraries | 0 | 16.95 |  | 21.36 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 1.39 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref Pre-1980 | PrimarySchool | Kitchen | 78_222_133 | DOE Ref Pre-1980 | PrimarySchool | Kitchen | DOE Ref Pre-1980PrimarySchoolKitchen | 1.6 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Kitchens (cooking) | ASHRAE 62.1-1999Food and Beverage ServiceKitchens (cooking) | 0 | 15 |  | 13.93 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | 302.6 | 0.1 | 0.2 | 0.7 | PrimarySchool Kitchen Gas | 17.7 | 0.25 | 0.3 | 0.2 | PrimarySchool Kitchen Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp | 100 | 1808 | 0.05530973451 | 49 | 0.2 | 0.05 | PrimarySchool SWH | 0.7 | 3300 | 0.1215379059 | 0.338 | 572.9644 | 0.5 |  | PrimarySchool Kitchen Exhaust
DOE Ref Pre-1980 | PrimarySchool | Gym | 154_230_120 | DOE Ref Pre-1980 | PrimarySchool | Gym | DOE Ref Pre-1980PrimarySchoolGym | 1.07 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Sports and Amusement | Playing floors (gymnasium) | ASHRAE 62.1-1999Sports and AmusementPlaying floors (gymnasium) | 0 | 20 |  | 27.9 | PrimarySchool Gym Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 0.46 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref Pre-1980 | PrimarySchool | Corridor | 169_31_31 | DOE Ref Pre-1980 | PrimarySchool | Corridor | DOE Ref Pre-1980PrimarySchoolCorridor | 0.9 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Corridors | ASHRAE 62.1-1999EducationCorridors | 0.1 | 0 |  | 9.29 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 0.37 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool BathCorrMechKitchen HtgSetp | PrimarySchool BathCorrMechKitchen ClgSetp
DOE Ref Pre-1980 | PrimarySchool | Classroom | 120_230_199 | DOE Ref Pre-1980 | PrimarySchool | Classroom | DOE Ref Pre-1980PrimarySchoolClassroom | 2 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Education | Classroom | ASHRAE 62.1-1999EducationClassroom | 0 | 16.95 |  | 23.22 | PrimarySchool Bldg Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 1.39 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
DOE Ref Pre-1980 | PrimarySchool | Cafeteria | 31_169_34 | DOE Ref Pre-1980 | PrimarySchool | Cafeteria | DOE Ref Pre-1980PrimarySchoolCafeteria | 1.4 |  |  |  | 0 | 0.37 | 0.2 | PrimarySchool Bldg Light | ASHRAE 62.1-1999 | Food and Beverage Service | Cafeteria, fast food | ASHRAE 62.1-1999Food and Beverage ServiceCafeteria, fast food | 0 | 20 |  | 66.67 | PrimarySchool Cafeteria Occ | PrimarySchool Activity |  | 0.2232 |  | PrimarySchool Infil | [5 empty] | 2.36 | 0 | 0.5 | 0 | PrimarySchool Bldg Equip | PrimarySchool HtgSetp | PrimarySchool ClgSetp
90.1-2013 | Outpatient | Xray | 169_31_159 | ASHRAE 90.1-2013 | Healthcare Facility | Radiology/Imaging | ASHRAE 90.1-2013Healthcare FacilityRadiology/Imaging | 1.51 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.95 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 900 | 0.001111111111 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2013 | Outpatient | Toilet | 169_169_31 | ASHRAE 90.1-2013 | Restrooms | General | ASHRAE 90.1-2013RestroomsGeneral | 0.98 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.29 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | [7 empty] | 1.6667 | 90 | 0.63103 | 0.31 | 34.0754 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2013 | Outpatient | Stair | 230_157_120 | ASHRAE 90.1-2013 | Stairway | General | ASHRAE 90.1-2013StairwayGeneral | 0.69 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | Soil Work | 204_120_230 | ASHRAE 90.1-2013 | Healthcare Facility | Medical Supply | ASHRAE 90.1-2013Healthcare FacilityMedical Supply | 0.74 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Soiled Linen, Sorting | GGHC v2.2Health CareSoiled Linen, Sorting | 1.5 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | [7 empty] | 1.6667 | 210 | 0.63103 | 0.31 | 79.5093 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2013 | Outpatient | ProcedureRoom | 169_31_159 | ASHRAE 90.1-2013 | Healthcare Facility | Operating Room | ASHRAE 90.1-2013Healthcare FacilityOperating Room | 2.48 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 285 | 0.00350877193 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2013 | Outpatient | PreOp | 169_31_159 | ASHRAE 90.1-2013 | Healthcare Facility | Patient Room | ASHRAE 90.1-2013Healthcare FacilityPatient Room | 0.62 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Patient Room | GGHC v2.2Health CarePatient Room | 0.3 |  |  | 9.29 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 263.5 | 0.003795066414 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2013 | Outpatient | PhysicalTherapy | 154_230_120 | ASHRAE 90.1-2013 | Healthcare Facility | Physical Therapy | ASHRAE 90.1-2013Healthcare FacilityPhysical Therapy | 0.91 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Physical therapy | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPhysical therapy |  | 15 |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.09 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 946 | 0.001057082452 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2013 | Outpatient | PACU | 169_31_159 | ASHRAE 90.1-2013 | Healthcare Facility | Recovery | ASHRAE 90.1-2013Healthcare FacilityRecovery | 1.15 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Recovery | GGHC v2.2Health CareRecovery | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 108 | 0.009259259259 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2013 | Outpatient | OR | 169_31_159 | ASHRAE 90.1-2013 | Healthcare Facility | Operating Room | ASHRAE 90.1-2013Healthcare FacilityOperating Room | 2.48 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | AIA 2001 | Surgery and Critical Care | Operating/Surgical Cystoscopic Rooms | AIA 2001Surgery and Critical CareOperating/Surgical Cystoscopic Rooms |  |  | 3 | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | 17.4 | 0 | 0 | 0.5 | OutPatientHealthCare BLDG_EQUIP_SCH | 2.92 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare OR_HTGSETP_SCH | OutPatientHealthCare OR_CLGSETP_SCH | 6 | 470 | 0.01276595745 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH
90.1-2013 | Outpatient | Office | 120_230_199 | ASHRAE 90.1-2013 | Office-Enclosed | General | ASHRAE 90.1-2013Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | NurseStation | 31_162_169 | ASHRAE 90.1-2013 | Healthcare Facility | Nurse Station | ASHRAE 90.1-2013Healthcare FacilityNurse Station | 0.71 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | MRI_Control | 136_78_222 | ASHRAE 90.1-2013 | Healthcare Facility | Radiology/Imaging | ASHRAE 90.1-2013Healthcare FacilityRadiology/Imaging | 1.51 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 168 | 0.005952380952 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1 | 168 | 0.37862 | 0.31 | 63.6075 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2013 | Outpatient | MRI | 169_31_159 | ASHRAE 90.1-2013 | Healthcare Facility | Radiology/Imaging | ASHRAE 90.1-2013Healthcare FacilityRadiology/Imaging | 1.51 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | X-ray, Diagnostic and Treatment | GGHC v2.2Health CareX-ray, Diagnostic and Treatment | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 38.63 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 440 | 0.002272727273 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1 | 440 | 0.37862 | 0.31 | 166.5909 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2013 | Outpatient | MedGas | 204_120_230 | ASHRAE 90.1-2013 | Storage | General | ASHRAE 90.1-2013StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.07 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | Lounge | 230_157_120 | ASHRAE 90.1-2013 | Lounge/Recreation | For Healthcare Facility | ASHRAE 90.1-2013Lounge/RecreationFor Healthcare Facility | 0.92 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Hotels, Motels, Resorts, Dormitories | Lobbies/prefunction | ASHRAE 62.1-2007Hotels, Motels, Resorts, DormitoriesLobbies/prefunction | 0.06 | 7.5 |  | 13.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | LockerRoom | 169_169_31 | ASHRAE 90.1-2013 | Locker Room | General | ASHRAE 90.1-2013Locker RoomGeneral | 0.75 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Lockers | GGHC v2.2Health CareLockers | 0.15 |  |  | 13.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 2.19 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | Lobby | 230_157_120 | ASHRAE 90.1-2013 | Lobby | General | ASHRAE 90.1-2013LobbyGeneral | 0.9 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2007Office BuildingsMain entry lobbies | 0.06 | 5 |  | 27.87 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | Janitor | 120_149_230 | ASHRAE 90.1-2013 | Storage | General | ASHRAE 90.1-2013StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | GGHC v2.2 | Health Care | Janitors Closet / Utility | GGHC v2.2Health CareJanitors Closet / Utility | 1.5 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | IT_Room | 41_31_169 | ASHRAE 90.1-2013 | Office-Enclosed | General | ASHRAE 90.1-2013Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | ASHRAE 62.1-2007Office BuildingsTelephone/data entry | 0.06 | 5 |  | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | Hall | 169_31_31 | ASHRAE 90.1-2013 | Corridor | For Hospital | ASHRAE 90.1-2013CorridorFor Hospital | 0.99 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.29 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | Exam | 136_78_222 | ASHRAE 90.1-2013 | Healthcare Facility | Exam/Treatment | ASHRAE 90.1-2013Healthcare FacilityExam/Treatment | 1.66 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | GGHC v2.2 | Health Care | Special Procedure Room, Diagnostic | GGHC v2.2Health CareSpecial Procedure Room, Diagnostic | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2013 | Electrical/Mechanical | General | ASHRAE 90.1-2013Electrical/MechanicalGeneral | 0.42 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | GGHC v2.2 | Health Care | Mechanical Equipment Room | GGHC v2.2Health CareMechanical Equipment Room | 0.15 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 3.64 | 0 | 0.3 | 0.7 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | DressingRoom | 136_78_222 | ASHRAE 90.1-2013 | Dressing/Fitting Room | For Retail | ASHRAE 90.1-2013Dressing/Fitting RoomFor Retail | 0.71 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Hospitals, Nursing and Convalescent Homes | Patient rooms | ASHRAE 62.1-2007Hospitals, Nursing and Convalescent HomesPatient rooms |  | 25 |  | 4.65 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.8 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | Conference | 230_196_120 | ASHRAE 90.1-2013 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2013Conference/Meeting/MultipurposeGeneral | 1.23 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 |  | 46.45 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.73 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | CleanWork | 204_120_230 | ASHRAE 90.1-2013 | Healthcare Facility | Medical Supply | ASHRAE 90.1-2013Healthcare FacilityMedical Supply | 0.74 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Clean Utility / Workroom | GGHC v2.2Health CareClean Utility / Workroom | 0.3 |  |  | 18.58 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | Cafe | 31_169_34 | ASHRAE 90.1-2013 | Dining Area | General | ASHRAE 90.1-2013Dining AreaGeneral | 0.65 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Food and Beverage Service | Cafeteria/fast food dining | ASHRAE 62.1-2007Food and Beverage ServiceCafeteria/fast food dining | 0.18 | 7.5 |  | 92.94 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.73 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | BioHazard | 204_120_230 | ASHRAE 90.1-2013 | Storage | General | ASHRAE 90.1-2013StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Bedpan Room | GGHC v2.2Health CareBedpan Room | 0.15 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 0.07 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Outpatient | Anesthesia | 204_120_230 | ASHRAE 90.1-2013 | Healthcare Facility | Operating Room | ASHRAE 90.1-2013Healthcare FacilityOperating Room | 2.48 |  |  |  | 0 | 0.7 | 0.2 | OutPatientHealthCare BLDG_LIGHT_SCH | GGHC v2.2 | Health Care | Anesthesia Storage | GGHC v2.2Health CareAnesthesia Storage | 1.2 |  |  | 0 | OutPatientHealthCare BLDG_OCC_SCH | OutPatientHealthCare ACTIVITY_SCH | 0.0446 |  |  | OutPatientHealthCare INFIL_SCH | [5 empty] | 1.46 | 0 | 0.5 | 0 | OutPatientHealthCare BLDG_EQUIP_SCH_BASE | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | 1 | 108 | 0.009259259259 | 43.3 | 0.2 | 0.05 | OutPatientHealthCare BLDG_SWH_SCH | 1.3333 | 144 | 0.50482 | 0.31 | 54.5207 | 1 |  | OutPatientHealthCare Hours_of_operation
90.1-2013 | SuperMarket | Sales/Produce | 230_196_120 | ASHRAE 90.1-2013 | Sales Area | General | ASHRAE 90.1-2013Sales AreaGeneral | 1.44 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | Retail | Supermarket | ASHRAE 62.1-2007RetailSupermarket | 0.06 | 7.5 |  | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | [5 empty] | 0.36 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2013 | SuperMarket | Office | 120_230_199 | ASHRAE 90.1-2013 | Office-Enclosed | General | ASHRAE 90.1-2013Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 5 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2013 | SuperMarket | DryStorage | 120_149_230 | ASHRAE 90.1-2013 | Storage | General | ASHRAE 90.1-2013StorageGeneral | 0.63 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 3.33 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | [5 empty] | 0.54 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp
90.1-2013 | SuperMarket | Deli/Bakery | 31_169_34 | ASHRAE 90.1-2013 | Sales Area | General | ASHRAE 90.1-2013Sales AreaGeneral | 1.44 |  |  |  | 0 | 0.7 | 0.2 | SuperMarket Bldg Light | ASHRAE 62.1-2007 | Retail | Supermarket | ASHRAE 62.1-2007RetailSupermarket | 0.06 | 7.5 |  | 8 | SuperMarket Bldg Occ | SuperMarket Activity | 0.0446 |  |  | SuperMarket Infil Half On | 6.25 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | 3.64 | 0 | 0.5 | 0 | SuperMarket Bldg Equip | SuperMarket HtgSetp | SuperMarket ClgSetp | 5 | 2334.5 | 0.00214178625 | 49 | 0.2 | 0.05 | SuperMarket SWH | 1.2403 | 3000 | 0.21534 | 0.338 | 520.8767 | 0.5 |  | SuperMarket_Deli_Exhaust
90.1-2013 | Warehouse | Office | 120_230_199 | ASHRAE 90.1-2013 | Office-Enclosed | General | ASHRAE 90.1-2013Office-EnclosedGeneral | 1.11 |  |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_OFFICE_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 1.96 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0446 |  |  | Warehouse ALWAYS_ON | [5 empty] | 0.54 | 0 | 0.5 | 0 | Warehouse Office_Plug_SCH | Warehouse HtgSetp | Warehouse ClgSetp
90.1-2013 | Warehouse | Fine | 120_149_230 | ASHRAE 90.1-2013 | Warehouse | Fine Material Storage | ASHRAE 90.1-2013WarehouseFine Material Storage | 0.95 |  |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses | ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | 0.06 |  |  | 0 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0446 |  |  | Warehouse ALWAYS_ON | [5 empty] | 0 | 0 | 0.5 | 0 | Warehouse ALWAYS_OFF | Warehouse Fine Storage Heating Setpoint Schedule | Warehouse Fine Storage Cooling Setpoint Schedule
90.1-2013 | Warehouse | Bulk | 41_31_169 | ASHRAE 90.1-2013 | Warehouse | Medium/Bulky Material Storage | ASHRAE 90.1-2013WarehouseMedium/Bulky Material Storage | 0.58 |  |  |  | 0 | 0.5 | 0.2 | Warehouse BLDG_LIGHT_STORAGE_SCH | ASHRAE 62.1-2007 | Miscellaneous Spaces | Warehouses | ASHRAE 62.1-2007Miscellaneous SpacesWarehouses | 0.06 |  |  | 0 | Warehouse BLDG_OCC_SCH | Warehouse Office Activity Schedule | 0.0446 |  |  | Warehouse ALWAYS_ON | [5 empty] | 0.17 | 0 | 0.5 | 0 | Warehouse ALWAYS_OFF | Warehouse Bulk Storage Heating Setpoint Schedule | Warehouse ClgSetp
90.1-2013 | Office | Vending | 230_157_120 | ASHRAE 90.1-2013 | Corridor | General | ASHRAE 90.1-2013CorridorGeneral | 0.66 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 1 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 3.85 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Office | Storage | 120_149_230 | ASHRAE 90.1-2013 | Storage | General | ASHRAE 90.1-2013StorageGeneral | 0.63 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Office | Stair | 230_157_120 | ASHRAE 90.1-2013 | Stairway | General | ASHRAE 90.1-2013StairwayGeneral | 0.69 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Office | Restroom | 169_169_31 | ASHRAE 90.1-2013 | Restrooms | General | ASHRAE 90.1-2013RestroomsGeneral | 0.98 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.07 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM |  |  |  | 43.3 | 0.2 | 0.05 | OfficeMedium BLDG_SWH_SCH
90.1-2013 | Office | PrintRoom | 41_31_169 | ASHRAE 90.1-2013 | Office-Enclosed | General | ASHRAE 90.1-2013Office-EnclosedGeneral | 1.11 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 2.79 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Office | OpenOffice | 120_230_199 | ASHRAE 90.1-2013 | Office-Open Plan | General | ASHRAE 90.1-2013Office-Open PlanGeneral | 0.98 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 5.25 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.71 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Office | Lobby | 230_157_120 | ASHRAE 90.1-2013 | Lobby | General | ASHRAE 90.1-2013LobbyGeneral | 0.9 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Main entry lobbies | ASHRAE 62.1-2007Office BuildingsMain entry lobbies | 0.06 | 5 |  | 10 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.07 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Office | IT_Room | 41_31_169 | ASHRAE 90.1-2013 | Office-Enclosed | General | ASHRAE 90.1-2013Office-EnclosedGeneral | 1.11 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Telephone/data entry | ASHRAE 62.1-2007Office BuildingsTelephone/data entry | 0.06 | 5 |  | 5 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 1.56 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Office | Elec/MechRoom | 41_31_169 | ASHRAE 90.1-2013 | Electrical/Mechanical | General | ASHRAE 90.1-2013Electrical/MechanicalGeneral | 0.42 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Storage rooms | ASHRAE 62.1-2007GeneralStorage rooms | 0.12 |  |  | 0 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.27 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Office | Corridor | 169_31_31 | ASHRAE 90.1-2013 | Corridor | General | ASHRAE 90.1-2013CorridorGeneral | 0.66 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Corridors | ASHRAE 62.1-2007GeneralCorridors | 0.06 |  |  | 1 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.16 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Office | Conference | 230_196_120 | ASHRAE 90.1-2013 | Conference/Meeting/Multipurpose | General | ASHRAE 90.1-2013Conference/Meeting/MultipurposeGeneral | 1.23 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 |  | 50 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.37 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Office | ClosedOffice | 120_230_199 | ASHRAE 90.1-2013 | Office-Enclosed | General | ASHRAE 90.1-2013Office-EnclosedGeneral | 1.11 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | Office Buildings | Office space | ASHRAE 62.1-2007Office BuildingsOffice space | 0.06 | 5 |  | 4.75 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 0.64 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Office | BreakRoom | 230_157_120 | ASHRAE 90.1-2013 | Lounge/Recreation | General | ASHRAE 90.1-2013Lounge/RecreationGeneral | 0.73 |  |  |  | 0.4 | 0.4 | 0.2 | OfficeMedium BLDG_LIGHT_SCH | ASHRAE 62.1-2007 | General | Conference/meeting | ASHRAE 62.1-2007GeneralConference/meeting | 0.06 | 5 |  | 50 | OfficeMedium BLDG_OCC_SCH | OfficeMedium ACTIVITY_SCH | 0.0446 |  |  | OfficeMedium INFIL_SCH_PNNL | [5 empty] | 4.46 | 0 | 0.5 | 0 | OfficeMedium BLDG_EQUIP_SCH | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_OPTIMUM
90.1-2013 | Office | Attic | 120_149_230 | ASHRAE 189.1-2009 | Attics | General | ASHRAE 189.1-2009AtticsGeneral | 0 | [17 empty] | 0.112 |  |  | OfficeMedium INFIL_SCH_PNNL

## Construction Sets
A Construction Set lists the typical constructions for each surface type in a building for a given building type and climate zone.
|  |  |  | Exterior Surfaces | [5 empty] | Interior Surfaces |  |  | Ground Contact Surfaces | [5 empty] | Exterior Sub Surfaces | [12 empty] | Interior Sub Surfaces |  |  | Misc Surfaces
Template | Building Type | Space Type | Is Residential | Exterior Wall Standards Construction Type | Exterior Wall Building Category | Exterior Floor Standards Construction Type | Exterior Floor Building Category | Exterior Roof Standards Construction Type | Exterior Roof Building Category | Interior Walls | Interior Floors | Interior Ceilings | Ground Contact Wall Standards Construction Type | Ground Contact Wall Building Category | Ground Contact Floor Standards Construction Type | Ground Contact Floor Building Category | Ground Contact Ceiling Standards Construction Type | Ground Contact Ceiling Building Category | Exterior Fixed Window Standards Construction Type | Exterior Fixed Window Building Category | Exterior Operable Window Standards Construction Type | Exterior Operable Window Building Category | Exterior Door Standards Construction Type | Exterior Door Building Category | Exterior Glass Doors | Exterior Overhead Door Standards Construction Type | Exterior Overhead Door Building Category | Exterior Skylight Standards Construction Type | Exterior Skylight Building Category | Tubular Daylight Domes | Tubular Daylight Diffusers | Interior Fixed Windows | Interior Operable Windows | Interior Doors | Space Shading | Building Shading | Site Shading | Interior Partitions
189.1-2009 | FullServiceRestaurant |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | Hospital |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | Hospital | PatRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | LargeHotel |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | LargeHotel | GuestRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | MidriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Hospital |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Hospital | PatRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | Outpatient |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | PrimarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | QuickServiceRestaurant |  | No | WoodFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | LargeHotel |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | SecondarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | SmallHotel |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | MediumOffice |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | SuperMarket |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | LargeHotel | GuestRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 |  | Attic | No |  | Nonresidential | Mass | Nonresidential |  | Nonresidential |  |  |  | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential
DOE Ref 1980-2004 | Hospital |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | Hospital | PatRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | LargeHotel |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | LargeHotel | GuestRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | LargeHotel | GuestRoom | No | Mass | Nonresidential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | LargeHotel |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | LargeHotel | GuestRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | LargeHotel |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | LargeHotel | GuestRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | LargeHotel | GuestRoom | No | Mass | Nonresidential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | LargeOffice |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | Retail |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | LargeOffice |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | MediumOffice |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | MediumOffice |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Retail |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Office |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | Office |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Outpatient |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | SteelFramed | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Retail |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Retail |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | Outpatient |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | SteelFramed | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | LargeOffice |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | PrimarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | LargeOffice |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | No | WoodFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | Retail |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Retail |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Retail |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | SecondarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | No | SteelFramed | Nonresidential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | FullServiceRestaurant |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Hospital |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Hospital | PatRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | LargeOffice |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | LargeOffice |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | MidriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | LargeOffice |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | MediumOffice |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | No | WoodFramed | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | MediumOffice |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Outpatient |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | PrimarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | QuickServiceRestaurant |  | No | WoodFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | MediumOffice |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | SecondarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | SmallHotel |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | MediumOffice |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | SuperMarket |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | Warehouse |  | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 |  | Attic | No |  | Nonresidential | Mass | Nonresidential |  | Nonresidential |  |  |  | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential
90.1-2007 | FullServiceRestaurant |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Hospital |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Hospital | PatRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | StripMall |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | StripMall |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | MidriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | StripMall |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | StripMall |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | Office |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Outpatient |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | PrimarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | QuickServiceRestaurant |  | No | WoodFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | SecondarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | SmallHotel |  | Yes | SteelFramed | Residential | Mass | Residential | IEAD | Residential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Residential | Unheated | Residential |  | Residential | Metal framing (all other) | Residential | Metal framing (all other) | Residential | Swinging | Residential |  | NonSwinging | Residential | Glass with Curb | Residential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | SmallHotel |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | StripMall |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | SuperMarket |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Warehouse |  | No | Metal Building | Semiheated | Mass | Nonresidential | IEAD | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Metal Building | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 |  | Attic | No |  | Nonresidential | Mass | Nonresidential |  | Nonresidential |  |  |  | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential
90.1-2010 | FullServiceRestaurant |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Hospital |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Hospital | PatRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | Warehouse |  | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Metal Building | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Office |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | MidriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Office |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Office |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Office |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | SmallOffice |  | No | Mass | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Outpatient |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | PrimarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | QuickServiceRestaurant |  | No | WoodFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Warehouse |  | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | SecondarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | SmallHotel |  | Yes | SteelFramed | Residential | Mass | Residential | IEAD | Residential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Residential | Unheated | Residential |  | Residential | Metal framing (all other) | Residential | Metal framing (all other) | Residential | Swinging | Residential |  | NonSwinging | Residential | Glass with Curb | Residential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | SmallHotel |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | StripMall |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | SuperMarket |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Warehouse |  | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 |  | Attic | No |  | Nonresidential | Mass | Nonresidential |  | Nonresidential |  |  |  | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential
90.1-2013 | FullServiceRestaurant |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Hospital |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Hospital | PatRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 |  | Attic | No |  | Nonresidential | Mass | Nonresidential |  | Nonresidential |  |  |  | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential
DOE Ref 1980-2004 |  | Attic | No |  | Nonresidential | Mass | Nonresidential |  | Nonresidential |  |  |  | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential
90.1-2013 | MidriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | SmallOffice |  | No | WoodFramed | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | SmallOffice |  | No | WoodFramed | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | SmallOffice |  | No | WoodFramed | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | SmallOffice |  | No | WoodFramed | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Outpatient |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | PrimarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | QuickServiceRestaurant |  | No | WoodFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Warehouse |  | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | SecondarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | SmallHotel |  | Yes | SteelFramed | Residential | Mass | Residential | IEAD | Residential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Residential | Unheated | Residential |  | Residential | Metal framing (all other) | Residential | Metal framing (all other) | Residential | Swinging | Residential |  | NonSwinging | Residential | Glass with Curb | Residential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | SmallHotel |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | SmallHotel |  | Yes | SteelFramed | Residential | Mass | Residential | IEAD | Residential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Residential | Unheated | Residential |  | Residential | Metal framing (all other) | Residential | Metal framing (all other) | Residential | Swinging | Residential |  | NonSwinging | Residential | Glass with Curb | Residential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | StripMall |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | U 0.60 SHGC 0.25 Dbl 2.5mm air | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | SuperMarket |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Warehouse |  | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 |  | Attic | No |  | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential

## Construction Properties
This table contains construction requirements for different classes of constructions
Template | Climate Zone Set | Intended Surface Type | Standards Construction Type | Building Category | Construction | Minimum Percent of Surface | Maximum Percent of Surface | Assembly Maximum U-Value | Assembly Maximum F Factor | Assembly Maximum C Factor | Assembly Maximum Solar Heat Gain Coefficient | Assembly Minimum VT SHGC | sort order
90.1-2010 | ClimateZone 2 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2574
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 658
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 640
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 370
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 352
90.1-2010 | ClimateZone 2 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2599
90.1-2010 | ClimateZone 2 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2624
90.1-2010 | ClimateZone 2 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2573
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 657
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 639
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 369
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 351
90.1-2010 | ClimateZone 2 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2598
90.1-2010 | ClimateZone 2 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2623
90.1-2010 | ClimateZone 2 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.107 |  |  |  |  | 2568
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 655
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 637
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 367
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 349
90.1-2010 | ClimateZone 2 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 2593
90.1-2010 | ClimateZone 1 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof - Highly Reflective |  |  | 0.065 |  |  |  |  | 2486
90.1-2010 | ClimateZone 1 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 2488
90.1-2010 | ClimateZone 1 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.093 |  |  |  |  | 2489
90.1-2010 | ClimateZone 1 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 2490
90.1-2010 | ClimateZone 1 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2491
90.1-2010 | ClimateZone 1 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2492
90.1-2010 | ClimateZone 1 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 2493
90.1-2010 | ClimateZone 1 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.35 |  |  |  |  | 2494
90.1-2010 | ClimateZone 1 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.282 |  |  |  |  | 2495
90.1-2010 | ClimateZone 1 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2496
90.1-2010 | ClimateZone 1 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 2497
90.1-2010 | ClimateZone 1 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2498
90.1-2010 | ClimateZone 1 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2499
90.1-2010 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2500
90.1-2010 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2501
90.1-2010 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2502
90.1-2010 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2503
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 645
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 663
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 375
90.1-2010 | ClimateZone 3 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2648
90.1-2010 | ClimateZone 3 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2649
90.1-2010 | ClimateZone 3 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.107 |  |  |  |  | 2643
90.1-2010 | ClimateZone 3 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.052 |  |  |  |  | 2644
90.1-2010 | ClimateZone 3 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.051 |  |  |  |  | 2645
90.1-2010 | ClimateZone 3 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.055 |  |  |  |  | 2636
90.1-2010 | ClimateZone 3 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.123 |  |  |  |  | 2638
90.1-2010 | ClimateZone 3 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.084 |  |  |  |  | 2639
90.1-2010 | ClimateZone 3 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.084 |  |  |  |  | 2640
90.1-2010 | ClimateZone 3 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2641
90.1-2010 | ClimateZone 3 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  | 0.25 |  | 2650
90.1-2010 | ClimateZone 3 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.6 |  |  | 0.25 |  | 2651
90.1-2010 | ClimateZone 3 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 0.9 |  |  | 0.25 |  | 2652
90.1-2010 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  | 0.25 |  | 2653
90.1-2010 | ClimateZone 3 | GroundContactFloor | Unheated | Nonresidential | Smallhotel 2010 Slab Floor |  |  |  | 0.73 |  |  |  | 2646
90.1-2010 | ClimateZone 3 | GroundContactFloor | Heated | Nonresidential | Smallhotel 2010 Slab Floor |  |  |  | 0.9 |  |  |  | 2647
90.1-2010 | ClimateZone 3 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2642
90.1-2010 | ClimateZone 1 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  | 0.063 |  |  |  |  | 2485
90.1-2010 | ClimateZone 1 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 2487
90.1-2010 | ClimateZone 4 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2723
90.1-2010 | ClimateZone 4 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2724
90.1-2010 | ClimateZone 4 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 2718
90.1-2010 | ClimateZone 4 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.038 |  |  |  |  | 2719
90.1-2010 | ClimateZone 4 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 2720
90.1-2010 | ClimateZone 4 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.055 |  |  |  |  | 2711
90.1-2010 | ClimateZone 4 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.104 |  |  |  |  | 2713
90.1-2010 | ClimateZone 4 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.084 |  |  |  |  | 2714
90.1-2010 | ClimateZone 4 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2715
90.1-2010 | ClimateZone 4 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2716
90.1-2010 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.39 SHGC 0.38 |  |  | 0.4 |  |  | 0.4 |  | 2725
90.1-2010 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.5 |  |  | 0.4 |  | 2726
90.1-2010 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.85 |  |  | 0.4 |  | 2727
90.1-2010 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  | 0.55 |  |  | 0.4 |  | 2728
90.1-2010 | ClimateZone 4 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2721
90.1-2010 | ClimateZone 4 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 2722
90.1-2010 | ClimateZone 4 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2717
90.1-2010 | ClimateZone 5 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2798
90.1-2010 | ClimateZone 5 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2799
90.1-2010 | ClimateZone 5 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.074 |  |  |  |  | 2793
90.1-2010 | ClimateZone 5 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.038 |  |  |  |  | 2794
90.1-2010 | ClimateZone 5 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 2795
90.1-2010 | ClimateZone 5 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.055 |  |  |  |  | 2786
90.1-2010 | ClimateZone 5 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.09 |  |  |  |  | 2788
90.1-2010 | ClimateZone 5 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.069 |  |  |  |  | 2789
90.1-2010 | ClimateZone 5 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2790
90.1-2010 | ClimateZone 5 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2791
90.1-2010 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.35 |  |  | 0.4 |  | 2800
90.1-2010 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  | 0.4 |  | 2801
90.1-2010 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  | 0.4 |  | 2802
90.1-2010 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  |  | 0.55 |  |  | 0.4 |  | 2803
90.1-2010 | ClimateZone 5 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2796
90.1-2010 | ClimateZone 5 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 2797
90.1-2010 | ClimateZone 5 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.19 |  |  | 2792
90.1-2010 | ClimateZone 6 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2873
90.1-2010 | ClimateZone 6 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2874
90.1-2010 | ClimateZone 6 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.064 |  |  |  |  | 2868
90.1-2010 | ClimateZone 6 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.038 |  |  |  |  | 2869
90.1-2010 | ClimateZone 6 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 2870
90.1-2010 | ClimateZone 6 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.049 |  |  |  |  | 2861
90.1-2010 | ClimateZone 6 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.08 |  |  |  |  | 2863
90.1-2010 | ClimateZone 6 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.069 |  |  |  |  | 2864
90.1-2010 | ClimateZone 6 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2865
90.1-2010 | ClimateZone 6 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 2866
90.1-2010 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.35 |  |  | 0.4 |  | 2875
90.1-2010 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  | 0.4 |  | 2876
90.1-2010 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  | 0.4 |  | 2877
90.1-2010 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  | 0.55 |  |  | 0.4 |  | 2878
90.1-2010 | ClimateZone 6 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.54 |  |  |  | 2871
90.1-2010 | ClimateZone 6 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 2872
90.1-2010 | ClimateZone 6 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 2867
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 357
90.1-2010 | ClimateZone 2 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 2618
90.1-2010 | ClimateZone 7 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.049 |  |  |  |  | 2936
90.1-2010 | ClimateZone 7 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.071 |  |  |  |  | 2938
90.1-2010 | ClimateZone 7 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 2939
90.1-2010 | ClimateZone 7 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2940
90.1-2010 | ClimateZone 7 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 2941
90.1-2010 | ClimateZone 7 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 2942
90.1-2010 | ClimateZone 7 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.064 |  |  |  |  | 2943
90.1-2010 | ClimateZone 7 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.038 |  |  |  |  | 2944
90.1-2010 | ClimateZone 7 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 2945
90.1-2010 | ClimateZone 7 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.52 |  |  |  | 2946
90.1-2010 | ClimateZone 7 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.843 |  |  |  | 2947
90.1-2010 | ClimateZone 7 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 2948
90.1-2010 | ClimateZone 7 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2949
90.1-2010 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.35 |  |  | 0.45 |  | 2950
90.1-2010 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  | 0.4 |  |  | 0.45 |  | 2951
90.1-2010 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  | 0.45 |  | 2952
90.1-2010 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  | 0.45 |  | 2953
90.1-2010 | ClimateZone 8 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.035 |  |  |  |  | 3011
90.1-2010 | ClimateZone 8 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.071 |  |  |  |  | 3013
90.1-2010 | ClimateZone 8 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 3014
90.1-2010 | ClimateZone 8 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 3015
90.1-2010 | ClimateZone 8 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.036 |  |  |  |  | 3016
90.1-2010 | ClimateZone 8 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 3017
90.1-2010 | ClimateZone 8 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.057 |  |  |  |  | 3018
90.1-2010 | ClimateZone 8 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.032 |  |  |  |  | 3019
90.1-2010 | ClimateZone 8 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 3020
90.1-2010 | ClimateZone 8 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.52 |  |  |  | 3021
90.1-2010 | ClimateZone 8 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.688 |  |  |  | 3022
90.1-2010 | ClimateZone 8 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3023
90.1-2010 | ClimateZone 8 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3024
90.1-2010 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.35 |  |  | 0.45 |  | 3025
90.1-2010 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  | 0.4 |  |  | 0.45 |  | 3026
90.1-2010 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  | 0.45 |  | 3027
90.1-2010 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  | 0.45 |  | 3028
90.1-2010 | ClimateZone 3 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  | 0.048 |  |  |  |  | 2635
90.1-2010 | ClimateZone 3 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2637
90.1-2010 | ClimateZone 4 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2710
90.1-2010 | ClimateZone 4 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2712
90.1-2010 | ClimateZone 5 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2785
90.1-2010 | ClimateZone 5 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2787
90.1-2010 | ClimateZone 6 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2860
90.1-2010 | ClimateZone 6 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2862
90.1-2010 | ClimateZone 7 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2935
90.1-2010 | ClimateZone 7 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2937
90.1-2010 | ClimateZone 8 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 3010
90.1-2010 | ClimateZone 8 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.021 |  |  |  |  | 3012
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 1 |  |  |  |  | 615
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 1 |  |  |  |  | 616
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 1 |  |  |  |  | 617
DOE Ref 1980-2004 | ClimateZone 1 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 618
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 619
DOE Ref 1980-2004 | ClimateZone 1 | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 620
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 621
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 622
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window |  |  | 1.22 |  |  | 0.25 |  | 623
90.1-2010 | ClimateZone 2 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.052 |  |  |  |  | 2569
90.1-2010 | ClimateZone 2 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.052 |  |  |  |  | 2594
90.1-2010 | ClimateZone 2 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.069 |  |  |  |  | 2619
90.1-2010 | ClimateZone 2 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.051 |  |  |  |  | 2570
90.1-2010 | ClimateZone 2 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 2595
90.1-2010 | ClimateZone 2 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.066 |  |  |  |  | 2620
90.1-2010 | ClimateZone 2 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2562
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.066 |  |  |  |  | 632
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.046 |  |  |  |  | 650
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.1 |  |  |  |  | 344
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.29 |  |  |  |  | 669
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.13 |  |  |  |  | 670
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.13 |  |  |  |  | 671
DOE Ref 1980-2004 | ClimateZone 3A | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0.143 |  |  |  |  | 672
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 673
DOE Ref Pre-1980 | ClimateZone 1 | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 332
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 675
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 676
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window |  |  | 1.22 |  |  | 0.25 |  | 641
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.29 |  |  |  |  | 687
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.16 |  |  |  |  | 688
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.16 |  |  |  |  | 689
DOE Ref 1980-2004 | ClimateZone 3B | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 690
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 691
DOE Ref 1980-2004 | ClimateZone 2A | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 638
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 693
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 694
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window |  |  | 1.22 |  |  | 0.25 |  | 659
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.49 |  |  |  |  | 705
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.13 |  |  |  |  | 706
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.13 |  |  |  |  | 707
DOE Ref 1980-2004 | ClimateZone 3C | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0.143 |  |  |  |  | 708
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 709
DOE Ref Pre-1980 | ClimateZone 2A | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 350
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 711
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 712
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.25 Simple Glazing Window |  |  | 0.72 |  |  | 0.25 |  | 677
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.12 |  |  |  |  | 723
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 724
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 725
DOE Ref 1980-2004 | ClimateZone 4A | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0.111 |  |  |  |  | 726
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.074 |  |  |  |  | 613
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.074 |  |  |  |  | 614
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 727
DOE Ref 1980-2004 | ClimateZone 2B | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 656
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 729
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 730
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window |  |  | 1.22 |  |  | 0.25 |  | 695
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.19 |  |  |  |  | 741
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.1 |  |  |  |  | 742
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.1 |  |  |  |  | 743
DOE Ref 1980-2004 | ClimateZone 4B | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0.125 |  |  |  |  | 744
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 745
DOE Ref Pre-1980 | ClimateZone 2B | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 368
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 747
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 748
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.1 |  |  |  |  | 362
90.1-2010 | ClimateZone 2 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2587
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.39 Simple Glazing Window |  |  | 0.72 |  |  | 0.25 |  | 713
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.1 |  |  |  |  | 759
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.092 |  |  |  |  | 760
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.092 |  |  |  |  | 761
DOE Ref 1980-2004 | ClimateZone 4C | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0.111 |  |  |  |  | 762
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 763
DOE Ref 1980-2004 | ClimateZone 3A | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 674
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 765
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 766
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.59 SHGC 0.36 Simple Glazing Window |  |  | 0.59 |  |  | 0.36 |  | 731
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.1 |  |  |  |  | 777
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.082 |  |  |  |  | 778
90.1-2010 | ClimateZone 2 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.081 |  |  |  |  | 2612
90.1-2010 | ClimateZone 2 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  | 0.048 |  |  |  |  | 2560
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.082 |  |  |  |  | 779
DOE Ref 1980-2004 | ClimateZone 5A | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0.1 |  |  |  |  | 780
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 781
DOE Ref Pre-1980 | ClimateZone 3A | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 386
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 783
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 784
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.36 Simple Glazing Window |  |  | 0.72 |  |  | 0.36 |  | 749
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.14 |  |  |  |  | 795
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.082 |  |  |  |  | 796
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.082 |  |  |  |  | 797
DOE Ref 1980-2004 | ClimateZone 5B | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0.1 |  |  |  |  | 798
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 799
DOE Ref 1980-2004 | ClimateZone 3B | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 692
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.072 |  |  |  |  | 667
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.072 |  |  |  |  | 668
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 801
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 802
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.39 Simple Glazing Window |  |  | 0.72 |  |  | 0.36 |  | 767
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.14 |  |  |  |  | 813
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.082 |  |  |  |  | 814
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.082 |  |  |  |  | 815
DOE Ref 1980-2004 | ClimateZone 5C | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0.1 |  |  |  |  | 816
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 817
DOE Ref Pre-1980 | ClimateZone 3B | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 404
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 819
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 820
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.59 SHGC 0.39 Simple Glazing Window |  |  | 0.59 |  |  | 0.39 |  | 785
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 685
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.048 |  |  |  |  | 686
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.071 |  |  |  |  | 831
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.065 |  |  |  |  | 832
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.065 |  |  |  |  | 833
DOE Ref 1980-2004 | ClimateZone 6A | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0.083 |  |  |  |  | 834
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 835
DOE Ref 1980-2004 | ClimateZone 3C | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 710
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 837
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 838
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.59 SHGC 0.39 Simple Glazing Window |  |  | 0.59 |  |  | 0.39 |  | 803
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.079 |  |  |  |  | 849
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.072 |  |  |  |  | 850
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.072 |  |  |  |  | 851
DOE Ref 1980-2004 | ClimateZone 6B | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0.091 |  |  |  |  | 852
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.088 |  |  |  |  | 703
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.088 |  |  |  |  | 704
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 853
DOE Ref Pre-1980 | ClimateZone 3C | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 422
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 855
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 856
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.59 SHGC 0.39 Simple Glazing Window |  |  | 0.59 |  |  | 0.39 |  | 821
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.061 |  |  |  |  | 867
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.058 |  |  |  |  | 868
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.058 |  |  |  |  | 869
DOE Ref 1980-2004 | ClimateZone 7 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0.077 |  |  |  |  | 870
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 871
DOE Ref 1980-2004 | ClimateZone 4A | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 728
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 873
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 874
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.058 |  |  |  |  | 721
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.058 |  |  |  |  | 722
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.52 SHGC 0.39 Simple Glazing Window |  |  | 0.52 |  |  | 0.39 |  | 839
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.047 |  |  |  |  | 885
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.045 |  |  |  |  | 886
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.045 |  |  |  |  | 887
DOE Ref 1980-2004 | ClimateZone 8 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0.063 |  |  |  |  | 888
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 889
DOE Ref Pre-1980 | ClimateZone 4A | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 440
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 891
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 892
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.52 SHGC 0.39 Simple Glazing Window |  |  | 0.52 |  |  | 0.39 |  | 857
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.059 |  |  |  |  | 739
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.059 |  |  |  |  | 740
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.064 |  |  |  |  | 757
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.064 |  |  |  |  | 758
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.053 |  |  |  |  | 775
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.053 |  |  |  |  | 776
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.051 |  |  |  |  | 793
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.051 |  |  |  |  | 794
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.051 |  |  |  |  | 811
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.051 |  |  |  |  | 812
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.045 |  |  |  |  | 829
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.045 |  |  |  |  | 830
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.049 |  |  |  |  | 847
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.049 |  |  |  |  | 848
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.04 |  |  |  |  | 865
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.04 |  |  |  |  | 866
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.031 |  |  |  |  | 883
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.031 |  |  |  |  | 884
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.066 |  |  |  |  | 631
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.046 |  |  |  |  | 649
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.1 |  |  |  |  | 343
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.1 |  |  |  |  | 361
90.1-2010 | ClimateZone 2 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  | 0.048 |  |  |  |  | 2585
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 643
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 661
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 355
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 373
90.1-2010 | ClimateZone 2 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.218 |  |  |  |  | 2610
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.1 |  |  |  |  | 325
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.1 |  |  |  |  | 326
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.23 |  |  |  |  | 327
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 328
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 329
DOE Ref Pre-1980 | ClimateZone 1 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 330
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 331
DOE Ref 1980-2004 | ClimateZone 4B | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 746
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 333
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 334
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  | 1.22 |  |  | 0.54 |  | 335
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 646
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 664
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 358
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 376
90.1-2010 | ClimateZone 2 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.055 |  |  |  |  | 2561
90.1-2010 | ClimateZone 2 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.055 |  |  |  |  | 2586
90.1-2010 | ClimateZone 2 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.097 |  |  |  |  | 2611
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 647
90.1-2004 | ClimateZone 1 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 902
90.1-2004 | ClimateZone 1 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 904
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 665
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 377
90.1-2004 | ClimateZone 1 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 905
90.1-2004 | ClimateZone 1 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 906
90.1-2004 | ClimateZone 1 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 907
90.1-2004 | ClimateZone 1 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 908
90.1-2004 | ClimateZone 1 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 909
90.1-2004 | ClimateZone 1 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.35 |  |  |  |  | 910
90.1-2004 | ClimateZone 1 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.282 |  |  |  |  | 911
90.1-2004 | ClimateZone 1 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 912
90.1-2004 | ClimateZone 1 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 913
90.1-2004 | ClimateZone 1 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 914
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 359
90.1-2004 | ClimateZone 1 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 915
90.1-2004 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  | 0.25 |  | 916
90.1-2010 | ClimateZone 2 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 2563
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  | 0.25 |  | 917
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  | 0.25 |  | 918
90.1-2010 | ClimateZone 2 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.123 |  |  |  |  | 2588
90.1-2010 | ClimateZone 2 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 2613
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  | 0.25 |  | 919
90.1-2004 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 920
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 921
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 922
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 923
90.1-2004 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 924
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 925
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 926
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 927
90.1-2004 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 928
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.225 |  |  |  |  | 381
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 929
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 930
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.225 |  |  |  |  | 382
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 931
90.1-2004 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.19 |  | 932
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.225 |  |  |  |  | 383
DOE Ref Pre-1980 | ClimateZone 3A | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 384
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.19 |  | 933
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.19 |  | 934
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.19 |  | 935
90.1-2007 | ClimateZone 1 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof - Highly Reflective |  |  | 0.065 |  |  |  |  | 1886
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 385
90.1-2007 | ClimateZone 1 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 1888
90.1-2007 | ClimateZone 1 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1889
DOE Ref Pre-1980 | ClimateZone 4B | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 458
90.1-2007 | ClimateZone 1 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 1890
90.1-2007 | ClimateZone 1 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1891
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 387
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 388
90.1-2007 | ClimateZone 1 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1892
90.1-2007 | ClimateZone 1 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 1893
90.1-2007 | ClimateZone 1 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.35 |  |  |  |  | 1894
90.1-2007 | ClimateZone 1 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.282 |  |  |  |  | 1895
90.1-2007 | ClimateZone 1 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1896
90.1-2007 | ClimateZone 1 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1897
90.1-2007 | ClimateZone 1 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1898
90.1-2007 | ClimateZone 1 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1899
90.1-2007 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 1900
90.1-2007 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 1901
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  | 1.22 |  |  | 0.54 |  | 389
90.1-2007 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 1902
90.1-2007 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 1903
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.23 |  |  |  |  | 399
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 400
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.1 |  |  |  |  | 379
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.1 |  |  |  |  | 380
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 401
DOE Ref Pre-1980 | ClimateZone 3B | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 402
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 403
DOE Ref 1980-2004 | ClimateZone 4C | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 764
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 405
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 406
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  | 1.22 |  |  | 0.54 |  | 407
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.224 |  |  |  |  | 417
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.224 |  |  |  |  | 418
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.224 |  |  |  |  | 419
DOE Ref Pre-1980 | ClimateZone 3C | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 420
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 421
DOE Ref Pre-1980 | ClimateZone 4C | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 476
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.1 |  |  |  |  | 397
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.1 |  |  |  |  | 398
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 423
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 424
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  | 1.22 |  |  | 0.54 |  | 425
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.178 |  |  |  |  | 435
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.178 |  |  |  |  | 436
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.178 |  |  |  |  | 437
DOE Ref Pre-1980 | ClimateZone 4A | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 438
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 439
DOE Ref 1980-2004 | ClimateZone 5A | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 782
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 441
90.1-2004 | ClimateZone 2 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1025
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 442
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  | 1.22 |  |  | 0.54 |  | 443
90.1-2004 | ClimateZone 2 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 1027
90.1-2004 | ClimateZone 2 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1028
90.1-2004 | ClimateZone 2 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 1029
90.1-2004 | ClimateZone 2 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1030
90.1-2004 | ClimateZone 2 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1031
90.1-2004 | ClimateZone 2 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.137 |  |  |  |  | 1032
90.1-2004 | ClimateZone 2 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.052 |  |  |  |  | 1033
90.1-2004 | ClimateZone 2 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.051 |  |  |  |  | 1034
90.1-2004 | ClimateZone 2 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1035
90.1-2004 | ClimateZone 2 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1036
90.1-2004 | ClimateZone 2 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1037
90.1-2004 | ClimateZone 2 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1038
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.1 |  |  |  |  | 415
90.1-2004 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  | 0.25 |  | 1039
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  | 0.25 |  | 1040
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.1 |  |  |  |  | 416
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.184 |  |  |  |  | 453
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  | 0.25 |  | 1041
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  | 0.25 |  | 1042
90.1-2004 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 1043
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 1044
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 1045
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 1046
90.1-2004 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 1047
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 1048
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 1049
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 1050
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.184 |  |  |  |  | 454
90.1-2004 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 1051
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 1052
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.184 |  |  |  |  | 455
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 1053
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 1054
DOE Ref Pre-1980 | ClimateZone 4B | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 456
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 457
90.1-2004 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.17 |  | 1055
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.17 |  | 1056
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.17 |  | 1057
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.17 |  | 1058
DOE Ref Pre-1980 | ClimateZone 5A | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 494
90.1-2007 | ClimateZone 2 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1961
90.1-2007 | ClimateZone 2 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 1963
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 459
90.1-2007 | ClimateZone 2 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1964
90.1-2007 | ClimateZone 2 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 1965
90.1-2004 | ClimateZone 1 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 901
90.1-2007 | ClimateZone 2 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1966
90.1-2004 | ClimateZone 1 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 903
90.1-2007 | ClimateZone 2 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1967
90.1-2007 | ClimateZone 2 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.107 |  |  |  |  | 1968
90.1-2007 | ClimateZone 2 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.052 |  |  |  |  | 1969
90.1-2007 | ClimateZone 2 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.051 |  |  |  |  | 1970
90.1-2007 | ClimateZone 2 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1971
90.1-2007 | ClimateZone 2 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1972
90.1-2007 | ClimateZone 2 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1973
90.1-2007 | ClimateZone 2 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1974
90.1-2007 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.75 |  |  | 0.25 |  | 1975
90.1-2007 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.7 |  |  | 0.25 |  | 1976
90.1-2007 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.1 |  |  | 0.25 |  | 1977
90.1-2007 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.75 |  |  | 0.25 |  | 1978
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 460
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  | 1.22 |  |  | 0.54 |  | 461
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.175 |  |  |  |  | 471
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.175 |  |  |  |  | 472
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.175 |  |  |  |  | 473
DOE Ref Pre-1980 | ClimateZone 4C | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 474
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.086 |  |  |  |  | 433
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.086 |  |  |  |  | 434
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 475
DOE Ref 1980-2004 | ClimateZone 5B | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 800
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 477
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 478
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  | 1.22 |  |  | 0.54 |  | 479
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.156 |  |  |  |  | 489
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.156 |  |  |  |  | 490
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.156 |  |  |  |  | 491
DOE Ref Pre-1980 | ClimateZone 5A | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 492
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 493
90.1-2004 | ClimateZone 1 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 942
DOE Ref Pre-1980 | ClimateZone 5B | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 512
90.1-2004 | ClimateZone 1 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 944
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 495
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 496
90.1-2004 | ClimateZone 3A | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1148
90.1-2004 | ClimateZone 3A | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 1150
90.1-2004 | ClimateZone 3A | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1151
90.1-2004 | ClimateZone 3A | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 1152
90.1-2004 | ClimateZone 3A | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1153
90.1-2004 | ClimateZone 3A | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1154
90.1-2004 | ClimateZone 3A | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.107 |  |  |  |  | 1155
90.1-2004 | ClimateZone 3A | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.052 |  |  |  |  | 1156
90.1-2004 | ClimateZone 3A | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.051 |  |  |  |  | 1157
90.1-2004 | ClimateZone 3A | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1158
90.1-2004 | ClimateZone 3A | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1159
90.1-2004 | ClimateZone 3A | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1160
90.1-2004 | ClimateZone 3A | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1161
90.1-2004 | ClimateZone 3A | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1162
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1163
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1164
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1165
90.1-2004 | ClimateZone 3A | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.25 |  | 1166
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.25 |  | 1167
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.25 |  | 1168
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.25 |  | 1169
90.1-2004 | ClimateZone 3A | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1170
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1171
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1172
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1173
90.1-2004 | ClimateZone 3A | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1174
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1175
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1176
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1177
90.1-2004 | ClimateZone 3A | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1178
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1179
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1180
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1181
90.1-2004 | ClimateZone 3B | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1162
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1163
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1164
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1165
90.1-2004 | ClimateZone 3B | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.25 |  | 1166
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.25 |  | 1167
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.25 |  | 1168
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.25 |  | 1169
90.1-2004 | ClimateZone 3B | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1170
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1171
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1172
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1173
90.1-2004 | ClimateZone 3B | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1174
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1175
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1176
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1177
90.1-2004 | ClimateZone 3B | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1178
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1179
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1180
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1181
90.1-2004 | ClimateZone 3C | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.61 Sgl Green 6mm | 1 | 10 | 1.22 |  |  | 0.61 |  | 1162
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.61 Sgl Green 6mm | 1 | 10 | 1.22 |  |  | 0.61 |  | 1163
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.61 Sgl Green 6mm | 1 | 10 | 1.22 |  |  | 0.61 |  | 1164
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.61 Sgl Green 6mm | 1 | 10 | 1.22 |  |  | 0.61 |  | 1165
90.1-2004 | ClimateZone 3C | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 10.001 | 20 | 1.22 |  |  | 0.39 |  | 1166
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 10.001 | 20 | 1.22 |  |  | 0.39 |  | 1167
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 10.001 | 20 | 1.22 |  |  | 0.39 |  | 1168
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 10.001 | 20 | 1.22 |  |  | 0.39 |  | 1169
90.1-2004 | ClimateZone 3C | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 20.001 | 30 | 1.22 |  |  | 0.39 |  | 1170
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 20.001 | 30 | 1.22 |  |  | 0.39 |  | 1171
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 20.001 | 30 | 1.22 |  |  | 0.39 |  | 1172
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 20.001 | 30 | 1.22 |  |  | 0.39 |  | 1173
90.1-2004 | ClimateZone 3C | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm | 30.001 | 40 | 1.22 |  |  | 0.34 |  | 1174
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm | 30.001 | 40 | 1.22 |  |  | 0.34 |  | 1175
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm | 30.001 | 40 | 1.22 |  |  | 0.34 |  | 1176
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm | 30.001 | 40 | 1.22 |  |  | 0.34 |  | 1177
90.1-2004 | ClimateZone 3C | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window | 40.001 | 100 | 1.22 |  |  | 0.25 |  | 1178
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window | 40.001 | 100 | 1.22 |  |  | 0.25 |  | 1179
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window | 40.001 | 100 | 1.22 |  |  | 0.25 |  | 1180
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window | 40.001 | 100 | 1.22 |  |  | 0.25 |  | 1181
90.1-2004 | ClimateZone 1 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 1.282 |  |  |  |  | 983
90.1-2004 | ClimateZone 1 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.614 |  |  |  |  | 985
90.1-2007 | ClimateZone 3 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 2036
90.1-2007 | ClimateZone 3 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.123 |  |  |  |  | 2038
90.1-2007 | ClimateZone 3 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 2039
90.1-2007 | ClimateZone 3 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.084 |  |  |  |  | 2040
90.1-2007 | ClimateZone 3 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2041
90.1-2007 | ClimateZone 3 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2042
90.1-2007 | ClimateZone 3 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.107 |  |  |  |  | 2043
90.1-2007 | ClimateZone 3 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.052 |  |  |  |  | 2044
90.1-2007 | ClimateZone 3 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.051 |  |  |  |  | 2045
90.1-2007 | ClimateZone 3 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2046
90.1-2007 | ClimateZone 3 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.9 |  |  |  | 2047
90.1-2007 | ClimateZone 3 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2048
90.1-2007 | ClimateZone 3 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2049
90.1-2007 | ClimateZone 3 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  | 0.25 |  | 2050
90.1-2007 | ClimateZone 3 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.6 |  |  | 0.25 |  | 2051
90.1-2007 | ClimateZone 3 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 0.9 |  |  | 0.25 |  | 2052
90.1-2007 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  | 0.25 |  | 2053
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.089 |  |  |  |  | 451
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.089 |  |  |  |  | 452
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.41 Simple Glazing Window |  |  | 0.62 |  |  | 0.41 |  | 497
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.161 |  |  |  |  | 507
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.161 |  |  |  |  | 508
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.161 |  |  |  |  | 509
DOE Ref Pre-1980 | ClimateZone 5B | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 510
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 511
DOE Ref 1980-2004 | ClimateZone 5C | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 818
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 513
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 514
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.41 Simple Glazing Window |  |  | 0.62 |  |  | 0.41 |  | 515
90.1-2007 | ClimateZone 1 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  | 0.063 |  |  |  |  | 1885
90.1-2007 | ClimateZone 1 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 1887
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.161 |  |  |  |  | 525
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.161 |  |  |  |  | 526
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.085 |  |  |  |  | 469
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.085 |  |  |  |  | 470
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.161 |  |  |  |  | 527
DOE Ref Pre-1980 | ClimateZone 5C | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 528
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 529
DOE Ref Pre-1980 | ClimateZone 5C | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 530
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 531
90.1-2004 | ClimateZone 4 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1271
90.1-2004 | ClimateZone 4 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 1273
90.1-2004 | ClimateZone 4 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1274
90.1-2004 | ClimateZone 4 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 1275
90.1-2004 | ClimateZone 4 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1276
90.1-2004 | ClimateZone 4 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1277
90.1-2004 | ClimateZone 4 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.107 |  |  |  |  | 1278
90.1-2004 | ClimateZone 4 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.052 |  |  |  |  | 1279
90.1-2004 | ClimateZone 4 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.051 |  |  |  |  | 1280
90.1-2004 | ClimateZone 4 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1281
90.1-2004 | ClimateZone 4 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.95 |  |  |  | 1282
90.1-2004 | ClimateZone 4 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1283
90.1-2004 | ClimateZone 4 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1284
90.1-2007 | ClimateZone 1 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  | 0.048 |  |  |  |  | 1910
90.1-2004 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1285
90.1-2007 | ClimateZone 1 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 1912
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1286
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1287
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1288
90.1-2004 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1289
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1290
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1291
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1292
90.1-2004 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1293
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1294
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1295
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1296
90.1-2004 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1297
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1298
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1299
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1300
90.1-2004 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.25 |  | 1301
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.25 |  | 1302
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.25 |  | 1303
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.25 |  | 1304
90.1-2007 | ClimateZone 1 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.218 |  |  |  |  | 1935
90.1-2007 | ClimateZone 1 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.081 |  |  |  |  | 1937
90.1-2007 | ClimateZone 4 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 2111
90.1-2007 | ClimateZone 4 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.104 |  |  |  |  | 2113
90.1-2007 | ClimateZone 4 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 2114
90.1-2007 | ClimateZone 4 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2115
90.1-2007 | ClimateZone 4 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2116
90.1-2007 | ClimateZone 4 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2117
90.1-2007 | ClimateZone 4 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 2118
90.1-2007 | ClimateZone 4 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.038 |  |  |  |  | 2119
90.1-2007 | ClimateZone 4 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 2120
90.1-2007 | ClimateZone 4 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2121
90.1-2007 | ClimateZone 4 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 2122
90.1-2007 | ClimateZone 4 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2123
90.1-2007 | ClimateZone 4 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 1.5 |  |  |  |  | 2124
90.1-2007 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.39 SHGC 0.38 |  |  | 0.4 |  |  | 0.4 |  | 2125
90.1-2007 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.5 |  |  | 0.4 |  | 2126
90.1-2007 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.85 |  |  | 0.4 |  | 2127
90.1-2007 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.55 |  |  | 0.4 |  | 2128
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 532
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.41 Simple Glazing Window |  |  | 0.62 |  |  | 0.41 |  | 533
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.145 |  |  |  |  | 543
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.145 |  |  |  |  | 544
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.145 |  |  |  |  | 545
DOE Ref Pre-1980 | ClimateZone 6A | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 546
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 547
DOE Ref 1980-2004 | ClimateZone 6A | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 836
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.072 |  |  |  |  | 487
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.072 |  |  |  |  | 488
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 549
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 550
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.41 Simple Glazing Window |  |  | 0.62 |  |  | 0.41 |  | 551
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.145 |  |  |  |  | 561
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.145 |  |  |  |  | 562
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.145 |  |  |  |  | 563
DOE Ref Pre-1980 | ClimateZone 6B | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 564
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 565
DOE Ref Pre-1980 | ClimateZone 6A | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 548
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 567
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 568
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.41 Simple Glazing Window |  |  | 0.62 |  |  | 0.41 |  | 569
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.076 |  |  |  |  | 505
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.076 |  |  |  |  | 506
90.1-2004 | ClimateZone 5 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1394
90.1-2004 | ClimateZone 5 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.123 |  |  |  |  | 1396
90.1-2004 | ClimateZone 5 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1397
90.1-2004 | ClimateZone 5 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.084 |  |  |  |  | 1398
90.1-2004 | ClimateZone 5 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1399
90.1-2004 | ClimateZone 5 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1400
90.1-2004 | ClimateZone 5 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 1401
90.1-2004 | ClimateZone 5 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.052 |  |  |  |  | 1402
90.1-2004 | ClimateZone 5 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 1403
90.1-2004 | ClimateZone 5 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1404
90.1-2004 | ClimateZone 5 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.84 |  |  |  | 1405
90.1-2004 | ClimateZone 5 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1406
90.1-2004 | ClimateZone 5 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1407
90.1-2004 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1408
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1409
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1410
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1411
90.1-2004 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1412
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1413
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1414
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.136 |  |  |  |  | 579
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1415
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.136 |  |  |  |  | 580
90.1-2004 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1416
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1417
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1418
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1419
90.1-2004 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1420
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1421
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1422
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1423
90.1-2004 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1424
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1425
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1426
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1427
90.1-2007 | ClimateZone 5 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 2186
90.1-2007 | ClimateZone 5 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.09 |  |  |  |  | 2188
90.1-2007 | ClimateZone 5 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 2189
90.1-2007 | ClimateZone 5 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2190
90.1-2013 | ClimateZone 1 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  | 0.048 |  |  |  |  | 3085
90.1-2013 | ClimateZone 1 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof - Highly Reflective |  |  | 0.041 |  |  |  |  | 3086
90.1-2013 | ClimateZone 1 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 3087
90.1-2013 | ClimateZone 1 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 3088
90.1-2013 | ClimateZone 1 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.094 |  |  |  |  | 3089
90.1-2013 | ClimateZone 1 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 3090
90.1-2013 | ClimateZone 1 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 3091
90.1-2013 | ClimateZone 1 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 3092
90.1-2013 | ClimateZone 1 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 3093
90.1-2013 | ClimateZone 1 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.35 |  |  |  |  | 3094
90.1-2013 | ClimateZone 1 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.282 |  |  |  |  | 3095
90.1-2013 | ClimateZone 1 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 3096
90.1-2013 | ClimateZone 1 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 3097
90.1-2013 | ClimateZone 1 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 3098
90.1-2013 | ClimateZone 1 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 3099
90.1-2013 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.5 |  |  | 0.25 | 1.1 | 3100
90.1-2013 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.57 |  |  | 0.25 | 1.1 | 3101
90.1-2013 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  | 0.25 | 1.1 | 3102
90.1-2013 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.1 |  |  | 0.25 | 1.1 | 3103
90.1-2013 | ClimateZone 1 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  | 0.039 |  |  |  |  | 3110
90.1-2013 | ClimateZone 1 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof - Highly Reflective |  |  | 0.041 |  |  |  |  | 3111
90.1-2013 | ClimateZone 1 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 3112
90.1-2013 | ClimateZone 1 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 1151 |  |  |  |  | 3113
90.1-2013 | ClimateZone 1 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.094 |  |  |  |  | 3114
90.1-2013 | ClimateZone 1 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 3115
90.1-2013 | ClimateZone 1 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 3116
90.1-2013 | ClimateZone 1 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 3117
90.1-2013 | ClimateZone 1 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 3118
90.1-2013 | ClimateZone 1 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.35 |  |  |  |  | 3119
90.1-2013 | ClimateZone 1 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.282 |  |  |  |  | 3120
90.1-2013 | ClimateZone 1 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 3121
90.1-2013 | ClimateZone 1 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 3122
90.1-2013 | ClimateZone 1 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3123
90.1-2013 | ClimateZone 1 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3124
90.1-2013 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.5 |  |  | 0.25 | 1.1 | 3125
90.1-2013 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.57 |  |  | 0.25 | 1.1 | 3126
90.1-2013 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  | 0.25 | 1.1 | 3127
90.1-2013 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.1 |  |  | 0.25 | 1.1 | 3128
90.1-2013 | ClimateZone 1 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.218 |  |  |  |  | 3135
90.1-2013 | ClimateZone 1 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.1156 |  |  |  |  | 3136
90.1-2013 | ClimateZone 1 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.081 |  |  |  |  | 3137
90.1-2013 | ClimateZone 1 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 3138
90.1-2013 | ClimateZone 1 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.352 |  |  |  |  | 3139
90.1-2013 | ClimateZone 1 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.352 |  |  |  |  | 3140
90.1-2013 | ClimateZone 1 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.292 |  |  |  |  | 3141
90.1-2013 | ClimateZone 1 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 3142
90.1-2013 | ClimateZone 1 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 3143
90.1-2013 | ClimateZone 1 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.35 |  |  |  |  | 3144
90.1-2013 | ClimateZone 1 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.282 |  |  |  |  | 3145
90.1-2013 | ClimateZone 1 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 3146
90.1-2013 | ClimateZone 1 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 3147
90.1-2013 | ClimateZone 1 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 3148
90.1-2013 | ClimateZone 1 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 3149
90.1-2013 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 0.93 |  |  | 0.25 |  | 3150
90.1-2013 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 3151
90.1-2013 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 3152
90.1-2013 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.1 |  |  | 0.25 |  | 3153
90.1-2004 | ClimateZone 2 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1024
90.1-2007 | ClimateZone 5 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2191
90.1-2004 | ClimateZone 2 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 1026
90.1-2007 | ClimateZone 5 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 2192
90.1-2007 | ClimateZone 5 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.074 |  |  |  |  | 2193
90.1-2007 | ClimateZone 5 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.038 |  |  |  |  | 2194
90.1-2007 | ClimateZone 5 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 2195
90.1-2007 | ClimateZone 5 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2196
90.1-2007 | ClimateZone 5 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 2197
90.1-2007 | ClimateZone 5 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2198
90.1-2007 | ClimateZone 5 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2199
90.1-2007 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  |  | 0.35 |  |  | 0.4 |  | 2200
90.1-2007 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  | 0.4 |  | 2201
90.1-2007 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  | 0.4 |  | 2202
90.1-2007 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  | 0.55 |  |  | 0.4 |  | 2203
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.136 |  |  |  |  | 581
DOE Ref Pre-1980 | ClimateZone 7 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 582
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 583
DOE Ref 1980-2004 | ClimateZone 6B | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 854
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 585
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 586
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.41 Simple Glazing Window |  |  | 0.62 |  |  | 0.41 |  | 587
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.125 |  |  |  |  | 597
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.125 |  |  |  |  | 598
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.125 |  |  |  |  | 599
DOE Ref Pre-1980 | ClimateZone 8 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 600
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.076 |  |  |  |  | 523
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.076 |  |  |  |  | 524
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0 |  |  |  |  | 601
DOE Ref Pre-1980 | ClimateZone 6B | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 566
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door | [7 empty] | 603
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door | [7 empty] | 604
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.41 Simple Glazing Window |  |  | 0.62 |  |  | 0.41 |  | 605
90.1-2004 | ClimateZone 2 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1065
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.06 |  |  |  |  | 541
90.1-2004 | ClimateZone 2 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 1067
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.06 |  |  |  |  | 542
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.06 |  |  |  |  | 559
90.1-2004 | ClimateZone 6 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1517
90.1-2004 | ClimateZone 6 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.104 |  |  |  |  | 1519
90.1-2004 | ClimateZone 6 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1520
90.1-2004 | ClimateZone 6 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.084 |  |  |  |  | 1521
90.1-2004 | ClimateZone 6 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1522
90.1-2004 | ClimateZone 6 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1523
90.1-2004 | ClimateZone 6 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 1524
90.1-2004 | ClimateZone 6 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.038 |  |  |  |  | 1525
90.1-2004 | ClimateZone 6 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 1526
90.1-2004 | ClimateZone 6 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1527
90.1-2004 | ClimateZone 6 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.84 |  |  |  | 1528
90.1-2004 | ClimateZone 6 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1529
90.1-2004 | ClimateZone 6 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 1530
90.1-2004 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1531
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1532
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1533
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1534
90.1-2004 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1535
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1536
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1537
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1538
90.1-2004 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1539
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1540
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1541
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1542
90.1-2004 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1543
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1544
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1545
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1546
90.1-2004 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1547
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1548
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1549
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1550
90.1-2004 | ClimateZone 2 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.218 |  |  |  |  | 1106
90.1-2004 | ClimateZone 2 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.081 |  |  |  |  | 1108
90.1-2007 | ClimateZone 6 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 2261
90.1-2007 | ClimateZone 6 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.08 |  |  |  |  | 2263
90.1-2007 | ClimateZone 6 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 2264
90.1-2007 | ClimateZone 6 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2265
90.1-2007 | ClimateZone 6 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 2266
90.1-2007 | ClimateZone 6 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 2267
90.1-2007 | ClimateZone 6 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.064 |  |  |  |  | 2268
90.1-2007 | ClimateZone 6 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.038 |  |  |  |  | 2269
90.1-2007 | ClimateZone 6 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 2270
90.1-2007 | ClimateZone 6 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.54 |  |  |  | 2271
90.1-2007 | ClimateZone 6 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 2272
90.1-2007 | ClimateZone 6 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2273
90.1-2007 | ClimateZone 6 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2274
90.1-2007 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.35 |  |  | 0.4 |  | 2275
90.1-2007 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  | 0.4 |  | 2276
90.1-2007 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  | 0.4 |  | 2277
90.1-2007 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  | 0.55 |  |  | 0.4 |  | 2278
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.06 |  |  |  |  | 560
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.06 |  |  |  |  | 577
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.06 |  |  |  |  | 578
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.06 |  |  |  |  | 595
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.06 |  |  |  |  | 596
90.1-2010 | ClimateZone 2 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.093 |  |  |  |  | 2564
90.1-2010 | ClimateZone 2 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.093 |  |  |  |  | 2589
90.1-2010 | ClimateZone 2 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 2614
90.1-2010 | ClimateZone 2 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 2565
90.1-2010 | ClimateZone 2 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2590
90.1-2010 | ClimateZone 2 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 2615
90.1-2010 | ClimateZone 2 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2566
90.1-2010 | ClimateZone 2 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2591
90.1-2007 | ClimateZone 2 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  | 0.048 |  |  |  |  | 1960
90.1-2010 | ClimateZone 2 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2616
90.1-2007 | ClimateZone 2 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 1962
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.41 |  |  |  |  | 651
90.1-2010 | ClimateZone 1 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  | 0.048 |  |  |  |  | 2510
90.1-2010 | ClimateZone 1 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2512
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.34 |  |  |  |  | 633
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 648
90.1-2010 | ClimateZone 1 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof - Highly Reflective |  |  | 0.065 |  |  |  |  | 2511
90.1-2010 | ClimateZone 1 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 2513
90.1-2010 | ClimateZone 1 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.093 |  |  |  |  | 2514
90.1-2010 | ClimateZone 1 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 2515
90.1-2004 | ClimateZone 7 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1640
90.1-2004 | ClimateZone 7 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.09 |  |  |  |  | 1642
90.1-2004 | ClimateZone 7 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 1643
90.1-2004 | ClimateZone 7 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 1644
90.1-2004 | ClimateZone 7 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1645
90.1-2004 | ClimateZone 7 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 1646
90.1-2004 | ClimateZone 7 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 1647
90.1-2004 | ClimateZone 7 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.038 |  |  |  |  | 1648
90.1-2004 | ClimateZone 7 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 1649
90.1-2004 | ClimateZone 7 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1650
90.1-2004 | ClimateZone 7 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.84 |  |  |  | 1651
90.1-2004 | ClimateZone 7 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1652
90.1-2004 | ClimateZone 7 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 1653
90.1-2007 | ClimateZone 2 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  | 0.048 |  |  |  |  | 1985
90.1-2004 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1654
90.1-2007 | ClimateZone 2 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 1987
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1655
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1656
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1657
90.1-2004 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.49 |  | 1658
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.49 |  | 1659
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.49 |  | 1660
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.49 |  | 1661
90.1-2004 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.49 |  | 1662
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.49 |  | 1663
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.49 |  | 1664
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.49 |  | 1665
90.1-2004 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.49 |  | 1666
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.49 |  | 1667
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.49 |  | 1668
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.49 |  | 1669
90.1-2004 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.36 |  | 1670
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.36 |  | 1671
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.36 |  | 1672
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.36 |  | 1673
90.1-2007 | ClimateZone 2 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.218 |  |  |  |  | 2010
90.1-2007 | ClimateZone 2 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.081 |  |  |  |  | 2012
90.1-2007 | ClimateZone 7 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 2336
90.1-2007 | ClimateZone 7 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.071 |  |  |  |  | 2338
90.1-2007 | ClimateZone 7 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 2339
90.1-2007 | ClimateZone 7 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2340
90.1-2007 | ClimateZone 7 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 2341
90.1-2007 | ClimateZone 7 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 2342
90.1-2007 | ClimateZone 7 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.064 |  |  |  |  | 2343
90.1-2007 | ClimateZone 7 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.038 |  |  |  |  | 2344
90.1-2007 | ClimateZone 7 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 2345
90.1-2007 | ClimateZone 7 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.52 |  |  |  | 2346
90.1-2007 | ClimateZone 7 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.843 |  |  |  | 2347
90.1-2007 | ClimateZone 7 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 2348
90.1-2007 | ClimateZone 7 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2349
90.1-2007 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.35 |  |  | 0.45 |  | 2350
90.1-2007 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  | 0.4 |  |  | 0.45 |  | 2351
90.1-2007 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  | 0.45 |  | 2352
90.1-2007 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  | 0.45 |  | 2353
90.1-2010 | ClimateZone 1 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2516
90.1-2010 | ClimateZone 1 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2517
90.1-2010 | ClimateZone 1 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.35 |  |  |  |  | 2518
90.1-2010 | ClimateZone 1 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.282 |  |  |  |  | 2519
90.1-2010 | ClimateZone 1 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 2520
90.1-2010 | ClimateZone 1 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2521
90.1-2010 | ClimateZone 1 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 2522
90.1-2010 | ClimateZone 1 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2523
90.1-2010 | ClimateZone 1 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2524
90.1-2010 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2525
90.1-2010 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2526
90.1-2010 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2527
90.1-2010 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2528
90.1-2010 | ClimateZone 3 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  | 0.048 |  |  |  |  | 2660
90.1-2010 | ClimateZone 3 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2662
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 666
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.24 |  |  |  |  | 652
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.15 |  |  |  |  | 634
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.24 |  |  |  |  | 653
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.15 |  |  |  |  | 635
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.15 |  |  |  |  | 644
90.1-2004 | ClimateZone 8 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.049 |  |  |  |  | 1763
90.1-2004 | ClimateZone 8 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.08 |  |  |  |  | 1765
90.1-2004 | ClimateZone 8 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 1766
90.1-2004 | ClimateZone 8 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 1767
90.1-2004 | ClimateZone 8 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 1768
90.1-2004 | ClimateZone 8 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 1769
90.1-2004 | ClimateZone 8 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.064 |  |  |  |  | 1770
90.1-2004 | ClimateZone 8 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.038 |  |  |  |  | 1771
90.1-2004 | ClimateZone 8 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 1772
90.1-2004 | ClimateZone 8 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.54 |  |  |  | 1773
90.1-2004 | ClimateZone 8 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.78 |  |  |  | 1774
90.1-2004 | ClimateZone 8 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 1775
90.1-2004 | ClimateZone 8 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 1776
90.1-2004 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 1 | 10 | 0.46 |  |  |  |  | 1777
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 1 | 10 | 0.46 |  |  |  |  | 1778
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 1 | 10 | 0.46 |  |  |  |  | 1779
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 1 | 10 | 0.46 |  |  |  |  | 1780
90.1-2004 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 10.001 | 20 | 0.46 |  |  |  |  | 1781
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 10.001 | 20 | 0.46 |  |  |  |  | 1782
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 10.001 | 20 | 0.46 |  |  |  |  | 1783
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.24 |  |  |  |  | 662
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 10.001 | 20 | 0.46 |  |  |  |  | 1784
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.23 |  |  |  |  | 363
90.1-2004 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 20.001 | 30 | 0.46 |  |  |  |  | 1785
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 20.001 | 30 | 0.46 |  |  |  |  | 1786
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 20.001 | 30 | 0.46 |  |  |  |  | 1787
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 20.001 | 30 | 0.46 |  |  |  |  | 1788
90.1-2004 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 30.001 | 40 | 0.46 |  |  |  |  | 1789
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 30.001 | 40 | 0.46 |  |  |  |  | 1790
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 30.001 | 40 | 0.46 |  |  |  |  | 1791
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 30.001 | 40 | 0.46 |  |  |  |  | 1792
90.1-2004 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg | 40.001 | 100 | 0.35 |  |  |  |  | 1793
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg | 40.001 | 100 | 0.35 |  |  |  |  | 1794
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg | 40.001 | 100 | 0.35 |  |  |  |  | 1795
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg | 40.001 | 100 | 0.35 |  |  |  |  | 1796
90.1-2007 | ClimateZone 8 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.049 |  |  |  |  | 2411
90.1-2007 | ClimateZone 8 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.071 |  |  |  |  | 2413
90.1-2007 | ClimateZone 8 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 2414
90.1-2007 | ClimateZone 8 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2415
90.1-2013 | ClimateZone 2 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  | 0.039 |  |  |  |  | 3160
90.1-2013 | ClimateZone 2 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.041 |  |  |  |  | 3161
90.1-2013 | ClimateZone 2 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 3162
90.1-2013 | ClimateZone 2 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 3163
90.1-2013 | ClimateZone 2 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.094 |  |  |  |  | 3164
90.1-2013 | ClimateZone 2 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.084 |  |  |  |  | 3165
90.1-2013 | ClimateZone 2 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 3166
90.1-2013 | ClimateZone 2 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 3167
90.1-2013 | ClimateZone 2 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.107 |  |  |  |  | 3168
90.1-2013 | ClimateZone 2 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.038 |  |  |  |  | 3169
90.1-2013 | ClimateZone 2 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 3170
90.1-2013 | ClimateZone 2 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 3171
90.1-2013 | ClimateZone 2 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.9 |  |  |  | 3172
90.1-2013 | ClimateZone 2 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 3173
90.1-2013 | ClimateZone 2 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3174
90.1-2013 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.38 SHGC 0.26 Dbl Ref B-H Tint 6mm/13mm Arg |  |  | 0.4 |  |  | 0.25 | 1.1 | 3175
90.1-2013 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.57 |  |  | 0.25 | 1.1 | 3176
90.1-2013 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  | 0.25 | 1.1 | 3177
90.1-2013 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.83 |  |  | 0.25 | 1.1 | 3178
90.1-2013 | ClimateZone 2 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  | 0.039 |  |  |  |  | 3185
90.1-2013 | ClimateZone 2 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.041 |  |  |  |  | 3186
90.1-2013 | ClimateZone 2 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 3187
90.1-2013 | ClimateZone 2 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.123 |  |  |  |  | 3188
90.1-2013 | ClimateZone 2 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.094 |  |  |  |  | 3189
90.1-2013 | ClimateZone 2 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 3190
90.1-2013 | ClimateZone 2 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 3191
90.1-2013 | ClimateZone 2 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 3192
90.1-2013 | ClimateZone 2 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 3193
90.1-2013 | ClimateZone 2 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.038 |  |  |  |  | 3194
90.1-2013 | ClimateZone 2 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 3195
90.1-2013 | ClimateZone 2 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 3196
90.1-2013 | ClimateZone 2 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 3197
90.1-2013 | ClimateZone 2 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3198
90.1-2013 | ClimateZone 2 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3199
90.1-2013 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.38 SHGC 0.26 Dbl Ref B-H Tint 6mm/13mm Arg |  |  | 0.4 |  |  | 0.25 | 1.1 | 3200
90.1-2013 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.57 |  |  | 0.25 | 1.1 | 3201
90.1-2013 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  | 0.25 | 1.1 | 3202
90.1-2013 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.77 |  |  | 0.25 | 1.1 | 3203
90.1-2013 | ClimateZone 2 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.173 |  |  |  |  | 3210
90.1-2013 | ClimateZone 2 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.096 |  |  |  |  | 3211
90.1-2013 | ClimateZone 2 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.053 |  |  |  |  | 3212
90.1-2013 | ClimateZone 2 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 3213
90.1-2013 | ClimateZone 2 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.162 |  |  |  |  | 3214
90.1-2013 | ClimateZone 2 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 3215
90.1-2013 | ClimateZone 2 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 3216
90.1-2013 | ClimateZone 2 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 3217
90.1-2013 | ClimateZone 2 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 3218
90.1-2013 | ClimateZone 2 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.069 |  |  |  |  | 3219
90.1-2013 | ClimateZone 2 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.066 |  |  |  |  | 3220
90.1-2013 | ClimateZone 2 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 3221
90.1-2013 | ClimateZone 2 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 3222
90.1-2013 | ClimateZone 2 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 3223
90.1-2013 | ClimateZone 2 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 3224
90.1-2013 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 0.93 |  |  |  |  | 3225
90.1-2013 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 3226
90.1-2013 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 3227
90.1-2013 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.83 |  |  |  |  | 3228
90.1-2004 | ClimateZone 3A | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1147
90.1-2007 | ClimateZone 8 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.036 |  |  |  |  | 2416
90.1-2004 | ClimateZone 3A | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 1149
90.1-2007 | ClimateZone 8 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 2417
90.1-2007 | ClimateZone 8 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.057 |  |  |  |  | 2418
90.1-2007 | ClimateZone 8 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.032 |  |  |  |  | 2419
90.1-2007 | ClimateZone 8 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 2420
90.1-2007 | ClimateZone 8 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.52 |  |  |  | 2421
90.1-2007 | ClimateZone 8 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.688 |  |  |  | 2422
90.1-2007 | ClimateZone 8 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 2423
90.1-2007 | ClimateZone 8 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2424
90.1-2007 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.35 |  |  | 0.45 |  | 2425
90.1-2007 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  | 0.4 |  |  | 0.45 |  | 2426
90.1-2007 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  | 0.45 |  | 2427
90.1-2007 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  | 0.45 |  | 2428
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.23 |  |  |  |  | 345
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 378
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 360
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 364
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 346
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 1 |  |  |  |  | 616
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.13 |  |  |  |  | 670
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.16 |  |  |  |  | 688
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.13 |  |  |  |  | 706
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 724
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.1 |  |  |  |  | 742
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.092 |  |  |  |  | 760
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.082 |  |  |  |  | 778
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.082 |  |  |  |  | 796
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.082 |  |  |  |  | 814
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.065 |  |  |  |  | 832
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.072 |  |  |  |  | 850
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.058 |  |  |  |  | 868
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.045 |  |  |  |  | 886
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 328
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.225 |  |  |  |  | 382
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 400
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.224 |  |  |  |  | 418
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.178 |  |  |  |  | 436
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.184 |  |  |  |  | 454
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.175 |  |  |  |  | 472
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.156 |  |  |  |  | 490
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.161 |  |  |  |  | 508
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.161 |  |  |  |  | 526
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.145 |  |  |  |  | 544
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.145 |  |  |  |  | 562
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.136 |  |  |  |  | 580
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.125 |  |  |  |  | 598
DOE Ref 1980-2004 | ClimateZone 2B | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.24 |  |  |  |  | 652
DOE Ref 1980-2004 | ClimateZone 2A | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.15 |  |  |  |  | 634
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 364
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 346
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 365
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 347
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 374
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 356
90.1-2010 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.75 |  |  | 0.25 |  | 2578
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.52 SHGC 0.49 Simple Glazing Window |  |  | 0.52 |  |  | 0.49 |  | 875
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.52 SHGC 0.615 Simple Glazing Window |  |  | 0.52 |  |  | 0.49 |  | 893
DOE Ref Pre-1980 | ClimateZone 2B | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  | 1.22 |  |  | 0.54 |  | 371
DOE Ref Pre-1980 | ClimateZone 2A | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  | 1.22 |  |  | 0.54 |  | 353
90.1-2010 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.75 |  |  | 0.25 |  | 2603
90.1-2010 | ClimateZone 3 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.055 |  |  |  |  | 2661
90.1-2010 | ClimateZone 3 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.104 |  |  |  |  | 2663
90.1-2010 | ClimateZone 3 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.084 |  |  |  |  | 2664
90.1-2010 | ClimateZone 3 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2665
90.1-2010 | ClimateZone 3 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2666
90.1-2004 | ClimateZone 3A | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1188
90.1-2010 | ClimateZone 3 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2667
90.1-2004 | ClimateZone 3A | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 1190
90.1-2010 | ClimateZone 3 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 2668
90.1-2010 | ClimateZone 3 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.052 |  |  |  |  | 2669
90.1-2010 | ClimateZone 3 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 2670
90.1-2010 | ClimateZone 3 | GroundContactFloor | Unheated | Residential | Smallhotel 2010 Slab Floor |  |  |  | 0.73 |  |  |  | 2671
90.1-2010 | ClimateZone 3 | GroundContactFloor | Heated | Residential | Smallhotel 2010 Slab Floor |  |  |  | 0.09 |  |  |  | 2672
90.1-2010 | ClimateZone 3 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2673
90.1-2010 | ClimateZone 3 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2674
90.1-2010 | ClimateZone 3 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  | 0.25 |  | 2675
90.1-2010 | ClimateZone 3 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.6 |  |  | 0.25 |  | 2676
90.1-2010 | ClimateZone 3 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 0.9 |  |  | 0.25 |  | 2677
90.1-2010 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  | 0.25 |  | 2678
90.1-2010 | ClimateZone 4 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.055 |  |  |  |  | 2736
90.1-2010 | ClimateZone 4 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.09 |  |  |  |  | 2738
90.1-2010 | ClimateZone 4 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.084 |  |  |  |  | 2739
90.1-2010 | ClimateZone 4 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2740
90.1-2010 | ClimateZone 4 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2741
90.1-2010 | ClimateZone 4 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 2742
90.1-2010 | ClimateZone 4 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.074 |  |  |  |  | 2743
90.1-2010 | ClimateZone 4 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.038 |  |  |  |  | 2744
90.1-2010 | ClimateZone 4 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 2745
90.1-2010 | ClimateZone 4 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.54 |  |  |  | 2746
90.1-2010 | ClimateZone 4 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 2747
90.1-2010 | ClimateZone 4 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2748
90.1-2010 | ClimateZone 4 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2749
90.1-2010 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.39 SHGC 0.38 |  |  | 0.4 |  |  | 0.4 |  | 2750
90.1-2010 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.5 |  |  | 0.4 |  | 2751
90.1-2010 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.85 |  |  | 0.4 |  | 2752
90.1-2010 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  | 0.55 |  |  | 0.4 |  | 2753
90.1-2004 | ClimateZone 3A | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.218 |  |  |  |  | 1229
90.1-2004 | ClimateZone 3A | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.081 |  |  |  |  | 1231
90.1-2010 | ClimateZone 4 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2735
90.1-2010 | ClimateZone 4 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2737
90.1-2010 | ClimateZone 5 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.055 |  |  |  |  | 2811
90.1-2010 | ClimateZone 5 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.08 |  |  |  |  | 2813
90.1-2010 | ClimateZone 5 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.069 |  |  |  |  | 2814
90.1-2010 | ClimateZone 5 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2815
90.1-2010 | ClimateZone 5 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 2816
90.1-2010 | ClimateZone 5 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 2817
90.1-2010 | ClimateZone 5 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.064 |  |  |  |  | 2818
90.1-2010 | ClimateZone 5 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.038 |  |  |  |  | 2819
90.1-2010 | ClimateZone 5 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 2820
90.1-2010 | ClimateZone 5 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.54 |  |  |  | 2821
90.1-2010 | ClimateZone 5 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 2822
90.1-2010 | ClimateZone 5 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 2823
90.1-2010 | ClimateZone 5 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2824
90.1-2010 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.35 |  |  | 0.4 |  | 2825
90.1-2010 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  | 0.4 |  | 2826
90.1-2010 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  | 0.4 |  | 2827
90.1-2010 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  | 0.55 |  |  | 0.4 |  | 2828
90.1-2010 | ClimateZone 6 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.049 |  |  |  |  | 2886
90.1-2004 | ClimateZone 1 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 943
90.1-2004 | ClimateZone 1 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 945
90.1-2004 | ClimateZone 1 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 946
90.1-2004 | ClimateZone 1 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 947
90.1-2004 | ClimateZone 1 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 948
90.1-2004 | ClimateZone 1 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 949
90.1-2004 | ClimateZone 1 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 950
90.1-2004 | ClimateZone 1 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.35 |  |  |  |  | 951
90.1-2004 | ClimateZone 1 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.282 |  |  |  |  | 952
90.1-2004 | ClimateZone 1 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 953
90.1-2004 | ClimateZone 1 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 954
90.1-2007 | ClimateZone 3 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  | 0.048 |  |  |  |  | 2035
90.1-2004 | ClimateZone 1 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 955
90.1-2007 | ClimateZone 3 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2037
90.1-2004 | ClimateZone 1 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 956
90.1-2004 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  | 0.25 |  | 957
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  | 0.25 |  | 958
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  | 0.25 |  | 959
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  | 0.25 |  | 960
90.1-2004 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 961
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 962
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 963
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 964
90.1-2004 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 965
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 966
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 967
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 968
90.1-2004 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 969
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 970
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 971
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 972
90.1-2004 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.19 |  | 973
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.19 |  | 974
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.19 |  | 975
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.19 |  | 976
90.1-2007 | ClimateZone 3 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  | 0.048 |  |  |  |  | 2060
90.1-2007 | ClimateZone 3 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2062
90.1-2007 | ClimateZone 1 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof - Highly Reflective |  |  | 0.65 |  |  |  |  | 1911
90.1-2007 | ClimateZone 1 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 1913
90.1-2007 | ClimateZone 1 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1914
90.1-2007 | ClimateZone 1 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 1915
90.1-2007 | ClimateZone 1 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1916
90.1-2007 | ClimateZone 1 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1917
90.1-2007 | ClimateZone 1 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 1918
90.1-2007 | ClimateZone 1 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.35 |  |  |  |  | 1919
90.1-2007 | ClimateZone 1 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.282 |  |  |  |  | 1920
90.1-2007 | ClimateZone 1 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1921
90.1-2007 | ClimateZone 1 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1922
90.1-2007 | ClimateZone 1 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1923
90.1-2007 | ClimateZone 1 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1924
90.1-2007 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 1925
90.1-2007 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 1926
90.1-2007 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 1927
90.1-2007 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 1928
90.1-2007 | ClimateZone 3 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.173 |  |  |  |  | 2085
90.1-2007 | ClimateZone 3 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.053 |  |  |  |  | 2087
90.1-2010 | ClimateZone 6 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.071 |  |  |  |  | 2888
90.1-2010 | ClimateZone 6 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.069 |  |  |  |  | 2889
90.1-2010 | ClimateZone 6 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2890
90.1-2010 | ClimateZone 6 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 2891
90.1-2010 | ClimateZone 6 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 2892
90.1-2010 | ClimateZone 6 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.057 |  |  |  |  | 2893
90.1-2010 | ClimateZone 6 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.032 |  |  |  |  | 2894
90.1-2010 | ClimateZone 6 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 2895
90.1-2010 | ClimateZone 6 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.52 |  |  |  | 2896
90.1-2010 | ClimateZone 6 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.688 |  |  |  | 2897
90.1-2010 | ClimateZone 6 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 2898
90.1-2010 | ClimateZone 6 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2899
90.1-2010 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.35 |  |  | 0.4 |  | 2900
90.1-2010 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  | 0.4 |  | 2901
90.1-2010 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  | 0.4 |  | 2902
90.1-2010 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  | 0.55 |  |  | 0.4 |  | 2903
90.1-2010 | ClimateZone 7 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.049 |  |  |  |  | 2961
90.1-2010 | ClimateZone 7 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.071 |  |  |  |  | 2963
90.1-2010 | ClimateZone 7 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 2964
90.1-2004 | ClimateZone 2 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1066
90.1-2004 | ClimateZone 2 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 1068
90.1-2004 | ClimateZone 2 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1069
90.1-2004 | ClimateZone 2 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 1070
90.1-2004 | ClimateZone 2 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1071
90.1-2004 | ClimateZone 2 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1072
90.1-2004 | ClimateZone 2 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.107 |  |  |  |  | 1073
90.1-2004 | ClimateZone 2 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.052 |  |  |  |  | 1074
90.1-2004 | ClimateZone 2 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.051 |  |  |  |  | 1075
90.1-2004 | ClimateZone 2 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1076
90.1-2004 | ClimateZone 2 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1077
90.1-2004 | ClimateZone 2 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1078
90.1-2004 | ClimateZone 2 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1079
90.1-2004 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 1 | 10 | 1.22 |  |  | 0.39 |  | 1080
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 1 | 10 | 1.22 |  |  | 0.39 |  | 1081
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 1 | 10 | 1.22 |  |  | 0.39 |  | 1082
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 1 | 10 | 1.22 |  |  | 0.39 |  | 1083
90.1-2004 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 1084
90.1-2010 | ClimateZone 7 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.042 |  |  |  |  | 2965
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 1085
90.1-2010 | ClimateZone 7 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 2966
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 1086
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  | 0.25 |  | 1087
90.1-2004 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 1088
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 1089
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 1090
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  | 0.25 |  | 1091
90.1-2004 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 1092
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 1093
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 1094
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  | 0.25 |  | 1095
90.1-2004 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.17 |  | 1096
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.17 |  | 1097
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.17 |  | 1098
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | 40.001 | 100 | 1.22 |  |  | 0.17 |  | 1099
90.1-2007 | ClimateZone 2 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1986
90.1-2007 | ClimateZone 2 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.123 |  |  |  |  | 1988
90.1-2010 | ClimateZone 7 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.092 |  |  | 2967
90.1-2007 | ClimateZone 2 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1989
90.1-2010 | ClimateZone 7 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.051 |  |  |  |  | 2968
90.1-2007 | ClimateZone 2 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 1990
90.1-2007 | ClimateZone 2 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1991
90.1-2007 | ClimateZone 2 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1992
90.1-2007 | ClimateZone 2 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 1993
90.1-2007 | ClimateZone 2 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.052 |  |  |  |  | 1994
90.1-2007 | ClimateZone 2 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 1995
90.1-2007 | ClimateZone 2 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1996
90.1-2007 | ClimateZone 2 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1997
90.1-2007 | ClimateZone 2 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1998
90.1-2007 | ClimateZone 2 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 1999
90.1-2007 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.75 |  |  | 0.25 |  | 2000
90.1-2007 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.7 |  |  | 0.25 |  | 2001
90.1-2007 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.1 |  |  | 0.25 |  | 2002
90.1-2007 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.75 |  |  | 0.25 |  | 2003
90.1-2010 | ClimateZone 7 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.032 |  |  |  |  | 2969
90.1-2010 | ClimateZone 7 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 2970
90.1-2013 | ClimateZone 3 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.039 |  |  |  |  | 3235
90.1-2013 | ClimateZone 3 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.041 |  |  |  |  | 3236
90.1-2013 | ClimateZone 3 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 3237
90.1-2013 | ClimateZone 3 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.123 |  |  |  |  | 3238
90.1-2013 | ClimateZone 3 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.094 |  |  |  |  | 3239
90.1-2013 | ClimateZone 3 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.077 |  |  |  |  | 3240
90.1-2013 | ClimateZone 3 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 3241
90.1-2013 | ClimateZone 3 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 3242
90.1-2013 | ClimateZone 3 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.074 |  |  |  |  | 3243
90.1-2013 | ClimateZone 3 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.038 |  |  |  |  | 3244
90.1-2013 | ClimateZone 3 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 3245
90.1-2013 | ClimateZone 3 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 3246
90.1-2013 | ClimateZone 3 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 3247
90.1-2013 | ClimateZone 3 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 3248
90.1-2013 | ClimateZone 3 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3249
90.1-2013 | ClimateZone 3 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  |  | 0.35 |  |  | 0.25 | 1.1 | 3250
90.1-2013 | ClimateZone 3 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.5 |  |  | 0.25 | 1.1 | 3251
90.1-2013 | ClimateZone 3 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.6 |  |  | 0.25 | 1.1 | 3252
90.1-2013 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.77 |  |  | 0.25 | 1.1 | 3253
90.1-2013 | ClimateZone 3 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  | 0.039 |  |  |  |  | 3260
90.1-2013 | ClimateZone 3 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.041 |  |  |  |  | 3261
90.1-2013 | ClimateZone 3 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 3262
90.1-2013 | ClimateZone 3 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.104 |  |  |  |  | 3263
90.1-2013 | ClimateZone 3 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.072 |  |  |  |  | 3264
90.1-2013 | ClimateZone 3 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 3265
90.1-2013 | ClimateZone 3 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 3266
90.1-2013 | ClimateZone 3 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 3267
90.1-2013 | ClimateZone 3 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.074 |  |  |  |  | 3268
90.1-2013 | ClimateZone 3 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.038 |  |  |  |  | 3269
90.1-2013 | ClimateZone 3 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 3270
90.1-2013 | ClimateZone 3 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.54 |  |  |  | 3271
90.1-2013 | ClimateZone 3 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 3272
90.1-2013 | ClimateZone 3 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3273
90.1-2013 | ClimateZone 3 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3274
90.1-2013 | ClimateZone 3 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  |  | 0.35 |  |  | 0.25 | 1.1 | 3275
90.1-2013 | ClimateZone 3 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.5 |  |  | 0.25 | 1.1 | 3276
90.1-2013 | ClimateZone 3 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.6 |  |  | 0.25 | 1.1 | 3277
90.1-2013 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.68 |  |  | 0.25 | 1.1 | 3278
90.1-2013 | ClimateZone 3 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.119 |  |  |  |  | 3285
90.1-2013 | ClimateZone 3 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.096 |  |  |  |  | 3286
90.1-2013 | ClimateZone 3 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.053 |  |  |  |  | 3287
90.1-2013 | ClimateZone 3 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 3288
90.1-2013 | ClimateZone 3 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.162 |  |  |  |  | 3289
90.1-2013 | ClimateZone 3 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 3290
90.1-2013 | ClimateZone 3 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 3291
90.1-2013 | ClimateZone 3 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 3292
90.1-2013 | ClimateZone 3 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.137 |  |  |  |  | 3293
90.1-2013 | ClimateZone 3 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 3294
90.1-2013 | ClimateZone 3 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.051 |  |  |  |  | 3295
90.1-2013 | ClimateZone 3 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 3296
90.1-2013 | ClimateZone 3 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 3297
90.1-2013 | ClimateZone 3 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 3298
90.1-2013 | ClimateZone 3 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 3299
90.1-2013 | ClimateZone 3 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.87 |  |  |  |  | 3300
90.1-2013 | ClimateZone 3 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 3301
90.1-2013 | ClimateZone 3 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 3302
90.1-2013 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.77 |  |  |  |  | 3303
90.1-2004 | ClimateZone 4 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1270
90.1-2010 | ClimateZone 7 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.52 |  |  |  | 2971
90.1-2004 | ClimateZone 4 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 1272
90.1-2010 | ClimateZone 7 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.688 |  |  |  | 2972
90.1-2010 | ClimateZone 7 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 2973
90.1-2010 | ClimateZone 7 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2974
90.1-2010 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  |  | 0.35 |  |  |  |  | 2975
90.1-2010 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  | 0.4 |  |  |  |  | 2976
90.1-2010 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  |  |  | 2977
90.1-2010 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  |  |  | 2978
90.1-2010 | ClimateZone 5 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2810
90.1-2010 | ClimateZone 5 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2812
90.1-2010 | ClimateZone 8 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.035 |  |  |  |  | 3036
90.1-2010 | ClimateZone 8 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.052 |  |  |  |  | 3038
90.1-2010 | ClimateZone 8 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 3039
90.1-2010 | ClimateZone 8 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.037 |  |  |  |  | 3040
90.1-2010 | ClimateZone 8 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.036 |  |  |  |  | 3041
90.1-2004 | ClimateZone 3A | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1189
90.1-2004 | ClimateZone 3A | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.123 |  |  |  |  | 1191
90.1-2004 | ClimateZone 3A | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1192
90.1-2004 | ClimateZone 3A | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.084 |  |  |  |  | 1193
90.1-2004 | ClimateZone 3A | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1194
90.1-2004 | ClimateZone 3A | GroundContactWall | Mass | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight |  |  |  |  | 1.14 |  |  | 1195
90.1-2004 | ClimateZone 3A | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 1196
90.1-2004 | ClimateZone 3A | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.052 |  |  |  |  | 1197
90.1-2004 | ClimateZone 3A | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 1198
90.1-2004 | ClimateZone 3A | GroundContactFloor | Unheated | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight |  |  |  | 0.73 |  |  |  | 1199
90.1-2004 | ClimateZone 3A | GroundContactFloor | Heated | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight |  |  |  | 1.02 |  |  |  | 1200
90.1-2004 | ClimateZone 3A | ExteriorDoor | Swinging | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight |  |  | 0.7 |  |  |  |  | 1201
90.1-2004 | ClimateZone 3A | ExteriorDoor | NonSwinging | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight |  |  | 0.5 |  |  |  |  | 1202
90.1-2004 | ClimateZone 3A | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 1 | 10 | 0.57 |  |  | 0.39 |  | 1203
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 1 | 10 | 0.57 |  |  | 0.39 |  | 1204
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 1 | 10 | 0.57 |  |  | 0.39 |  | 1205
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 1 | 10 | 0.57 |  |  | 0.39 |  | 1206
90.1-2004 | ClimateZone 3A | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1207
90.1-2004 | ClimateZone 4 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1311
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1208
90.1-2004 | ClimateZone 4 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 1313
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1209
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1210
90.1-2004 | ClimateZone 3A | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1211
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1212
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1213
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1214
90.1-2004 | ClimateZone 3A | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1215
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1216
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1217
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1218
90.1-2004 | ClimateZone 3A | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1219
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1220
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1221
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1222
90.1-2004 | ClimateZone 3B | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 1 | 10 | 0.57 |  |  | 0.39 |  | 1203
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 1 | 10 | 0.57 |  |  | 0.39 |  | 1204
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 1 | 10 | 0.57 |  |  | 0.39 |  | 1205
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 1 | 10 | 0.57 |  |  | 0.39 |  | 1206
90.1-2004 | ClimateZone 3B | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1207
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1208
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1209
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1210
90.1-2004 | ClimateZone 3B | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1211
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1212
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1213
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 20.001 | 30 | 0.57 |  |  | 0.25 |  | 1214
90.1-2004 | ClimateZone 3B | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1215
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1216
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1217
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 30.001 | 40 | 0.57 |  |  | 0.25 |  | 1218
90.1-2004 | ClimateZone 3B | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1219
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1220
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1221
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight | 40.001 | 100 | 0.46 |  |  | 0.19 |  | 1222
90.1-2004 | ClimateZone 3C | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm | 1 | 10 | 1.22 |  |  | 0.61 |  | 1203
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm | 1 | 10 | 1.22 |  |  | 0.61 |  | 1204
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm | 1 | 10 | 1.22 |  |  | 0.61 |  | 1205
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm | 1 | 10 | 1.22 |  |  | 0.61 |  | 1206
90.1-2004 | ClimateZone 3C | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm | 10.001 | 20 | 1.22 |  |  | 0.61 |  | 1207
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm | 10.001 | 20 | 1.22 |  |  | 0.61 |  | 1208
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm | 10.001 | 20 | 1.22 |  |  | 0.61 |  | 1209
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm | 10.001 | 20 | 1.22 |  |  | 0.61 |  | 1210
90.1-2004 | ClimateZone 3C | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 20.001 | 30 | 1.22 |  |  | 0.39 |  | 1211
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 20.001 | 30 | 1.22 |  |  | 0.39 |  | 1212
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 20.001 | 30 | 1.22 |  |  | 0.39 |  | 1213
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | 20.001 | 30 | 1.22 |  |  | 0.39 |  | 1214
90.1-2004 | ClimateZone 3C | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm | 30.001 | 40 | 1.22 |  |  | 0.34 |  | 1215
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm | 30.001 | 40 | 1.22 |  |  | 0.34 |  | 1216
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm | 30.001 | 40 | 1.22 |  |  | 0.34 |  | 1217
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm | 30.001 | 40 | 1.22 |  |  | 0.34 |  | 1218
90.1-2004 | ClimateZone 3C | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.72 SHGC 0.25 Simple Glazing Window | 40.001 | 100 | 0.72 |  |  | 0.25 |  | 1219
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.72 SHGC 0.25 Simple Glazing Window | 40.001 | 100 | 0.72 |  |  | 0.25 |  | 1220
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Simple Glazing Window | 40.001 | 100 | 0.72 |  |  | 0.25 |  | 1221
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Residential | U 0.72 SHGC 0.25 Simple Glazing Window | 40.001 | 100 | 0.72 |  |  | 0.25 |  | 1222
90.1-2007 | ClimateZone 3 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.055 |  |  |  |  | 2061
90.1-2007 | ClimateZone 3 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.104 |  |  |  |  | 2063
90.1-2007 | ClimateZone 3 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.084 |  |  |  |  | 2064
90.1-2007 | ClimateZone 3 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2065
90.1-2007 | ClimateZone 3 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2066
90.1-2007 | ClimateZone 3 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2067
90.1-2007 | ClimateZone 3 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 2068
90.1-2007 | ClimateZone 3 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.052 |  |  |  |  | 2069
90.1-2007 | ClimateZone 3 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 2070
90.1-2007 | ClimateZone 3 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2071
90.1-2007 | ClimateZone 3 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.09 |  |  |  | 2072
90.1-2007 | ClimateZone 3 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2073
90.1-2007 | ClimateZone 3 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2074
90.1-2007 | ClimateZone 3 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  | 0.25 |  | 2075
90.1-2007 | ClimateZone 3 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.6 |  |  | 0.25 |  | 2076
90.1-2007 | ClimateZone 3 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 0.9 |  |  | 0.25 |  | 2077
90.1-2007 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  | 0.25 |  | 2078
90.1-2004 | ClimateZone 4 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.218 |  |  |  |  | 1352
90.1-2004 | ClimateZone 4 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.081 |  |  |  |  | 1354
90.1-2010 | ClimateZone 8 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.075 |  |  | 3042
90.1-2010 | ClimateZone 8 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.051 |  |  |  |  | 3043
90.1-2010 | ClimateZone 8 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.032 |  |  |  |  | 3044
90.1-2010 | ClimateZone 8 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 3045
90.1-2010 | ClimateZone 8 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.51 |  |  |  | 3046
90.1-2010 | ClimateZone 8 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.688 |  |  |  | 3047
90.1-2010 | ClimateZone 8 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3048
90.1-2010 | ClimateZone 8 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3049
90.1-2010 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  |  | 0.35 |  |  |  |  | 3050
90.1-2010 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  | 0.4 |  |  |  |  | 3051
90.1-2010 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  |  |  | 3052
90.1-2010 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  |  |  | 3053
90.1-2010 | ClimateZone 6 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2885
90.1-2010 | ClimateZone 6 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2887
90.1-2010 | ClimateZone 7 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2960
90.1-2010 | ClimateZone 7 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2962
90.1-2010 | ClimateZone 8 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 3035
90.1-2004 | ClimateZone 4 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1312
90.1-2004 | ClimateZone 4 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.104 |  |  |  |  | 1314
90.1-2004 | ClimateZone 4 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1315
90.1-2004 | ClimateZone 4 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 1316
90.1-2004 | ClimateZone 4 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1317
90.1-2004 | ClimateZone 4 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1318
90.1-2004 | ClimateZone 4 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 1319
90.1-2004 | ClimateZone 4 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.038 |  |  |  |  | 1320
90.1-2004 | ClimateZone 4 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 1321
90.1-2004 | ClimateZone 4 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1322
90.1-2004 | ClimateZone 4 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.84 |  |  |  | 1323
90.1-2007 | ClimateZone 4 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2110
90.1-2004 | ClimateZone 4 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1324
90.1-2007 | ClimateZone 4 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2112
90.1-2004 | ClimateZone 4 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 1325
90.1-2004 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1326
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1327
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1328
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.39 |  | 1329
90.1-2004 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1330
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1331
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1332
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1333
90.1-2004 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1334
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1335
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1336
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1337
90.1-2004 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1338
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1339
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1340
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1341
90.1-2004 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.25 |  | 1342
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.25 |  | 1343
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.25 |  | 1344
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.25 |  | 1345
90.1-2007 | ClimateZone 4 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2135
90.1-2007 | ClimateZone 4 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2137
90.1-2007 | ClimateZone 4 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 2136
90.1-2007 | ClimateZone 4 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.09 |  |  |  |  | 2138
90.1-2007 | ClimateZone 4 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 2139
90.1-2007 | ClimateZone 4 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2140
90.1-2007 | ClimateZone 4 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2141
90.1-2007 | ClimateZone 4 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 2142
90.1-2007 | ClimateZone 4 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.074 |  |  |  |  | 2143
90.1-2007 | ClimateZone 4 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.038 |  |  |  |  | 2144
90.1-2007 | ClimateZone 4 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 2145
90.1-2007 | ClimateZone 4 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.54 |  |  |  | 2146
90.1-2007 | ClimateZone 4 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 2147
90.1-2007 | ClimateZone 4 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2148
90.1-2007 | ClimateZone 4 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2149
90.1-2007 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.39 SHGC 0.38 |  |  | 0.4 |  |  | 0.4 |  | 2150
90.1-2007 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.5 |  |  | 0.4 |  | 2151
90.1-2007 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.85 |  |  | 0.4 |  | 2152
90.1-2007 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  | 0.55 |  |  | 0.4 |  | 2153
90.1-2007 | ClimateZone 4 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.173 |  |  |  |  | 2160
90.1-2007 | ClimateZone 4 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.053 |  |  |  |  | 2162
90.1-2010 | ClimateZone 8 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.021 |  |  |  |  | 3037
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 625
90.1-2010 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2628
90.1-2010 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.7 |  |  | 0.25 |  | 2576
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 679
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 697
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 715
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 733
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 751
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 769
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 787
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 805
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 823
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 841
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 859
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 877
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 895
90.1-2010 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.7 |  |  | 0.25 |  | 2601
90.1-2010 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2626
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 1 |  |  |  |  | 626
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 627
90.1-2010 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.1 |  |  | 0.25 |  | 2577
90.1-2010 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.1 |  |  | 0.25 |  | 2602
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.13 |  |  |  |  | 680
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 681
90.1-2004 | ClimateZone 5 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1435
90.1-2004 | ClimateZone 5 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.09 |  |  |  |  | 1437
90.1-2004 | ClimateZone 5 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 1438
90.1-2004 | ClimateZone 5 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 1439
90.1-2004 | ClimateZone 5 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1440
90.1-2004 | ClimateZone 5 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1441
90.1-2004 | ClimateZone 5 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.074 |  |  |  |  | 1442
90.1-2004 | ClimateZone 5 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.038 |  |  |  |  | 1443
90.1-2004 | ClimateZone 5 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 1444
90.1-2004 | ClimateZone 5 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1445
90.1-2004 | ClimateZone 5 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.84 |  |  |  | 1446
90.1-2004 | ClimateZone 5 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1447
90.1-2004 | ClimateZone 5 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 1448
90.1-2004 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1449
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1450
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1451
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1452
90.1-2004 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1453
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.16 |  |  |  |  | 698
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1454
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 699
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1455
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1456
90.1-2004 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1457
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1458
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1459
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1460
90.1-2004 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1461
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1462
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1463
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1464
90.1-2004 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1465
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1466
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1467
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1468
90.1-2007 | ClimateZone 5 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 2211
90.1-2007 | ClimateZone 5 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.08 |  |  |  |  | 2213
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.13 |  |  |  |  | 716
90.1-2007 | ClimateZone 5 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 2214
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 717
90.1-2007 | ClimateZone 5 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2215
90.1-2007 | ClimateZone 5 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 2216
90.1-2007 | ClimateZone 5 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 2217
90.1-2007 | ClimateZone 5 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.064 |  |  |  |  | 2218
90.1-2007 | ClimateZone 5 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.038 |  |  |  |  | 2219
90.1-2007 | ClimateZone 5 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 2220
90.1-2007 | ClimateZone 5 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.54 |  |  |  | 2221
90.1-2007 | ClimateZone 5 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 2222
90.1-2007 | ClimateZone 5 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 2223
90.1-2007 | ClimateZone 5 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2224
90.1-2007 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.35 |  |  | 0.4 |  | 2225
90.1-2007 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  | 0.4 |  | 2226
90.1-2007 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  | 0.4 |  | 2227
90.1-2007 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  | 0.55 |  |  | 0.4 |  | 2228
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 734
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 735
90.1-2013 | ClimateZone 4 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.032 |  |  |  |  | 3310
90.1-2013 | ClimateZone 4 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.037 |  |  |  |  | 3311
90.1-2013 | ClimateZone 4 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.021 |  |  |  |  | 3312
90.1-2013 | ClimateZone 4 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.104 |  |  |  |  | 3313
90.1-2013 | ClimateZone 4 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.06 |  |  |  |  | 3314
90.1-2013 | ClimateZone 4 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 3315
90.1-2013 | ClimateZone 4 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 3316
90.1-2013 | ClimateZone 4 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 3317
90.1-2013 | ClimateZone 4 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.057 |  |  |  |  | 3318
90.1-2013 | ClimateZone 4 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.038 |  |  |  |  | 3319
90.1-2013 | ClimateZone 4 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 3320
90.1-2013 | ClimateZone 4 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.52 |  |  |  | 3321
90.1-2013 | ClimateZone 4 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.843 |  |  |  | 3322
90.1-2013 | ClimateZone 4 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3323
90.1-2013 | ClimateZone 4 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3324
90.1-2013 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.35 |  |  | 0.4 | 1.1 | 3325
90.1-2013 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.42 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/6mm Air |  |  | 0.42 |  |  | 0.4 | 1.1 | 3326
90.1-2013 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.5 |  |  | 0.4 | 1.1 | 3327
90.1-2013 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.77 |  |  | 0.4 | 1.1 | 3328
90.1-2013 | ClimateZone 4 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.032 |  |  |  |  | 3335
90.1-2013 | ClimateZone 4 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.037 |  |  |  |  | 3336
90.1-2013 | ClimateZone 4 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.021 |  |  |  |  | 3337
90.1-2013 | ClimateZone 4 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.09 |  |  |  |  | 3338
90.1-2013 | ClimateZone 4 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.05 |  |  |  |  | 3339
90.1-2013 | ClimateZone 4 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 3340
90.1-2013 | ClimateZone 4 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 3341
90.1-2013 | ClimateZone 4 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.092 |  |  | 3342
90.1-2013 | ClimateZone 4 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.051 |  |  |  |  | 3343
90.1-2013 | ClimateZone 4 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.038 |  |  |  |  | 3344
90.1-2013 | ClimateZone 4 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 3345
90.1-2013 | ClimateZone 4 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.52 |  |  |  | 3346
90.1-2013 | ClimateZone 4 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.688 |  |  |  | 3347
90.1-2013 | ClimateZone 4 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3348
90.1-2013 | ClimateZone 4 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3349
90.1-2013 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.35 |  |  | 0.4 | 1.1 | 3350
90.1-2013 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.42 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/6mm Air |  |  | 0.42 |  |  | 0.4 | 1.1 | 3351
90.1-2013 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.5 |  |  | 0.4 | 1.1 | 3352
90.1-2013 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.68 |  |  | 0.4 | 1.1 | 3353
90.1-2013 | ClimateZone 4 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.093 |  |  |  |  | 3360
90.1-2013 | ClimateZone 4 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.082 |  |  |  |  | 3361
90.1-2013 | ClimateZone 4 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 3362
90.1-2013 | ClimateZone 4 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 3363
90.1-2013 | ClimateZone 4 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.162 |  |  |  |  | 3364
90.1-2013 | ClimateZone 4 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 3365
90.1-2013 | ClimateZone 4 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 3366
90.1-2013 | ClimateZone 4 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 3367
90.1-2013 | ClimateZone 4 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.107 |  |  |  |  | 3368
90.1-2013 | ClimateZone 4 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 3369
90.1-2013 | ClimateZone 4 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.051 |  |  |  |  | 3370
90.1-2013 | ClimateZone 4 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 3371
90.1-2013 | ClimateZone 4 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.9 |  |  |  | 3372
90.1-2013 | ClimateZone 4 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 3373
90.1-2013 | ClimateZone 4 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 3374
90.1-2013 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  |  | 0.51 |  |  |  |  | 3375
90.1-2013 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.73 |  |  |  |  | 3376
90.1-2013 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.81 |  |  |  |  | 3377
90.1-2013 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.77 |  |  |  |  | 3378
90.1-2004 | ClimateZone 5 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1393
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.1 |  |  |  |  | 752
90.1-2004 | ClimateZone 5 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 1395
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 753
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.092 |  |  |  |  | 770
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 771
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.082 |  |  |  |  | 788
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 789
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.082 |  |  |  |  | 806
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 807
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.082 |  |  |  |  | 824
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 825
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.065 |  |  |  |  | 842
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 843
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.072 |  |  |  |  | 860
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 861
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.058 |  |  |  |  | 878
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 879
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.045 |  |  |  |  | 896
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 897
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 337
90.1-2010 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2627
90.1-2010 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.75 |  |  | 0.25 |  | 2575
90.1-2004 | ClimateZone 6 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1558
90.1-2004 | ClimateZone 6 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.09 |  |  |  |  | 1560
90.1-2004 | ClimateZone 6 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 1561
90.1-2004 | ClimateZone 6 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 1562
90.1-2004 | ClimateZone 6 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 1563
90.1-2004 | ClimateZone 6 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 1564
90.1-2004 | ClimateZone 6 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.064 |  |  |  |  | 1565
90.1-2004 | ClimateZone 6 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.038 |  |  |  |  | 1566
90.1-2004 | ClimateZone 6 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 1567
90.1-2004 | ClimateZone 6 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1568
90.1-2004 | ClimateZone 6 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.78 |  |  |  | 1569
90.1-2004 | ClimateZone 6 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 1570
90.1-2004 | ClimateZone 6 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 1571
90.1-2004 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1572
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1573
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1574
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1575
90.1-2004 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1576
90.1-2004 | ClimateZone 5 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1434
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1577
90.1-2004 | ClimateZone 5 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 1436
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1578
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.39 |  | 1579
90.1-2004 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1580
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1581
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1582
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.39 |  | 1583
90.1-2004 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1584
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1585
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1586
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.39 |  | 1587
90.1-2004 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1588
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1589
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1590
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.26 |  | 1591
90.1-2007 | ClimateZone 6 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 2286
90.1-2007 | ClimateZone 6 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.071 |  |  |  |  | 2288
90.1-2007 | ClimateZone 6 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 2289
90.1-2007 | ClimateZone 6 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 2290
90.1-2007 | ClimateZone 6 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 2291
90.1-2007 | ClimateZone 6 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 2292
90.1-2007 | ClimateZone 6 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.057 |  |  |  |  | 2293
90.1-2007 | ClimateZone 6 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.032 |  |  |  |  | 2294
90.1-2007 | ClimateZone 6 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 2295
90.1-2007 | ClimateZone 6 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.52 |  |  |  | 2296
90.1-2007 | ClimateZone 6 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.688 |  |  |  | 2297
90.1-2007 | ClimateZone 6 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 2298
90.1-2007 | ClimateZone 6 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2299
90.1-2007 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.35 |  |  | 0.4 |  | 2300
90.1-2007 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  | 0.4 |  | 2301
90.1-2007 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  | 0.4 |  | 2302
90.1-2007 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  | 0.55 |  |  | 0.4 |  | 2303
90.1-2004 | ClimateZone 5 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.173 |  |  |  |  | 1475
90.1-2004 | ClimateZone 5 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.053 |  |  |  |  | 1477
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 391
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 409
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 427
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 445
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 463
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 481
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 499
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 517
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 535
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 553
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 571
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 589
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof | [7 empty] | 607
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 338
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 339
90.1-2010 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.75 |  |  | 0.25 |  | 2600
90.1-2010 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2625
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.225 |  |  |  |  | 392
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 393
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.23 |  |  |  |  | 410
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 411
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.224 |  |  |  |  | 428
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 429
90.1-2004 | ClimateZone 7 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1681
90.1-2004 | ClimateZone 7 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.08 |  |  |  |  | 1683
90.1-2004 | ClimateZone 7 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 1684
90.1-2004 | ClimateZone 7 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 1685
90.1-2004 | ClimateZone 7 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 1686
90.1-2004 | ClimateZone 7 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 1687
90.1-2004 | ClimateZone 7 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.064 |  |  |  |  | 1688
90.1-2004 | ClimateZone 7 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.038 |  |  |  |  | 1689
90.1-2004 | ClimateZone 7 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 1690
90.1-2004 | ClimateZone 7 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.54 |  |  |  | 1691
90.1-2004 | ClimateZone 7 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.78 |  |  |  | 1692
90.1-2007 | ClimateZone 5 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2185
90.1-2004 | ClimateZone 7 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 1693
90.1-2007 | ClimateZone 5 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2187
90.1-2004 | ClimateZone 7 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 1694
90.1-2004 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1695
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1696
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1697
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 1 | 10 | 0.57 |  |  | 0.49 |  | 1698
90.1-2004 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.49 |  | 1699
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.49 |  | 1700
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.49 |  | 1701
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 10.001 | 20 | 0.57 |  |  | 0.49 |  | 1702
90.1-2004 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.49 |  | 1703
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.49 |  | 1704
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.49 |  | 1705
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 20.001 | 30 | 0.57 |  |  | 0.49 |  | 1706
90.1-2004 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.49 |  | 1707
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.49 |  | 1708
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.49 |  | 1709
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 30.001 | 40 | 0.57 |  |  | 0.49 |  | 1710
90.1-2004 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.36 |  | 1711
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.36 |  | 1712
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.36 |  | 1713
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air | 40.001 | 100 | 0.46 |  |  | 0.36 |  | 1714
90.1-2007 | ClimateZone 5 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2210
90.1-2007 | ClimateZone 5 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2212
90.1-2007 | ClimateZone 7 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 2361
90.1-2007 | ClimateZone 7 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.071 |  |  |  |  | 2363
90.1-2007 | ClimateZone 7 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 2364
90.1-2007 | ClimateZone 7 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.042 |  |  |  |  | 2365
90.1-2007 | ClimateZone 7 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 2366
90.1-2007 | ClimateZone 7 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.092 |  |  | 2367
90.1-2007 | ClimateZone 7 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.051 |  |  |  |  | 2368
90.1-2007 | ClimateZone 7 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.032 |  |  |  |  | 2369
90.1-2007 | ClimateZone 7 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 2370
90.1-2007 | ClimateZone 7 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.52 |  |  |  | 2371
90.1-2007 | ClimateZone 7 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.688 |  |  |  | 2372
90.1-2007 | ClimateZone 7 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 2373
90.1-2007 | ClimateZone 7 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2374
90.1-2007 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  |  | 0.35 |  |  |  |  | 2375
90.1-2007 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  | 0.4 |  |  |  |  | 2376
90.1-2007 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  |  |  | 2377
90.1-2007 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  |  |  | 2378
90.1-2007 | ClimateZone 5 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.119 |  |  |  |  | 2235
90.1-2007 | ClimateZone 5 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.053 |  |  |  |  | 2237
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.178 |  |  |  |  | 446
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 447
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.184 |  |  |  |  | 464
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 465
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.175 |  |  |  |  | 482
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 483
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.156 |  |  |  |  | 500
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 501
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.161 |  |  |  |  | 518
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 519
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.161 |  |  |  |  | 536
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 537
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.145 |  |  |  |  | 554
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 555
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.145 |  |  |  |  | 572
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 573
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.136 |  |  |  |  | 590
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 591
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.125 |  |  |  |  | 608
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor | [7 empty] | 609
90.1-2010 | ClimateZone 2 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 2572
90.1-2010 | ClimateZone 2 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 2597
90.1-2010 | ClimateZone 1 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.218 |  |  |  |  | 2535
90.1-2010 | ClimateZone 1 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.081 |  |  |  |  | 2537
90.1-2010 | ClimateZone 2 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 2622
90.1-2004 | ClimateZone 8 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.049 |  |  |  |  | 1804
90.1-2004 | ClimateZone 8 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.071 |  |  |  |  | 1806
90.1-2004 | ClimateZone 8 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 1807
90.1-2004 | ClimateZone 8 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.055 |  |  |  |  | 1808
90.1-2004 | ClimateZone 8 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 1809
90.1-2004 | ClimateZone 8 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 1810
90.1-2004 | ClimateZone 8 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.057 |  |  |  |  | 1811
90.1-2004 | ClimateZone 8 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.032 |  |  |  |  | 1812
90.1-2004 | ClimateZone 8 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 1813
90.1-2004 | ClimateZone 8 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.52 |  |  |  | 1814
90.1-2004 | ClimateZone 8 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.78 |  |  |  | 1815
90.1-2004 | ClimateZone 8 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 1816
90.1-2004 | ClimateZone 8 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 1817
90.1-2004 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 1 | 10 | 0.46 |  |  |  |  | 1818
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 1 | 10 | 0.46 |  |  |  |  | 1819
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 1 | 10 | 0.46 |  |  |  |  | 1820
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 1 | 10 | 0.46 |  |  |  |  | 1821
90.1-2004 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 10.001 | 20 | 0.46 |  |  |  |  | 1822
90.1-2010 | ClimateZone 2 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2571
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 10.001 | 20 | 0.46 |  |  |  |  | 1823
90.1-2010 | ClimateZone 3 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.173 |  |  |  |  | 2685
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 10.001 | 20 | 0.46 |  |  |  |  | 1824
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 10.001 | 20 | 0.46 |  |  |  |  | 1825
90.1-2004 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 20.001 | 30 | 0.46 |  |  |  |  | 1826
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 20.001 | 30 | 0.46 |  |  |  |  | 1827
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 20.001 | 30 | 0.46 |  |  |  |  | 1828
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 20.001 | 30 | 0.46 |  |  |  |  | 1829
90.1-2004 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 30.001 | 40 | 0.46 |  |  |  |  | 1830
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 30.001 | 40 | 0.46 |  |  |  |  | 1831
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 30.001 | 40 | 0.46 |  |  |  |  | 1832
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | 30.001 | 40 | 0.46 |  |  |  |  | 1833
90.1-2004 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg | 40.001 | 100 | 0.35 |  |  |  |  | 1834
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg | 40.001 | 100 | 0.35 |  |  |  |  | 1835
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg | 40.001 | 100 | 0.35 |  |  |  |  | 1836
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg | 40.001 | 100 | 0.35 |  |  |  |  | 1837
90.1-2007 | ClimateZone 8 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.049 |  |  |  |  | 2436
90.1-2007 | ClimateZone 8 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.052 |  |  |  |  | 2438
90.1-2010 | ClimateZone 3 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.053 |  |  |  |  | 2687
90.1-2007 | ClimateZone 8 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.057 |  |  |  |  | 2439
90.1-2010 | ClimateZone 4 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.173 |  |  |  |  | 2760
90.1-2007 | ClimateZone 8 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.037 |  |  |  |  | 2440
90.1-2007 | ClimateZone 8 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.036 |  |  |  |  | 2441
90.1-2007 | ClimateZone 8 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.075 |  |  | 2442
90.1-2007 | ClimateZone 8 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.051 |  |  |  |  | 2443
90.1-2007 | ClimateZone 8 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.032 |  |  |  |  | 2444
90.1-2007 | ClimateZone 8 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 2445
90.1-2007 | ClimateZone 8 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.51 |  |  |  | 2446
90.1-2007 | ClimateZone 8 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.688 |  |  |  | 2447
90.1-2007 | ClimateZone 8 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 2448
90.1-2007 | ClimateZone 8 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2449
90.1-2007 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  |  | 0.35 |  |  |  |  | 2450
90.1-2007 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  | 0.4 |  |  |  |  | 2451
90.1-2007 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.8 |  |  |  |  | 2452
90.1-2007 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  |  |  | 2453
90.1-2010 | ClimateZone 4 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.053 |  |  |  |  | 2762
90.1-2010 | ClimateZone 5 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.119 |  |  |  |  | 2835
90.1-2013 | ClimateZone 5 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.032 |  |  |  |  | 3385
90.1-2013 | ClimateZone 5 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.037 |  |  |  |  | 3386
90.1-2013 | ClimateZone 5 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.021 |  |  |  |  | 3387
90.1-2013 | ClimateZone 5 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.09 |  |  |  |  | 3388
90.1-2013 | ClimateZone 5 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.05 |  |  |  |  | 3389
90.1-2013 | ClimateZone 5 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.055 |  |  |  |  | 3390
90.1-2013 | ClimateZone 5 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 3391
90.1-2013 | ClimateZone 5 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 3392
90.1-2013 | ClimateZone 5 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.057 |  |  |  |  | 3393
90.1-2013 | ClimateZone 5 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.038 |  |  |  |  | 3394
90.1-2013 | ClimateZone 5 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.033 |  |  |  |  | 3395
90.1-2013 | ClimateZone 5 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.52 |  |  |  | 3396
90.1-2013 | ClimateZone 5 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.688 |  |  |  | 3397
90.1-2013 | ClimateZone 5 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3398
90.1-2013 | ClimateZone 5 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3399
90.1-2013 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.32 |  |  | 0.4 | 1.1 | 3400
90.1-2013 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.42 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/6mm Air |  |  | 0.42 |  |  | 0.4 | 1.1 | 3401
90.1-2013 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.5 |  |  | 0.4 | 1.1 | 3402
90.1-2013 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.77 |  |  | 0.4 | 1.1 | 3403
90.1-2013 | ClimateZone 5 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.032 |  |  |  |  | 3410
90.1-2013 | ClimateZone 5 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.037 |  |  |  |  | 3411
90.1-2013 | ClimateZone 5 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.021 |  |  |  |  | 3412
90.1-2013 | ClimateZone 5 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.08 |  |  |  |  | 3413
90.1-2013 | ClimateZone 5 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.05 |  |  |  |  | 3414
90.1-2013 | ClimateZone 5 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.055 |  |  |  |  | 3415
90.1-2013 | ClimateZone 5 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 3416
90.1-2013 | ClimateZone 5 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.092 |  |  | 3417
90.1-2013 | ClimateZone 5 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.051 |  |  |  |  | 3418
90.1-2013 | ClimateZone 5 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.038 |  |  |  |  | 3419
90.1-2013 | ClimateZone 5 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 3420
90.1-2013 | ClimateZone 5 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.51 |  |  |  | 3421
90.1-2013 | ClimateZone 5 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.688 |  |  |  | 3422
90.1-2013 | ClimateZone 5 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3423
90.1-2013 | ClimateZone 5 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3424
90.1-2013 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.32 |  |  | 0.4 | 1.1 | 3425
90.1-2013 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.42 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/6mm Air |  |  | 0.42 |  |  | 0.4 | 1.1 | 3426
90.1-2013 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.5 |  |  | 0.4 | 1.1 | 3427
90.1-2013 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.68 |  |  | 0.4 | 1.1 | 3428
90.1-2013 | ClimateZone 5 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 3435
90.1-2013 | ClimateZone 5 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.082 |  |  |  |  | 3436
90.1-2013 | ClimateZone 5 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 3437
90.1-2013 | ClimateZone 5 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 3438
90.1-2013 | ClimateZone 5 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.094 |  |  |  |  | 3439
90.1-2013 | ClimateZone 5 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.084 |  |  |  |  | 3440
90.1-2013 | ClimateZone 5 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 3441
90.1-2013 | ClimateZone 5 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 3442
90.1-2013 | ClimateZone 5 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.107 |  |  |  |  | 3443
90.1-2013 | ClimateZone 5 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 3444
90.1-2013 | ClimateZone 5 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.051 |  |  |  |  | 3445
90.1-2013 | ClimateZone 5 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 3446
90.1-2013 | ClimateZone 5 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.9 |  |  |  | 3447
90.1-2013 | ClimateZone 5 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 3448
90.1-2013 | ClimateZone 5 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 3449
90.1-2013 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  |  |  | 3450
90.1-2013 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.62 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  | 0.62 |  |  |  |  | 3451
90.1-2013 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.67 SHGC 0.77 Sgl LoE (e2-.2) Clr 3mm |  |  | 0.7 |  |  |  |  | 3452
90.1-2013 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.77 |  |  |  |  | 3453
90.1-2004 | ClimateZone 6 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1516
90.1-2010 | ClimateZone 5 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.053 |  |  |  |  | 2837
90.1-2004 | ClimateZone 6 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 1518
90.1-2010 | ClimateZone 1 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.167 |  |  |  |  | 2536
90.1-2010 | ClimateZone 1 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 2538
90.1-2010 | ClimateZone 1 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 2539
90.1-2010 | ClimateZone 1 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.352 |  |  |  |  | 2540
90.1-2010 | ClimateZone 1 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.292 |  |  |  |  | 2541
90.1-2010 | ClimateZone 1 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2542
90.1-2010 | ClimateZone 1 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 2543
90.1-2010 | ClimateZone 1 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.35 |  |  |  |  | 2544
90.1-2010 | ClimateZone 1 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.282 |  |  |  |  | 2545
90.1-2010 | ClimateZone 1 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2546
90.1-2010 | ClimateZone 1 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 2547
90.1-2010 | ClimateZone 1 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2548
90.1-2010 | ClimateZone 1 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2549
90.1-2010 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2550
90.1-2010 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2551
90.1-2010 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2552
90.1-2010 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 1.2 |  |  | 0.25 |  | 2553
90.1-2010 | ClimateZone 6 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.093 |  |  |  |  | 2910
DOE Ref 1980-2004 | ClimateZone 7 | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 872
90.1-2010 | ClimateZone 6 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 2912
DOE Ref Pre-1980 | ClimateZone 7 | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 584
DOE Ref 1980-2004 | ClimateZone 8 | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 890
DOE Ref Pre-1980 | ClimateZone 8 | GroundContactFloor | Mass | Nonresidential | ext-slab-mass | [7 empty] | 602
90.1-2010 | ClimateZone 2 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2596
90.1-2010 | ClimateZone 2 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2621
90.1-2010 | ClimateZone 2 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2567
DOE Ref 1980-2004 | ClimateZone 2B | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 654
DOE Ref 1980-2004 | ClimateZone 2A | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 636
DOE Ref Pre-1980 | ClimateZone 2B | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 366
DOE Ref Pre-1980 | ClimateZone 2A | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  | 0 |  |  |  |  | 348
90.1-2010 | ClimateZone 2 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2592
90.1-2010 | ClimateZone 2 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2617
90.1-2004 | ClimateZone 6 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1557
90.1-2004 | ClimateZone 6 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 1559
90.1-2010 | ClimateZone 3 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.097 |  |  |  |  | 2686
90.1-2010 | ClimateZone 3 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 2688
90.1-2010 | ClimateZone 3 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 2689
90.1-2010 | ClimateZone 3 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 2690
90.1-2010 | ClimateZone 3 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2691
90.1-2010 | ClimateZone 3 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2692
90.1-2010 | ClimateZone 3 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 2693
90.1-2010 | ClimateZone 3 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.069 |  |  |  |  | 2694
90.1-2010 | ClimateZone 3 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.066 |  |  |  |  | 2695
90.1-2010 | ClimateZone 3 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2696
90.1-2010 | ClimateZone 3 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 2697
90.1-2010 | ClimateZone 3 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2698
90.1-2010 | ClimateZone 3 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2699
90.1-2010 | ClimateZone 3 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2700
90.1-2010 | ClimateZone 3 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2701
90.1-2010 | ClimateZone 3 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2702
90.1-2010 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2703
90.1-2010 | ClimateZone 4 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.097 |  |  |  |  | 2761
90.1-2010 | ClimateZone 4 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 2763
90.1-2010 | ClimateZone 4 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 2764
90.1-2010 | ClimateZone 4 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 2765
90.1-2010 | ClimateZone 4 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2766
90.1-2010 | ClimateZone 4 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2767
90.1-2004 | ClimateZone 6 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.173 |  |  |  |  | 1598
90.1-2010 | ClimateZone 4 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.137 |  |  |  |  | 2768
90.1-2004 | ClimateZone 6 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.053 |  |  |  |  | 1600
90.1-2010 | ClimateZone 4 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.069 |  |  |  |  | 2769
90.1-2010 | ClimateZone 4 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.066 |  |  |  |  | 2770
90.1-2010 | ClimateZone 4 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2771
90.1-2010 | ClimateZone 4 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 2772
90.1-2010 | ClimateZone 4 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2773
90.1-2010 | ClimateZone 4 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2774
90.1-2004 | ClimateZone 1 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 1.28 |  |  |  |  | 984
90.1-2004 | ClimateZone 1 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 986
90.1-2004 | ClimateZone 1 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 1.18 |  |  |  |  | 987
90.1-2004 | ClimateZone 1 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.352 |  |  |  |  | 988
90.1-2004 | ClimateZone 1 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.292 |  |  |  |  | 989
90.1-2004 | ClimateZone 1 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 990
90.1-2004 | ClimateZone 1 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 991
90.1-2004 | ClimateZone 1 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.35 |  |  |  |  | 992
90.1-2004 | ClimateZone 1 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.282 |  |  |  |  | 993
90.1-2004 | ClimateZone 1 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 994
90.1-2004 | ClimateZone 1 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 995
90.1-2004 | ClimateZone 1 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 996
90.1-2004 | ClimateZone 1 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 997
90.1-2004 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 998
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 999
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1000
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1001
90.1-2004 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1002
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1003
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1004
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1005
90.1-2004 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1006
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1007
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1008
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1009
90.1-2004 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1010
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1011
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1012
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1013
90.1-2004 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1014
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1015
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1016
90.1-2007 | ClimateZone 6 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2260
90.1-2004 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1017
90.1-2007 | ClimateZone 6 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2262
90.1-2007 | ClimateZone 1 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 1.28 |  |  |  |  | 1936
90.1-2007 | ClimateZone 1 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 1938
90.1-2007 | ClimateZone 1 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 1.18 |  |  |  |  | 1939
90.1-2007 | ClimateZone 1 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.352 |  |  |  |  | 1940
90.1-2007 | ClimateZone 1 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.292 |  |  |  |  | 1941
90.1-2007 | ClimateZone 1 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1942
90.1-2007 | ClimateZone 1 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 1943
90.1-2007 | ClimateZone 1 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.35 |  |  |  |  | 1944
90.1-2007 | ClimateZone 1 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.282 |  |  |  |  | 1945
90.1-2007 | ClimateZone 1 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1946
90.1-2007 | ClimateZone 1 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1947
90.1-2007 | ClimateZone 1 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1948
90.1-2007 | ClimateZone 1 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1949
90.1-2007 | ClimateZone 1 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 1950
90.1-2007 | ClimateZone 1 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 1951
90.1-2007 | ClimateZone 1 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 1952
90.1-2007 | ClimateZone 6 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2285
90.1-2007 | ClimateZone 1 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 1953
90.1-2007 | ClimateZone 6 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2287
90.1-2010 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2775
90.1-2010 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2776
90.1-2010 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2777
90.1-2010 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2778
90.1-2010 | ClimateZone 7 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.093 |  |  |  |  | 2985
90.1-2010 | ClimateZone 5 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.083 |  |  |  |  | 2836
90.1-2010 | ClimateZone 7 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 2987
90.1-2010 | ClimateZone 5 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 2838
90.1-2010 | ClimateZone 5 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 2839
90.1-2010 | ClimateZone 5 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 2840
90.1-2007 | ClimateZone 6 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.093 |  |  |  |  | 2310
90.1-2010 | ClimateZone 5 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2841
90.1-2007 | ClimateZone 6 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 2312
90.1-2010 | ClimateZone 5 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2842
90.1-2010 | ClimateZone 5 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.137 |  |  |  |  | 2843
90.1-2010 | ClimateZone 5 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 2844
90.1-2010 | ClimateZone 5 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.051 |  |  |  |  | 2845
90.1-2010 | ClimateZone 5 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2846
90.1-2010 | ClimateZone 5 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 2847
90.1-2004 | ClimateZone 2 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.167 |  |  |  |  | 1107
90.1-2004 | ClimateZone 2 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 1109
90.1-2004 | ClimateZone 2 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.184 |  |  |  |  | 1110
90.1-2004 | ClimateZone 2 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.352 |  |  |  |  | 1111
90.1-2004 | ClimateZone 2 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.292 |  |  |  |  | 1112
90.1-2004 | ClimateZone 2 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1113
90.1-2004 | ClimateZone 2 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 1114
90.1-2004 | ClimateZone 2 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.35 |  |  |  |  | 1115
90.1-2004 | ClimateZone 2 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.282 |  |  |  |  | 1116
90.1-2004 | ClimateZone 2 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1117
90.1-2004 | ClimateZone 2 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1118
90.1-2004 | ClimateZone 2 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1119
90.1-2004 | ClimateZone 2 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1120
90.1-2004 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1121
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1122
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1123
90.1-2010 | ClimateZone 5 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2848
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1124
90.1-2010 | ClimateZone 5 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2849
90.1-2004 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1125
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1126
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1127
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1128
90.1-2004 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1129
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1130
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1131
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1132
90.1-2004 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1133
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1134
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1135
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1136
90.1-2004 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1137
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1138
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1139
90.1-2004 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1140
90.1-2010 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2850
90.1-2007 | ClimateZone 2 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.167 |  |  |  |  | 2011
90.1-2010 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2851
90.1-2007 | ClimateZone 2 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 2013
90.1-2007 | ClimateZone 2 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.184 |  |  |  |  | 2014
90.1-2007 | ClimateZone 2 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 2015
90.1-2007 | ClimateZone 2 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2016
90.1-2007 | ClimateZone 2 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2017
90.1-2007 | ClimateZone 2 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 2018
90.1-2007 | ClimateZone 2 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.069 |  |  |  |  | 2019
90.1-2007 | ClimateZone 2 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.066 |  |  |  |  | 2020
90.1-2007 | ClimateZone 2 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2021
90.1-2007 | ClimateZone 2 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 2022
90.1-2007 | ClimateZone 2 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2023
90.1-2007 | ClimateZone 2 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2024
90.1-2007 | ClimateZone 2 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2025
90.1-2007 | ClimateZone 2 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2026
90.1-2007 | ClimateZone 2 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2027
90.1-2007 | ClimateZone 2 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2028
90.1-2010 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2852
90.1-2010 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2853
90.1-2010 | ClimateZone 6 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.072 |  |  |  |  | 2911
90.1-2010 | ClimateZone 6 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 2913
90.1-2010 | ClimateZone 6 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 2914
90.1-2010 | ClimateZone 6 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 2915
90.1-2010 | ClimateZone 6 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2916
90.1-2010 | ClimateZone 6 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2917
90.1-2010 | ClimateZone 6 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.137 |  |  |  |  | 2918
90.1-2010 | ClimateZone 6 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 2919
90.1-2010 | ClimateZone 6 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.051 |  |  |  |  | 2920
90.1-2010 | ClimateZone 6 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2921
90.1-2010 | ClimateZone 6 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 2922
90.1-2010 | ClimateZone 6 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2923
90.1-2010 | ClimateZone 6 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2924
90.1-2010 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  |  |  | 2925
90.1-2010 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  | 0.6 |  |  |  |  | 2926
90.1-2010 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 0.9 |  |  |  |  | 2927
90.1-2010 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  |  |  | 2928
90.1-2013 | ClimateZone 6 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.032 |  |  |  |  | 3460
90.1-2013 | ClimateZone 6 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.031 |  |  |  |  | 3461
90.1-2013 | ClimateZone 6 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.021 |  |  |  |  | 3462
90.1-2013 | ClimateZone 6 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.08 |  |  |  |  | 3463
90.1-2013 | ClimateZone 6 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.05 |  |  |  |  | 3464
90.1-2013 | ClimateZone 6 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.049 |  |  |  |  | 3465
90.1-2013 | ClimateZone 6 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 3466
90.1-2013 | ClimateZone 6 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.092 |  |  | 3467
90.1-2013 | ClimateZone 6 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.051 |  |  |  |  | 3468
90.1-2013 | ClimateZone 6 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.032 |  |  |  |  | 3469
90.1-2013 | ClimateZone 6 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.027 |  |  |  |  | 3470
90.1-2013 | ClimateZone 6 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.51 |  |  |  | 3471
90.1-2013 | ClimateZone 6 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.688 |  |  |  | 3472
90.1-2013 | ClimateZone 6 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3473
90.1-2013 | ClimateZone 6 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3474
90.1-2013 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.32 |  |  | 0.4 | 1.1 | 3475
90.1-2013 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.42 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/6mm Air |  |  | 0.42 |  |  | 0.4 | 1.1 | 3476
90.1-2013 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.5 |  |  | 0.4 | 1.1 | 3477
90.1-2013 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.77 |  |  | 0.4 | 1.1 | 3478
90.1-2013 | ClimateZone 6 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.032 |  |  |  |  | 3485
90.1-2013 | ClimateZone 6 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.029 |  |  |  |  | 3486
90.1-2013 | ClimateZone 6 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.021 |  |  |  |  | 3487
90.1-2013 | ClimateZone 6 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.071 |  |  |  |  | 3488
90.1-2013 | ClimateZone 6 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.05 |  |  |  |  | 3489
90.1-2013 | ClimateZone 6 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.049 |  |  |  |  | 3490
90.1-2013 | ClimateZone 6 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 3491
90.1-2013 | ClimateZone 6 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.063 |  |  | 3492
90.1-2013 | ClimateZone 6 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.051 |  |  |  |  | 3493
90.1-2013 | ClimateZone 6 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.032 |  |  |  |  | 3494
90.1-2013 | ClimateZone 6 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.027 |  |  |  |  | 3495
90.1-2013 | ClimateZone 6 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.434 |  |  |  | 3496
90.1-2013 | ClimateZone 6 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.671 |  |  |  | 3497
90.1-2013 | ClimateZone 6 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3498
90.1-2013 | ClimateZone 6 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3499
90.1-2013 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.32 |  |  | 0.4 | 1.1 | 3500
90.1-2013 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.42 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/6mm Air |  |  | 0.42 |  |  | 0.4 | 1.1 | 3501
90.1-2013 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.5 |  |  | 0.4 | 1.1 | 3502
90.1-2013 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.68 |  |  | 0.4 | 1.1 | 3503
90.1-2013 | ClimateZone 6 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 3510
90.1-2013 | ClimateZone 6 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.06 |  |  |  |  | 3511
90.1-2013 | ClimateZone 6 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 3512
90.1-2013 | ClimateZone 6 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 3513
90.1-2013 | ClimateZone 6 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.094 |  |  |  |  | 3514
90.1-2013 | ClimateZone 6 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.084 |  |  |  |  | 3515
90.1-2013 | ClimateZone 6 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 3516
90.1-2013 | ClimateZone 6 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 3517
90.1-2013 | ClimateZone 6 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 3518
90.1-2013 | ClimateZone 6 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 3519
90.1-2013 | ClimateZone 6 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.051 |  |  |  |  | 3520
90.1-2013 | ClimateZone 6 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 3521
90.1-2013 | ClimateZone 6 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 3522
90.1-2013 | ClimateZone 6 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 3523
90.1-2013 | ClimateZone 6 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3524
90.1-2013 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  | 0.45 |  |  |  |  | 3525
90.1-2013 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  |  | 0.51 |  |  |  |  | 3526
90.1-2013 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  | 0.59 |  |  |  |  | 3527
90.1-2013 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.77 |  |  |  |  | 3528
90.1-2004 | ClimateZone 7 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1639
90.1-2004 | ClimateZone 3A | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.097 |  |  |  |  | 1230
90.1-2004 | ClimateZone 7 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 1641
90.1-2004 | ClimateZone 3A | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 1232
90.1-2004 | ClimateZone 3A | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.184 |  |  |  |  | 1233
90.1-2004 | ClimateZone 3A | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.352 |  |  |  |  | 1234
90.1-2004 | ClimateZone 3A | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1235
90.1-2004 | ClimateZone 3A | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1236
90.1-2004 | ClimateZone 3A | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 1237
90.1-2004 | ClimateZone 3A | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.069 |  |  |  |  | 1238
90.1-2004 | ClimateZone 3A | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.282 |  |  |  |  | 1239
90.1-2004 | ClimateZone 3A | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1240
90.1-2004 | ClimateZone 3A | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1241
90.1-2004 | ClimateZone 3A | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1242
90.1-2004 | ClimateZone 3A | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1243
90.1-2004 | ClimateZone 3A | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1244
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1245
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1246
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1247
90.1-2004 | ClimateZone 3A | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1248
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1249
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1250
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1251
90.1-2004 | ClimateZone 3A | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1252
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1253
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1254
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1255
90.1-2004 | ClimateZone 3A | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1256
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1257
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1258
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1259
90.1-2004 | ClimateZone 3A | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1260
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1261
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1262
90.1-2004 | ClimateZone 3A | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1263
90.1-2004 | ClimateZone 3B | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1244
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1245
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1246
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1247
90.1-2004 | ClimateZone 3B | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1248
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1249
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1250
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1251
90.1-2004 | ClimateZone 3B | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1252
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1253
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1254
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1255
90.1-2004 | ClimateZone 3B | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1256
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1257
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1258
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1259
90.1-2004 | ClimateZone 3B | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1260
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1261
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1262
90.1-2004 | ClimateZone 3B | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1263
90.1-2004 | ClimateZone 3C | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1244
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1245
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1246
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1247
90.1-2004 | ClimateZone 3C | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1248
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1249
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1250
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1251
90.1-2004 | ClimateZone 3C | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1252
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1253
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1254
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1255
90.1-2004 | ClimateZone 3C | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1256
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1257
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1258
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1259
90.1-2004 | ClimateZone 3C | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1260
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1261
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1262
90.1-2004 | ClimateZone 3C | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1263
90.1-2004 | ClimateZone 3B | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1148
90.1-2004 | ClimateZone 3B | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 1150
90.1-2004 | ClimateZone 3B | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1151
90.1-2004 | ClimateZone 3B | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 1152
90.1-2004 | ClimateZone 3B | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1153
90.1-2004 | ClimateZone 3B | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1154
90.1-2004 | ClimateZone 3B | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.107 |  |  |  |  | 1155
90.1-2004 | ClimateZone 3B | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.052 |  |  |  |  | 1156
90.1-2004 | ClimateZone 3B | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.051 |  |  |  |  | 1157
90.1-2004 | ClimateZone 3B | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1158
90.1-2004 | ClimateZone 3B | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1159
90.1-2004 | ClimateZone 3B | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1160
90.1-2004 | ClimateZone 3B | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1161
90.1-2004 | ClimateZone 3B | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1147
90.1-2004 | ClimateZone 3B | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 1149
90.1-2004 | ClimateZone 3B | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1188
90.1-2004 | ClimateZone 3B | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 1190
90.1-2004 | ClimateZone 3B | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.218 |  |  |  |  | 1229
90.1-2004 | ClimateZone 3B | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.081 |  |  |  |  | 1231
90.1-2004 | ClimateZone 3B | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1189
90.1-2004 | ClimateZone 3B | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.123 |  |  |  |  | 1191
90.1-2004 | ClimateZone 3B | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1192
90.1-2004 | ClimateZone 3B | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.084 |  |  |  |  | 1193
90.1-2004 | ClimateZone 3B | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1194
90.1-2004 | ClimateZone 3B | GroundContactWall | Mass | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight |  |  |  |  | 1.14 |  |  | 1195
90.1-2004 | ClimateZone 3B | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 1196
90.1-2004 | ClimateZone 3B | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.052 |  |  |  |  | 1197
90.1-2004 | ClimateZone 3B | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 1198
90.1-2004 | ClimateZone 3B | GroundContactFloor | Unheated | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight |  |  |  | 0.73 |  |  |  | 1199
90.1-2004 | ClimateZone 3B | GroundContactFloor | Heated | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight |  |  |  | 1.02 |  |  |  | 1200
90.1-2004 | ClimateZone 3B | ExteriorDoor | Swinging | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight |  |  | 0.7 |  |  |  |  | 1201
90.1-2004 | ClimateZone 3B | ExteriorDoor | NonSwinging | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight |  |  | 0.5 |  |  |  |  | 1202
90.1-2004 | ClimateZone 3B | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.097 |  |  |  |  | 1230
90.1-2004 | ClimateZone 3B | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 1232
90.1-2004 | ClimateZone 3B | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.184 |  |  |  |  | 1233
90.1-2004 | ClimateZone 3B | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.352 |  |  |  |  | 1234
90.1-2004 | ClimateZone 3B | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1235
90.1-2004 | ClimateZone 3B | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1236
90.1-2004 | ClimateZone 3B | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 1237
90.1-2004 | ClimateZone 3B | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.069 |  |  |  |  | 1238
90.1-2004 | ClimateZone 3B | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.282 |  |  |  |  | 1239
90.1-2004 | ClimateZone 3B | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1240
90.1-2004 | ClimateZone 3B | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1241
90.1-2004 | ClimateZone 3B | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1242
90.1-2004 | ClimateZone 3B | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1243
90.1-2004 | ClimateZone 3C | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1148
90.1-2004 | ClimateZone 3C | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 1150
90.1-2004 | ClimateZone 3C | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1151
90.1-2004 | ClimateZone 3C | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 1152
90.1-2004 | ClimateZone 3C | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1153
90.1-2004 | ClimateZone 3C | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1154
90.1-2004 | ClimateZone 3C | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.107 |  |  |  |  | 1155
90.1-2004 | ClimateZone 3C | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.052 |  |  |  |  | 1156
90.1-2004 | ClimateZone 3C | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.051 |  |  |  |  | 1157
90.1-2004 | ClimateZone 3C | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1158
90.1-2004 | ClimateZone 3C | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1159
90.1-2004 | ClimateZone 3C | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1160
90.1-2004 | ClimateZone 3C | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1161
90.1-2004 | ClimateZone 3C | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1147
90.1-2004 | ClimateZone 3C | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 1149
90.1-2004 | ClimateZone 3C | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1188
90.1-2004 | ClimateZone 3C | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 1190
90.1-2004 | ClimateZone 3C | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.218 |  |  |  |  | 1229
90.1-2004 | ClimateZone 3C | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.081 |  |  |  |  | 1231
90.1-2004 | ClimateZone 3C | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 1189
90.1-2004 | ClimateZone 3C | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.123 |  |  |  |  | 1191
90.1-2004 | ClimateZone 3C | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1192
90.1-2004 | ClimateZone 3C | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.084 |  |  |  |  | 1193
90.1-2004 | ClimateZone 3C | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1194
90.1-2004 | ClimateZone 3C | GroundContactWall | Mass | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight |  |  |  |  | 1.14 |  |  | 1195
90.1-2004 | ClimateZone 3C | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 1196
90.1-2004 | ClimateZone 3C | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.052 |  |  |  |  | 1197
90.1-2004 | ClimateZone 3C | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.033 |  |  |  |  | 1198
90.1-2004 | ClimateZone 3C | GroundContactFloor | Unheated | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight |  |  |  | 0.73 |  |  |  | 1199
90.1-2004 | ClimateZone 3C | GroundContactFloor | Heated | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight |  |  |  | 1.02 |  |  |  | 1200
90.1-2004 | ClimateZone 3C | ExteriorDoor | Swinging | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight |  |  | 0.7 |  |  |  |  | 1201
90.1-2004 | ClimateZone 3C | ExteriorDoor | NonSwinging | Residential | U 0.58 SHGC 0.19 Simple Glazing Skylight |  |  | 0.5 |  |  |  |  | 1202
90.1-2004 | ClimateZone 3C | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.097 |  |  |  |  | 1230
90.1-2004 | ClimateZone 3C | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 1232
90.1-2004 | ClimateZone 3C | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.184 |  |  |  |  | 1233
90.1-2004 | ClimateZone 3C | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.352 |  |  |  |  | 1234
90.1-2004 | ClimateZone 3C | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1235
90.1-2004 | ClimateZone 3C | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1236
90.1-2004 | ClimateZone 3C | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 1237
90.1-2004 | ClimateZone 3C | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.069 |  |  |  |  | 1238
90.1-2004 | ClimateZone 3C | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.282 |  |  |  |  | 1239
90.1-2004 | ClimateZone 3C | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1240
90.1-2004 | ClimateZone 3C | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1241
90.1-2004 | ClimateZone 3C | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1242
90.1-2004 | ClimateZone 3C | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1243
90.1-2004 | ClimateZone 7 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 1680
90.1-2007 | ClimateZone 3 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.097 |  |  |  |  | 2086
90.1-2004 | ClimateZone 7 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 1682
90.1-2007 | ClimateZone 3 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 2088
90.1-2007 | ClimateZone 3 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.184 |  |  |  |  | 2089
90.1-2007 | ClimateZone 3 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 2090
90.1-2007 | ClimateZone 3 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2091
90.1-2007 | ClimateZone 3 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2092
90.1-2007 | ClimateZone 3 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 2093
90.1-2007 | ClimateZone 3 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.069 |  |  |  |  | 2094
90.1-2007 | ClimateZone 3 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.066 |  |  |  |  | 2095
90.1-2007 | ClimateZone 3 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2096
90.1-2007 | ClimateZone 3 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 2097
90.1-2007 | ClimateZone 3 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2098
90.1-2007 | ClimateZone 3 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2099
90.1-2007 | ClimateZone 3 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2100
90.1-2007 | ClimateZone 3 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2101
90.1-2007 | ClimateZone 3 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2102
90.1-2007 | ClimateZone 3 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2103
90.1-2010 | ClimateZone 7 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.072 |  |  |  |  | 2986
90.1-2010 | ClimateZone 7 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.123 |  |  |  |  | 2988
90.1-2010 | ClimateZone 7 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 2989
90.1-2010 | ClimateZone 7 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 2990
90.1-2010 | ClimateZone 7 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2991
90.1-2010 | ClimateZone 7 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2992
90.1-2010 | ClimateZone 7 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.107 |  |  |  |  | 2993
90.1-2010 | ClimateZone 7 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 2994
90.1-2010 | ClimateZone 7 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.051 |  |  |  |  | 2995
90.1-2010 | ClimateZone 7 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2996
90.1-2004 | ClimateZone 7 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.173 |  |  |  |  | 1721
90.1-2010 | ClimateZone 7 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.9 |  |  |  | 2997
90.1-2004 | ClimateZone 7 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.053 |  |  |  |  | 1723
90.1-2010 | ClimateZone 7 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2998
90.1-2010 | ClimateZone 7 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2999
90.1-2010 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  |  |  | 3000
90.1-2010 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  | 0.6 |  |  |  |  | 3001
90.1-2010 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 0.9 |  |  |  |  | 3002
90.1-2010 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  |  |  | 3003
90.1-2004 | ClimateZone 4 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.097 |  |  |  |  | 1353
90.1-2004 | ClimateZone 4 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 1355
90.1-2004 | ClimateZone 4 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.134 |  |  |  |  | 1356
90.1-2004 | ClimateZone 4 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 1357
90.1-2004 | ClimateZone 4 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1358
90.1-2004 | ClimateZone 4 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1359
90.1-2004 | ClimateZone 4 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 1360
90.1-2004 | ClimateZone 4 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.069 |  |  |  |  | 1361
90.1-2004 | ClimateZone 4 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.066 |  |  |  |  | 1362
90.1-2004 | ClimateZone 4 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1363
90.1-2004 | ClimateZone 4 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1364
90.1-2004 | ClimateZone 4 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1365
90.1-2004 | ClimateZone 4 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1366
90.1-2004 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1367
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1368
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1369
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1370
90.1-2004 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1371
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1372
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1373
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1374
90.1-2004 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1375
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1376
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1377
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1378
90.1-2004 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1379
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1380
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1381
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1382
90.1-2004 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1383
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1384
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1385
90.1-2007 | ClimateZone 7 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2335
90.1-2004 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1386
90.1-2007 | ClimateZone 7 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2337
90.1-2007 | ClimateZone 4 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.097 |  |  |  |  | 2161
90.1-2007 | ClimateZone 4 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 2163
90.1-2007 | ClimateZone 4 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.134 |  |  |  |  | 2164
90.1-2007 | ClimateZone 4 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 2165
90.1-2007 | ClimateZone 4 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2166
90.1-2007 | ClimateZone 4 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2167
90.1-2007 | ClimateZone 4 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.137 |  |  |  |  | 2168
90.1-2007 | ClimateZone 4 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.069 |  |  |  |  | 2169
90.1-2007 | ClimateZone 4 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.066 |  |  |  |  | 2170
90.1-2007 | ClimateZone 4 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2171
90.1-2007 | ClimateZone 4 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 2172
90.1-2007 | ClimateZone 4 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2173
90.1-2007 | ClimateZone 4 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2174
90.1-2007 | ClimateZone 4 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2175
90.1-2007 | ClimateZone 4 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2176
90.1-2007 | ClimateZone 4 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2177
90.1-2007 | ClimateZone 7 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2360
90.1-2007 | ClimateZone 4 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2178
90.1-2007 | ClimateZone 7 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 2362
90.1-2010 | ClimateZone 8 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 3060
90.1-2010 | ClimateZone 8 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.065 |  |  |  |  | 3061
90.1-2010 | ClimateZone 8 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 3062
90.1-2010 | ClimateZone 8 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.104 |  |  |  |  | 3063
90.1-2010 | ClimateZone 8 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 3064
90.1-2010 | ClimateZone 8 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.084 |  |  |  |  | 3065
90.1-2010 | ClimateZone 8 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 3066
90.1-2010 | ClimateZone 8 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 3067
90.1-2010 | ClimateZone 8 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 3068
90.1-2010 | ClimateZone 8 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 3069
90.1-2007 | ClimateZone 7 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.093 |  |  |  |  | 2385
90.1-2010 | ClimateZone 8 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.033 |  |  |  |  | 3070
90.1-2007 | ClimateZone 7 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 2387
90.1-2010 | ClimateZone 8 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 3071
90.1-2010 | ClimateZone 8 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.9 |  |  |  | 3072
90.1-2010 | ClimateZone 8 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 3073
90.1-2010 | ClimateZone 8 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3074
90.1-2010 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  |  |  | 3075
90.1-2010 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  | 0.6 |  |  |  |  | 3076
90.1-2004 | ClimateZone 5 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.097 |  |  |  |  | 1476
90.1-2004 | ClimateZone 5 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 1478
90.1-2004 | ClimateZone 5 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.123 |  |  |  |  | 1479
90.1-2004 | ClimateZone 5 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 1480
90.1-2004 | ClimateZone 5 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1481
90.1-2004 | ClimateZone 5 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1482
90.1-2004 | ClimateZone 5 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 1483
90.1-2004 | ClimateZone 5 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.069 |  |  |  |  | 1484
90.1-2004 | ClimateZone 5 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.066 |  |  |  |  | 1485
90.1-2004 | ClimateZone 5 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1486
90.1-2004 | ClimateZone 5 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1487
90.1-2004 | ClimateZone 5 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1488
90.1-2004 | ClimateZone 5 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1489
90.1-2004 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1490
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1491
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1492
90.1-2010 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 0.9 |  |  |  |  | 3077
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1493
90.1-2010 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  |  |  | 3078
90.1-2004 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1494
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1495
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1496
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1497
90.1-2004 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1498
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1499
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1500
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1501
90.1-2004 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1502
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1503
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1504
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1505
90.1-2004 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1506
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1507
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1508
90.1-2004 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1509
90.1-2007 | ClimateZone 5 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.097 |  |  |  |  | 2236
90.1-2007 | ClimateZone 5 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 2238
90.1-2007 | ClimateZone 5 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.123 |  |  |  |  | 2239
90.1-2007 | ClimateZone 5 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 2240
90.1-2007 | ClimateZone 5 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2241
90.1-2007 | ClimateZone 5 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2242
90.1-2007 | ClimateZone 5 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.137 |  |  |  |  | 2243
90.1-2007 | ClimateZone 5 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 2244
90.1-2007 | ClimateZone 5 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.051 |  |  |  |  | 2245
90.1-2007 | ClimateZone 5 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2246
90.1-2007 | ClimateZone 5 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 2247
90.1-2007 | ClimateZone 5 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2248
90.1-2007 | ClimateZone 5 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2249
90.1-2007 | ClimateZone 5 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2250
90.1-2007 | ClimateZone 5 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2251
90.1-2007 | ClimateZone 5 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2252
90.1-2007 | ClimateZone 5 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  | 1.2 |  |  |  |  | 2253
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 628
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 682
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 700
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 718
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 736
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 754
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 772
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 790
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 808
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 826
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 844
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 862
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 880
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 898
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 629
DOE Ref 1980-2004 | ClimateZone 1 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 630
90.1-2013 | ClimateZone 7 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.028 |  |  |  |  | 3535
90.1-2013 | ClimateZone 7 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.029 |  |  |  |  | 3536
90.1-2013 | ClimateZone 7 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.017 |  |  |  |  | 3537
90.1-2013 | ClimateZone 7 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.071 |  |  |  |  | 3538
90.1-2013 | ClimateZone 7 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.044 |  |  |  |  | 3539
90.1-2013 | ClimateZone 7 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.049 |  |  |  |  | 3540
90.1-2013 | ClimateZone 7 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 3541
90.1-2013 | ClimateZone 7 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.063 |  |  | 3542
90.1-2013 | ClimateZone 7 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.042 |  |  |  |  | 3543
90.1-2013 | ClimateZone 7 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.032 |  |  |  |  | 3544
90.1-2013 | ClimateZone 7 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.027 |  |  |  |  | 3545
90.1-2013 | ClimateZone 7 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.51 |  |  |  | 3546
90.1-2013 | ClimateZone 7 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.671 |  |  |  | 3547
90.1-2013 | ClimateZone 7 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3548
90.1-2013 | ClimateZone 7 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3549
90.1-2013 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.32 |  |  | 0.45 | 1.1 | 3550
90.1-2013 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.38 SHGC 0.30 Dbl Ref-B-H Clr 6mm/13mm Arg |  |  | 0.38 |  |  | 0.45 | 1.1 | 3551
90.1-2013 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  | 0.4 |  |  | 0.45 | 1.1 | 3552
90.1-2013 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.77 |  |  | 0.45 | 1.1 | 3553
90.1-2013 | ClimateZone 7 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.028 |  |  |  |  | 3560
90.1-2013 | ClimateZone 7 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.029 |  |  |  |  | 3561
90.1-2013 | ClimateZone 7 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.017 |  |  |  |  | 3562
90.1-2013 | ClimateZone 7 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.071 |  |  |  |  | 3563
90.1-2013 | ClimateZone 7 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.044 |  |  |  |  | 3564
90.1-2013 | ClimateZone 7 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.042 |  |  |  |  | 3565
90.1-2013 | ClimateZone 7 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 3566
90.1-2013 | ClimateZone 7 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.063 |  |  | 3567
90.1-2013 | ClimateZone 7 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.042 |  |  |  |  | 3568
90.1-2013 | ClimateZone 7 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.032 |  |  |  |  | 3569
90.1-2013 | ClimateZone 7 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.27 |  |  |  |  | 3570
90.1-2013 | ClimateZone 7 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.434 |  |  |  | 3571
90.1-2013 | ClimateZone 7 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.671 |  |  |  | 3572
90.1-2013 | ClimateZone 7 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3573
90.1-2013 | ClimateZone 7 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3574
90.1-2013 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.32 |  |  | 0.45 | 1.1 | 3575
90.1-2013 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.38 SHGC 0.30 Dbl Ref-B-H Clr 6mm/13mm Arg |  |  | 0.38 |  |  | 0.45 | 1.1 | 3576
90.1-2013 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  | 0.4 |  |  | 0.45 | 1.1 | 3577
90.1-2013 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.68 |  |  | 0.45 | 1.1 | 3578
90.1-2013 | ClimateZone 7 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.039 |  |  |  |  | 3585
90.1-2013 | ClimateZone 7 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.037 |  |  |  |  | 3586
90.1-2013 | ClimateZone 7 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 3587
90.1-2013 | ClimateZone 7 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.123 |  |  |  |  | 3588
90.1-2013 | ClimateZone 7 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.072 |  |  |  |  | 3589
90.1-2013 | ClimateZone 7 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 3590
90.1-2013 | ClimateZone 7 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 3591
90.1-2013 | ClimateZone 7 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 3592
90.1-2013 | ClimateZone 7 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.074 |  |  |  |  | 3593
90.1-2013 | ClimateZone 7 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 3594
90.1-2013 | ClimateZone 7 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.051 |  |  |  |  | 3595
90.1-2013 | ClimateZone 7 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 3596
90.1-2013 | ClimateZone 7 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 3597
90.1-2013 | ClimateZone 7 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 3598
90.1-2013 | ClimateZone 7 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3599
90.1-2013 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.32 |  |  |  |  | 3600
90.1-2013 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.38 SHGC 0.26 Dbl Ref B-H Tint 6mm/13mm Arg |  |  | 0.38 |  |  |  |  | 3601
90.1-2013 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  |  | 0.44 |  |  |  |  | 3602
90.1-2013 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.77 |  |  |  |  | 3603
90.1-2004 | ClimateZone 8 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 1762
90.1-2004 | ClimateZone 6 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.097 |  |  |  |  | 1599
90.1-2004 | ClimateZone 8 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 1764
90.1-2004 | ClimateZone 6 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 1601
90.1-2004 | ClimateZone 6 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1602
90.1-2004 | ClimateZone 6 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 1603
90.1-2004 | ClimateZone 6 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1604
90.1-2004 | ClimateZone 6 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1605
90.1-2004 | ClimateZone 6 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.322 |  |  |  |  | 1606
90.1-2004 | ClimateZone 6 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.069 |  |  |  |  | 1607
90.1-2004 | ClimateZone 6 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.0066 |  |  |  |  | 1608
90.1-2004 | ClimateZone 6 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1609
90.1-2004 | ClimateZone 6 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1610
90.1-2004 | ClimateZone 6 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1611
90.1-2004 | ClimateZone 6 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1612
90.1-2004 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1613
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1614
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1615
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1616
90.1-2004 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1617
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1618
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1619
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1620
90.1-2004 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1621
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1622
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1623
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1624
90.1-2004 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1625
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1626
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1627
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1628
90.1-2004 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1629
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1630
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1631
90.1-2004 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1632
90.1-2004 | ClimateZone 8 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 1803
90.1-2007 | ClimateZone 6 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.097 |  |  |  |  | 2311
90.1-2004 | ClimateZone 8 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 1805
90.1-2007 | ClimateZone 6 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 2313
90.1-2007 | ClimateZone 6 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 2314
90.1-2007 | ClimateZone 6 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 2315
90.1-2007 | ClimateZone 6 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2316
90.1-2007 | ClimateZone 6 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2317
90.1-2007 | ClimateZone 6 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.137 |  |  |  |  | 2318
90.1-2007 | ClimateZone 6 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 2319
90.1-2007 | ClimateZone 6 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.051 |  |  |  |  | 2320
90.1-2007 | ClimateZone 6 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2321
90.1-2007 | ClimateZone 6 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 2322
90.1-2007 | ClimateZone 6 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2323
90.1-2007 | ClimateZone 6 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2324
90.1-2007 | ClimateZone 6 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  |  |  | 2325
90.1-2007 | ClimateZone 6 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  | 0.6 |  |  |  |  | 2326
90.1-2007 | ClimateZone 6 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 0.9 |  |  |  |  | 2327
90.1-2007 | ClimateZone 6 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  |  |  | 2328
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 683
DOE Ref 1980-2004 | ClimateZone 3A | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 684
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 701
DOE Ref 1980-2004 | ClimateZone 3B | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 702
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 719
DOE Ref 1980-2004 | ClimateZone 3C | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 720
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 737
DOE Ref 1980-2004 | ClimateZone 4A | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 738
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 755
DOE Ref 1980-2004 | ClimateZone 4B | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 756
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 773
DOE Ref 1980-2004 | ClimateZone 4C | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 774
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 791
DOE Ref 1980-2004 | ClimateZone 5A | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 792
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 809
90.1-2004 | ClimateZone 8 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.093 |  |  |  |  | 1844
DOE Ref 1980-2004 | ClimateZone 5B | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 810
90.1-2004 | ClimateZone 8 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 1846
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 827
DOE Ref 1980-2004 | ClimateZone 5C | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 828
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 845
DOE Ref 1980-2004 | ClimateZone 6A | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 846
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 863
DOE Ref 1980-2004 | ClimateZone 6B | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 864
90.1-2004 | ClimateZone 7 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.097 |  |  |  |  | 1722
90.1-2004 | ClimateZone 7 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.58 |  |  |  |  | 1724
90.1-2004 | ClimateZone 7 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1725
90.1-2004 | ClimateZone 7 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 1726
90.1-2004 | ClimateZone 7 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1727
90.1-2004 | ClimateZone 7 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1728
90.1-2004 | ClimateZone 7 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.137 |  |  |  |  | 1729
90.1-2004 | ClimateZone 7 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 1730
90.1-2004 | ClimateZone 7 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.066 |  |  |  |  | 1731
90.1-2004 | ClimateZone 7 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1732
90.1-2004 | ClimateZone 7 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 1.02 |  |  |  | 1733
90.1-2004 | ClimateZone 7 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1734
90.1-2004 | ClimateZone 7 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1735
90.1-2004 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1736
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1737
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1738
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1739
90.1-2004 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1740
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1741
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1742
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1743
90.1-2004 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1744
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1745
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1746
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1747
90.1-2004 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1748
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1749
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1750
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1751
90.1-2004 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1752
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1753
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1754
90.1-2007 | ClimateZone 8 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2410
90.1-2004 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1755
90.1-2007 | ClimateZone 8 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.021 |  |  |  |  | 2412
90.1-2007 | ClimateZone 7 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.097 |  |  |  |  | 2386
90.1-2007 | ClimateZone 7 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.123 |  |  |  |  | 2388
90.1-2007 | ClimateZone 7 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 2389
90.1-2007 | ClimateZone 7 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 2390
90.1-2007 | ClimateZone 7 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2391
90.1-2007 | ClimateZone 7 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2392
90.1-2007 | ClimateZone 7 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.107 |  |  |  |  | 2393
90.1-2007 | ClimateZone 7 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 2394
90.1-2007 | ClimateZone 7 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.051 |  |  |  |  | 2395
90.1-2007 | ClimateZone 7 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2396
90.1-2007 | ClimateZone 7 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.9 |  |  |  | 2397
90.1-2007 | ClimateZone 7 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2398
90.1-2007 | ClimateZone 7 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 2399
90.1-2007 | ClimateZone 7 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  |  |  | 2400
90.1-2007 | ClimateZone 7 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  | 0.6 |  |  |  |  | 2401
90.1-2007 | ClimateZone 7 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 0.9 |  |  |  |  | 2402
90.1-2007 | ClimateZone 8 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.048 |  |  |  |  | 2435
90.1-2007 | ClimateZone 7 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  |  |  | 2403
90.1-2007 | ClimateZone 8 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.021 |  |  |  |  | 2437
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 881
DOE Ref 1980-2004 | ClimateZone 7 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 882
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 899
DOE Ref 1980-2004 | ClimateZone 8 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 900
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 340
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 394
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 412
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 430
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 448
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 466
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 484
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 502
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 520
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 538
90.1-2007 | ClimateZone 8 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.063 |  |  |  |  | 2460
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 556
90.1-2007 | ClimateZone 8 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.034 |  |  |  |  | 2462
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 574
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 592
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof | [7 empty] | 610
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 341
DOE Ref Pre-1980 | ClimateZone 1 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 342
90.1-2004 | ClimateZone 8 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.072 |  |  |  |  | 1845
90.1-2004 | ClimateZone 8 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.151 |  |  |  |  | 1847
90.1-2004 | ClimateZone 8 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 1848
90.1-2004 | ClimateZone 8 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.124 |  |  |  |  | 1849
90.1-2004 | ClimateZone 8 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 1850
90.1-2004 | ClimateZone 8 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 1851
90.1-2004 | ClimateZone 8 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.137 |  |  |  |  | 1852
90.1-2004 | ClimateZone 8 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 1853
90.1-2004 | ClimateZone 8 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.051 |  |  |  |  | 1854
90.1-2004 | ClimateZone 8 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 1855
90.1-2004 | ClimateZone 8 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.95 |  |  |  | 1856
90.1-2004 | ClimateZone 8 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 1857
90.1-2004 | ClimateZone 8 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 1.45 |  |  |  |  | 1858
90.1-2004 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1859
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1860
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1861
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 1 | 10 | 1.22 |  |  |  |  | 1862
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 395
90.1-2004 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1863
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1864
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1865
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 10.001 | 20 | 1.22 |  |  |  |  | 1866
90.1-2004 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1867
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1868
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1869
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 20.001 | 30 | 1.22 |  |  |  |  | 1870
90.1-2004 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1871
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1872
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1873
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | 30.001 | 40 | 1.22 |  |  |  |  | 1874
90.1-2004 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1875
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1876
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1877
90.1-2004 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | 40.001 | 100 | 0.98 |  |  |  |  | 1878
DOE Ref 1980-2004 | ClimateZone 1 | Skylight | Glass with Curb | Nonresidential | [8 empty] | 624
DOE Ref 1980-2004 | ClimateZone 2A | Skylight | Glass with Curb | Nonresidential | [8 empty] | 642
DOE Ref 1980-2004 | ClimateZone 2B | Skylight | Glass with Curb | Nonresidential | [8 empty] | 660
DOE Ref 1980-2004 | ClimateZone 3A | Skylight | Glass with Curb | Nonresidential | [8 empty] | 678
DOE Ref 1980-2004 | ClimateZone 3B | Skylight | Glass with Curb | Nonresidential | [8 empty] | 696
DOE Ref 1980-2004 | ClimateZone 3C | Skylight | Glass with Curb | Nonresidential | [8 empty] | 714
DOE Ref Pre-1980 | ClimateZone 3A | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 396
90.1-2007 | ClimateZone 8 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.072 |  |  |  |  | 2461
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 413
90.1-2007 | ClimateZone 8 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.104 |  |  |  |  | 2463
90.1-2007 | ClimateZone 8 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.113 |  |  |  |  | 2464
90.1-2007 | ClimateZone 8 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.084 |  |  |  |  | 2465
90.1-2007 | ClimateZone 8 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.089 |  |  |  |  | 2466
90.1-2007 | ClimateZone 8 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 1.14 |  |  | 2467
90.1-2007 | ClimateZone 8 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.087 |  |  |  |  | 2468
90.1-2007 | ClimateZone 8 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 2469
90.1-2007 | ClimateZone 8 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.033 |  |  |  |  | 2470
90.1-2007 | ClimateZone 8 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.73 |  |  |  | 2471
90.1-2007 | ClimateZone 8 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.9 |  |  |  | 2472
90.1-2007 | ClimateZone 8 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.7 |  |  |  |  | 2473
90.1-2007 | ClimateZone 8 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 2474
90.1-2007 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  |  |  | 2475
90.1-2007 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  | 0.6 |  |  |  |  | 2476
90.1-2007 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  | 0.9 |  |  |  |  | 2477
90.1-2007 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.65 |  |  |  |  | 2478
DOE Ref 1980-2004 | ClimateZone 4A | Skylight | Glass with Curb | Nonresidential | [8 empty] | 732
DOE Ref 1980-2004 | ClimateZone 4B | Skylight | Glass with Curb | Nonresidential | [8 empty] | 750
DOE Ref 1980-2004 | ClimateZone 4C | Skylight | Glass with Curb | Nonresidential | [8 empty] | 768
DOE Ref 1980-2004 | ClimateZone 5A | Skylight | Glass with Curb | Nonresidential | [8 empty] | 786
DOE Ref 1980-2004 | ClimateZone 5B | Skylight | Glass with Curb | Nonresidential | [8 empty] | 804
DOE Ref 1980-2004 | ClimateZone 5C | Skylight | Glass with Curb | Nonresidential | [8 empty] | 822
DOE Ref Pre-1980 | ClimateZone 3B | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 414
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 431
DOE Ref Pre-1980 | ClimateZone 3C | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 432
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 449
DOE Ref Pre-1980 | ClimateZone 4A | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 450
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 467
DOE Ref Pre-1980 | ClimateZone 4B | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 468
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 485
DOE Ref Pre-1980 | ClimateZone 4C | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 486
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 503
DOE Ref Pre-1980 | ClimateZone 5A | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 504
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 521
DOE Ref Pre-1980 | ClimateZone 5B | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 522
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 539
DOE Ref Pre-1980 | ClimateZone 5C | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 540
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 557
DOE Ref Pre-1980 | ClimateZone 6A | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 558
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 575
DOE Ref Pre-1980 | ClimateZone 6B | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 576
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 593
DOE Ref Pre-1980 | ClimateZone 7 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 594
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof | [7 empty] | 611
DOE Ref Pre-1980 | ClimateZone 8 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall | [7 empty] | 612
DOE Ref 1980-2004 | ClimateZone 6A | Skylight | Glass with Curb | Nonresidential | [8 empty] | 840
DOE Ref 1980-2004 | ClimateZone 6B | Skylight | Glass with Curb | Nonresidential | [8 empty] | 858
90.1-2013 | ClimateZone 8 | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  | 0.028 |  |  |  |  | 3610
90.1-2013 | ClimateZone 8 | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  | 0.026 |  |  |  |  | 3611
90.1-2013 | ClimateZone 8 | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  | 0.017 |  |  |  |  | 3612
90.1-2013 | ClimateZone 8 | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  | 0.048 |  |  |  |  | 3613
90.1-2013 | ClimateZone 8 | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  | 0.039 |  |  |  |  | 3614
90.1-2013 | ClimateZone 8 | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.037 |  |  |  |  | 3615
90.1-2013 | ClimateZone 8 | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.032 |  |  |  |  | 3616
90.1-2013 | ClimateZone 8 | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.063 |  |  | 3617
90.1-2013 | ClimateZone 8 | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  | 0.038 |  |  |  |  | 3618
90.1-2013 | ClimateZone 8 | ExteriorFloor | SteelFramed | Nonresidential |  |  |  | 0.032 |  |  |  |  | 3619
90.1-2013 | ClimateZone 8 | ExteriorFloor | WoodFramed | Nonresidential |  |  |  | 0.027 |  |  |  |  | 3620
90.1-2013 | ClimateZone 8 | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.434 |  |  |  | 3621
90.1-2013 | ClimateZone 8 | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.671 |  |  |  | 3622
90.1-2013 | ClimateZone 8 | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3623
90.1-2013 | ClimateZone 8 | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3624
90.1-2013 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.32 |  |  | 0.45 | 1.1 | 3625
90.1-2013 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.38 SHGC 0.30 Dbl Ref-B-H Clr 6mm/13mm Arg |  |  | 0.38 |  |  | 0.45 | 1.1 | 3626
90.1-2013 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Nonresidential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  | 0.4 |  |  | 0.45 | 1.1 | 3627
90.1-2013 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.77 |  |  | 0.45 | 1.1 | 3628
DOE Ref 1980-2004 | ClimateZone 7 | Skylight | Glass with Curb | Nonresidential | [8 empty] | 876
DOE Ref 1980-2004 | ClimateZone 8 | Skylight | Glass with Curb | Nonresidential | [8 empty] | 894
DOE Ref Pre-1980 | ClimateZone 1 | Skylight | Glass with Curb | Nonresidential | [8 empty] | 336
DOE Ref Pre-1980 | ClimateZone 2A | Skylight | Glass with Curb | Nonresidential | [8 empty] | 354
DOE Ref Pre-1980 | ClimateZone 2B | Skylight | Glass with Curb | Nonresidential | [8 empty] | 372
DOE Ref Pre-1980 | ClimateZone 3A | Skylight | Glass with Curb | Nonresidential | [8 empty] | 390
90.1-2013 | ClimateZone 8 | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  | 0.028 |  |  |  |  | 3635
90.1-2013 | ClimateZone 8 | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  | 0.026 |  |  |  |  | 3636
90.1-2013 | ClimateZone 8 | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  | 0.017 |  |  |  |  | 3637
90.1-2013 | ClimateZone 8 | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  | 0.048 |  |  |  |  | 3638
90.1-2013 | ClimateZone 8 | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  | 0.039 |  |  |  |  | 3639
90.1-2013 | ClimateZone 8 | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  | 0.037 |  |  |  |  | 3640
90.1-2013 | ClimateZone 8 | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  | 0.032 |  |  |  |  | 3641
90.1-2013 | ClimateZone 8 | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | 0.063 |  |  | 3642
90.1-2013 | ClimateZone 8 | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  | 0.038 |  |  |  |  | 3643
90.1-2013 | ClimateZone 8 | ExteriorFloor | SteelFramed | Residential |  |  |  | 0.032 |  |  |  |  | 3644
90.1-2013 | ClimateZone 8 | ExteriorFloor | WoodFramed | Residential |  |  |  | 0.027 |  |  |  |  | 3645
90.1-2013 | ClimateZone 8 | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.424 |  |  |  | 3646
90.1-2013 | ClimateZone 8 | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.373 |  |  |  | 3647
90.1-2013 | ClimateZone 8 | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3648
90.1-2013 | ClimateZone 8 | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3649
90.1-2013 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.32 |  |  | 0.45 | 1.1 | 3650
90.1-2013 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.38 SHGC 0.26 Dbl Ref B-H Tint 6mm/13mm Arg |  |  | 0.38 |  |  | 0.45 | 1.1 | 3651
90.1-2013 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Residential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  | 0.4 |  |  | 0.45 | 1.1 | 3652
90.1-2013 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  | 0.68 |  |  | 0.45 | 1.1 | 3653
DOE Ref Pre-1980 | ClimateZone 3B | Skylight | Glass with Curb | Nonresidential | [8 empty] | 408
DOE Ref Pre-1980 | ClimateZone 3C | Skylight | Glass with Curb | Nonresidential | [8 empty] | 426
DOE Ref Pre-1980 | ClimateZone 4A | Skylight | Glass with Curb | Nonresidential | [8 empty] | 444
DOE Ref Pre-1980 | ClimateZone 4B | Skylight | Glass with Curb | Nonresidential | [8 empty] | 462
DOE Ref Pre-1980 | ClimateZone 4C | Skylight | Glass with Curb | Nonresidential | [8 empty] | 480
DOE Ref Pre-1980 | ClimateZone 5A | Skylight | Glass with Curb | Nonresidential | [8 empty] | 498
90.1-2013 | ClimateZone 8 | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  | 0.039 |  |  |  |  | 3660
90.1-2013 | ClimateZone 8 | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  | 0.037 |  |  |  |  | 3661
90.1-2013 | ClimateZone 8 | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  | 0.027 |  |  |  |  | 3662
90.1-2013 | ClimateZone 8 | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  | 0.104 |  |  |  |  | 3663
90.1-2013 | ClimateZone 8 | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  | 0.06 |  |  |  |  | 3664
90.1-2013 | ClimateZone 8 | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  | 0.064 |  |  |  |  | 3665
90.1-2013 | ClimateZone 8 | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  | 0.051 |  |  |  |  | 3666
90.1-2013 | ClimateZone 8 | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | 0.119 |  |  | 3667
90.1-2013 | ClimateZone 8 | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  | 0.064 |  |  |  |  | 3668
90.1-2013 | ClimateZone 8 | ExteriorFloor | SteelFramed | Semiheated |  |  |  | 0.052 |  |  |  |  | 3669
90.1-2013 | ClimateZone 8 | ExteriorFloor | WoodFramed | Semiheated |  |  |  | 0.033 |  |  |  |  | 3670
90.1-2013 | ClimateZone 8 | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.54 |  |  |  | 3671
90.1-2013 | ClimateZone 8 | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  | 0.86 |  |  |  | 3672
90.1-2013 | ClimateZone 8 | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  | 0.5 |  |  |  |  | 3673
90.1-2013 | ClimateZone 8 | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  | 0.5 |  |  |  |  | 3674
90.1-2013 | ClimateZone 8 | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  | 0.32 |  |  |  |  | 3675
90.1-2013 | ClimateZone 8 | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.38 SHGC 0.26 Dbl Ref B-H Tint 6mm/13mm Arg |  |  | 0.38 |  |  |  |  | 3676
90.1-2013 | ClimateZone 8 | ExteriorWindow | Metal framing (entrance door) | Semiheated | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  |  | 0.44 |  |  |  |  | 3677
90.1-2013 | ClimateZone 8 | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  | 0.77 |  |  |  |  | 3678
DOE Ref Pre-1980 | ClimateZone 5B | Skylight | Glass with Curb | Nonresidential | [8 empty] | 516
DOE Ref Pre-1980 | ClimateZone 5C | Skylight | Glass with Curb | Nonresidential | [8 empty] | 534
DOE Ref Pre-1980 | ClimateZone 6A | Skylight | Glass with Curb | Nonresidential | [8 empty] | 552
DOE Ref Pre-1980 | ClimateZone 6B | Skylight | Glass with Curb | Nonresidential | [8 empty] | 570
DOE Ref Pre-1980 | ClimateZone 7 | Skylight | Glass with Curb | Nonresidential | [8 empty] | 588
DOE Ref Pre-1980 | ClimateZone 8 | Skylight | Glass with Curb | Nonresidential | [8 empty] | 606
DOE Ref 1980-2004 | ClimateZone 1 | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 620
DOE Ref Pre-1980 | ClimateZone 1 | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 332
DOE Ref 1980-2004 | ClimateZone 2A | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 638
DOE Ref Pre-1980 | ClimateZone 2A | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 350
DOE Ref 1980-2004 | ClimateZone 2B | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 656
DOE Ref Pre-1980 | ClimateZone 2B | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 368
DOE Ref 1980-2004 | ClimateZone 3A | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 674
DOE Ref Pre-1980 | ClimateZone 3A | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 386
DOE Ref 1980-2004 | ClimateZone 3B | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 692
DOE Ref Pre-1980 | ClimateZone 3B | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 404
DOE Ref 1980-2004 | ClimateZone 3C | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 710
DOE Ref Pre-1980 | ClimateZone 3C | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 422
DOE Ref 1980-2004 | ClimateZone 4A | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 728
DOE Ref Pre-1980 | ClimateZone 4A | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 440
DOE Ref 1980-2004 | ClimateZone 4B | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 746
DOE Ref Pre-1980 | ClimateZone 4B | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 458
DOE Ref 1980-2004 | ClimateZone 4C | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 764
DOE Ref Pre-1980 | ClimateZone 4C | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 476
DOE Ref 1980-2004 | ClimateZone 5A | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 782
DOE Ref Pre-1980 | ClimateZone 5A | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 494
DOE Ref 1980-2004 | ClimateZone 5B | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 800
DOE Ref Pre-1980 | ClimateZone 5B | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 512
DOE Ref 1980-2004 | ClimateZone 5C | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 818
DOE Ref Pre-1980 | ClimateZone 5C | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 530
DOE Ref 1980-2004 | ClimateZone 6A | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 836
DOE Ref Pre-1980 | ClimateZone 6A | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 548
DOE Ref 1980-2004 | ClimateZone 6B | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 854
DOE Ref Pre-1980 | ClimateZone 6B | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 566
DOE Ref 1980-2004 | ClimateZone 7 | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 872
DOE Ref Pre-1980 | ClimateZone 7 | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 584
DOE Ref 1980-2004 | ClimateZone 8 | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 890
DOE Ref Pre-1980 | ClimateZone 8 | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame | [7 empty] | 602
DOE Ref 1980-2004 | ClimateZone 1 | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 620
DOE Ref Pre-1980 | ClimateZone 1 | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 332
DOE Ref 1980-2004 | ClimateZone 2A | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 638
DOE Ref Pre-1980 | ClimateZone 2A | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 350
DOE Ref 1980-2004 | ClimateZone 2B | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 656
DOE Ref Pre-1980 | ClimateZone 2B | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 368
DOE Ref 1980-2004 | ClimateZone 3A | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 674
DOE Ref Pre-1980 | ClimateZone 3A | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 386
DOE Ref 1980-2004 | ClimateZone 3B | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 692
DOE Ref Pre-1980 | ClimateZone 3B | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 404
DOE Ref 1980-2004 | ClimateZone 3C | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 710
DOE Ref Pre-1980 | ClimateZone 3C | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 422
DOE Ref 1980-2004 | ClimateZone 4A | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 728
DOE Ref Pre-1980 | ClimateZone 4A | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 440
DOE Ref 1980-2004 | ClimateZone 4B | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 746
DOE Ref Pre-1980 | ClimateZone 4B | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 458
DOE Ref 1980-2004 | ClimateZone 4C | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 764
DOE Ref Pre-1980 | ClimateZone 4C | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 476
DOE Ref 1980-2004 | ClimateZone 5A | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 782
DOE Ref Pre-1980 | ClimateZone 5A | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 494
DOE Ref 1980-2004 | ClimateZone 5B | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 800
DOE Ref Pre-1980 | ClimateZone 5B | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 512
DOE Ref 1980-2004 | ClimateZone 5C | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 818
DOE Ref Pre-1980 | ClimateZone 5C | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 530
DOE Ref 1980-2004 | ClimateZone 6A | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 836
DOE Ref Pre-1980 | ClimateZone 6A | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 548
DOE Ref 1980-2004 | ClimateZone 6B | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 854
DOE Ref Pre-1980 | ClimateZone 6B | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 566
DOE Ref 1980-2004 | ClimateZone 7 | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 872
DOE Ref Pre-1980 | ClimateZone 7 | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 584
DOE Ref 1980-2004 | ClimateZone 8 | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 890
DOE Ref Pre-1980 | ClimateZone 8 | GroundContactFloor | Unheated | Nonresidential | ext-slab | [7 empty] | 602
DOE Ref 1980-2004 | ClimateZone 1 | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 620
DOE Ref Pre-1980 | ClimateZone 1 | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 332
DOE Ref 1980-2004 | ClimateZone 2A | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 638
DOE Ref Pre-1980 | ClimateZone 2A | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 350
DOE Ref 1980-2004 | ClimateZone 2B | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 656
DOE Ref Pre-1980 | ClimateZone 2B | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 368
DOE Ref 1980-2004 | ClimateZone 3A | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 674
DOE Ref Pre-1980 | ClimateZone 3A | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 386
DOE Ref 1980-2004 | ClimateZone 3B | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 692
DOE Ref Pre-1980 | ClimateZone 3B | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 404
DOE Ref 1980-2004 | ClimateZone 3C | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 710
DOE Ref Pre-1980 | ClimateZone 3C | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 422
DOE Ref 1980-2004 | ClimateZone 4A | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 728
DOE Ref Pre-1980 | ClimateZone 4A | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 440
DOE Ref 1980-2004 | ClimateZone 4B | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 746
DOE Ref Pre-1980 | ClimateZone 4B | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 458
DOE Ref 1980-2004 | ClimateZone 4C | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 764
DOE Ref Pre-1980 | ClimateZone 4C | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 476
DOE Ref 1980-2004 | ClimateZone 5A | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 782
DOE Ref Pre-1980 | ClimateZone 5A | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 494
DOE Ref 1980-2004 | ClimateZone 5B | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 800
DOE Ref Pre-1980 | ClimateZone 5B | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 512
DOE Ref 1980-2004 | ClimateZone 5C | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 818
DOE Ref Pre-1980 | ClimateZone 5C | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 530
DOE Ref 1980-2004 | ClimateZone 6A | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 836
DOE Ref Pre-1980 | ClimateZone 6A | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 548
DOE Ref 1980-2004 | ClimateZone 6B | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 854
DOE Ref Pre-1980 | ClimateZone 6B | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 566
DOE Ref 1980-2004 | ClimateZone 7 | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 872
DOE Ref Pre-1980 | ClimateZone 7 | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 584
DOE Ref 1980-2004 | ClimateZone 8 | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 890
DOE Ref Pre-1980 | ClimateZone 8 | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building | [7 empty] | 602
90.1-2004 | ClimateZone 1 | Skylight | Glass with Curb | Nonresidential | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.36 |  | 936
90.1-2004 | ClimateZone 1 | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight | 0 | 2 | 1.98 |  |  | 0.19 |  | 977
90.1-2004 | ClimateZone 1 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.16 |  | 978
90.1-2004 | ClimateZone 1 | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.34 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 1018
90.1-2004 | ClimateZone 1 | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 1019
90.1-2004 | ClimateZone 1 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.34 |  | 938
90.1-2004 | ClimateZone 1 | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.27 |  | 979
90.1-2004 | ClimateZone 1 | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.27 |  | 980
90.1-2004 | ClimateZone 1 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  |  |  | 1020
90.1-2004 | ClimateZone 2 | Skylight | Glass with Curb | Nonresidential | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  |  |  | 1021
90.1-2004 | ClimateZone 2 | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight | 0 | 2 | 1.98 |  |  | 0.36 |  | 940
90.1-2004 | ClimateZone 2 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.19 |  | 981
90.1-2004 | ClimateZone 2 | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.34 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.19 |  | 982
90.1-2004 | ClimateZone 2 | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 1022
90.1-2004 | ClimateZone 2 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 1023
90.1-2004 | ClimateZone 2 | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.36 |  | 1059
90.1-2004 | ClimateZone 2 | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.19 |  | 1100
90.1-2004 | ClimateZone 2 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.19 |  | 1101
90.1-2004 | ClimateZone 3A | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  |  |  | 1141
90.1-2004 | ClimateZone 3A | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  |  |  | 1142
90.1-2004 | ClimateZone 3A | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.34 |  | 1061
90.1-2004 | ClimateZone 3A | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  | 0.27 |  | 1102
90.1-2004 | ClimateZone 3A | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.27 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  | 0.27 |  | 1103
90.1-2004 | ClimateZone 3A | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 1143
90.1-2004 | ClimateZone 3A | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  |  |  | 1144
90.1-2004 | ClimateZone 3A | Skylight | Without Curb | Residential | U 0.69 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  | 0.36 |  | 1063
90.1-2004 | ClimateZone 3A | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.19 |  | 1104
90.1-2004 | ClimateZone 3B | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  | 0.19 |  | 1105
90.1-2004 | ClimateZone 3B | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  |  |  | 1145
90.1-2004 | ClimateZone 3B | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  |  |  | 1146
90.1-2004 | ClimateZone 3B | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  | 0.39 |  | 1182
90.1-2004 | ClimateZone 3B | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.27 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  | 0.36 |  | 1223
90.1-2004 | ClimateZone 3B | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.19 |  | 1224
90.1-2004 | ClimateZone 3B | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  |  |  | 1264
90.1-2004 | ClimateZone 3B | Skylight | Without Curb | Residential | U 0.69 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  |  |  | 1265
90.1-2004 | ClimateZone 3B | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.65 |  | 1184
90.1-2004 | ClimateZone 3C | Skylight | Glass with Curb | Nonresidential | U 1.98 SHGC 0.61 Simple Glazing Skylight | 0 | 2 | 1.98 |  |  | 0.27 |  | 1225
90.1-2004 | ClimateZone 3C | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.98 |  |  | 0.27 |  | 1226
90.1-2004 | ClimateZone 3C | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.98 |  |  |  |  | 1266
90.1-2004 | ClimateZone 3C | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 1267
90.1-2004 | ClimateZone 3C | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.39 |  | 1186
90.1-2004 | ClimateZone 3C | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.36 |  | 1227
90.1-2004 | ClimateZone 3C | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.61 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.19 |  | 1228
90.1-2004 | ClimateZone 3C | Skylight | Without Curb | Residential | U 1.36 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  |  |  | 1268
90.1-2004 | ClimateZone 3C | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  |  |  | 1269
90.1-2004 | ClimateZone 4 | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  | 0.39 |  | 1182
90.1-2004 | ClimateZone 4 | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 0.98 |  |  | 0.36 |  | 1223
90.1-2004 | ClimateZone 4 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.19 |  | 1224
90.1-2004 | ClimateZone 4 | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  |  |  | 1264
90.1-2004 | ClimateZone 4 | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.62 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  |  |  | 1265
90.1-2004 | ClimateZone 4 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.65 |  | 1184
90.1-2004 | ClimateZone 4 | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  | 0.27 |  | 1225
90.1-2004 | ClimateZone 4 | Skylight | Without Curb | Residential | U 0.58 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 0.58 |  |  | 0.27 |  | 1226
90.1-2004 | ClimateZone 4 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  |  |  | 1266
90.1-2004 | ClimateZone 5 | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  |  |  | 1267
90.1-2004 | ClimateZone 5 | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  | 0.39 |  | 1186
90.1-2004 | ClimateZone 5 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.36 |  | 1227
90.1-2004 | ClimateZone 5 | Skylight | Plastic with Curb | Nonresidential | U 1.10 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 1.1 |  |  | 0.19 |  | 1228
90.1-2004 | ClimateZone 5 | Skylight | Plastic with Curb | Residential | U 1.10 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 1.1 |  |  |  |  | 1268
90.1-2004 | ClimateZone 5 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 1269
90.1-2004 | ClimateZone 5 | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  | 0.61 |  | 1182
90.1-2004 | ClimateZone 5 | Skylight | Without Curb | Residential | U 0.69 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  | 0.39 |  | 1223
90.1-2004 | ClimateZone 5 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.19 |  | 1224
90.1-2004 | ClimateZone 6 | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  |  |  | 1264
90.1-2004 | ClimateZone 6 | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm | 0 | 2 | 0.98 |  |  |  |  | 1265
90.1-2004 | ClimateZone 6 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.65 |  | 1184
90.1-2004 | ClimateZone 6 | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.71 Simple Glazing Skylight | 0 | 2 | 0.87 |  |  | 0.65 |  | 1225
90.1-2004 | ClimateZone 6 | Skylight | Plastic with Curb | Residential | U 0.74 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 0.74 |  |  | 0.34 |  | 1226
90.1-2004 | ClimateZone 6 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 1266
90.1-2004 | ClimateZone 6 | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  |  |  | 1267
90.1-2004 | ClimateZone 6 | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 0 | 2 | 0.58 |  |  | 0.61 |  | 1186
90.1-2004 | ClimateZone 6 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.39 |  | 1227
90.1-2004 | ClimateZone 7 | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.68 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  | 0.19 |  | 1228
90.1-2004 | ClimateZone 7 | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.64 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  |  |  | 1268
90.1-2004 | ClimateZone 7 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  |  |  | 1269
90.1-2004 | ClimateZone 7 | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 0.87 |  |  | 0.49 |  | 1305
90.1-2004 | ClimateZone 7 | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 0.61 |  |  | 0.36 |  | 1346
90.1-2004 | ClimateZone 7 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.19 |  | 1347
90.1-2004 | ClimateZone 7 | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.68 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  |  |  | 1387
90.1-2004 | ClimateZone 7 | Skylight | Without Curb | Residential | U 0.69 SHGC 0.64 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  |  |  | 1388
90.1-2004 | ClimateZone 7 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.65 |  | 1307
90.1-2004 | ClimateZone 8 | Skylight | Glass with Curb | Nonresidential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm | 0 | 2 | 0.98 |  |  | 0.62 |  | 1348
90.1-2004 | ClimateZone 8 | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm | 0 | 2 | 0.98 |  |  | 0.27 |  | 1349
90.1-2004 | ClimateZone 8 | Skylight | Glass with Curb | Semiheated | U 1.30 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  |  |  | 1389
90.1-2004 | ClimateZone 8 | Skylight | Plastic with Curb | Nonresidential | U 0.61 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 0.61 |  |  |  |  | 1390
90.1-2004 | ClimateZone 8 | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 0.61 |  |  | 0.49 |  | 1309
90.1-2004 | ClimateZone 8 | Skylight | Plastic with Curb | Semiheated | U 1.10 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 1.1 |  |  | 0.36 |  | 1350
90.1-2004 | ClimateZone 8 | Skylight | Without Curb | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 0 | 2 | 0.58 |  |  | 0.19 |  | 1351
90.1-2004 | ClimateZone 8 | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 0 | 2 | 0.58 |  |  |  |  | 1391
90.1-2004 | ClimateZone 8 | Skylight | Without Curb | Semiheated | U 0.81 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 0.81 |  |  |  |  | 1392
90.1-2007 | ClimateZone 1 | Skylight | Glass with Curb | Nonresidential | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.49 |  | 1428
90.1-2007 | ClimateZone 1 | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight | 0 | 2 | 1.98 |  |  | 0.49 |  | 1469
90.1-2007 | ClimateZone 1 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.39 |  | 1470
90.1-2007 | ClimateZone 1 | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.34 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 1510
90.1-2007 | ClimateZone 1 | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 1511
90.1-2007 | ClimateZone 1 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.77 |  | 1430
90.1-2007 | ClimateZone 1 | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.77 |  | 1471
90.1-2007 | ClimateZone 1 | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.62 |  | 1472
90.1-2007 | ClimateZone 1 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  |  |  | 1512
90.1-2007 | ClimateZone 2 | Skylight | Glass with Curb | Nonresidential | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  |  |  | 1513
90.1-2007 | ClimateZone 2 | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight | 0 | 2 | 1.98 |  |  | 0.49 |  | 1432
90.1-2007 | ClimateZone 2 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.49 |  | 1473
90.1-2007 | ClimateZone 2 | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.39 |  | 1474
90.1-2007 | ClimateZone 2 | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 1514
90.1-2007 | ClimateZone 2 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 1515
90.1-2007 | ClimateZone 2 | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.49 |  | 1551
90.1-2007 | ClimateZone 2 | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.46 |  | 1592
90.1-2007 | ClimateZone 2 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.36 |  | 1593
90.1-2007 | ClimateZone 3 | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  |  |  | 1633
90.1-2007 | ClimateZone 3 | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  |  |  | 1634
90.1-2007 | ClimateZone 3 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.71 |  | 1553
90.1-2007 | ClimateZone 3 | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  | 0.65 |  | 1594
90.1-2007 | ClimateZone 3 | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.27 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  | 0.55 |  | 1595
90.1-2007 | ClimateZone 3 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 1635
90.1-2007 | ClimateZone 3 | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  |  |  | 1636
90.1-2007 | ClimateZone 3 | Skylight | Without Curb | Residential | U 0.69 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  | 0.49 |  | 1555
90.1-2007 | ClimateZone 3 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.49 |  | 1596
90.1-2007 | ClimateZone 4 | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  | 0.39 |  | 1597
90.1-2007 | ClimateZone 4 | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 0.98 |  |  |  |  | 1637
90.1-2007 | ClimateZone 4 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  |  |  | 1638
90.1-2007 | ClimateZone 4 | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  | 0.68 |  | 1674
90.1-2007 | ClimateZone 4 | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.62 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  | 0.64 |  | 1715
90.1-2007 | ClimateZone 4 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.64 |  | 1716
90.1-2007 | ClimateZone 4 | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  |  |  | 1756
90.1-2007 | ClimateZone 4 | Skylight | Without Curb | Residential | U 0.58 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 0.58 |  |  |  |  | 1757
90.1-2007 | ClimateZone 4 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.77 |  | 1676
90.1-2007 | ClimateZone 5 | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  | 0.77 |  | 1717
90.1-2007 | ClimateZone 5 | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  | 0.77 |  | 1718
90.1-2007 | ClimateZone 5 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  |  |  | 1758
90.1-2007 | ClimateZone 5 | Skylight | Plastic with Curb | Nonresidential | U 1.10 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 1.1 |  |  |  |  | 1759
90.1-2007 | ClimateZone 5 | Skylight | Plastic with Curb | Residential | U 1.10 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 1.1 |  |  | 0.68 |  | 1678
90.1-2007 | ClimateZone 5 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.64 |  | 1719
90.1-2007 | ClimateZone 5 | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  | 0.64 |  | 1720
90.1-2007 | ClimateZone 5 | Skylight | Without Curb | Residential | U 0.69 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  |  |  | 1760
90.1-2007 | ClimateZone 5 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  |  |  | 1761
90.1-2007 | ClimateZone 6 | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  |  |  | 1797
90.1-2007 | ClimateZone 6 | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm | 0 | 2 | 0.98 |  |  |  |  | 1838
90.1-2007 | ClimateZone 6 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  |  |  | 1839
90.1-2007 | ClimateZone 6 | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.71 Simple Glazing Skylight | 0 | 2 | 0.87 |  |  |  |  | 1879
90.1-2007 | ClimateZone 6 | Skylight | Plastic with Curb | Residential | U 0.74 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 0.74 |  |  |  |  | 1880
90.1-2007 | ClimateZone 6 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 1799
90.1-2007 | ClimateZone 6 | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  |  |  | 1840
90.1-2007 | ClimateZone 6 | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 0 | 2 | 0.58 |  |  |  |  | 1841
90.1-2007 | ClimateZone 6 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  |  |  | 1881
90.1-2007 | ClimateZone 7 | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.68 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  |  |  | 1882
90.1-2007 | ClimateZone 7 | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.64 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  |  |  | 1801
90.1-2007 | ClimateZone 7 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  |  |  | 1842
90.1-2007 | ClimateZone 7 | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 0.87 |  |  |  |  | 1843
90.1-2007 | ClimateZone 7 | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 0.61 |  |  |  |  | 1883
90.1-2007 | ClimateZone 7 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 1884
90.1-2007 | ClimateZone 7 | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.68 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  | 0.36 |  | 1904
90.1-2007 | ClimateZone 7 | Skylight | Without Curb | Residential | U 0.69 SHGC 0.64 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  | 0.19 |  | 1929
90.1-2007 | ClimateZone 7 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.16 |  | 1930
90.1-2007 | ClimateZone 8 | Skylight | Glass with Curb | Nonresidential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm | 0 | 2 | 0.98 |  |  |  |  | 1954
90.1-2007 | ClimateZone 8 | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm | 0 | 2 | 0.98 |  |  |  |  | 1955
90.1-2007 | ClimateZone 8 | Skylight | Glass with Curb | Semiheated | U 1.30 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  | 0.34 |  | 1906
90.1-2007 | ClimateZone 8 | Skylight | Plastic with Curb | Nonresidential | U 0.61 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 0.61 |  |  | 0.27 |  | 1931
90.1-2007 | ClimateZone 8 | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 0.61 |  |  | 0.27 |  | 1932
90.1-2007 | ClimateZone 8 | Skylight | Plastic with Curb | Semiheated | U 1.10 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 1.1 |  |  |  |  | 1956
90.1-2007 | ClimateZone 8 | Skylight | Without Curb | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 0 | 2 | 0.58 |  |  |  |  | 1957
90.1-2007 | ClimateZone 8 | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 0 | 2 | 0.58 |  |  | 0.36 |  | 1908
90.1-2007 | ClimateZone 8 | Skylight | Without Curb | Semiheated | U 0.81 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 0.81 |  |  | 0.19 |  | 1933
90.1-2010 | ClimateZone 1 | Skylight | Glass with Curb | Nonresidential | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.19 |  | 1934
90.1-2010 | ClimateZone 1 | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight | 0 | 2 | 1.98 |  |  |  |  | 1958
90.1-2010 | ClimateZone 1 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  |  |  | 1959
90.1-2010 | ClimateZone 1 | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.34 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.36 |  | 1979
90.1-2010 | ClimateZone 1 | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.19 |  | 2004
90.1-2010 | ClimateZone 1 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.19 |  | 2005
90.1-2010 | ClimateZone 1 | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  |  |  | 2029
90.1-2010 | ClimateZone 1 | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  |  |  | 2030
90.1-2010 | ClimateZone 1 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.39 |  | 1981
90.1-2010 | ClimateZone 2 | Skylight | Glass with Curb | Nonresidential | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.27 |  | 2006
90.1-2010 | ClimateZone 2 | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight | 0 | 2 | 1.98 |  |  | 0.27 |  | 2007
90.1-2010 | ClimateZone 2 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  |  |  | 2031
90.1-2010 | ClimateZone 2 | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 2032
90.1-2010 | ClimateZone 2 | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.36 |  | 1983
90.1-2010 | ClimateZone 2 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.19 |  | 2008
90.1-2010 | ClimateZone 2 | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.19 |  | 2009
90.1-2010 | ClimateZone 2 | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  |  |  | 2033
90.1-2010 | ClimateZone 2 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  |  |  | 2034
90.1-2010 | ClimateZone 3 | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  | 0.39 |  | 2054
90.1-2010 | ClimateZone 3 | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  | 0.36 |  | 2079
90.1-2010 | ClimateZone 3 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.19 |  | 2080
90.1-2010 | ClimateZone 3 | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  |  |  | 2104
90.1-2010 | ClimateZone 3 | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.27 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  |  |  | 2105
90.1-2010 | ClimateZone 3 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.65 |  | 2056
90.1-2010 | ClimateZone 3 | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  | 0.27 |  | 2081
90.1-2010 | ClimateZone 3 | Skylight | Without Curb | Residential | U 0.69 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  | 0.27 |  | 2082
90.1-2010 | ClimateZone 3 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  |  |  | 2106
90.1-2010 | ClimateZone 4 | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  |  |  | 2107
90.1-2010 | ClimateZone 4 | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 0.98 |  |  | 0.39 |  | 2058
90.1-2010 | ClimateZone 4 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.36 |  | 2083
90.1-2010 | ClimateZone 4 | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  | 0.19 |  | 2084
90.1-2010 | ClimateZone 4 | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.62 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  |  |  | 2108
90.1-2010 | ClimateZone 4 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 2109
90.1-2010 | ClimateZone 4 | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  | 0.49 |  | 2129
90.1-2010 | ClimateZone 4 | Skylight | Without Curb | Residential | U 0.58 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 0.58 |  |  | 0.36 |  | 2154
90.1-2010 | ClimateZone 4 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.19 |  | 2155
90.1-2010 | ClimateZone 5 | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Sgl Ref-D Clr 6mm | 0 | 2 | 1.17 |  |  |  |  | 2179
90.1-2010 | ClimateZone 5 | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  |  |  | 2180
90.1-2010 | ClimateZone 5 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  | 0.65 |  | 2131
90.1-2010 | ClimateZone 5 | Skylight | Plastic with Curb | Nonresidential | U 1.10 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 1.1 |  |  | 0.62 |  | 2156
90.1-2010 | ClimateZone 5 | Skylight | Plastic with Curb | Residential | U 1.10 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 1.1 |  |  | 0.27 |  | 2157
90.1-2010 | ClimateZone 5 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  |  |  | 2181
90.1-2010 | ClimateZone 5 | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  |  |  | 2182
90.1-2010 | ClimateZone 5 | Skylight | Without Curb | Residential | U 0.69 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  | 0.49 |  | 2133
90.1-2010 | ClimateZone 5 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.36 |  | 2158
90.1-2010 | ClimateZone 6 | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  | 0.19 |  | 2159
90.1-2010 | ClimateZone 6 | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm | 0 | 2 | 0.98 |  |  |  |  | 2183
90.1-2010 | ClimateZone 6 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  |  |  | 2184
90.1-2010 | ClimateZone 6 | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.71 Simple Glazing Skylight | 0 | 2 | 0.87 |  |  | 0.49 |  | 2204
90.1-2010 | ClimateZone 6 | Skylight | Plastic with Curb | Residential | U 0.74 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 0.74 |  |  | 0.49 |  | 2229
90.1-2010 | ClimateZone 6 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.39 |  | 2230
90.1-2010 | ClimateZone 6 | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  |  |  | 2254
90.1-2010 | ClimateZone 6 | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 0 | 2 | 0.58 |  |  |  |  | 2255
90.1-2010 | ClimateZone 6 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  | 0.77 |  | 2206
90.1-2010 | ClimateZone 7 | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.68 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  | 0.77 |  | 2231
90.1-2010 | ClimateZone 7 | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.64 Simple Glazing Skylight | 0 | 2 | 1.17 |  |  | 0.62 |  | 2232
90.1-2010 | ClimateZone 7 | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | 0 | 2 | 1.98 |  |  |  |  | 2256
90.1-2010 | ClimateZone 7 | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 0.87 |  |  |  |  | 2257
90.1-2010 | ClimateZone 7 | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 0.61 |  |  | 0.49 |  | 2208
90.1-2010 | ClimateZone 7 | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight | 0 | 2 | 1.9 |  |  | 0.49 |  | 2233
90.1-2010 | ClimateZone 7 | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.68 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  | 0.39 |  | 2234
90.1-2010 | ClimateZone 7 | Skylight | Without Curb | Residential | U 0.69 SHGC 0.64 Simple Glazing Skylight | 0 | 2 | 0.69 |  |  |  |  | 2258
90.1-2010 | ClimateZone 7 | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.36 |  |  |  |  | 2259
90.1-2010 | ClimateZone 8 | Skylight | Glass with Curb | Nonresidential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm | 0 | 2 | 0.98 |  |  | 0.49 |  | 2279
90.1-2010 | ClimateZone 8 | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm | 0 | 2 | 0.98 |  |  | 0.46 |  | 2304
90.1-2010 | ClimateZone 8 | Skylight | Glass with Curb | Semiheated | U 1.30 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 1.3 |  |  | 0.36 |  | 2305
90.1-2010 | ClimateZone 8 | Skylight | Plastic with Curb | Nonresidential | U 0.61 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 0.61 |  |  |  |  | 2329
90.1-2010 | ClimateZone 8 | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 0.61 |  |  |  |  | 2330
90.1-2010 | ClimateZone 8 | Skylight | Plastic with Curb | Semiheated | U 1.10 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 1.1 |  |  | 0.71 |  | 2281
90.1-2010 | ClimateZone 8 | Skylight | Without Curb | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 0 | 2 | 0.58 |  |  | 0.65 |  | 2306
90.1-2010 | ClimateZone 8 | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | 0 | 2 | 0.58 |  |  | 0.55 |  | 2307
90.1-2010 | ClimateZone 8 | Skylight | Without Curb | Semiheated | U 0.81 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 0.81 |  |  |  |  | 2331
90.1-2013 | ClimateZone 1 | Skylight | Glass with Curb | Nonresidential | U 0.75 SHGC 0.35 Simple Glazing Skylight | 0 | 2 | 0.75 |  |  |  |  | 2332
90.1-2013 | ClimateZone 1 | Skylight | Glass with Curb | Residential | U 0.75 SHGC 0.35 Simple Glazing Skylight | 0 | 2 | 0.75 |  |  | 0.49 |  | 2283
90.1-2013 | ClimateZone 1 | Skylight | Glass with Curb | Semiheated | U 1.80 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.8 |  |  | 0.49 |  | 2308
90.1-2013 | ClimateZone 1 | Skylight | Plastic with Curb | Nonresidential | U 0.75 SHGC 0.35 Simple Glazing Skylight | 0 | 2 | 0.75 |  |  | 0.39 |  | 2309
90.1-2013 | ClimateZone 1 | Skylight | Plastic with Curb | Residential | U 0.75 SHGC 0.35 Simple Glazing Skylight | 0 | 2 | 0.75 |  |  |  |  | 2333
90.1-2013 | ClimateZone 1 | Skylight | Plastic with Curb | Semiheated | U 1.80 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.8 |  |  |  |  | 2334
90.1-2013 | ClimateZone 1 | Skylight | Without Curb | Nonresidential | U 0.75 SHGC 0.35 Simple Glazing Skylight | 0 | 2 | 0.75 |  |  | 0.68 |  | 2354
90.1-2013 | ClimateZone 1 | Skylight | Without Curb | Residential | U 0.75 SHGC 0.35 Simple Glazing Skylight | 0 | 2 | 0.75 |  |  | 0.64 |  | 2379
90.1-2013 | ClimateZone 1 | Skylight | Without Curb | Semiheated | U 1.80 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.8 |  |  | 0.64 |  | 2380
90.1-2013 | ClimateZone 2 | Skylight | Glass with Curb | Nonresidential | U 0.65 SHGC 0.35 Simple Glazing Skylight | 0 | 2 | 0.65 |  |  |  |  | 2404
90.1-2013 | ClimateZone 2 | Skylight | Glass with Curb | Residential | U 0.65 SHGC 0.35 Simple Glazing Skylight | 0 | 2 | 0.65 |  |  |  |  | 2405
90.1-2013 | ClimateZone 2 | Skylight | Glass with Curb | Semiheated | U 1.80 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.8 |  |  | 0.77 |  | 2356
90.1-2013 | ClimateZone 2 | Skylight | Plastic with Curb | Nonresidential | U 0.65 SHGC 0.35 Simple Glazing Skylight | 0 | 2 | 0.65 |  |  | 0.77 |  | 2381
90.1-2013 | ClimateZone 2 | Skylight | Plastic with Curb | Residential | U 0.65 SHGC 0.35 Simple Glazing Skylight | 0 | 2 | 0.65 |  |  | 0.77 |  | 2382
90.1-2013 | ClimateZone 2 | Skylight | Plastic with Curb | Semiheated | U 1.80 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.8 |  |  |  |  | 2406
90.1-2013 | ClimateZone 2 | Skylight | Without Curb | Nonresidential | U 0.65 SHGC 0.35 Simple Glazing Skylight | 0 | 2 | 0.65 |  |  |  |  | 2407
90.1-2013 | ClimateZone 2 | Skylight | Without Curb | Residential | U 0.65 SHGC 0.35 Simple Glazing Skylight | 0 | 2 | 0.65 |  |  | 0.68 |  | 2358
90.1-2013 | ClimateZone 2 | Skylight | Without Curb | Semiheated | U 1.80 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.8 |  |  | 0.64 |  | 2383
90.1-2013 | ClimateZone 3 | Skylight | Glass with Curb | Nonresidential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air | 0 | 2 | 0.55 |  |  | 0.64 |  | 2384
90.1-2013 | ClimateZone 3 | Skylight | Glass with Curb | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air | 0 | 2 | 0.55 |  |  |  |  | 2408
90.1-2013 | ClimateZone 3 | Skylight | Glass with Curb | Semiheated | U 1.70 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.7 |  |  |  |  | 2409
90.1-2013 | ClimateZone 3 | Skylight | Plastic with Curb | Nonresidential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air | 0 | 2 | 0.55 |  |  |  |  | 2429
90.1-2013 | ClimateZone 3 | Skylight | Plastic with Curb | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air | 0 | 2 | 0.55 |  |  |  |  | 2454
90.1-2013 | ClimateZone 3 | Skylight | Plastic with Curb | Semiheated | U 1.70 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.7 |  |  |  |  | 2455
90.1-2013 | ClimateZone 3 | Skylight | Without Curb | Nonresidential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air | 0 | 2 | 0.55 |  |  |  |  | 2479
90.1-2013 | ClimateZone 3 | Skylight | Without Curb | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air | 0 | 2 | 0.55 |  |  |  |  | 2480
90.1-2013 | ClimateZone 3 | Skylight | Without Curb | Semiheated | U 1.70 SHGC 0.36 Simple Glazing Skylight | 0 | 2 | 1.7 |  |  |  |  | 2431
90.1-2013 | ClimateZone 4 | Skylight | Glass with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2456
90.1-2013 | ClimateZone 4 | Skylight | Glass with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2457
90.1-2013 | ClimateZone 4 | Skylight | Glass with Curb | Semiheated | U 1.15 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 1.15 |  |  |  |  | 2481
90.1-2013 | ClimateZone 4 | Skylight | Plastic with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2482
90.1-2013 | ClimateZone 4 | Skylight | Plastic with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2433
90.1-2013 | ClimateZone 4 | Skylight | Plastic with Curb | Semiheated | U 1.15 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 1.15 |  |  |  |  | 2458
90.1-2013 | ClimateZone 4 | Skylight | Without Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2459
90.1-2013 | ClimateZone 4 | Skylight | Without Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2483
90.1-2013 | ClimateZone 4 | Skylight | Without Curb | Semiheated | U 1.15 SHGC 0.77 Simple Glazing Skylight | 0 | 2 | 1.15 |  |  |  |  | 2484
90.1-2013 | ClimateZone 5 | Skylight | Glass with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  | 0.36 |  | 2504
90.1-2013 | ClimateZone 5 | Skylight | Glass with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  | 0.19 |  | 2529
90.1-2013 | ClimateZone 5 | Skylight | Glass with Curb | Semiheated | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm | 0 | 2 | 0.98 |  |  |  |  | 2554
90.1-2013 | ClimateZone 5 | Skylight | Plastic with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2555
90.1-2013 | ClimateZone 5 | Skylight | Plastic with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  | 0.34 |  | 2506
90.1-2013 | ClimateZone 5 | Skylight | Plastic with Curb | Semiheated | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm | 0 | 2 | 0.98 |  |  | 0.27 |  | 2531
90.1-2013 | ClimateZone 5 | Skylight | Without Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2556
90.1-2013 | ClimateZone 5 | Skylight | Without Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2557
90.1-2013 | ClimateZone 5 | Skylight | Without Curb | Semiheated | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm | 0 | 2 | 0.98 |  |  | 0.36 |  | 2508
90.1-2013 | ClimateZone 6 | Skylight | Glass with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  | 0.19 |  | 2533
90.1-2013 | ClimateZone 6 | Skylight | Glass with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2558
90.1-2013 | ClimateZone 6 | Skylight | Glass with Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 0.85 |  |  |  |  | 2559
90.1-2013 | ClimateZone 6 | Skylight | Plastic with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  | 0.36 |  | 2579
90.1-2013 | ClimateZone 6 | Skylight | Plastic with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  | 0.19 |  | 2604
90.1-2013 | ClimateZone 6 | Skylight | Plastic with Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 0.85 |  |  | 0.19 |  | 2605
90.1-2013 | ClimateZone 6 | Skylight | Without Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2629
90.1-2013 | ClimateZone 6 | Skylight | Without Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2630
90.1-2013 | ClimateZone 6 | Skylight | Without Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 0.85 |  |  | 0.39 |  | 2581
90.1-2013 | ClimateZone 7 | Skylight | Glass with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  | 0.27 |  | 2606
90.1-2013 | ClimateZone 7 | Skylight | Glass with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  | 0.27 |  | 2607
90.1-2013 | ClimateZone 7 | Skylight | Glass with Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 0.85 |  |  |  |  | 2631
90.1-2013 | ClimateZone 7 | Skylight | Plastic with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2632
90.1-2013 | ClimateZone 7 | Skylight | Plastic with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  | 0.36 |  | 2583
90.1-2013 | ClimateZone 7 | Skylight | Plastic with Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 0.85 |  |  | 0.19 |  | 2608
90.1-2013 | ClimateZone 7 | Skylight | Without Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  | 0.19 |  | 2609
90.1-2013 | ClimateZone 7 | Skylight | Without Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2633
90.1-2013 | ClimateZone 7 | Skylight | Without Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 0.85 |  |  |  |  | 2634
90.1-2013 | ClimateZone 8 | Skylight | Glass with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  | 0.39 |  | 2654
90.1-2013 | ClimateZone 8 | Skylight | Glass with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  | 0.36 |  | 2679
90.1-2013 | ClimateZone 8 | Skylight | Glass with Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 0.85 |  |  |  |  | 2704
90.1-2013 | ClimateZone 8 | Skylight | Plastic with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2705
90.1-2013 | ClimateZone 8 | Skylight | Plastic with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  | 0.65 |  | 2656
90.1-2013 | ClimateZone 8 | Skylight | Plastic with Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 0.85 |  |  | 0.27 |  | 2681
90.1-2013 | ClimateZone 8 | Skylight | Without Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2706
90.1-2013 | ClimateZone 8 | Skylight | Without Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | 0 | 2 | 0.5 |  |  |  |  | 2707
90.1-2013 | ClimateZone 8 | Skylight | Without Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight | 0 | 2 | 0.85 |  |  | 0.39 |  | 2658

## Constructions
|  |  |  | Outside |  |  |  | Inside
Name | Intended Surface Type | Standards Construction Type | Insulation Layer | Material 1 | Material 2 | Material 3 | Material 4 | Material 5 | Material 6 | Sort
ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ExteriorWindow |  |  | Theoretical Glass [167] | [5 empty] | 160
ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ExteriorWindow |  |  | Theoretical Glass [197] | [5 empty] | 161
ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ExteriorWindow |  |  | Theoretical Glass [202] | [5 empty] | 162
ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ExteriorWindow |  |  | Theoretical Glass [207] | [5 empty] | 163
ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ExteriorWindow |  |  | Theoretical Glass [216] | [5 empty] | 165
ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ExteriorWindow |  |  | Theoretical Glass [221] | [5 empty] | 166
ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | ExteriorWindow |  |  | Theoretical Glass [216] | [5 empty] | 164
ext-slab | GroundContactFloor | Unheated |  | HW CONCRETE
ext-slab-mass | GroundContactFloor | Mass | CP02 CARPET PAD | HW CONCRETE | CP02 CARPET PAD
ext-slab-metal-building | GroundContactFloor | Metal Building |  | HW CONCRETE 8 in
ext-slab-steel-frame | GroundContactFloor | SteelFramed | CP02 CARPET PAD | HW CONCRETE 8 in | CP02 CARPET PAD
int_slab_ceiling_smallhotel | InteriorCeiling |  |  | CP02 CARPET PAD | 4 in. Normalweight Concrete Floor
int_slab_floor_smallhotel | InteriorFloor |  |  | 4 in. Normalweight Concrete Floor | CP02 CARPET PAD
int_wall_smallhotel | InteriorWall |  |  | 1/2 in. Gypsum Board | 1/2 in. Gypsum Board
LargeHotel Interior Ceiling | InteriorCeiling |  |  | CP02 CARPET PAD | 100mm Normalweight concrete floor | Nonres_Floor_Insulation
LargeHotel Interior Floor | InteriorFloor |  |  | Nonres_Floor_Insulation | 100mm Normalweight concrete floor | CP02 CARPET PAD
LargeHotel Interior Wall | InteriorWall |  |  | G01 13mm gypsum board | G01 13mm gypsum board
Smallhotel 2010 Slab Floor | GroundContactFloor | Mass | Typical Insulation | 8 in. Normalweight Concrete Floor | CP02 CARPET PAD
Typical Attic Floor | AtticFloor | WoodFramed | Typical Insulation | 1/2IN Gypsum | Typical Insulation | 1/2IN Gypsum |  |  |  | 1
Typical Attic Soffit | AtticWall |  |  | 5/8 in. Plywood | [5 empty] | 12
Typical Built Up Roof | ExteriorRoof | IEAD | Typical Insulation | Built-up Roofing | Typical Insulation | Metal Surface |  |  |  | 24
Typical Built Up Roof - Highly Reflective | ExteriorRoof | IEAD | Typical Insulation | Built-up Roofing - Highly Reflective | Typical Insulation | Metal Surface |  |  |  | 24
Typical Carpeted 4in Slab Floor | ExteriorFloor |  |  | MAT-CC05 4 HW CONCRETE | Typical Carpet Pad |  |  |  |  | 21
Typical Carpeted 6in Slab Floor | GroundContactFloor | Mass |  | 6 in. Normalweight Concrete Floor | Typical Carpet Pad |  |  |  |  | 169
Typical Carpeted 8in Slab Floor | GroundContactFloor | Mass |  | 8 in. Concrete Block Basement Wall | Typical Carpet Pad |  |  |  |  | 170
Typical IEAD Roof | ExteriorRoof | IEAD | Typical Insulation | Roof Membrane | Typical Insulation | Metal Roof Surface |  |  |  | 27
Typical IEAD Roof - Highly Reflective | ExteriorRoof | IEAD | Typical Insulation | Roof Membrane - Highly Reflective | Typical Insulation | Metal Roof Surface |  |  |  | 27
Typical Insulated Basement Mass Wall | GroundContactWall | Mass | Typical Insulation | Typical Insulation | 8 in. Concrete Block Basement Wall
Typical Insulated Carpeted 4in Slab Floor | ExteriorFloor |  | Typical Insulation | Typical Insulation | MAT-CC05 4 HW CONCRETE | Typical Carpet Pad
Typical Insulated Carpeted 6in Slab Floor | GroundContactFloor | Mass | Typical Insulation | Typical Insulation | 6 in. Normalweight Concrete Floor | Typical Carpet Pad
Typical Insulated Carpeted 8in Slab Floor | GroundContactFloor | Mass | Typical Insulation | Typical Insulation | 8 in. Concrete Block Basement Wall | Typical Carpet Pad
Typical Insulated Exterior Mass Floor | ExteriorFloor | Mass | Typical Insulation | Typical Insulation | 4 in. Normalweight Concrete Floor | Typical Carpet Pad |  |  |  | 16
Typical Insulated Exterior Mass Floor Ceiling | ExteriorFloor | Mass | Typical Insulation | Typical Carpet Pad | 4 in. Normalweight Concrete Floor | Typical Insulation |  |  |  | 17
Typical Insulated Exterior Mass Wall | ExteriorWall | Mass | Typical Insulation | 1IN Stucco | 8IN CONCRETE HW RefBldg | Typical Insulation | 1/2IN Gypsum |  |  | 115
Typical Insulated Interior Wall | InteriorWall | WoodFramed | Typical Insulation | 25mm Stucco | 5/8 in. Gypsum Board | Typical Insulation | Steel Frame/Cavity | 5/8 in. Gypsum Board |  | 180
Typical Insulated Metal Building Roof | ExteriorRoof | Metal | Typical Insulation | Metal Roof Surface | Typical Insulation |  |  |  |  | 25
Typical Insulated Metal Building Roof - Highly Reflective | ExteriorRoof | Metal | Typical Insulation | Metal Roof Surface - Highly Reflective | Typical Insulation |  |  |  |  | 25
Typical Insulated Metal Building Wall | ExteriorWall | Metal | Typical Insulation | Metal Siding | Typical Insulation | 1/2IN Gypsum |  |  |  | 113
Typical Insulated Metal Door | ExteriorDoor |  | Typical Insulation | F08 Metal surface | Typical Insulation |  |  |  |  | 15
Typical Insulated Steel Framed Exterior Wall | ExteriorWall | SteelFramed | Typical Insulation | 25mm Stucco | 5/8 in. Gypsum Board | Typical Insulation | 5/8 in. Gypsum Board |  |  | 109
Typical Insulated Wood Framed Exterior Wall | ExteriorWall | WoodFramed | Typical Insulation | 25mm Stucco | 5/8 in. Gypsum Board | Typical Insulation | 5/8 in. Gypsum Board |  |  | 36
Typical Interior Ceiling | InteriorCeiling |  |  | CP02 CARPET PAD | 100mm Normalweight concrete floor |  |  |  |  | 174
Typical Interior Door | InteriorDoor |  |  | G05 25mm wood | [5 empty] | 175
Typical Interior Floor | InteriorFloor |  |  | 100mm Normalweight concrete floor | CP02 CARPET PAD |  |  |  |  | 177
Typical Interior Partition | InteriorPartition |  |  | G05 25mm wood | [5 empty] | 178
Typical Interior Slab Floor | InteriorFloor | Mass |  | 4 in. Normalweight Concrete Floor | Typical Carpet Pad |  |  |  |  | 176
Typical Interior Wall | InteriorWall |  |  | G01 13mm gypsum board | G01 13mm gypsum board |  |  |  |  | 182
Typical Interior Window | InteriorWindow |  |  | Clear 3mm | [5 empty] | 184
Typical Overhead Door | ExteriorDoor | RollUp | Typical Insulation | Typical Insulation | [5 empty] | 14
Typical Uncarpeted 4in Slab Floor | ExteriorFloor |  |  | MAT-CC05 4 HW CONCRETE | [5 empty] | 22
Typical Uncarpeted 6in Slab Floor | GroundContactFloor | Mass |  | 6 in. Normalweight Concrete Floor | [5 empty] | 159
Typical Uninsulated Basement Mass Wall | GroundContactWall | Mass |  | 8 in. Concrete Block Basement Wall | [5 empty] | 171
Typical Uninsulated Exterior Mass Wall | ExteriorWall | Mass |  | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum |  |  |  | 116
Typical Uninsulated Interior Wall | InteriorWall | WoodFramed |  | 1/2 in. Gypsum Board | 1/2 in. Gypsum Board |  |  |  |  | 179
Typical Uninsulated Metal Building Roof | ExteriorRoof | Metal |  | Metal Roofing | [5 empty] | 26
Typical Uninsulated Metal Building Roof - Highly Reflective | ExteriorRoof | Metal |  | Metal Roofing - Highly Reflective | [5 empty] | 26
Typical Uninsulated Metal Building Wall | ExteriorWall | Metal |  | Metal Siding | 1/2IN Gypsum |  |  |  |  | 114
Typical Uninsulated Metal Roof Attic Roof | AtticRoof | WoodFramed |  | Roof Membrane | Metal Decking |  |  |  |  | 8
Typical Uninsulated Steel Framed Exterior Wall | ExteriorWall | SteelFramed |  | Wood Siding | 1/2IN Gypsum |  |  |  |  | 110
Typical Uninsulated Swinging Door | ExteriorDoor | Swinging | Typical Insulation | Typical Insulation | [5 empty] | 13
Typical Uninsulated Wood Joist Attic Roof | AtticRoof |  |  | Asphalt Shingles | 5/8 in. Plywood |  |  |  |  | 11
Typical Wood Joist Attic Floor | AtticFloor | WoodFramed | Typical Insulation | 5/8 in. Gypsum Board | Typical Insulation |  |  |  |  | 2
Typical Wood Joist Attic Floor Ceiling | AtticFloor | WoodFramed |  | Typical Insulation | 5/8 in. Gypsum Board |  |  |  |  | 3
U 0.19 SHGC 0.20 Trp LoE Film (55) Bronze 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | BRONZE 6MM | AIR 13MM | COATED POLY-55 | AIR 13MM | CLEAR 3MM |  | 6
U 0.24 SHGC 0.11 Dbl LoE Elec Abs Colored 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  | ECABS-2 COLORED 6MM | ARGON 13MM | LoE SPEC SEL CLEAR 6MM Rev |  |  |  | 29
U 0.24 SHGC 0.16 Dbl Elec Abs Colored 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  | ECABS-2 COLORED 6MM | ARGON 13MM | CLEAR 6MM |  |  |  | 30
U 0.24 SHGC 0.23 Dbl LoE Spec Sel Tint 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  | LoE SPEC SEL TINT 6MM | ARGON 13MM | CLEAR 6MM |  |  |  | 100
U 0.25 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  | LoE TINT 6MM | ARGON 13MM | CLEAR 6MM |  |  |  | 103
U 0.29 SHGC 0.11 Dbl LoE Elec Ref Colored 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | ECREF-2 COLORED 6MM | AIR 13MM | LoE SPEC SEL CLEAR 6MM Rev |  |  |  | 34
U 0.29 SHGC 0.17 Dbl Elec Abs Colored 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | ECABS-2 COLORED 6MM | AIR 13MM | CLEAR 6MM |  |  |  | 31
U 0.29 SHGC 0.22 Trp LoE Film (55) Bronze 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | BRONZE 6MM | AIR 6MM | COATED POLY-55 | AIR 6MM | CLEAR 3MM |  | 7
U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | LoE TINT 6MM | AIR 13MM | CLEAR 6MM |  |  |  | 102
U 0.33 SHGC 0.11 Dbl LoE Elec Ref Colored 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | ECREF-2 COLORED 6MM | AIR 13MM | LoE SPEC SEL CLEAR 6MM Rev |  |  |  | 35
U 0.33 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | LoE TINT 6MM | AIR 13MM | CLEAR 6MM |  |  |  | 106
U 0.33 SHGC 0.45 Trp LoE Film (77) Clr 3mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | CLEAR 3MM | AIR 6MM | COATED POLY-77 | AIR 6MM | CLEAR 3MM |  | 10
U 0.34 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | LoE TINT 6MM | AIR 13MM | CLEAR 6MM |  |  |  | 105
U 0.34 SHGC 0.45 Dbl LoE (e2-.2) Clr 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | PYR B CLEAR 6MM | AIR 13MM | CLEAR 6MM |  |  |  | 119
U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  | REF C CLEAR MID 6MM | ARGON 13MM | CLEAR 6MM |  |  |  | 142
U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | LoE TINT 6MM | AIR 13MM | CLEAR 6MM |  |  |  | 104
U 0.36 SHGC 0.35 Dbl LoE Spec Sel Tint 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | LoE SPEC SEL TINT 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 99
U 0.38 SHGC 0.26 Dbl Ref B-H Tint 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  | REF B TINT HI 6MM | ARGON 13MM | CLEAR 6MM |  |  |  | 134
U 0.38 SHGC 0.30 Dbl Ref-B-H Clr 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  | REF B CLEAR HI 6MM | ARGON 13MM | CLEAR 6MM |  |  |  | 127
U 0.39 SHGC 0.32 | ExteriorWindow | Metal framing (all other) |  | Theoretical Glass 347 | [5 empty] | 168
U 0.39 SHGC 0.38 | ExteriorWindow | Metal framing (all other) |  | Theoretical Glass 297 | [5 empty] | 167
U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | LoE SPEC SEL CLEAR 3MM | AIR 6MM | CLEAR 6MM |  |  |  | 98
U 0.42 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | LoE TINT 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 107
U 0.42 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | LoE TINT 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 108
U 0.42 SHGC 0.45 Dbl Ref-D Clr 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  | REF D CLEAR 6MM | ARGON 13MM | CLEAR 6MM |  |  |  | 144
U 0.43 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | REF B CLEAR HI 6MM | AIR 13MM | CLEAR 6MM |  |  |  | 130
U 0.43 SHGC 0.29 Dbl LoE Spec Sel Tint 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | LoE SPEC SEL TINT 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 101
U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | REF B TINT HI 6MM | AIR 13MM | CLEAR 6MM |  |  |  | 133
U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | REF B CLEAR HI 6MM | AIR 13MM | CLEAR 6MM |  |  |  | 129
U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | REF B CLEAR HI 6MM | AIR 13MM | CLEAR 6MM |  |  |  | 128
U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | GREY 6MM | AIR 13MM | CLEAR 6MM |  |  |  | 97
U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | ExteriorWindow | Metal framing (all other) |  | REF D CLEAR 6MM | AIR 13MM | CLEAR 6MM |  |  |  | 145
U 0.52 SHGC 0.22 Dbl Ref-B-L Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | REF B CLEAR LO 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 132
U 0.52 SHGC 0.39 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  | U 0.52 SHGC 0.39 Simple Glazing
U 0.52 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | REF D CLEAR 6MM | AIR 13MM | CLEAR 6MM |  |  |  | 146
U 0.52 SHGC 0.49 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  | U 0.52 SHGC 0.49 Simple Glazing
U 0.52 SHGC 0.615 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  | U 0.52 SHGC 0.615 Simple Glazing
U 0.54 SHGC 0.13 Dbl Ref-A-L Clr 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  | REF A CLEAR LO 6MM | AIR 13MM | CLEAR 6MM |  |  |  | 121
U 0.54 SHGC 0.18 Dbl Ref-A-M Tint 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | REF A TINT MID 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 122
U 0.54 SHGC 0.27 Dbl Ref-C-H Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | REF C CLEAR HI 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 137
U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | REF D TINT 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 150
U 0.56 SHGC 0.35 Dbl Ref-D Tint 6mm/6mm | ExteriorWindow | Metal framing (all other) |  | REF D TINT 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 149
U 0.56 SHGC 0.76 Dbl Clr 3mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | CLEAR 3MM | AIR 6MM | CLEAR 3MM |  |  |  | 9
U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | REF C CLEAR HI 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 138
U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | REF D CLEAR 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 147
U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | BLUE 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 4
U 0.58 SHGC 0.19 Simple Glazing Skylight | Skylight | Glass with Curb |  | U 0.58 SHGC 0.19 Simple Glazing
U 0.58 SHGC 0.36 Simple Glazing Skylight | Skylight | Glass with Curb |  | U 0.58 SHGC 0.36 Simple Glazing
U 0.59 SHGC 0.36 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  | U 0.59 SHGC 0.36 Simple Glazing
U 0.59 SHGC 0.39 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  | U 0.59 SHGC 0.39 Simple Glazing
U 0.60 SHGC 0.25 Dbl 2.5mm air |  |  |  | Glass_2175_LayerAvg | Gap_1_W_0_0025 | Glass_2022F_LayerAvg
U 0.61 SHGC 0.77 Simple Glazing Skylight |  |  |  | U 0.61 SHGC 0.77 Simple Glazing
U 0.62 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | REF C CLEAR HI 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 139
U 0.62 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | REF D CLEAR 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 148
U 0.62 SHGC 0.41 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  | U 0.62 SHGC 0.41 Simple Glazing
U 0.62 SHGC 0.49 Dbl Blue 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | BLUE 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 5
U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | REF C CLEAR HI 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 140
U 0.65 SHGC 0.35 Simple Glazing Skylight |  |  |  | U 0.65 SHGC 0.35 Simple Glazing
U 0.67 SHGC 0.77 Sgl LoE (e2-.2) Clr 3mm | ExteriorWindow | Metal framing (all other) |  | PYR B CLEAR 3MM | [5 empty] | 117
U 0.69 SHGC 0.19 Simple Glazing Skylight |  |  |  | U 0.69 SHGC 0.19 Simple Glazing
U 0.69 SHGC 0.36 Simple Glazing Skylight |  |  |  | U 0.69 SHGC 0.36 Simple Glazing
U 0.69 SHGC 0.39 Simple Glazing Skylight |  |  |  | U 0.69 SHGC 0.39 Simple Glazing
U 0.69 SHGC 0.49 Simple Glazing Skylight |  |  |  | U 0.69 SHGC 0.49 Simple Glazing
U 0.69 SHGC 0.64 Simple Glazing Skylight |  |  |  | U 0.69 SHGC 0.64 Simple Glazing
U 0.69 SHGC 0.68 Simple Glazing Skylight |  |  |  | U 0.69 SHGC 0.68 Simple Glazing
U 0.71 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  | REF C CLEAR HI 6MM | AIR 6MM | CLEAR 6MM |  |  |  | 136
U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm | ExteriorWindow | Metal framing (all other) |  | REF B TINT MID 6MM | [5 empty] | 135
U 0.72 SHGC 0.25 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  | U 0.72 SHGC 0.25 Simple Glazing
U 0.72 SHGC 0.36 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  | U 0.72 SHGC 0.36 Simple Glazing
U 0.72 SHGC 0.39 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  | U 0.72 SHGC 0.39 Simple Glazing
U 0.74 SHGC 0.55 Simple Glazing Skylight |  |  |  | U 0.74 SHGC 0.55 Simple Glazing
U 0.74 SHGC 0.65 Simple Glazing Skylight |  |  |  | U 0.74 SHGC 0.65 Simple Glazing
U 0.75 SHGC 0.35 Simple Glazing Skylight |  |  |  | U 0.75 SHGC 0.35 Simple Glazing
U 0.75 SHGC 0.72 Sgl LoE (e2-.2) Clr 6mm | ExteriorWindow | Metal framing (all other) |  | PYR B CLEAR 6MM | [5 empty] | 118
U 0.81 SHGC 0.65 Simple Glazing Skylight |  |  |  | U 0.81 SHGC 0.65 Simple Glazing
U 0.85 SHGC 0.65 Simple Glazing Skylight |  |  |  | U 0.85 SHGC 0.65 Simple Glazing
U 0.87 SHGC 0.58 Simple Glazing Skylight |  |  |  | U 0.87 SHGC 0.58 Simple Glazing
U 0.87 SHGC 0.71 Simple Glazing Skylight |  |  |  | U 0.87 SHGC 0.71 Simple Glazing
U 0.87 SHGC 0.77 Simple Glazing Skylight |  |  |  | U 0.87 SHGC 0.77 Simple Glazing
U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | ExteriorWindow | Metal framing (all other) |  | REF A CLEAR LO 6MM | [5 empty] | 120
U 0.88 SHGC 0.27 Sgl Elec Ref Colored 6mm | ExteriorWindow | Metal framing (all other) |  | ECREF-1 COLORED 6MM | [5 empty] | 32
U 0.98 SHGC 0.19 Simple Glazing Skylight |  |  |  | U 0.98 SHGC 0.19 Simple Glazing
U 0.98 SHGC 0.36 Simple Glazing Skylight |  |  |  | U 0.98 SHGC 0.36 Simple Glazing
U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm | ExteriorWindow | Metal framing (all other) |  | REF B CLEAR HI 6MM | [5 empty] | 124
U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | ExteriorWindow | Metal framing (all other) |  | REF B CLEAR HI 6MM | [5 empty] | 123
U 1.10 SHGC 0.62 Simple Glazing Skylight |  |  |  | U 1.10 SHGC 0.62 Simple Glazing
U 1.10 SHGC 0.77 Simple Glazing Skylight |  |  |  | U 1.10 SHGC 0.77 Simple Glazing
U 1.15 SHGC 0.77 Simple Glazing Skylight |  |  |  | U 1.15 SHGC 0.77 Simple Glazing
U 1.17 SHGC 0.19 Simple Glazing Skylight |  |  |  | U 1.17 SHGC 0.19 Simple Glazing
U 1.17 SHGC 0.36 Simple Glazing Skylight |  |  |  | U 1.17 SHGC 0.36 Simple Glazing
U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm | ExteriorWindow | Metal framing (all other) |  | REF B CLEAR HI 6MM | [5 empty] | 125
U 1.17 SHGC 0.39 Simple Glazing Skylight |  |  |  | U 1.17 SHGC 0.39 Simple Glazing
U 1.17 SHGC 0.49 Sgl Ref-D Clr 6mm | ExteriorWindow | Metal framing (all other) |  | REF D CLEAR 6MM | [5 empty] | 143
U 1.17 SHGC 0.49 Simple Glazing Skylight |  |  |  | U 1.17 SHGC 0.49 Simple Glazing
U 1.17 SHGC 0.64 Simple Glazing Skylight |  |  |  | U 1.17 SHGC 0.64 Simple Glazing
U 1.17 SHGC 0.68 Sgl Green 3mm | ExteriorWindow | Metal framing (all other) |  | GREEN 3MM | [5 empty] | 94
U 1.17 SHGC 0.68 Simple Glazing Skylight |  |  |  | U 1.17 SHGC 0.68 Simple Glazing
U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | ExteriorWindow | Metal framing (all other) |  | ECREF-1 COLORED 6MM | [5 empty] | 33
U 1.22 SHGC 0.25 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  | U 1.22 SHGC 0.25 Simple Glazing
U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm | ExteriorWindow | Metal framing (all other) |  | REF C CLEAR HI 6MM | [5 empty] | 141
U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | ExteriorWindow | Metal framing (all other) |  | REF B CLEAR HI 6MM | [5 empty] | 131
U 1.22 SHGC 0.54 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  | U 1.22 SHGC 0.54 Simple Glazing
U 1.22 SHGC 0.61 Sgl Green 6mm | ExteriorWindow | Metal framing (all other) |  | GREEN 6MM | [5 empty] | 96
U 1.30 SHGC 0.27 Simple Glazing Skylight |  |  |  | U 1.30 SHGC 0.27 Simple Glazing
U 1.30 SHGC 0.34 Simple Glazing Skylight |  |  |  | U 1.30 SHGC 0.34 Simple Glazing
U 1.30 SHGC 0.62 Simple Glazing Skylight |  |  |  | U 1.30 SHGC 0.62 Simple Glazing
U 1.30 SHGC 0.65 Simple Glazing Skylight |  |  |  | U 1.30 SHGC 0.65 Simple Glazing
U 1.36 SHGC 0.19 Simple Glazing Skylight |  |  |  | U 1.36 SHGC 0.19 Simple Glazing
U 1.36 SHGC 0.36 Simple Glazing Skylight |  |  |  | U 1.36 SHGC 0.36 Simple Glazing
U 1.36 SHGC 0.39 Simple Glazing Skylight |  |  |  | U 1.36 SHGC 0.39 Simple Glazing
U 1.36 SHGC 0.61 Simple Glazing Skylight |  |  |  | U 1.36 SHGC 0.61 Simple Glazing
U 1.70 SHGC 0.36 Simple Glazing Skylight |  |  |  | U 1.70 SHGC 0.36 Simple Glazing
U 1.80 SHGC 0.36 Simple Glazing Skylight |  |  |  | U 1.80 SHGC 0.36 Simple Glazing
U 1.90 SHGC 0.27 Simple Glazing Skylight |  |  |  | U 1.90 SHGC 0.27 Simple Glazing
U 1.90 SHGC 0.34 Simple Glazing Skylight |  |  |  | U 1.90 SHGC 0.34 Simple Glazing
U 1.90 SHGC 0.39 Simple Glazing Skylight |  |  |  | U 1.90 SHGC 0.39 Simple Glazing
U 1.90 SHGC 0.65 Simple Glazing Skylight |  |  |  | U 1.90 SHGC 0.65 Simple Glazing
U 1.98 SHGC 0.16 Simple Glazing Skylight |  |  |  | U 1.98 SHGC 0.16 Simple Glazing
U 1.98 SHGC 0.19 Simple Glazing Skylight |  |  |  | U 1.98 SHGC 0.19 Simple Glazing
U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | ExteriorWindow | Metal framing (all other) |  | REF B CLEAR HI 6MM | [5 empty] | 126
U 1.98 SHGC 0.36 Simple Glazing Skylight |  |  |  | U 1.98 SHGC 0.36 Simple Glazing
U 1.98 SHGC 0.39 Simple Glazing Skylight |  |  |  | U 1.98 SHGC 0.39 Simple Glazing
U 1.98 SHGC 0.61 Sgl Green 6mm | ExteriorWindow | Metal framing (all other) |  | GREEN 6MM | [5 empty] | 95
U 1.98 SHGC 0.61 Simple Glazing Skylight |  |  |  | U 1.98 SHGC 0.61 Simple Glazing
WoodWallU110 | ExteriorWall |  |  | Plywood - 5/8 in. | Compliance Insulation R6.46 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 3/8 in. |  |  | 156

## Materials
Each Material represents a layer of typical building material. Materials are referenced on the Constructions tab.
|  | Opaque Material Properties | [9 empty] | Simple Glazing Material Properties |  |  | Detailed Glazing Material Properties | [11 empty] | Standards Information
Name | Material Type | Roughness | Thickness (in) | Conductivity (Btu*in/hr*ft^2*F) | Resistance (hr*ft^2*F/Btu) | Density (lb/ft^3) | Specific Heat (Btu/lbm*F) | Thermal Absorptance | Solar Absorptance | Visible Absorptance | Gas Type | U-Factor (Btu/hr*ft^2*F) | Solar Heat Gain Coefficient | Visible Transmittance | Optical Data Type | Solar Transmittance At Normal Incidence | Front Side Solar Reflectance At Normal Incidence | Back Side Solar Reflectance At Normal Incidence | Visible Transmittance At Normal Incidence | Front Side Visible Reflectance At Normal Incidence | Back Side Visible Reflectance At Normal Incidence | Infrared Transmittance At Normal Incidence | Front Side Infrared Hemispherical Emissivity | Back Side Infrared Hemispherical Emissivity | Dirt Correction Factor For Solar And Visible Transmittance | Solar Diffusing | Material Standard | Material Standard Source | Code Category | Code Identifier | Framing Material | Framing Configuration | Framing Depth | Framing Size | Cavity Insulation (hr*ft^2*F/Btu) | sort
1 Coat Stucco | StandardOpaqueMaterial | MediumRough | 0.38 | 5.0004 | 0.07599392049 | 115.81 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Masonry Materials | 1 Coat Stucco | [5 empty] | 605
1/2 in. Gypsum Board | StandardOpaqueMaterial | Smooth | 0.5 | 1.1094 | 0.4507121527 | 49.9424 | 0.26034 | 0.9 | 0.7 | 0.5 | [25 empty] | 1190
1/2IN Gypsum | StandardOpaqueMaterial | Smooth | 0.5 | 1.1094 | 0.4507121527 | 48.9997 | 0.19824 | 0.9 | 0.4 | 0.4 | [25 empty] | 1
10 PSF Roof - 1 in. | StandardOpaqueMaterial | VeryRough | 1 | 12.0048 | 0.08330001333 | 120 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Bruce | Roofing | 10 PSF Roof - 1 in. | [5 empty] | 684
100mm Normalweight concrete floor | StandardOpaqueMaterial | MediumRough | 4 | 16.0194 | 2.50E-01 | 144.9578 | 0.19885
15 PSF Roof - 1 1/2 in. | StandardOpaqueMaterial | VeryRough | 1.5 | 18.0072 | 0.08330001333 | 120 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Bruce | Roofing | 15 PSF Roof - 1 1/2 in. | [5 empty] | 685
1IN Stucco | StandardOpaqueMaterial | Smooth | 0.99606 | 4.7966 | 0.2076612641 | 115.9912 | 0.19991 | 0.9 | 0.92 | 0.92 | [25 empty] | 2
25 PSF Roof - 2 1/2 in. | StandardOpaqueMaterial | VeryRough | 2.5 | 30.012 | 0.08330001333 | 120 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Bruce | Roofing | 25 PSF Roof - 2 1/2 in. | [5 empty] | 686
25mm Stucco | StandardOpaqueMaterial | Smooth | 1 | 4.9921 | 0.2003165123 | 115.8663 | 0.20063 | 0.9 | 0.7 | 0.7 | [25 empty] | 1191
3 Coat Stucco | StandardOpaqueMaterial | MediumRough | 0.88 | 4.3752 | 0.2011336625 | 116 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Bruce | Masonry Materials | 3 Coat Stucco | [5 empty] | 606
4 in. Normalweight Concrete Floor | StandardOpaqueMaterial | MediumRough | 4 | 16.0163 | 0.2497452621 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7 | [25 empty] | 1192
4 in. Normalweight Concrete Wall | StandardOpaqueMaterial | MediumRough | 4 | 16.0163 | 0.2497452621 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7 | [25 empty] | 1193
5 PSF Roof - 1/2 in. | StandardOpaqueMaterial | VeryRough | 0.5 | 6.0024 | 0.08330001333 | 120 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Bruce | Roofing | 5 PSF Roof - 1/2 in. | [5 empty] | 683
5/8 in. Gypsum Board | StandardOpaqueMaterial | MediumSmooth | 0.62598 | 1.1094 | 0.5642774195 | 49.9424 | 0.26034 | 0.9 | 0.7 | 0.7 | [25 empty] | 1194
5/8 in. Plywood | StandardOpaqueMaterial | Smooth | 0.62598 | 0.83202 | 0.7523698927 | 33.9608 | 0.289 | 0.9 | 0.7 | 0.7 | [25 empty] | 1195
6 in. Heavyweight Concrete Roof | StandardOpaqueMaterial | MediumRough | 6 | 16.0163 | 0.3746178932 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7 | [25 empty] | 1196
6 in. Normalweight Concrete Floor | StandardOpaqueMaterial | MediumRough | 6 | 16.0163 | 0.3746178932 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7 | [25 empty] | 1197
8 in. Concrete Block Basement Wall | StandardOpaqueMaterial | MediumRough | 8 | 9.1938 | 0.8701531757 | 114.9923 | 0.21783 | 0.9 | 0.7 | 0.7 | [25 empty] | 1198
8 in. Concrete Block Wall | StandardOpaqueMaterial | MediumRough | 8 | 4.9921 | 1.602532098 | 49.9424 | 0.19872 | 0.9 | 0.7 | 0.7 | [25 empty] | 1199
8 in. Normalweight Concrete Floor | StandardOpaqueMaterial | MediumRough | 8 | 16.0163 | 0.4994905242 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7 | [25 empty] | 1200
8 in. Normalweight Concrete Wall | StandardOpaqueMaterial | MediumRough | 8 | 16.0163 | 0.4994905242 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7 | [25 empty] | 1201
8IN Concrete HW | StandardOpaqueMaterial | MediumRough | 8.0039 | 11.9921 | 0.667432318 | 140.0259 | 0.19991 | 0.9 | 0.65 | 0.65 | [25 empty] | 3
8IN CONCRETE HW RefBldg | StandardOpaqueMaterial | Rough | 8 | 9.0898 | 0.8801091616 | 139.8386 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 4
Acoustic Ceiling | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.39521 | 1.26515692 | 17.9793 | 0.31981 | 0.9 | 0.7 | 0.2 | [25 empty] | 1202
Acoustic Tile - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.3996 | 1.251251251 | 18 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Finish Materials | Acoustic Tile - 1/2 in. | [5 empty] | 398
Acoustic Tile - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.3996 | 1.876876877 | 18 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Finish Materials | Acoustic Tile - 3/4 in. | [5 empty] | 399
Acoustic Tile - 3/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.38 | 0.39 | 0.9743589744 | 18 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Finish Materials | Acoustic Tile - 3/8 in. | [5 empty] | 397
Aggregate - 45 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 1.56 | 0.3205128205 | 45 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - 45 lb/ft3 - 1/2 in. | [5 empty] | 657
Aggregate - 45 lb/ft3 - 5/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.63 | 1.5996 | 0.3938484621 | 45 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - 45 lb/ft3 - 5/8 in. | [5 empty] | 658
Aggregate - 45 lb/ft3 - on metal lath - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 1.5996 | 0.4688672168 | 45 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - 45 lb/ft3 - on metal lath - 3/4 in. | [5 empty] | 659
Aggregate - Perlite - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 1.2996 | 0.3847337642 | 45 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - Perlite - 1/2 in. | [5 empty] | 660
Aggregate - Perlite - 5/8 in. | StandardOpaqueMaterial | Smooth | 0.63 | 1.5 | 0.42 | 45 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - Perlite - 5/8 in. | [5 empty] | 661
Aggregate - Perlite - on metal lath - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 1.7004 | 0.4410726888 | 45 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - Perlite - on metal lath - 3/4 in. | [5 empty] | 662
Air - Cavity - Wall Roof Ceiling - 4 in. or more | StandardOpaqueMaterial |  | 6 | 6.5196 | 0.920301859 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | JA4 | Air | Air - Cavity - Wall Roof Ceiling - 4 in. or more | [5 empty] | 290
Air - Ceiling - 1 1/2 in. | StandardOpaqueMaterial |  | 1.5 | 1.95 | 0.7692307692 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Ceiling - 1 1/2 in. | [5 empty] | 298
Air - Ceiling - 1/2 in. | StandardOpaqueMaterial |  | 0.5 | 0.6804 | 0.734861846 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Ceiling - 1/2 in. | [5 empty] | 296
Air - Ceiling - 3 1/2 in. | StandardOpaqueMaterial |  | 3.5 | 4.38 | 0.799086758 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Ceiling - 3 1/2 in. | [5 empty] | 299
Air - Ceiling - 3/4 in. | StandardOpaqueMaterial |  | 0.75 | 0.9996 | 0.75030012 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Ceiling - 3/4 in. | [5 empty] | 297
Air - Floor - 1 1/2 in. | StandardOpaqueMaterial |  | 1.5 | 1.5996 | 0.9377344336 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Floor - 1 1/2 in. | [5 empty] | 306
Air - Floor - 1/2 in. | StandardOpaqueMaterial |  | 0.5 | 0.6504 | 0.7687576876 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Floor - 1/2 in. | [5 empty] | 304
Air - Floor - 3 1/2 in. | StandardOpaqueMaterial |  | 3.5 | 3.5004 | 0.9998857273 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Floor - 3 1/2 in. | [5 empty] | 307
Air - Floor - 3/4 in. | StandardOpaqueMaterial |  | 0.75 | 0.8796 | 0.8526603001 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Floor - 3/4 in. | [5 empty] | 305
Air - Metal Wall Framing - 16 or 24 in. OC | StandardOpaqueMaterial |  | 5.5 | 8.46 | 0.6501182033 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | JA4 | Air | Air - Metal Wall Framing - 16 or 24 in. OC | [5 empty] | 291
Air - Roof - 1 1/2 in. | StandardOpaqueMaterial |  | 1.5 | 1.8804 | 0.7977026165 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Roof - 1 1/2 in. | [5 empty] | 302
Air - Roof - 1/2 in. | StandardOpaqueMaterial |  | 0.5 | 0.66 | 0.7575757576 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Roof - 1/2 in. | [5 empty] | 300
Air - Roof - 3 1/2 in. | StandardOpaqueMaterial |  | 3.5 | 4.2696 | 0.8197489226 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Roof - 3 1/2 in. | [5 empty] | 303
Air - Roof - 3/4 in. | StandardOpaqueMaterial |  | 0.75 | 0.93 | 0.8064516129 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Roof - 3/4 in. | [5 empty] | 301
Air - Wall - 1 1/2 in. | StandardOpaqueMaterial |  | 1.5 | 1.7196 | 0.8722958828 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Wall - 1 1/2 in. | [5 empty] | 294
Air - Wall - 1/2 in. | StandardOpaqueMaterial |  | 0.5 | 0.6504 | 0.7687576876 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Wall - 1/2 in. | [5 empty] | 292
Air - Wall - 3 1/2 in. | StandardOpaqueMaterial |  | 3.5 | 4.1196 | 0.8495970483 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Wall - 3 1/2 in. | [5 empty] | 295
Air - Wall - 3/4 in. | StandardOpaqueMaterial |  | 0.75 | 0.8904 | 0.8423180593 | 0.08 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Wall - 3/4 in. | [5 empty] | 293
Air 13mm | Gas |  | 0.5 | [7 empty] | Air | [24 empty] | 5
AIR 13MM | Gas |  | 0.5 | [7 empty] | Air | [24 empty] | 1350
AIR 3MM | Gas |  | 0.12598 | [7 empty] | Air | [24 empty] | 1351
AIR 6MM | Gas |  | 0.24803 | [7 empty] | Air | [24 empty] | 1352
Aluminum w/ Thrml Break - Double glass with no low e - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.9 | 2.522222222 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - No Ins. | [5 empty] | 819
Aluminum w/ Thrml Break - Double glass with no low e - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.8196 | 3.989751098 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R10 Ins. | [5 empty] | 822
Aluminum w/ Thrml Break - Double glass with no low e - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 1.08 | 4.138888889 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R15 Ins. | [5 empty] | 823
Aluminum w/ Thrml Break - Double glass with no low e - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 1.3296 | 4.264440433 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R20 Ins. | [5 empty] | 824
Aluminum w/ Thrml Break - Double glass with no low e - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.5996 | 4.294823706 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R25 Ins. | [5 empty] | 825
Aluminum w/ Thrml Break - Double glass with no low e - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.8504 | 4.361219196 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R30 Ins. | [5 empty] | 826
Aluminum w/ Thrml Break - Double glass with no low e - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.5304 | 3.450226244 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R4 Ins. | [5 empty] | 820
Aluminum w/ Thrml Break - Double glass with no low e - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.6696 | 3.808243728 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R7 Ins. | [5 empty] | 821
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 1.1796 | 1.924381146 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - No Ins. | [5 empty] | 811
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.8496 | 3.848870056 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R10 Ins. | [5 empty] | 814
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 1.1004 | 4.062159215 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R15 Ins. | [5 empty] | 815
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 1.35 | 4.2 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R20 Ins. | [5 empty] | 816
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.6104 | 4.266020864 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R25 Ins. | [5 empty] | 817
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.86 | 4.338709677 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R30 Ins. | [5 empty] | 818
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.5604 | 3.265524625 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R4 Ins. | [5 empty] | 812
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.6996 | 3.644939966 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R7 Ins. | [5 empty] | 813
Aluminum w/ Thrml Break - Triple or low e glass - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.78 | 2.91025641 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - No Ins. | [5 empty] | 827
Aluminum w/ Thrml Break - Triple or low e glass - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.8196 | 3.989751098 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R10 Ins. | [5 empty] | 830
Aluminum w/ Thrml Break - Triple or low e glass - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 1.08 | 4.138888889 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R15 Ins. | [5 empty] | 831
Aluminum w/ Thrml Break - Triple or low e glass - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 1.3296 | 4.264440433 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R20 Ins. | [5 empty] | 832
Aluminum w/ Thrml Break - Triple or low e glass - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.5996 | 4.294823706 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R25 Ins. | [5 empty] | 833
Aluminum w/ Thrml Break - Triple or low e glass - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.8504 | 4.361219196 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R30 Ins. | [5 empty] | 834
Aluminum w/ Thrml Break - Triple or low e glass - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.51 | 3.588235294 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R4 Ins. | [5 empty] | 828
Aluminum w/ Thrml Break - Triple or low e glass - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.6696 | 3.808243728 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R7 Ins. | [5 empty] | 829
Aluminum w/out Thrml Break - Double glass with no low e coatings - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.8304 | 2.733622351 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - No Ins. | [5 empty] | 795
Aluminum w/out Thrml Break - Double glass with no low e coatings - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.6504 | 5.027675277 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R10 Ins. | [5 empty] | 798
Aluminum w/out Thrml Break - Double glass with no low e coatings - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.8304 | 5.382947977 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R15 Ins. | [5 empty] | 799
Aluminum w/out Thrml Break - Double glass with no low e coatings - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 1.0046 | 5.643812709 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R20 Ins. | [5 empty] | 800
Aluminum w/out Thrml Break - Double glass with no low e coatings - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.1904 | 5.771169355 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R25 Ins. | [5 empty] | 801
Aluminum w/out Thrml Break - Double glass with no low e coatings - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.3704 | 5.888791594 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R30 Ins. | [5 empty] | 802
Aluminum w/out Thrml Break - Double glass with no low e coatings - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.4404 | 4.155313351 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R4 Ins. | [5 empty] | 796
Aluminum w/out Thrml Break - Double glass with no low e coatings - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.54 | 4.722222222 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R7 Ins. | [5 empty] | 797
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 1.1304 | 2.008138712 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - No Ins. | [5 empty] | 787
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.66 | 4.954545455 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R10 Ins. | [5 empty] | 790
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.84 | 5.321428571 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R15 Ins. | [5 empty] | 791
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 1.0104 | 5.611638955 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R20 Ins. | [5 empty] | 792
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.1904 | 5.771169355 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R25 Ins. | [5 empty] | 793
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.38 | 5.847826087 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R30 Ins. | [5 empty] | 794
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.4704 | 3.890306122 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R4 Ins. | [5 empty] | 788
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.5604 | 4.550321199 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R7 Ins. | [5 empty] | 789
Aluminum w/out Thrml Break - Triple or low e glass - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.69 | 3.289855072 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - No Ins. | [5 empty] | 803
Aluminum w/out Thrml Break - Triple or low e glass - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.63648 | 5.137631976 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R10 Ins. | [5 empty] | 806
Aluminum w/out Thrml Break - Triple or low e glass - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.8196 | 5.453879941 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R15 Ins. | [5 empty] | 807
Aluminum w/out Thrml Break - Triple or low e glass - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.9996 | 5.672268908 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R20 Ins. | [5 empty] | 808
Aluminum w/out Thrml Break - Triple or low e glass - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.1796 | 5.824008138 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R25 Ins. | [5 empty] | 809
Aluminum w/out Thrml Break - Triple or low e glass - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.3704 | 5.888791594 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R30 Ins. | [5 empty] | 810
Aluminum w/out Thrml Break - Triple or low e glass - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.41724 | 4.385964912 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R4 Ins. | [5 empty] | 804
Aluminum w/out Thrml Break - Triple or low e glass - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.5304 | 4.807692308 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R7 Ins. | [5 empty] | 805
ARGON 13MM | Gas |  | 0.5 | [7 empty] | Argon | [24 empty] | 1353
Asbestos or cement shingles - 3/8 in. | StandardOpaqueMaterial | VeryRough | 0.38 | 1.7904 | 0.2122430742 | 120 | 0.24 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Asbestos or cement shingles - 3/8 in. | [5 empty] | 687
Ash - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.1004 | 0.9087604507 | 40.06 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Ash - 1 in. | [5 empty] | 884
Asphalt - bitumen with inert fill - 100 lb/ft3 - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 3 | 0.25 | 100 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Asphalt - bitumen with inert fill - 100 lb/ft3 - 3/4 in. | [5 empty] | 688
Asphalt - bitumen with inert fill - 144 lb/ft3 - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 8.0004 | 0.09374531273 | 144 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Asphalt - bitumen with inert fill - 144 lb/ft3 - 3/4 in. | [5 empty] | 689
Asphalt roll roofing - 1/4 in. | StandardOpaqueMaterial | VeryRough | 0.25 | 1.6704 | 0.149664751 | 70 | 0.36 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Asphalt roll roofing - 1/4 in. | [5 empty] | 690
Asphalt Shingles | StandardOpaqueMaterial | VeryRough | 0.12598 | 0.27734 | 0.4542610673 | 69.9193 | 0.30095 | 0.9 | 0.7 | 0.7 | [25 empty] | 1203
Asphalt shingles - 1/4 in. | StandardOpaqueMaterial | VeryRough | 0.25 | 0.5604 | 0.4461099215 | 69.89 | 0.3 | [19 empty] | CEC Title24-2013 | CEC Doug | Roofing | Asphalt shingles - 1/4 in. | [5 empty] | 691
AtticFloor Insulation | StandardOpaqueMaterial | MediumRough | 9.3661 | 0.33974 | 27.56854794 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 6
Birch - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.1904 | 0.8400537634 | 43.93 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Birch - 1 in. | [5 empty] | 885
BLUE 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.48 | 0.05 | 0.05 | 0.57 | 0.06 | 0.06 | 0 | 0.84 | 0.84 | 1 | FALSE | [9 empty] | 1310
Brick - 48 lb/ft3 - 3 5/8 in. | StandardOpaqueMaterial | Rough | 3.63 | 1.5 | 2.42 | 48 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Brick - 48 lb/ft3 - 3 5/8 in. | [5 empty] | 591
Brick - fired clay - 140 lb/ft3 - 3 5/8 in. | StandardOpaqueMaterial | MediumRough | 3.63 | 8.22 | 0.4416058394 | 139.78 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Brick - fired clay - 140 lb/ft3 - 3 5/8 in. | [5 empty] | 592
BRONZE 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.482 | 0.054 | 0.054 | 0.534 | 0.057 | 0.057 | 0 | 0.84 | 0.84 | 1 | FALSE | [9 empty] | 1311
Building Paper - 1/16 in. | StandardOpaqueMaterial | MediumSmooth | 0.06 | 2.0004 | 0.0299940012 | 70 | 0.3 | [19 empty] | CEC Title24-2013 | CEC Doug | Building Membrane | Building Paper - 1/16 in. | [5 empty] | 344
Built-up Roofing | StandardOpaqueMaterial | Rough | 0.37402 | 1.1094 | 0.3371468859 | 69.9193 | 0.34872 | 0.9 | 0.7 | 0.7 | [25 empty] | 1204
Built-up roofing - 3/8 in. | StandardOpaqueMaterial | VeryRough | 0.38 | 1.14 | 0.3333333333 | 70 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Built-up roofing - 3/8 in. | [5 empty] | 692
Built-up Roofing - Highly Reflective | StandardOpaqueMaterial | Rough | 0.37402 | 1.1094 | 0.3371468859 | 69.9193 | 0.34872 | 0.75 | 0.45 | 0.7 | [25 empty] | 1204
Bulk Storage Products Material | StandardOpaqueMaterial | Rough | 96.0002 | 9.9981 | 9.601875846 | 12.5 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 1205
California Redwood - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 0.78 | 1.282051282 | 26.21 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | California Redwood - 1 in. | [5 empty] | 886
Carpet - 3/4 in. | StandardOpaqueMaterial | Rough | 0.75 | 0.3156 | 2.376425856 | 18 | 0.33 | [19 empty] | CEC Title24-2013 | CEC Doug | Finish Materials | Carpet - 3/4 in. | [5 empty] | 400
Cellular polyisocyanurate (unfaced) - 1 1/2 in. R8.8 | StandardOpaqueMaterial | Rough | 1.5 | 0.1704 | 8.802816901 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 1 1/2 in. R8.8 | [5 empty] | 444
Cellular polyisocyanurate (unfaced) - 1 in. R5.9 | StandardOpaqueMaterial | Rough | 1 | 0.1704 | 5.868544601 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 1 in. R5.9 | [5 empty] | 443
Cellular polyisocyanurate (unfaced) - 1/2 in. R2.9 | StandardOpaqueMaterial | Rough | 0.5 | 0.1704 | 2.9342723 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 1/2 in. R2.9 | [5 empty] | 442
Cellular polyisocyanurate (unfaced) - 1/4 in. R1.5 | StandardOpaqueMaterial | Rough | 0.25 | 0.1704 | 1.46713615 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 1/4 in. R1.5 | [5 empty] | 441
Cellular polyisocyanurate (unfaced) - 1/8 in. R0.7 | StandardOpaqueMaterial | Rough | 0.13 | 0.1704 | 0.7629107981 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 1/8 in. R0.7 | [5 empty] | 440
Cellular polyisocyanurate (unfaced) - 2 1/2 in. R15 | StandardOpaqueMaterial | Rough | 2.5 | 0.1704 | 14.6713615 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 2 1/2 in. R15 | [5 empty] | 446
Cellular polyisocyanurate (unfaced) - 2 in. R12 | StandardOpaqueMaterial | Rough | 2 | 0.1704 | 11.7370892 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 2 in. R12 | [5 empty] | 445
Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 | StandardOpaqueMaterial | Rough | 3.5 | 0.1704 | 20.5399061 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 | [5 empty] | 448
Cellular polyisocyanurate (unfaced) - 3 in. R18 | StandardOpaqueMaterial | Rough | 3 | 0.1704 | 17.6056338 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 3 in. R18 | [5 empty] | 447
Cellular polyisocyanurate (unfaced) - 4 1/2 in. R26 | StandardOpaqueMaterial | Rough | 4.5 | 0.1704 | 26.4084507 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 4 1/2 in. R26 | [5 empty] | 450
Cellular polyisocyanurate (unfaced) - 4 in. R23 | StandardOpaqueMaterial | Rough | 4 | 0.1704 | 23.4741784 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 4 in. R23 | [5 empty] | 449
Cellular polyisocyanurate (unfaced) - 5 1/2 in. R32 | StandardOpaqueMaterial | Rough | 5.5 | 0.1704 | 32.27699531 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 5 1/2 in. R32 | [5 empty] | 452
Cellular polyisocyanurate (unfaced) - 5 in. R29 | StandardOpaqueMaterial | Rough | 5 | 0.1704 | 29.342723 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 5 in. R29 | [5 empty] | 451
Cellular polyisocyanurate (unfaced) - 6 1/2 in. R38 | StandardOpaqueMaterial | Rough | 6.5 | 0.1704 | 38.14553991 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 6 1/2 in. R38 | [5 empty] | 454
Cellular polyisocyanurate (unfaced) - 6 in. R35 | StandardOpaqueMaterial | Rough | 6 | 0.1704 | 35.21126761 | 1.5 | 0.38 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 6 in. R35 | [5 empty] | 453
Clay - Part Grouted and Empty - 130 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.12 | 1.923076923 | 130 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Clay - Part Grouted and Empty - 130 lb/ft3 - 6 in. | [5 empty] | 609
Clay - Part Grouted and Empty - 130 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.7596 | 2.127885945 | 130 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Clay - Part Grouted and Empty - 130 lb/ft3 - 8 in. | [5 empty] | 610
Clay - Part Grouted and Insulated - 130 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 2.7 | 2.222222222 | 130 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Clay - Part Grouted and Insulated - 130 lb/ft3 - 6 in. | [5 empty] | 637
Clay - Part Grouted and Insulated - 130 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.12 | 2.564102564 | 130 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Clay - Part Grouted and Insulated - 130 lb/ft3 - 8 in. | [5 empty] | 638
Clay - Solid Grout - 130 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.9 | 1.538461538 | 130 | 0.17 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Clay - Solid Grout - 130 lb/ft3 - 6 in. | [5 empty] | 623
Clay - Solid Grout - 130 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 4.56 | 1.754385965 | 130 | 0.17 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Clay - Solid Grout - 130 lb/ft3 - 8 in. | [5 empty] | 624
Clay tile - 1/2 in. | StandardOpaqueMaterial | MediumRough | 0.5 | 0.1896 | 2.637130802 | 85 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Clay tile - 1/2 in. | [5 empty] | 693
Clay tile - hollow - 1 cell deep - 3 in. | StandardOpaqueMaterial | MediumRough | 3 | 3.75 | 0.8 | 85 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 1 cell deep - 3 in. | [5 empty] | 593
Clay tile - hollow - 1 cell deep - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 3.6 | 1.111111111 | 85 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 1 cell deep - 4 in. | [5 empty] | 594
Clay tile - hollow - 2 cells deep - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 4.5 | 2.222222222 | 85 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 2 cells deep - 10 in. | [5 empty] | 597
Clay tile - hollow - 2 cells deep - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.9504 | 1.518833536 | 85 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 2 cells deep - 6 in. | [5 empty] | 595
Clay tile - hollow - 2 cells deep - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 4.32 | 1.851851852 | 85 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 2 cells deep - 8 in. | [5 empty] | 596
Clay tile - hollow - 3 cells deep - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 4.8 | 2.5 | 85 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 3 cells deep - 12 in. | [5 empty] | 598
Clay Tile - Paver | StandardOpaqueMaterial | MediumRough | 0.38 | 12.504 | 0.03039027511 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | CEC Doug | Masonry Materials | Clay Tile - Paver | [5 empty] | 599
CLEAR 2.5MM | StandardGlazing |  | 0.098425 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.8 | 0.075 | 0.075 | 0.901 | 0.081 | 0.081 | 0 | 0.84 | 0.84 | 1 | FALSE | [9 empty] | 1312
Clear 3mm | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.837 | 0.075 | 0.075 | 0.898 | 0.081 | 0.081 | 0 | 0.84 | 0.84 | 1 | FALSE | [9 empty] | 32
CLEAR 3MM | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.837 | 0.075 | 0.075 | 0.898 | 0.081 | 0.081 | 0 | 0.84 | 0.84 | 1 | FALSE | [9 empty] | 1313
CLEAR 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.775 | 0.071 | 0.071 | 0.881 | 0.08 | 0.08 | 0 | 0.84 | 0.84 | 1 | FALSE | [9 empty] | 1314
COATED POLY-55 | StandardGlazing |  | 0.020079 | 0.97069 | 1.0302 | [9 empty] | SpectralAverage | 0.32 | 0.582 | 0.593 | 0.551 | 0.336 | 0.375 | 0 | 0.046 | 0.72 | 1 | FALSE | [9 empty] | 1315
COATED POLY-77 | StandardGlazing |  | 0.020079 | 0.97069 | 1.0302 | [9 empty] | SpectralAverage | 0.504 | 0.402 | 0.398 | 0.766 | 0.147 | 0.167 | 0 | 0.075 | 0.72 | 1 | FALSE | [9 empty] | 1316
Compliance Insulation R0.01 | StandardOpaqueMaterial | MediumSmooth | 0.0016 | 0.1596 | 0.01002506266 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R0.01 | [5 empty] | 515
Compliance Insulation R0.02 | StandardOpaqueMaterial | MediumSmooth | 0.0032 | 0.1596 | 0.02005012531 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R0.02 | [5 empty] | 516
Compliance Insulation R0.10 | StandardOpaqueMaterial | MediumSmooth | 0.016 | 0.1596 | 0.1002506266 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R0.10 | [5 empty] | 517
Compliance Insulation R1.35 | StandardOpaqueMaterial | MediumSmooth | 0.216 | 0.1596 | 1.353383459 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R1.35 | [5 empty] | 518
Compliance Insulation R1.41 | StandardOpaqueMaterial | MediumSmooth | 0.2256 | 0.1596 | 1.413533835 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R1.41 | [5 empty] | 519
Compliance Insulation R1.54 | StandardOpaqueMaterial | MediumSmooth | 0.2464 | 0.1596 | 1.543859649 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R1.54 | [5 empty] | 520
Compliance Insulation R10.06 | StandardOpaqueMaterial | MediumSmooth | 1.6096 | 0.1596 | 10.08521303 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R10.06 | [5 empty] | 536
Compliance Insulation R12.55 | StandardOpaqueMaterial | MediumSmooth | 2.008 | 0.1596 | 12.58145363 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R12.55 | [5 empty] | 537
Compliance Insulation R12.69 | StandardOpaqueMaterial | MediumSmooth | 2.0304 | 0.1596 | 12.72180451 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R12.69 | [5 empty] | 538
Compliance Insulation R13.99 | StandardOpaqueMaterial | MediumSmooth | 2.2384 | 0.1596 | 14.02506266 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R13.99 | [5 empty] | 539
Compliance Insulation R14.14 | StandardOpaqueMaterial | MediumSmooth | 2.2624 | 0.1596 | 14.1754386 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R14.14 | [5 empty] | 540
Compliance Insulation R14.32 | StandardOpaqueMaterial | MediumSmooth | 2.2912 | 0.1596 | 14.35588972 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R14.32 | [5 empty] | 541
Compliance Insulation R14.60 | StandardOpaqueMaterial | MediumSmooth | 2.336 | 0.1596 | 14.63659148 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R14.60 | [5 empty] | 542
Compliance Insulation R15.54 | StandardOpaqueMaterial | MediumSmooth | 2.4864 | 0.1596 | 15.57894737 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R15.54 | [5 empty] | 543
Compliance Insulation R16.58 | StandardOpaqueMaterial | MediumSmooth | 2.6528 | 0.1596 | 16.62155388 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R16.58 | [5 empty] | 544
Compliance Insulation R16.69 | StandardOpaqueMaterial | MediumSmooth | 2.6704 | 0.1596 | 16.73182957 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R16.69 | [5 empty] | 545
Compliance Insulation R17.67 | StandardOpaqueMaterial | MediumSmooth | 2.8272 | 0.1596 | 17.71428571 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R17.67 | [5 empty] | 546
Compliance Insulation R19.63 | StandardOpaqueMaterial | MediumSmooth | 3.1408 | 0.1596 | 19.67919799 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R19.63 | [5 empty] | 547
Compliance Insulation R2.15 | StandardOpaqueMaterial | MediumSmooth | 0.344 | 0.1596 | 2.155388471 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R2.15 | [5 empty] | 521
Compliance Insulation R2.19 | StandardOpaqueMaterial | MediumSmooth | 0.3504 | 0.1596 | 2.195488722 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R2.19 | [5 empty] | 522
Compliance Insulation R2.85 | StandardOpaqueMaterial | MediumSmooth | 0.456 | 0.1596 | 2.857142857 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R2.85 | [5 empty] | 523
Compliance Insulation R2.89 | StandardOpaqueMaterial | MediumSmooth | 0.4624 | 0.1596 | 2.897243108 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R2.89 | [5 empty] | 524
Compliance Insulation R20.05 | StandardOpaqueMaterial | MediumSmooth | 3.208 | 0.1596 | 20.10025063 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R20.05 | [5 empty] | 548
Compliance Insulation R21.18 | StandardOpaqueMaterial | MediumSmooth | 3.3888 | 0.1596 | 21.23308271 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R21.18 | [5 empty] | 549
Compliance Insulation R21.39 | StandardOpaqueMaterial | MediumSmooth | 3.4224 | 0.1596 | 21.44360902 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R21.39 | [5 empty] | 550
Compliance Insulation R22.48 | StandardOpaqueMaterial | MediumSmooth | 3.5968 | 0.1596 | 22.53634085 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R22.48 | [5 empty] | 551
Compliance Insulation R24.86 | StandardOpaqueMaterial | MediumSmooth | 3.9776 | 0.1596 | 24.92230576 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R24.86 | [5 empty] | 552
Compliance Insulation R25.16 | StandardOpaqueMaterial | MediumSmooth | 4.0256 | 0.1596 | 25.22305764 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R25.16 | [5 empty] | 553
Compliance Insulation R28.63 | StandardOpaqueMaterial | MediumSmooth | 4.5808 | 0.1596 | 28.70175439 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R28.63 | [5 empty] | 554
Compliance Insulation R3.63 | StandardOpaqueMaterial | MediumSmooth | 0.5808 | 0.1596 | 3.639097744 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R3.63 | [5 empty] | 525
Compliance Insulation R3.70 | StandardOpaqueMaterial | MediumSmooth | 0.592 | 0.1596 | 3.709273183 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R3.70 | [5 empty] | 526
Compliance Insulation R34.93 | StandardOpaqueMaterial | MediumSmooth | 5.5888 | 0.1596 | 35.01754386 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R34.93 | [5 empty] | 555
Compliance Insulation R6.32 | StandardOpaqueMaterial | MediumSmooth | 1.0112 | 0.1596 | 6.335839599 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R6.32 | [5 empty] | 527
Compliance Insulation R6.46 | StandardOpaqueMaterial | MediumSmooth | 1.0336 | 0.1596 | 6.476190476 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R6.46 | [5 empty] | 528
Compliance Insulation R7.10 | StandardOpaqueMaterial | MediumSmooth | 1.136 | 0.1596 | 7.117794486 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R7.10 | [5 empty] | 529
Compliance Insulation R7.18 | StandardOpaqueMaterial | MediumSmooth | 1.1488 | 0.1596 | 7.197994987 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R7.18 | [5 empty] | 530
Compliance Insulation R7.39 | StandardOpaqueMaterial | MediumSmooth | 1.1824 | 0.1596 | 7.408521303 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R7.39 | [5 empty] | 531
Compliance Insulation R8.00 | StandardOpaqueMaterial | MediumSmooth | 1.28 | 0.1596 | 8.020050125 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R8.00 | [5 empty] | 532
Compliance Insulation R8.07 | StandardOpaqueMaterial | MediumSmooth | 1.2912 | 0.1596 | 8.090225564 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R8.07 | [5 empty] | 533
Compliance Insulation R9.83 | StandardOpaqueMaterial | MediumSmooth | 1.5697 | 0.1596 | 9.835213033 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R9.83 | [5 empty] | 534
Compliance Insulation R9.94 | StandardOpaqueMaterial | MediumSmooth | 1.5904 | 0.1596 | 9.964912281 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R9.94 | [5 empty] | 535
Concrete - 100 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 6.2496 | 1.600102407 | 100 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 10 in. | [5 empty] | 359
Concrete - 100 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 6.2496 | 1.920122888 | 100 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 12 in. | [5 empty] | 360
Concrete - 100 lb/ft3 - 2 in. | StandardOpaqueMaterial | MediumRough | 2 | 6.2496 | 0.3200204813 | 100 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 2 in. | [5 empty] | 355
Concrete - 100 lb/ft3 - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 6.2496 | 0.6400409626 | 100 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 4 in. | [5 empty] | 356
Concrete - 100 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 6.2496 | 0.9600614439 | 100 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 6 in. | [5 empty] | 357
Concrete - 100 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 6.2496 | 1.280081925 | 100 | 0.21 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 8 in. | [5 empty] | 358
Concrete - 140 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 13.53 | 0.7390983001 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 10 in. | [5 empty] | 365
Concrete - 140 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 13.53 | 0.8869179601 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 12 in. | [5 empty] | 366
Concrete - 140 lb/ft3 - 2 in. | StandardOpaqueMaterial | MediumRough | 2 | 13.53 | 0.14781966 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 2 in. | [5 empty] | 361
Concrete - 140 lb/ft3 - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 13.53 | 0.29563932 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 4 in. | [5 empty] | 362
Concrete - 140 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 13.53 | 0.44345898 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 6 in. | [5 empty] | 363
Concrete - 140 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 13.53 | 0.5912786401 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 8 in. | [5 empty] | 364
Concrete - 80 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 3.6804 | 2.717095968 | 79.87 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 10 in. | [5 empty] | 353
Concrete - 80 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 3.6804 | 3.260515161 | 79.87 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 12 in. | [5 empty] | 354
Concrete - 80 lb/ft3 - 2 in. | StandardOpaqueMaterial | MediumRough | 2 | 3.6804 | 0.5434191936 | 79.87 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 2 in. | [5 empty] | 349
Concrete - 80 lb/ft3 - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 3.6804 | 1.086838387 | 79.87 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 4 in. | [5 empty] | 350
Concrete - 80 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.6804 | 1.630257581 | 79.87 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 6 in. | [5 empty] | 351
Concrete - 80 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.6804 | 2.173676774 | 79.87 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 8 in. | [5 empty] | 352
Concrete - Part Grouted and Empty - 105 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 4.5996 | 2.174102096 | 105 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 105 lb/ft3 - 10 in. | [5 empty] | 613
Concrete - Part Grouted and Empty - 105 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 5.16 | 2.325581395 | 105 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 105 lb/ft3 - 12 in. | [5 empty] | 614
Concrete - Part Grouted and Empty - 105 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.24 | 1.851851852 | 105 | 0.15 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 105 lb/ft3 - 6 in. | [5 empty] | 611
Concrete - Part Grouted and Empty - 105 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.9996 | 2.00020002 | 105 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 105 lb/ft3 - 8 in. | [5 empty] | 612
Concrete - Part Grouted and Empty - 115 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 4.8996 | 2.040982937 | 115 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 115 lb/ft3 - 10 in. | [5 empty] | 617
Concrete - Part Grouted and Empty - 115 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 5.52 | 2.173913043 | 115 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 115 lb/ft3 - 12 in. | [5 empty] | 618
Concrete - Part Grouted and Empty - 115 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.48 | 1.724137931 | 115 | 0.15 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 115 lb/ft3 - 6 in. | [5 empty] | 615
Concrete - Part Grouted and Empty - 115 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 4.2396 | 1.886970469 | 115 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 115 lb/ft3 - 8 in. | [5 empty] | 616
Concrete - Part Grouted and Empty - 125 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 5.1996 | 1.923224863 | 125 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 125 lb/ft3 - 10 in. | [5 empty] | 621
Concrete - Part Grouted and Empty - 125 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 5.88 | 2.040816327 | 125 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 125 lb/ft3 - 12 in. | [5 empty] | 622
Concrete - Part Grouted and Empty - 125 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.66 | 1.639344262 | 125 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 125 lb/ft3 - 6 in. | [5 empty] | 619
Concrete - Part Grouted and Empty - 125 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 4.4796 | 1.785873739 | 125 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 125 lb/ft3 - 8 in. | [5 empty] | 620
Concrete - Part Grouted and Insulated - 105 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 3.3996 | 2.941522532 | 105 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 10 in. | [5 empty] | 641
Concrete - Part Grouted and Insulated - 105 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 3.6 | 3.333333333 | 105 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 12 in. | [5 empty] | 642
Concrete - Part Grouted and Insulated - 105 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 2.64 | 2.272727273 | 105 | 0.15 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 6 in. | [5 empty] | 639
Concrete - Part Grouted and Insulated - 105 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 2.9604 | 2.702337522 | 105 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 8 in. | [5 empty] | 640
Concrete - Part Grouted and Insulated - 115 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 3.6996 | 2.702994918 | 115 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 10 in. | [5 empty] | 645
Concrete - Part Grouted and Insulated - 115 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 3.96 | 3.03030303 | 115 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 12 in. | [5 empty] | 646
Concrete - Part Grouted and Insulated - 115 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 2.88 | 2.083333333 | 115 | 0.15 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 6 in. | [5 empty] | 643
Concrete - Part Grouted and Insulated - 115 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.2796 | 2.439321869 | 115 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 8 in. | [5 empty] | 644
Concrete - Part Grouted and Insulated - 125 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 4.1004 | 2.43878646 | 125 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 10 in. | [5 empty] | 649
Concrete - Part Grouted and Insulated - 125 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 4.32 | 2.777777778 | 125 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 12 in. | [5 empty] | 650
Concrete - Part Grouted and Insulated - 125 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.12 | 1.923076923 | 125 | 0.14 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 6 in. | [5 empty] | 647
Concrete - Part Grouted and Insulated - 125 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.5196 | 2.272985567 | 125 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 8 in. | [5 empty] | 648
Concrete - Solid Grout - 105 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 8.4744 | 1.180024545 | 105 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 105 lb/ft3 - 10 in. | [5 empty] | 627
Concrete - Solid Grout - 105 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 8.5704 | 1.40016802 | 105 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 105 lb/ft3 - 12 in. | [5 empty] | 628
Concrete - Solid Grout - 105 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 8.3328 | 0.7200460829 | 105 | 0.21 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 105 lb/ft3 - 6 in. | [5 empty] | 625
Concrete - Solid Grout - 105 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 8.3328 | 0.9600614439 | 105 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 105 lb/ft3 - 8 in. | [5 empty] | 626
Concrete - Solid Grout - 115 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 9.174 | 1.090037061 | 115 | 0.21 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 115 lb/ft3 - 10 in. | [5 empty] | 631
Concrete - Solid Grout - 115 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 9.2304 | 1.300052002 | 115 | 0.21 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 115 lb/ft3 - 12 in. | [5 empty] | 632
Concrete - Solid Grout - 115 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 10.17 | 0.5899705015 | 115 | 0.2 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 115 lb/ft3 - 6 in. | [5 empty] | 629
Concrete - Solid Grout - 115 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 9.1224 | 0.8769622029 | 115 | 0.2 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 115 lb/ft3 - 8 in. | [5 empty] | 630
Concrete - Solid Grout - 125 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 10.1016 | 0.9899421874 | 125 | 0.2 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 125 lb/ft3 - 10 in. | [5 empty] | 635
Concrete - Solid Grout - 125 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 10.0836 | 1.190051172 | 125 | 0.2 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 125 lb/ft3 - 12 in. | [5 empty] | 636
Concrete - Solid Grout - 125 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 10.17 | 0.5899705015 | 125 | 0.19 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 125 lb/ft3 - 6 in. | [5 empty] | 633
Concrete - Solid Grout - 125 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 10.1268 | 0.7899830154 | 125 | 0.2 | [19 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 125 lb/ft3 - 8 in. | [5 empty] | 634
Concrete Paver | StandardOpaqueMaterial | MediumRough | 0.38 | 4.5024 | 0.08439943141 | 144 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Bruce | Masonry Materials | Concrete Paver | [5 empty] | 600
Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 1.8396 | 7.338551859 | 133.44 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | [5 empty] | 387
Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 1.4496 | 9.657836645 | 128.71 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 2 in. | [5 empty] | 388
Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 1.05 | 14.28571429 | 120.2 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 3 in. | [5 empty] | 389
Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 0.8496 | 18.83239171 | 112.75 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 4 in. | [5 empty] | 390
Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 0.63 | 28.57142857 | 100.33 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 6 in. | [5 empty] | 391
Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 2.5704 | 5.25210084 | 133.44 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | [5 empty] | 392
Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 2.01 | 6.965174129 | 128.71 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 2 in. | [5 empty] | 393
Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 1.4796 | 10.1378751 | 120.2 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 3 in. | [5 empty] | 394
Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 1.1904 | 13.44086022 | 112.75 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 4 in. | [5 empty] | 395
Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 0.9 | 20 | 100.33 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 6 in. | [5 empty] | 396
Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 15.8604 | 0.8511765151 | 133.44 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | [5 empty] | 367
Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 14.7504 | 0.9491268033 | 128.71 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 2 in. | [5 empty] | 368
Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 11.9904 | 1.251000801 | 120.2 | 0.12 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 3 in. | [5 empty] | 369
Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 10.3404 | 1.547328923 | 112.75 | 0.12 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 4 in. | [5 empty] | 370
Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 8.3604 | 2.153007033 | 100.33 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 6 in. | [5 empty] | 371
Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 15.8604 | 0.8511765151 | 133.44 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | [5 empty] | 372
Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 25.1796 | 0.5560056554 | 128.71 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 2 in. | [5 empty] | 373
Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 31.5096 | 0.4760453957 | 120.2 | 0.12 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 3 in. | [5 empty] | 374
Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 38.37 | 0.416992442 | 112.75 | 0.12 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 4 in. | [5 empty] | 375
Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 54.0504 | 0.3330225123 | 100.33 | 0.13 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 6 in. | [5 empty] | 376
Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 10.7904 | 1.2511121 | 133.44 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | [5 empty] | 377
Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 9.66 | 1.449275362 | 128.71 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 2 in. | [5 empty] | 378
Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 7.32 | 2.049180328 | 120.2 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 3 in. | [5 empty] | 379
Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 6.0396 | 2.649182065 | 112.75 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 4 in. | [5 empty] | 380
Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 4.7904 | 3.75751503 | 100.33 | 0.12 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 6 in. | [5 empty] | 381
Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 11.7396 | 1.149954002 | 133.44 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | [5 empty] | 382
Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 9.66 | 1.449275362 | 128.71 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 2 in. | [5 empty] | 383
Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 7.6896 | 1.950686642 | 120.2 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 3 in. | [5 empty] | 384
Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 6.5304 | 2.450079628 | 112.75 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 4 in. | [5 empty] | 385
Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 5.0604 | 3.557031065 | 100.33 | 0.12 | [19 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 6 in. | [5 empty] | 386
Concrete/Sand Aggregate - 6 in. | StandardOpaqueMaterial | Smooth | 6.01 | 4.29 | 1.400932401 | 116 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Concrete/Sand Aggregate - 6 in. | [5 empty] | 663
Continuous Ins. - Double glass with no low e coatings - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.9 | 2.522222222 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - No Ins. | [5 empty] | 843
Continuous Ins. - Double glass with no low e coatings - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.26196 | 12.4828218 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R10 Ins. | [5 empty] | 846
Continuous Ins. - Double glass with no low e coatings - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.25296 | 17.67077799 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R15 Ins. | [5 empty] | 847
Continuous Ins. - Double glass with no low e coatings - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.25308 | 22.40398293 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R20 Ins. | [5 empty] | 848
Continuous Ins. - Double glass with no low e coatings - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 0.2478 | 27.72397094 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R25 Ins. | [5 empty] | 849
Continuous Ins. - Double glass with no low e coatings - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 0.2484 | 32.48792271 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R30 Ins. | [5 empty] | 850
Continuous Ins. - Double glass with no low e coatings - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.2814 | 6.503198294 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R4 Ins. | [5 empty] | 844
Continuous Ins. - Double glass with no low e coatings - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.27 | 9.444444444 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R7 Ins. | [5 empty] | 845
Continuous Ins. - Single glass pane. stone. or metal pane - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 1.1796 | 1.924381146 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - No Ins. | [5 empty] | 835
Continuous Ins. - Single glass pane. stone. or metal pane - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.27312 | 11.97275923 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R10 Ins. | [5 empty] | 838
Continuous Ins. - Single glass pane. stone. or metal pane - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.2628 | 17.00913242 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R15 Ins. | [5 empty] | 839
Continuous Ins. - Single glass pane. stone. or metal pane - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.2592 | 21.875 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R20 Ins. | [5 empty] | 840
Continuous Ins. - Single glass pane. stone. or metal pane - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 0.25512 | 26.92850423 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R25 Ins. | [5 empty] | 841
Continuous Ins. - Single glass pane. stone. or metal pane - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 0.25692 | 31.41055582 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R30 Ins. | [5 empty] | 842
Continuous Ins. - Single glass pane. stone. or metal pane - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.3096 | 5.910852713 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R4 Ins. | [5 empty] | 836
Continuous Ins. - Single glass pane. stone. or metal pane - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.28476 | 8.954909397 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R7 Ins. | [5 empty] | 837
Continuous Ins. - Triple or low e glass - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.78 | 2.91025641 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - No Ins. | [5 empty] | 851
Continuous Ins. - Triple or low e glass - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.25452 | 12.84771334 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R10 Ins. | [5 empty] | 854
Continuous Ins. - Triple or low e glass - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.24804 | 18.02128689 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R15 Ins. | [5 empty] | 855
Continuous Ins. - Triple or low e glass - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.24696 | 22.95918367 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R20 Ins. | [5 empty] | 856
Continuous Ins. - Triple or low e glass - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 0.2478 | 27.72397094 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R25 Ins. | [5 empty] | 857
Continuous Ins. - Triple or low e glass - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 0.2484 | 32.48792271 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R30 Ins. | [5 empty] | 858
Continuous Ins. - Triple or low e glass - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.2652 | 6.900452489 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R4 Ins. | [5 empty] | 852
Continuous Ins. - Triple or low e glass - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.25752 | 9.902143523 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R7 Ins. | [5 empty] | 853
CP02 CARPET PAD | MasslessOpaqueMaterial | VeryRough |  |  | 1.2292 |  |  | 0.9 | 0.7 | 0.8
Douglas Fir-Larch - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 0.9804 | 1.01999184 | 34.88 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Douglas Fir-Larch - 1 in. | [5 empty] | 887
ECABS-2 BLEACHED 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.814 | 0.086 | 0.086 | 0.847 | 0.099 | 0.099 | 0 | 0.84 | 0.1 | 1 | FALSE | [9 empty] | 1317
ECABS-2 COLORED 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.111 | 0.179 | 0.179 | 0.128 | 0.081 | 0.081 | 0 | 0.84 | 0.1 | 1 | FALSE | [9 empty] | 1318
ECREF-1 COLORED 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.099 | 0.219 | 0.219 | 0.155 | 0.073 | 0.073 | 0 | 0.84 | 0.84 | 1 | FALSE | [9 empty] | 1319
ECREF-2 BLEACHED 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.694 | 0.168 | 0.168 | 0.818 | 0.11 | 0.11 | 0 | 0.84 | 0.1 | 1 | FALSE | [9 empty] | 1320
ECREF-2 COLORED 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.099 | 0.219 | 0.219 | 0.155 | 0.073 | 0.073 | 0 | 0.84 | 0.1 | 1 | FALSE | [9 empty] | 1321
Expanded perlite - organic bonded - 1 1/2 in. R4.2 | StandardOpaqueMaterial | MediumSmooth | 1.5 | 0.36 | 4.166666667 | 1 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 1 1/2 in. R4.2 | [5 empty] | 457
Expanded perlite - organic bonded - 1 in. R2.8 | StandardOpaqueMaterial | MediumSmooth | 1 | 0.36 | 2.777777778 | 1 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 1 in. R2.8 | [5 empty] | 456
Expanded perlite - organic bonded - 2 in. R5.6 | StandardOpaqueMaterial | MediumSmooth | 2 | 0.36 | 5.555555556 | 1 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 2 in. R5.6 | [5 empty] | 458
Expanded perlite - organic bonded - 3 in. R8.3 | StandardOpaqueMaterial | MediumSmooth | 3 | 0.36 | 8.333333333 | 1 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 3 in. R8.3 | [5 empty] | 459
Expanded perlite - organic bonded - 3/4 in. R2.1 | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.36 | 2.083333333 | 1 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 3/4 in. R2.1 | [5 empty] | 455
Expanded perlite - organic bonded - 4 in. R11 | StandardOpaqueMaterial | MediumSmooth | 4 | 0.36 | 11.11111111 | 1 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 4 in. R11 | [5 empty] | 460
Expanded perlite - organic bonded - 6 in. R17 | StandardOpaqueMaterial | MediumSmooth | 6 | 0.36 | 16.66666667 | 1 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 6 in. R17 | [5 empty] | 461
Expanded Polystyrene - EPS - 1 1/2 in. R6.3 | StandardOpaqueMaterial | MediumSmooth | 1.5 | 0.24 | 6.25 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 1 1/2 in. R6.3 | [5 empty] | 467
Expanded Polystyrene - EPS - 1 1/4 in. R5.2 | StandardOpaqueMaterial | MediumSmooth | 1.25 | 0.24 | 5.208333333 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polystyrene - EPS - 1 1/4 in. R5.2 | [5 empty] | 466
Expanded Polystyrene - EPS - 1 15/16 in. R8.1 | StandardOpaqueMaterial | MediumSmooth | 1.94 | 0.24 | 8.083333333 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 1 15/16 in. R8.1 | [5 empty] | 470
Expanded Polystyrene - EPS - 1 3/4 in. R7.3 | StandardOpaqueMaterial | MediumSmooth | 1.75 | 0.24 | 7.291666667 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 1 3/4 in. R7.3 | [5 empty] | 468
Expanded Polystyrene - EPS - 1 7/8 in. R8.0 | StandardOpaqueMaterial | MediumSmooth | 1.92 | 0.24 | 8 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 1 7/8 in. R8.0 | [5 empty] | 469
Expanded Polystyrene - EPS - 1 in. R4.2 | StandardOpaqueMaterial | MediumSmooth | 1 | 0.24 | 4.166666667 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polystyrene - EPS - 1 in. R4.2 | [5 empty] | 465
Expanded Polystyrene - EPS - 1/2 in. R2.1 | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.24 | 2.083333333 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polystyrene - EPS - 1/2 in. R2.1 | [5 empty] | 463
Expanded Polystyrene - EPS - 1/4 in. R1.0 | StandardOpaqueMaterial | MediumSmooth | 0.25 | 0.24 | 1.041666667 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 1/4 in. R1.0 | [5 empty] | 462
Expanded Polystyrene - EPS - 2 2/5 in. R10 | StandardOpaqueMaterial | MediumSmooth | 2.4 | 0.24 | 10 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 2 2/5 in. R10 | [5 empty] | 472
Expanded Polystyrene - EPS - 2 7/16 in. R10 | StandardOpaqueMaterial | MediumSmooth | 2.43 | 0.24 | 10.125 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 2 7/16 in. R10 | [5 empty] | 473
Expanded Polystyrene - EPS - 2 in. R8.3 | StandardOpaqueMaterial | MediumSmooth | 2 | 0.24 | 8.333333333 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polystyrene - EPS - 2 in. R8.3 | [5 empty] | 471
Expanded Polystyrene - EPS - 3 1/2 in. R15 | StandardOpaqueMaterial | MediumSmooth | 3.5 | 0.24 | 14.58333333 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 3 1/2 in. R15 | [5 empty] | 477
Expanded Polystyrene - EPS - 3 1/3 in. R14 | StandardOpaqueMaterial | MediumSmooth | 3.35 | 0.24 | 13.95833333 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 3 1/3 in. R14 | [5 empty] | 475
Expanded Polystyrene - EPS - 3 2/5 in. R14 | StandardOpaqueMaterial | MediumSmooth | 3.39 | 0.24 | 14.125 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 3 2/5 in. R14 | [5 empty] | 476
Expanded Polystyrene - EPS - 3 in. R13 | StandardOpaqueMaterial | MediumSmooth | 3.01 | 0.24 | 12.54166667 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 3 in. R13 | [5 empty] | 474
Expanded Polystyrene - EPS - 3/4 in. R3.1 | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.24 | 3.125 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 3/4 in. R3.1 | [5 empty] | 464
Expanded Polystyrene - EPS - 4 1/16 in. R17 | StandardOpaqueMaterial | MediumSmooth | 4.05 | 0.24 | 16.875 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 4 1/16 in. R17 | [5 empty] | 478
Expanded Polystyrene - EPS - 4 7/10 in. R20 | StandardOpaqueMaterial | MediumSmooth | 4.71 | 0.24 | 19.625 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 4 7/10 in. R20 | [5 empty] | 479
Expanded Polystyrene - EPS - 5 19/20 in. R25 | StandardOpaqueMaterial | MediumSmooth | 5.96 | 0.24 | 24.83333333 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 5 19/20 in. R25 | [5 empty] | 481
Expanded Polystyrene - EPS - 5 2/5 in. R22 | StandardOpaqueMaterial | MediumSmooth | 5.2 | 0.24 | 21.66666667 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 5 2/5 in. R22 | [5 empty] | 480
Expanded Polystyrene - EPS - 6 1/10 in. R25 | StandardOpaqueMaterial | MediumSmooth | 6.11 | 0.24 | 25.45833333 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 6 1/10 in. R25 | [5 empty] | 482
Expanded Polystyrene - EPS - 6 7/8 in. R29 | StandardOpaqueMaterial | MediumSmooth | 6.87 | 0.24 | 28.625 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 6 7/8 in. R29 | [5 empty] | 483
Expanded Polystyrene - EPS - 8 3/5 in. R35 | StandardOpaqueMaterial | MediumSmooth | 8.38 | 0.24 | 34.91666667 | 1.2 | 0.27 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 8 3/5 in. R35 | [5 empty] | 484
Expanded Polyurethane - 1 1/4 in. R7.8 | StandardOpaqueMaterial | MediumSmooth | 1.25 | 0.1596 | 7.832080201 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polyurethane - 1 1/4 in. R7.8 | [5 empty] | 508
Expanded Polyurethane - 1 in. R6.3 | StandardOpaqueMaterial | MediumSmooth | 1 | 0.1596 | 6.26566416 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polyurethane - 1 in. R6.3 | [5 empty] | 507
Expanded Polyurethane - 1/2 in. R3.1 | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.1596 | 3.13283208 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polyurethane - 1/2 in. R3.1 | [5 empty] | 505
Expanded Polyurethane - 2 in. R12.6 | StandardOpaqueMaterial | MediumSmooth | 2 | 0.1596 | 12.53132832 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polyurethane - 2 in. R12.6 | [5 empty] | 509
Expanded Polyurethane - 3/4 in. R4.7 | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.1596 | 4.69924812 | 1 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polyurethane - 3/4 in. R4.7 | [5 empty] | 506
Extruded Polystyrene - XPS - 1 1/2 in. R7.50 | StandardOpaqueMaterial | MediumSmooth | 1.5 | 0.2 | 7.49999985 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1 1/2 in. R7.50 | [5 empty] | 490
Extruded Polystyrene - XPS - 1 1/4 in. R6.25 | StandardOpaqueMaterial | MediumSmooth | 1.25 | 0.2 | 6.249999875 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1 1/4 in. R6.25 | [5 empty] | 489
Extruded Polystyrene - XPS - 1 3/4 in. R8.75 | StandardOpaqueMaterial | MediumSmooth | 1.75 | 0.2 | 8.749999825 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1 3/4 in. R8.75 | [5 empty] | 491
Extruded Polystyrene - XPS - 1 7/8 in. R9.37 | StandardOpaqueMaterial | MediumSmooth | 1.88 | 0.2 | 9.399999812 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1 7/8 in. R9.37 | [5 empty] | 492
Extruded Polystyrene - XPS - 1 in. R5.00 | StandardOpaqueMaterial | MediumSmooth | 1 | 0.2 | 4.9999999 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1 in. R5.00 | [5 empty] | 488
Extruded Polystyrene - XPS - 1/2 in. R2.50 | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.2 | 2.49999995 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1/2 in. R2.50 | [5 empty] | 486
Extruded Polystyrene - XPS - 1/4 in. R1.25 | StandardOpaqueMaterial | MediumSmooth | 0.25 | 0.2 | 1.249999975 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1/4 in. R1.25 | [5 empty] | 485
Extruded Polystyrene - XPS - 2 1/2 in. R12.50 | StandardOpaqueMaterial | MediumSmooth | 2.5 | 0.2 | 12.49999975 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 2 1/2 in. R12.50 | [5 empty] | 494
Extruded Polystyrene - XPS - 2 in. R10.00 | StandardOpaqueMaterial | MediumSmooth | 2 | 0.2 | 9.9999998 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 2 in. R10.00 | [5 empty] | 493
Extruded Polystyrene - XPS - 3 1/2 in. R17.50 | StandardOpaqueMaterial | MediumSmooth | 3.5 | 0.2 | 17.49999965 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 3 1/2 in. R17.50 | [5 empty] | 496
Extruded Polystyrene - XPS - 3 in. R15.00 | StandardOpaqueMaterial | MediumSmooth | 3 | 0.2 | 14.9999997 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 3 in. R15.00 | [5 empty] | 495
Extruded Polystyrene - XPS - 3/4 in. R3.75 | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.2 | 3.749999925 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 3/4 in. R3.75 | [5 empty] | 487
Extruded Polystyrene - XPS - 4 1/2 in. R22.50 | StandardOpaqueMaterial | MediumSmooth | 4.5 | 0.2 | 22.49999955 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 4 1/2 in. R22.50 | [5 empty] | 498
Extruded Polystyrene - XPS - 4 in. R20.00 | StandardOpaqueMaterial | MediumSmooth | 4 | 0.2 | 19.9999996 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 4 in. R20.00 | [5 empty] | 497
Extruded Polystyrene - XPS - 5 1/2 in. R27.50 | StandardOpaqueMaterial | MediumSmooth | 5.5 | 0.2 | 27.49999945 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 5 1/2 in. R27.50 | [5 empty] | 500
Extruded Polystyrene - XPS - 5 in. R25.00 | StandardOpaqueMaterial | MediumSmooth | 5 | 0.2 | 24.9999995 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 5 in. R25.00 | [5 empty] | 499
Extruded Polystyrene - XPS - 6 1/2 in. R32.50 | StandardOpaqueMaterial | MediumSmooth | 6.5 | 0.2 | 32.49999935 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 6 1/2 in. R32.50 | [5 empty] | 502
Extruded Polystyrene - XPS - 6 in. R30.00 | StandardOpaqueMaterial | MediumSmooth | 6 | 0.2 | 29.9999994 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 6 in. R30.00 | [5 empty] | 501
Extruded Polystyrene - XPS - 8 1/2 in. R42.50 | StandardOpaqueMaterial | MediumSmooth | 8.5 | 0.2 | 42.49999915 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 8 1/2 in. R42.50 | [5 empty] | 504
Extruded Polystyrene - XPS - 8 in. R40.00 | StandardOpaqueMaterial | MediumSmooth | 8 | 0.2 | 39.9999992 | 1.3 | 0.35 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 8 in. R40.00 | [5 empty] | 503
F04 Wall air space resistance | AirGap |  |  | 46.2231 | 0.021634 | [30 empty] | 34
F05 Ceiling air space resistance | AirGap |  |  | 38.5193 | 0.025961 | [30 empty] | 35
F08 Metal surface | StandardOpaqueMaterial | Smooth | 0.031496 | 313.9476 | 0.0001003226739 | 488.4364 | 0.11942 | 0.9 | 0.7 | 0.7 | [25 empty] | 36
F16 Acoustic tile | StandardOpaqueMaterial | MediumSmooth | 0.75197 | 0.41601 | 1.807580497 | 22.9735 | 0.14092 | 0.9 | 0.3 | 0.3 | [25 empty] | 37
Fiber cement board - 63 lb/ft3 - 1/3 in. | StandardOpaqueMaterial | Smooth | 0.31 | 1.2996 | 0.2385349338 | 63 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Fiber cement board - 63 lb/ft3 - 1/3 in. | [5 empty] | 308
Fiber cement board - 88 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.47 | 1.7004 | 0.2764055516 | 88 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Fiber cement board - 88 lb/ft3 - 1/2 in. | [5 empty] | 310
Fiber cement board - 88 lb/ft3 - 1/3 in. | StandardOpaqueMaterial | Smooth | 0.31 | 1.7004 | 0.1823100447 | 88 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Fiber cement board - 88 lb/ft3 - 1/3 in. | [5 empty] | 309
Fiberboard sheathing - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.4896 | 1.02124183 | 24.96 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Fiberboard sheathing - 1/2 in. | [5 empty] | 311
Fixed Window 2.00/0.40/0.31 | SimpleGlazing | [10 empty] | 0.35 | 0.4 | 0.31 | [21 empty] | 38
Fixed Window 2.00/0.45/0.35 | SimpleGlazing | [10 empty] | 0.35 | 0.45 | 0.35 | [21 empty] | 39
Fixed Window 2.30/0.40/0.31 | SimpleGlazing | [10 empty] | 0.4 | 0.4 | 0.31 | [21 empty] | 40
Fixed Window 2.56/0.45/0.35 | SimpleGlazing | [10 empty] | 0.45 | 0.45 | 0.35 | [21 empty] | 41
Fixed Window 2.62/0.30/0.21 | SimpleGlazing | [10 empty] | 0.45998 | 0.3 | 0.21 | [21 empty] | 42
Fixed Window 2.67/0.30/0.21 | SimpleGlazing | [10 empty] | 0.46998 | 0.49 | 0.38 | [21 empty] | 43
Fixed Window 2.96/0.39/0.31 | SimpleGlazing | [10 empty] | 0.51998 | 0.39 | 0.31 | [21 empty] | 44
Fixed Window 2.96/0.49/0.41 | SimpleGlazing | [10 empty] | 0.51998 | 0.49 | 0.41 | [21 empty] | 45
Fixed Window 2.96/0.62/0.54 | SimpleGlazing | [10 empty] | 0.51998 | 0.62 | 0.54 | [21 empty] | 46
Fixed Window 3.12/0.40/0.31 | SimpleGlazing | [10 empty] | 0.55 | 0.4 | 0.31 | [21 empty] | 47
Fixed Window 3.24/0.25/0.16 | SimpleGlazing | [10 empty] | 0.56997 | 0.25 | 0.16 | [21 empty] | 48
Fixed Window 3.24/0.39/0.31 | SimpleGlazing | [10 empty] | 0.56997 | 0.39 | 0.31 | [21 empty] | 49
Fixed Window 3.24/0.49/0.41 | SimpleGlazing | [10 empty] | 0.56997 | 0.49 | 0.41 | [21 empty] | 50
Fixed Window 3.35/0.36/0.27 | SimpleGlazing | [10 empty] | 0.58997 | 0.36 | 0.27 | [21 empty] | 51
Fixed Window 3.35/0.39/0.31 | SimpleGlazing | [10 empty] | 0.58997 | 0.39 | 0.31 | [21 empty] | 52
Fixed Window 3.53/0.41/0.32 | SimpleGlazing | [10 empty] | 0.61997 | 0.41 | 0.32 | [21 empty] | 53
Fixed Window 3.69/0.25/0.16 | SimpleGlazing | [10 empty] | 0.65 | 0.25 | 0.16 | [21 empty] | 54
Fixed Window 3.69/0.70/0.60 | SimpleGlazing | [10 empty] | 0.65 | 0.7 | 0.6 | [21 empty] | 55
Fixed Window 3.81/0.39/0.27 | SimpleGlazing | [10 empty] | 0.51998 | 0.39 | 0.27 | [21 empty] | 56
Fixed Window 3.81/0.49/0.38 | SimpleGlazing | [10 empty] | 0.51998 | 0.49 | 0.38 | [21 empty] | 57
Fixed Window 4.09/0.26/0.13 | SimpleGlazing | [10 empty] | 0.71997 | 0.25 | 0.13 | [21 empty] | 58
Fixed Window 4.09/0.36/0.23 | SimpleGlazing | [10 empty] | 0.71997 | 0.36 | 0.23 | [21 empty] | 59
Fixed Window 4.09/0.39/0.25 | SimpleGlazing | [10 empty] | 0.71997 | 0.39 | 0.25 | [21 empty] | 60
Fixed Window 4.26/0.25/0.16 | SimpleGlazing | [10 empty] | 0.75 | 0.25 | 0.16 | [21 empty] | 61
Fixed Window 5.84/0.25/0.11 | SimpleGlazing | [10 empty] | 1.0285 | 0.25 | 0.11 | [21 empty] | 62
Fixed Window 5.84/0.39/0.22 | SimpleGlazing | [10 empty] | 1.0285 | 0.39 | 0.22 | [21 empty] | 63
Fixed Window 5.84/0.44/0.27 | SimpleGlazing | [10 empty] | 1.0285 | 0.44 | 0.27 | [21 empty] | 64
Fixed Window 5.84/0.54/0.38 | SimpleGlazing | [10 empty] | 1.0285 | 0.54 | 0.38 | [21 empty] | 65
Fixed Window 5.84/0.61/0.47 | SimpleGlazing | [10 empty] | 1.0285 | 0.61 | 0.47 | [21 empty] | 66
Fixed Window 5.84/0.70/0.60 | SimpleGlazing | [10 empty] | 1.0285 | 0.7 | 0.6 | [21 empty] | 67
G01 13mm gypsum board | StandardOpaqueMaterial | Smooth | 0.5 | 1.1096 | 4.51E-01 | 49.9424 | 0.26052 | 0.9 | 0.7 | 0.5
G01a 19mm gypsum board | StandardOpaqueMaterial | MediumSmooth | 0.74803 | 1.1094 | 0.6742937718 | 49.9424 | 0.26034 | 0.9 | 0.4 | 0.4 | [25 empty] | 68
G05 25mm wood | StandardOpaqueMaterial | MediumSmooth | 1 | 1.04 | 0.9615192591 | 37.9562 | 0.38932 | 0.9 | 0.5 | 0.5 | [25 empty] | 69
Gap_1_W_0_0018 | Gas |  | 0.070866 | [7 empty] | Air | [24 empty] | 1354
Gap_1_W_0_0024 | Gas |  | 0.094488 | [7 empty] | Air | [24 empty] | 1355
Gap_1_W_0_0025 | Gas |  | 0.098425 | [7 empty] | Air | [24 empty] | 1356
Gap_1_W_0_0032 | Gas |  | 0.12598 | [7 empty] | Air | [24 empty] | 1357
Gap_1_W_0_0038 | Gas |  | 0.14961 | [7 empty] | Air | [24 empty] | 1358
Gap_1_W_0_0042 | Gas |  | 0.16535 | [7 empty] | Air | [24 empty] | 1359
Gap_1_W_0_0043 | Gas |  | 0.16929 | [7 empty] | Air | [24 empty] | 1360
Glass fiber batt - 10 in. R30 (CEC Default) | StandardOpaqueMaterial | MediumRough | 10 | 0.3336 | 29.97601918 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 10 in. R30 (CEC Default) | [5 empty] | 433
Glass fiber batt - 12 in. R38 (CEC Default) | StandardOpaqueMaterial | MediumRough | 12 | 0.3156 | 38.02281369 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 12 in. R38 (CEC Default) | [5 empty] | 434
Glass fiber batt - 3 1/2 in. R11 (CEC Default) | StandardOpaqueMaterial | MediumRough | 3.5 | 0.318 | 11.00628931 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 3 1/2 in. R11 (CEC Default) | [5 empty] | 425
Glass fiber batt - 3 1/2 in. R13 (CEC Default) | StandardOpaqueMaterial | MediumRough | 3.5 | 0.2688 | 13.02083333 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 3 1/2 in. R13 (CEC Default) | [5 empty] | 426
Glass fiber batt - 3 1/2 in. R15 (CEC Default) | StandardOpaqueMaterial | MediumRough | 3.5 | 0.2328 | 15.03436426 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 3 1/2 in. R15 (CEC Default) | [5 empty] | 427
Glass fiber batt - 4 1/2 in. | StandardOpaqueMaterial | MediumRough | 4.5 | 0.3 | 15 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Batt | Glass fiber batt - 4 1/2 in. | [5 empty] | 436
Glass fiber batt - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 0.3 | 13.33333333 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Batt | Glass fiber batt - 4 in. | [5 empty] | 435
Glass fiber batt - 5 1/2 in. R19 (CEC Default) | StandardOpaqueMaterial | MediumRough | 5.5 | 0.306 | 17.97385621 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 5 1/2 in. R19 (CEC Default) | [5 empty] | 428
Glass fiber batt - 5 1/2 in. R21 (CEC Default) | StandardOpaqueMaterial | MediumRough | 5.5 | 0.2616 | 21.02446483 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 5 1/2 in. R21 (CEC Default) | [5 empty] | 429
Glass fiber batt - 5 in. | StandardOpaqueMaterial | MediumRough | 5 | 0.3 | 16.66666667 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Batt | Glass fiber batt - 5 in. | [5 empty] | 437
Glass fiber batt - 6 1/2 in. | StandardOpaqueMaterial | MediumRough | 6.5 | 0.3 | 21.66666667 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Batt | Glass fiber batt - 6 1/2 in. | [5 empty] | 439
Glass fiber batt - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 0.3 | 20 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Batt | Glass fiber batt - 6 in. | [5 empty] | 438
Glass fiber batt - 7 1/4 in. R25 (CEC Default) | StandardOpaqueMaterial | MediumRough | 7.25 | 0.3024 | 23.97486772 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 7 1/4 in. R25 (CEC Default) | [5 empty] | 430
Glass fiber batt - 7 1/4 in. R30 (CEC Default) | StandardOpaqueMaterial | MediumRough | 7.25 | 0.2904 | 24.96556474 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 7 1/4 in. R30 (CEC Default) | [5 empty] | 431
Glass fiber batt - 8 1/4 in. R30C (CEC Default) | StandardOpaqueMaterial | MediumRough | 8.25 | 0.2748 | 30.02183406 | 0.7 | 0.2 | [19 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 8 1/4 in. R30C (CEC Default) | [5 empty] | 432
Glass_2010F_LayerAvg | StandardGlazing |  | 0.087008 | 6.9335 | 0.14423 | [9 empty] | SpectralAverage | 0.43429 | 0.41837 | 0.34107 | 0.79758 | 0.043577 | 0.056031 | 0 | 0.042274 | 0.84 | 1 | FALSE | [9 empty] | 1322
Glass_2022F_LayerAvg | StandardGlazing |  | 0.15354 | 6.9335 | 0.14423 | [9 empty] | SpectralAverage | 0.3559 | 0.39409 | 0.26565 | 0.67769 | 0.042734 | 0.05547 | 0 | 0.046 | 0.84 | 1 | FALSE | [9 empty] | 1323
Glass_2027F_LayerAvg | StandardGlazing |  | 0.15748 | 6.9335 | 0.14423 | [9 empty] | SpectralAverage | 0.36974 | 0.47007 | 0.34093 | 0.76522 | 0.0546 | 0.073741 | 0 | 0.03675 | 0.84 | 1 | FALSE | [9 empty] | 1324
Glass_2052_LayerAvg | StandardGlazing |  | 0.32953 | 6.9335 | 0.14423 | [9 empty] | SpectralAverage | 0.50777 | 0.054228 | 0.054493 | 0.58683 | 0.05805 | 0.058397 | 0 | 0.84 | 0.84 | 1 | FALSE | [9 empty] | 1325
Glass_2175_LayerAvg | StandardGlazing |  | 0.33858 | 6.9335 | 0.14423 | [9 empty] | SpectralAverage | 0.16776 | 0.21761 | 0.43798 | 0.41604 | 0.078729 | 0.10654 | 0 | 0.84 | 0.84 | 1 | FALSE | [9 empty] | 1326
GREEN 3MM | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.635 | 0.063 | 0.063 | 0.822 | 0.075 | 0.075 | 0 | 0.84 | 0.84 | 1 | FALSE | [9 empty] | 1327
GREEN 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.487 | 0.056 | 0.056 | 0.749 | 0.07 | 0.07 | 0 | 0.84 | 0.84 | 1 | FALSE | [9 empty] | 1328
GREY 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.455 | 0.053 | 0.053 | 0.431 | 0.052 | 0.052 | 0 | 0.84 | 0.84 | 1 | FALSE | [9 empty] | 1329
Gypsum Board - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 1.1 | 0.4545289262 | 40 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Gypsum Board - 1/2 in. | [5 empty] | 313
Gypsum Board - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 1.1 | 0.6817933893 | 40 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Gypsum Board - 3/4 in. | [5 empty] | 315
Gypsum Board - 3/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.38 | 1.1 | 0.3454419839 | 40 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Gypsum Board - 3/8 in. | [5 empty] | 312
Gypsum Board - 5/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.63 | 1.1 | 0.572706447 | 40 | 0.27 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Gypsum Board - 5/8 in. | [5 empty] | 314
Gypsum Or Plaster Board - 3/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.37402 | 4.0214 | 0.09300603748 | 49.9424 | 0.26034 | 0.9 | 0.7 | 0.7 | [25 empty] | 1206
Gypsum partition block - 3 cells - 4 in. x 12 in. x 30 in. - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 2.4 | 1.666666667 | 53.1 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Gypsum partition block - 3 cells - 4 in. x 12 in. x 30 in. - 4 in. | [5 empty] | 603
Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. | StandardOpaqueMaterial | MediumRough | 3 | 2.22 | 1.351351351 | 53.1 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. | [5 empty] | 602
Gypsum partition block - solid - 3 in. x 12 in. x 30 in. - 3 in. | StandardOpaqueMaterial | MediumRough | 3 | 2.3796 | 1.260716087 | 62.4 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Gypsum partition block - solid - 3 in. x 12 in. x 30 in. - 3 in. | [5 empty] | 601
Gypsum plaster - 80 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 3.2004 | 0.1562304712 | 80 | 0.26 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Gypsum plaster - 80 lb/ft3 - 1/2 in. | [5 empty] | 664
Gypsum plaster - 80 lb/ft3 - 5/8 in. | StandardOpaqueMaterial | Smooth | 0.63 | 3.2004 | 0.1968503937 | 80 | 0.26 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Gypsum plaster - 80 lb/ft3 - 5/8 in. | [5 empty] | 665
Gypsum plaster - on metal lath 70 lb/ft3 - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 2.6004 | 0.2884171666 | 70 | 0.26 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Gypsum plaster - on metal lath 70 lb/ft3 - 3/4 in. | [5 empty] | 666
Gypsum plaster - on metal lath 80 lb/ft3 - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 3.2004 | 0.2343457068 | 80 | 0.26 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Gypsum plaster - on metal lath 80 lb/ft3 - 3/4 in. | [5 empty] | 667
Hard Board - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 0.72 | 1.041666667 | 50 | 0.31 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Hard Board - 3/4 in. | [5 empty] | 316
Hardboard - HDF - 50 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.7296 | 0.6853070175 | 50 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Hardboard - HDF - 50 lb/ft3 - 1/2 in. | [5 empty] | 318
Hardboard - HDF - 50 lb/ft3 - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 0.7296 | 1.027960526 | 50 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Hardboard - HDF - 50 lb/ft3 - 3/4 in. | [5 empty] | 320
Hardboard - HDF - 50 lb/ft3 - 3/8 in. | StandardOpaqueMaterial | Smooth | 0.38 | 0.7296 | 0.5208333333 | 50 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Hardboard - HDF - 50 lb/ft3 - 3/8 in. | [5 empty] | 317
Hardboard - HDF - 50 lb/ft3 - 5/8 in. | StandardOpaqueMaterial | Smooth | 0.63 | 0.7296 | 0.8634868421 | 50 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Hardboard - HDF - 50 lb/ft3 - 5/8 in. | [5 empty] | 319
Hardwood - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.1604 | 0.8617718028 | 42.43 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Hardwood - 1 in. | [5 empty] | 888
Hardwood - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 1.1604 | 0.4308859014 | 42.43 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Hardwood - 1/2 in. | [5 empty] | 889
Hardwood - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 1.1604 | 0.6463288521 | 42.43 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Hardwood - 3/4 in. | [5 empty] | 890
HB Part. Brd - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 1.18 | 0.6356147666 | 50 | 0.31 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | HB Part. Brd - 3/4 in. | [5 empty] | 321
HW CONCRETE | StandardOpaqueMaterial | Rough | 4 | 9.0915 | 0.4399694889 | 139.8387 | 0.2 | 0.9 | 0.7 | 0.7
HW CONCRETE 8 in | StandardOpaqueMaterial | Rough | 8 | 9.0915 | 0.8799389777 | 139.8387 | 0.2 | 0.9 | 0.7 | 0.7
I01 25mm insulation board | StandardOpaqueMaterial | MediumRough | 1 | 0.208 | 4.807596295 | 2.6844 | 0.289 | 0.9 | 0.6 | 0.6 | [25 empty] | 70
I02 50mm insulation board | StandardOpaqueMaterial | MediumRough | 2 | 0.208 | 9.615192591 | 2.6844 | 0.289 | 0.9 | 0.6 | 0.6 | [25 empty] | 71
IEAD NonRes Roof Insulation-1.76 | StandardOpaqueMaterial | MediumRough | 2.9126 | 0.33974 | 8.573077103 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 72
IEAD Roof Insulation R-3.47 IP | StandardOpaqueMaterial | MediumRough | 1.1788 | 0.33974 | 3.469819827 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 97
Insulating Concrete Forms - 1 1/2 in. Polyurethane Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 9 | 0.4704 | 19.13265306 | 100.33 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 1 1/2 in. Polyurethane Ins. each side - concrete 6 in. | [5 empty] | 405
Insulating Concrete Forms - 1 1/2 in. Polyurethane Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 11 | 0.57 | 19.29824561 | 109.36 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 1 1/2 in. Polyurethane Ins. each side - concrete 8 in. | [5 empty] | 406
Insulating Concrete Forms - 2 1/2 in. EPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 11 | 0.51648 | 21.29801735 | 76.81 | 0.23 | [19 empty] | CEC Title24-2013 | CEC RJ | ICF Wall | Insulating Concrete Forms - 2 1/2 in. EPS Ins. each side - concrete 6 in. | [5 empty] | 413
Insulating Concrete Forms - 2 1/2 in. EPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 13 | 0.60612 | 21.44789811 | 86.54 | 0.22 | [19 empty] | CEC Title24-2013 | CEC RJ | ICF Wall | Insulating Concrete Forms - 2 1/2 in. EPS Ins. each side - concrete 8 in. | [5 empty] | 414
Insulating Concrete Forms - 2 in. EPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 10 | 0.6096 | 16.40419948 | 90.4 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. EPS Ins. each side - concrete 6 in. | [5 empty] | 411
Insulating Concrete Forms - 2 in. EPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 12 | 0.72 | 16.66666667 | 100.33 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. EPS Ins. each side - concrete 8 in. | [5 empty] | 412
Insulating Concrete Forms - 2 in. Polyurethane Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 10 | 0.4404 | 22.70663034 | 90.4 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. Polyurethane Ins. each side - concrete 6 in. | [5 empty] | 407
Insulating Concrete Forms - 2 in. Polyurethane Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 12 | 0.5196 | 23.09468822 | 100.33 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. Polyurethane Ins. each side - concrete 8 in. | [5 empty] | 408
Insulating Concrete Forms - 2 in. XPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 10 | 0.4704 | 21.2585034 | 90.4 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. XPS Ins. each side - concrete 6 in. | [5 empty] | 419
Insulating Concrete Forms - 2 in. XPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 12 | 0.57 | 21.05263158 | 100.33 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. XPS Ins. each side - concrete 8 in. | [5 empty] | 420
Insulating Concrete Forms - 3 in. EPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 12 | 0.5004 | 23.98081535 | 75.5 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 3 in. EPS Ins. each side - concrete 6 in. | [5 empty] | 415
Insulating Concrete Forms - 3 in. EPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 14 | 0.57 | 24.56140351 | 86.14 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 3 in. EPS Ins. each side - concrete 8 in. | [5 empty] | 416
Insulating Concrete Forms - 3 in. XPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 12 | 0.39 | 30.76923077 | 75.5 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 3 in. XPS Ins. each side - concrete 6 in. | [5 empty] | 421
Insulating Concrete Forms - 3 in. XPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 14 | 0.45 | 31.11111111 | 86.14 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 3 in. XPS Ins. each side - concrete 8 in. | [5 empty] | 422
Insulating Concrete Forms - 4 1/2 in. Polyurethane Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 15 | 0.3504 | 42.80821918 | 60.6 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 1/2 in. Polyurethane Ins. each side - concrete 6 in. | [5 empty] | 409
Insulating Concrete Forms - 4 1/2 in. Polyurethane Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 17 | 0.3996 | 42.54254254 | 71.12 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 1/2 in. Polyurethane Ins. each side - concrete 8 in. | [5 empty] | 410
Insulating Concrete Forms - 4 in. EPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 14 | 0.4296 | 32.58845438 | 64.86 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 in. EPS Ins. each side - concrete 6 in. | [5 empty] | 417
Insulating Concrete Forms - 4 in. EPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 16 | 0.5004 | 31.97442046 | 75.5 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 in. EPS Ins. each side - concrete 8 in. | [5 empty] | 418
Insulating Concrete Forms - 4 in. XPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 14 | 0.3504 | 39.9543379 | 64.86 | 0.23 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 in. XPS Ins. each side - concrete 6 in. | [5 empty] | 423
Insulating Concrete Forms - 4 in. XPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 16 | 0.39 | 41.02564103 | 75.5 | 0.22 | [19 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 in. XPS Ins. each side - concrete 8 in. | [5 empty] | 424
Interior Wall Addi Insul | StandardOpaqueMaterial | MediumRough | 1e-06 | 0.29994 | 0.000003333984669 | 1.4 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 1207
Light Roof - 2/5 in. | StandardOpaqueMaterial | VeryRough | 0.2 | 2.4012 | 0.08329168749 | 120 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Bruce | Roofing | Light Roof - 2/5 in. | [5 empty] | 694
Linoleum/cork tile - 1/4 in. | StandardOpaqueMaterial | MediumRough | 0.25 | 0.51 | 0.4901960784 | 29 | 0.45 | [19 empty] | CEC Title24-2013 | AEC | Finish Materials | Linoleum/cork tile - 1/4 in. | [5 empty] | 401
LoE CLEAR 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.6 | 0.17 | 0.22 | 0.84 | 0.055 | 0.078 | 0 | 0.84 | 0.1 | 1 | FALSE | [9 empty] | 1330
LoE SPEC SEL CLEAR 3MM | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.45 | 0.34 | 0.37 | 0.78 | 0.07 | 0.06 | 0 | 0.84 | 0.03 | 1 | FALSE | [9 empty] | 1331
LoE SPEC SEL CLEAR 6MM Rev | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.43 | 0.42 | 0.3 | 0.77 | 0.06 | 0.07 | 0 | 0.03 | 0.84 | 1 | FALSE | [9 empty] | 1332
LoE SPEC SEL TINT 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.26 | 0.14 | 0.41 | 0.46 | 0.06 | 0.04 | 0 | 0.84 | 0.03 | 1 | FALSE | [9 empty] | 1333
LoE TINT 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.36 | 0.093 | 0.2 | 0.5 | 0.035 | 0.054 | 0 | 0.84 | 0.1 | 1 | FALSE | [9 empty] | 1334
Loose fill - Mineral fiber - 2 lb/ft3 - 13 3/4 in. | StandardOpaqueMaterial | Rough | 13.75 | 0.336 | 40.92261905 | 2 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - 2 lb/ft3 - 13 3/4 in. | [5 empty] | 561
Loose fill - Mineral fiber - 2 lb/ft3 - 4 in. | StandardOpaqueMaterial | Rough | 4 | 0.336 | 11.9047619 | 2 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - 2 lb/ft3 - 4 in. | [5 empty] | 557
Loose fill - Mineral fiber - 2 lb/ft3 - 6 1/2 in. | StandardOpaqueMaterial | Rough | 6.5 | 0.336 | 19.3452381 | 2 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - 2 lb/ft3 - 6 1/2 in. | [5 empty] | 558
Loose fill - Mineral fiber - 2 lb/ft3 - 7 1/2 in. | StandardOpaqueMaterial | Rough | 7.5 | 0.336 | 22.32142857 | 2 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - 2 lb/ft3 - 7 1/2 in. | [5 empty] | 559
Loose fill - Mineral fiber - 2 lb/ft3 - 8 1/4 in. | StandardOpaqueMaterial | Rough | 8.25 | 0.336 | 24.55357143 | 2 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - 2 lb/ft3 - 8 1/4 in. | [5 empty] | 560
Loose fill - Mineral fiber - closed sidewalls - 3 1/2 in. | StandardOpaqueMaterial | Rough | 3.5 | 0.336 | 10.41666667 | 2 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - closed sidewalls - 3 1/2 in. | [5 empty] | 556
M01 100mm brick | StandardOpaqueMaterial | MediumRough | 4 | 6.1708 | 0.6482152309 | 119.8617 | 0.18869 | 0.9 | 0.7 | 0.7 | [25 empty] | 103
M11 100mm lightweight concrete | StandardOpaqueMaterial | MediumRough | 4 | 3.6747 | 1.088512369 | 79.9078 | 0.20063 | 0.9 | 0.5 | 0.5 | [25 empty] | 104
M15 200mm heavyweight concrete | StandardOpaqueMaterial | MediumRough | 8 | 13.5203 | 0.5917041594 | 139.8386 | 0.21496 | 0.9 | 0.5 | 0.5 | [25 empty] | 105
Maple - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.14 | 0.8771929825 | 41.87 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Maple - 1 in. | [5 empty] | 891
Mass NonRes Wall Insulation-0.43 | StandardOpaqueMaterial | MediumRough | 0.017196 | 0.33974 | 0.05061550945 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 106
Mass Wall Insulation R-4.23 IP | StandardOpaqueMaterial | MediumRough | 1.4385 | 0.33974 | 4.234033978 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 133
Mastic asphalt (heavy - 20% grit) - 1 in. | StandardOpaqueMaterial | VeryRough | 1 | 1.2996 | 0.7694675285 | 59 | 0.22 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Mastic asphalt (heavy - 20% grit) - 1 in. | [5 empty] | 695
MAT-CC05 4 HW CONCRETE | StandardOpaqueMaterial | Rough | 4 | 9.0898 | 0.4400545808 | 139.8386 | 0.19987 | 0.9 | 0.85 | 0.85 | [25 empty] | 140
MAT-CC05 8 HW CONCRETE | StandardOpaqueMaterial | Rough | 8 | 9.0898 | 0.8801091616 | 139.8386 | 0.19987 | 0.9 | 0.85 | 0.85 | [25 empty] | 141
MAT-SHEATH | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7 | [25 empty] | 142
Metal Building Semi-Cond Wall Insulation-0.54 | StandardOpaqueMaterial | MediumRough | 0.60417 | 0.33974 | 1.778337913 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 143
Metal Building Wall Insulation R-4.14 IP | StandardOpaqueMaterial | MediumRough | 1.4044 | 0.33974 | 4.133881011 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 169
Metal Deck - 1/16 in. | StandardOpaqueMaterial | Smooth | 0.0625 | 314.4 | 0.0001987913486 | 488.22 | 0.12 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Metal Deck - 1/16 in. | [5 empty] | 322
Metal Decking | StandardOpaqueMaterial | MediumSmooth | 0.059055 | 312.0478 | 0.0001892502113 | 479.4467 | 0.099933 | 0.9 | 0.6 | 0.6 | [25 empty] | 177
Metal Framed Floor - 16inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 9.383 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 9_25in | 2x10 | 30 | 927
Metal Framed Floor - 16inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 10.756 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 11_25in | 2x12 | 38 | 928
Metal Framed Floor - 16inOC - 2x6 - R0 ins. | MasslessOpaqueMaterial |  |  |  | 0.003 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 5_5in | 2x6 | 0 | 921
Metal Framed Floor - 16inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 5.309 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 5_5in | 2x6 | 11 | 922
Metal Framed Floor - 16inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 5.854 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 5_5in | 2x6 | 13 | 923
Metal Framed Floor - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 6.92 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 5_5in | 2x6 | 19 | 924
Metal Framed Floor - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 7.414 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 7_25in | 2x8 | 19 | 925
Metal Framed Floor - 16inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 7.815 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 7_25in | 2x8 | 22 | 926
Metal Framed Floor - 24inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 12.443 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 9_25in | 2x10 | 30 | 935
Metal Framed Floor - 24inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 14.569 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 11_25in | 2x12 | 38 | 936
Metal Framed Floor - 24inOC - 2x6 - R0 ins. | MasslessOpaqueMaterial |  |  |  | 0.003 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 5_5in | 2x6 | 0 | 929
Metal Framed Floor - 24inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 6.576 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 5_5in | 2x6 | 11 | 930
Metal Framed Floor - 24inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 7.544 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 5_5in | 2x6 | 13 | 931
Metal Framed Floor - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 9.037 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 5_5in | 2x6 | 19 | 932
Metal Framed Floor - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 9.564 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 7_25in | 2x8 | 19 | 933
Metal Framed Floor - 24inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 10.336 | [21 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 7_25in | 2x8 | 22 | 934
Metal Framed Roof - 16inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 10.16 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 9_25In | 2x10 | 25 | 970
Metal Framed Roof - 16inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 10.92 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 9_25In | 2x10 | 30 | 971
Metal Framed Roof - 16inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 11.42 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 11_25In | 2x12 | 30 | 972
Metal Framed Roof - 16inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 12.34 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 11_25In | 2x12 | 38 | 973
Metal Framed Roof - 16inOC - 2x14 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 12.97 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 13_25In | 2x14 | 38 | 974
Metal Framed Roof - 16inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 6.01 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 3_5In | 2x4 | 11 | 960
Metal Framed Roof - 16inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 6.52 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 3_5In | 2x4 | 13 | 961
Metal Framed Roof - 16inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 6.96 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 3_5In | 2x4 | 15 | 962
Metal Framed Roof - 16inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 6.52 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 3_5In | 2x4 | 19 | 963
Metal Framed Roof - 16inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 6.39 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 5_5In | 2x6 | 11 | 964
Metal Framed Roof - 16inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 6.96 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 5_5In | 2x6 | 13 | 965
Metal Framed Roof - 16inOC - 2x6 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 8.16 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 5_5In | 2x6 | 15 | 966
Metal Framed Roof - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 8.26 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 5_5In | 2x6 | 19 | 967
Metal Framed Roof - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 8.68 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 7_25In | 2x8 | 19 | 968
Metal Framed Roof - 16inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 9.01 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 7_25In | 2x8 | 21 | 969
Metal Framed Roof - 24inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 12.97 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 9_25In | 2x10 | 25 | 985
Metal Framed Roof - 24inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 14.13 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 9_25In | 2x10 | 30 | 986
Metal Framed Roof - 24inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 14.65 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 11_25In | 2x12 | 30 | 987
Metal Framed Roof - 24inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 16.44 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 11_25In | 2x12 | 38 | 988
Metal Framed Roof - 24inOC - 2x14 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 17.13 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 13_25In | 2x14 | 38 | 989
Metal Framed Roof - 24inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 7.27 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 3_5In | 2x4 | 11 | 975
Metal Framed Roof - 24inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 8.06 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 3_5In | 2x4 | 13 | 976
Metal Framed Roof - 24inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 8.68 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 3_5In | 2x4 | 15 | 977
Metal Framed Roof - 24inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 8.06 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 3_5In | 2x4 | 19 | 978
Metal Framed Roof - 24inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 7.61 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 5_5In | 2x6 | 11 | 979
Metal Framed Roof - 24inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 8.36 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 5_5In | 2x6 | 13 | 980
Metal Framed Roof - 24inOC - 2x6 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 9.89 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 5_5In | 2x6 | 15 | 981
Metal Framed Roof - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 10.31 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 5_5In | 2x6 | 19 | 982
Metal Framed Roof - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 10.76 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 7_25In | 2x8 | 19 | 983
Metal Framed Roof - 24inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 11.42 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 7_25In | 2x8 | 21 | 984
Metal Framed Wall - 16inOC - 2x4 - R0 ins. | MasslessOpaqueMaterial |  |  |  | 0.643 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 3_5in | 2x4 | 0 | 899
Metal Framed Wall - 16inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 2.924 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 3_5in | 2x4 | 11 | 901
Metal Framed Wall - 16inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 3.068 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 3_5in | 2x4 | 13 | 902
Metal Framed Wall - 16inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 3.199 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 3_5in | 2x4 | 15 | 903
Metal Framed Wall - 16inOC - 2x4 - R5 ins. | MasslessOpaqueMaterial |  |  |  | 1.309 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 3_5in | 2x4 | 5 | 900
Metal Framed Wall - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 3.924 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 5_5in | 2x6 | 19 | 904
Metal Framed Wall - 16inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 4.078 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 5_5in | 2x6 | 21 | 905
Metal Framed Wall - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 4.558 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 7_25in | 2x8 | 19 | 906
Metal Framed Wall - 16inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 4.71 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 7_25in | 2x8 | 22 | 907
Metal Framed Wall - 16inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 4.789 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 7_25in | 2x8 | 25 | 908
Metal Framed Wall - 16inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 4.829 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 7_25in | 2x8 | 30 | 909
Metal Framed Wall - 24inOC - 2x4 - R0 ins. | MasslessOpaqueMaterial |  |  |  | 0.658 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 3_5in | 2x4 | 0 | 910
Metal Framed Wall - 24inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 3.222 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 3_5in | 2x4 | 11 | 912
Metal Framed Wall - 24inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 3.386 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 3_5in | 2x4 | 13 | 913
Metal Framed Wall - 24inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 3.536 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 3_5in | 2x4 | 15 | 914
Metal Framed Wall - 24inOC - 2x4 - R5 ins. | MasslessOpaqueMaterial |  |  |  | 1.463 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 3_5in | 2x4 | 5 | 911
Metal Framed Wall - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 4.558 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 5_5in | 2x6 | 19 | 915
Metal Framed Wall - 24inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 4.671 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 5_5in | 2x6 | 21 | 916
Metal Framed Wall - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 4.996 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 7_25in | 2x8 | 19 | 917
Metal Framed Wall - 24inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 5.171 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 7_25in | 2x8 | 22 | 918
Metal Framed Wall - 24inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 5.263 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 7_25in | 2x8 | 25 | 919
Metal Framed Wall - 24inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 5.309 | [21 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 7_25in | 2x8 | 30 | 920
Metal Insulated Panels - 2 1/2 in. | StandardOpaqueMaterial | Smooth | 2.5 | 0.16644 | 15.02042778 | 28.47 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 2 1/2 in. | [5 empty] | 652
Metal Insulated Panels - 2 in. | StandardOpaqueMaterial | Smooth | 2 | 0.16704 | 11.97318008 | 34.87 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 2 in. | [5 empty] | 651
Metal Insulated Panels - 3 in. | StandardOpaqueMaterial | Smooth | 3 | 0.16656 | 18.01152738 | 24.11 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 3 in. | [5 empty] | 653
Metal Insulated Panels - 4 in. | StandardOpaqueMaterial | Smooth | 4 | 0.16992 | 23.54048964 | 18.54 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 4 in. | [5 empty] | 654
Metal Insulated Panels - 5 in. | StandardOpaqueMaterial | Smooth | 5 | 0.1698 | 29.44640754 | 15.14 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 5 in. | [5 empty] | 655
Metal Insulated Panels - 6 in. | StandardOpaqueMaterial | Smooth | 6 | 0.16584 | 36.17945007 | 12.84 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 6 in. | [5 empty] | 656
Metal Roof Insulation R-5.21 IP | StandardOpaqueMaterial | MediumRough | 1.7692 | 0.33974 | 5.207645452 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 198
Metal Roof Surface | StandardOpaqueMaterial | Smooth | 0.031496 | 313.9476 | 0.0001003226739 | 488.4364 | 0.11942 | 0.9 | 0.7 | 0.7 | [25 empty] | 1208
Metal Roof Surface - Highly Reflective | StandardOpaqueMaterial | Smooth | 0.031496 | 313.9476 | 0.0001003226739 | 488.4364 | 0.11942 | 0.75 | 0.45 | 0.7 | [25 empty] | 1208
Metal Roofing | StandardOpaqueMaterial | MediumSmooth | 0.059055 | 312.0478 | 0.0001892502113 | 479.4467 | 0.099933 | 0.9 | 0.6 | 0.6 | [25 empty] | 178
Metal Roofing - Highly Reflective | StandardOpaqueMaterial | MediumSmooth | 0.059055 | 312.0478 | 0.0001892502113 | 479.4467 | 0.099933 | 0.75 | 0.45 | 0.6 | [25 empty] | 178
Metal Screw Down Roof - No Thrml Blk - R10 ins. | MasslessOpaqueMaterial |  |  |  | 5.756 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalScrewDown | NA | NA | 10 | 937
Metal Screw Down Roof - No Thrml Blk - R11 ins. | MasslessOpaqueMaterial |  |  |  | 6.414 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalScrewDown | NA | NA | 11 | 938
Metal Screw Down Roof - No Thrml Blk - R13ins. | MasslessOpaqueMaterial |  |  |  | 6.912 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalScrewDown | NA | NA | 13 | 939
Metal Screw Down Roof - No Thrml Blk - R16 ins. | MasslessOpaqueMaterial |  |  |  | 8.654 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalScrewDown | NA | NA | 16 | 940
Metal Screw Down Roof - No Thrml Blk - R19 ins. | MasslessOpaqueMaterial |  |  |  | 9.424 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalScrewDown | NA | NA | 19 | 941
Metal Semi-Cond Roof Insulation-1.05 | StandardOpaqueMaterial | MediumRough | 1.6641 | 0.33974 | 4.898061868 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 179
Metal Siding | StandardOpaqueMaterial | Smooth | 0.059055 | 311.7289 | 0.0001894438392 | 479.9998 | 0.097927 | 0.9 | 0.6 | 0.6 | [25 empty] | 206
Metal Siding - 1/16 in. | StandardOpaqueMaterial | Smooth | 0.0625 | 314.4 | 0.0001987913486 | 488.22 | 0.12 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Metal Siding - 1/16 in. | [5 empty] | 323
Metal Standing Seam - 1/16 in. | StandardOpaqueMaterial | Smooth | 0.0625 | 3.9996 | 0.01562656266 | 488.22 | 0.12 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Metal Standing Seam - 1/16 in. | [5 empty] | 696
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R10 + R10 Ins. | MasslessOpaqueMaterial |  |  |  | 15.093 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 20 | 948
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R10 + R11 Ins. | MasslessOpaqueMaterial |  |  |  | 15.613 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 21 | 949
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R10 + R13 Ins. | MasslessOpaqueMaterial |  |  |  | 16.461 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 23 | 951
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R10 + R19 Ins. | MasslessOpaqueMaterial |  |  |  | 18.451 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 29 | 954
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R11 + R11 Ins. | MasslessOpaqueMaterial |  |  |  | 15.887 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 22 | 950
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R11 + R13 Ins. | MasslessOpaqueMaterial |  |  |  | 16.764 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 24 | 952
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R11 + R19 Ins. | MasslessOpaqueMaterial |  |  |  | 18.828 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 30 | 955
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R13 + R13 Ins. | MasslessOpaqueMaterial |  |  |  | 17.402 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 26 | 953
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R13 + R19 Ins. | MasslessOpaqueMaterial |  |  |  | 19.628 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 32 | 956
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R16 + R19 Ins. | MasslessOpaqueMaterial |  |  |  | 20.497 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 35 | 957
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R19 + R19 Ins. | MasslessOpaqueMaterial |  |  |  | 20.959 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 36 | 958
Metal Standing Seam Roof - Thrml Blk - Ins. and Filled Cavity - R19 + R10 Ins. | MasslessOpaqueMaterial |  |  |  | 23.61 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeamFilledCavity | NA | NA | 29 | 959
Metal Standing Seam Roof - Thrml Blk - R10 ins. | MasslessOpaqueMaterial |  |  |  | 9.529 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 10 | 943
Metal Standing Seam Roof - Thrml Blk - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.09 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 11 | 944
Metal Standing Seam Roof - Thrml Blk - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.268 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 13 | 945
Metal Standing Seam Roof - Thrml Blk - R16 ins. | MasslessOpaqueMaterial |  |  |  | 13.109 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 16 | 946
Metal Standing Seam Roof - Thrml Blk - R19 ins. | MasslessOpaqueMaterial |  |  |  | 14.605 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 19 | 947
Metal Standing Seam Roof - Thrml Blk - R6 ins. | MasslessOpaqueMaterial |  |  |  | 5.208 | [21 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 6 | 942
Metal Surface | StandardOpaqueMaterial | Smooth | 0.031496 | 313.9476 | 0.0001003226739 | 488.4364 | 0.11942 | 0.9 | 0.7 | 0.7 | [25 empty] | 1209
Mortar - Cement - 1 3/4 in. | StandardOpaqueMaterial | Smooth | 1.76 | 5.01 | 0.3512974052 | 116 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Mortar - Cement - 1 3/4 in. | [5 empty] | 669
Mortar - Cement - 1 in. | StandardOpaqueMaterial | Smooth | 1.01 | 5.0304 | 0.2007792621 | 116 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Mortar - Cement - 1 in. | [5 empty] | 668
Nonres_Floor_Insulation | MasslessOpaqueMaterial | MediumSmooth |  |  | 16.37 |  |  | 0.9 | 0.7 | 0.7
Oak - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.1796 | 0.8477449983 | 43.93 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Oak - 1 in. | [5 empty] | 892
OSB - Oriented Strand Board - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.6204 | 0.805931657 | 41 | 0.45 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | OSB - Oriented Strand Board - 1/2 in. | [5 empty] | 324
OSB - Oriented Strand Board - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.9096 | 0.8245382586 | 41 | 0.45 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | OSB - Oriented Strand Board - 3/4 in. | [5 empty] | 326
OSB - Oriented Strand Board - 5/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.63 | 0.7596 | 0.8293838863 | 41 | 0.45 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | OSB - Oriented Strand Board - 5/8 in. | [5 empty] | 325
Perlite board - 1 1/2 in. R3.8 | StandardOpaqueMaterial | Rough | 1.5 | 0.3996 | 3.753753754 | 10 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Perlite board - 1 1/2 in. R3.8 | [5 empty] | 512
Perlite board - 1 in. R2.5 | StandardOpaqueMaterial | Rough | 1 | 0.3996 | 2.502502503 | 10 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Perlite board - 1 in. R2.5 | [5 empty] | 511
Perlite board - 2 in. R5.0 | StandardOpaqueMaterial | Rough | 2 | 0.3996 | 5.005005005 | 10 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Perlite board - 2 in. R5.0 | [5 empty] | 513
Perlite board - 3/4 in. R1.9 | StandardOpaqueMaterial | Rough | 0.75 | 0.3996 | 1.876876877 | 10 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Insulation Board | Perlite board - 3/4 in. R1.9 | [5 empty] | 510
Perlite plaster - 25 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.6 | 0.8333333333 | 25 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Perlite plaster - 25 lb/ft3 - 1/2 in. | [5 empty] | 670
Perlite plaster - 38 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 1.2996 | 0.3847337642 | 38 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Perlite plaster - 38 lb/ft3 - 1/2 in. | [5 empty] | 671
Pine (oven-dried) - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 0.6396 | 1.563477173 | 23 | 0.45 | [19 empty] | CEC Title24-2013 | AEC | Woods | Pine (oven-dried) - 1 in. | [5 empty] | 893
Plaster/Sand Aggregate - 1 in. | StandardOpaqueMaterial | Smooth | 1.01 | 5.0304 | 0.2007792621 | 116 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Plaster/Sand Aggregate - 1 in. | [5 empty] | 672
Plywood - 1 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 1.5 | 0.8004 | 1.874062969 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC RJ | Bldg Board and Siding | Plywood - 1 1/2 in. | [5 empty] | 334
Plywood - 1 1/4 in. | StandardOpaqueMaterial | MediumSmooth | 1.25 | 0.8004 | 1.56171914 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC RJ | Bldg Board and Siding | Plywood - 1 1/4 in. | [5 empty] | 333
Plywood - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 0.8004 | 1.249375312 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 1 in. | [5 empty] | 332
Plywood - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.8004 | 0.6246876562 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 1/2 in. | [5 empty] | 329
Plywood - 1/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.25 | 0.8004 | 0.3123438281 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 1/4 in. | [5 empty] | 327
Plywood - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.8004 | 0.9370314843 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 3/4 in. | [5 empty] | 331
Plywood - 3/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.38 | 0.8004 | 0.4747626187 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 3/8 in. | [5 empty] | 328
Plywood - 5/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.63 | 0.8004 | 0.7871064468 | 30 | 0.45 | [19 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 5/8 in. | [5 empty] | 330
Pulpboard or paper plaster - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.5004 | 0.9992006395 | 38 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Pulpboard or paper plaster - 1/2 in. | [5 empty] | 673
PYR B CLEAR 3MM | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.74 | 0.09 | 0.1 | 0.82 | 0.11 | 0.12 | 0 | 0.84 | 0.2 | 1 | FALSE | [9 empty] | 1335
PYR B CLEAR 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.68 | 0.09 | 0.1 | 0.81 | 0.11 | 0.12 | 0 | 0.84 | 0.2 | 1 | FALSE | [9 empty] | 1336
R-24 Batt Wall - 8 in. R24 | StandardOpaqueMaterial | VeryRough | 8 | 0.3336 | 23.98081535 | 1.19 | 0.23 | [19 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | R-24 Batt Wall - 8 in. R24 | [5 empty] | 514
Rammed Earth | StandardOpaqueMaterial | Rough | 18 | 1.4796 | 12.16545012 | 115 | 0.2 | [19 empty] | CEC Title24-2013 | CEC | Insulation Other | Rammed Earth | [5 empty] | 562
REF A CLEAR LO 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.066 | 0.341 | 0.493 | 0.08 | 0.41 | 0.37 | 0 | 0.84 | 0.4 | 1 | FALSE | [9 empty] | 1337
REF A CLEAR MID 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.11 | 0.27 | 0.43 | 0.14 | 0.31 | 0.35 | 0 | 0.84 | 0.47 | 1 | FALSE | [9 empty] | 1338
REF A TINT MID 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.06 | 0.13 | 0.42 | 0.09 | 0.14 | 0.35 | 0 | 0.84 | 0.47 | 1 | FALSE | [9 empty] | 1339
REF B CLEAR HI 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.24 | 0.16 | 0.32 | 0.3 | 0.16 | 0.29 | 0 | 0.84 | 0.6 | 1 | FALSE | [9 empty] | 1340
REF B CLEAR LO 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.15 | 0.22 | 0.38 | 0.2 | 0.23 | 0.33 | 0 | 0.84 | 0.58 | 1 | FALSE | [9 empty] | 1341
REF B TINT HI 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.15 | 0.09 | 0.33 | 0.18 | 0.08 | 0.28 | 0 | 0.84 | 0.6 | 1 | FALSE | [9 empty] | 1342
REF B TINT MID 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.1 | 0.11 | 0.41 | 0.13 | 0.1 | 0.32 | 0 | 0.84 | 0.45 | 1 | FALSE | [9 empty] | 1343
REF C CLEAR HI 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.2 | 0.16 | 0.39 | 0.22 | 0.17 | 0.35 | 0 | 0.84 | 0.55 | 1 | FALSE | [9 empty] | 1344
REF C CLEAR MID 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.17 | 0.2 | 0.42 | 0.19 | 0.21 | 0.38 | 0 | 0.84 | 0.51 | 1 | FALSE | [9 empty] | 1345
REF D CLEAR 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.429 | 0.308 | 0.379 | 0.334 | 0.453 | 0.505 | 0 | 0.84 | 0.82 | 1 | FALSE | [9 empty] | 1346
REF D TINT 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.3 | 0.14 | 0.36 | 0.25 | 0.18 | 0.45 | 0 | 0.84 | 0.82 | 1 | FALSE | [9 empty] | 1347
Roof Gravel - 1 in. | StandardOpaqueMaterial | VeryRough | 1 | 9.9996 | 0.1000040002 | 159.74 | 0.19 | [19 empty] | CEC Title24-2013 | CEC Doug | Roofing | Roof Gravel - 1 in. | [5 empty] | 697
Roof Gravel - 1/2 in. | StandardOpaqueMaterial | VeryRough | 0.5 | 9.9996 | 0.05000200008 | 159.74 | 0.19 | [19 empty] | CEC Title24-2013 | CEC Doug | Roofing | Roof Gravel - 1/2 in. | [5 empty] | 698
Roof Insulation [18] | StandardOpaqueMaterial | MediumRough | 6.6654 | 0.33974 | 19.61897926 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 207
Roof Membrane | StandardOpaqueMaterial | VeryRough | 0.37402 | 1.1094 | 0.3371468859 | 69.9998 | 0.34872 | 0.9 | 0.77 | 0.7 | [25 empty] | 215
Roof Membrane - Highly Reflective | StandardOpaqueMaterial | VeryRough | 0.37402 | 1.1094 | 0.3371468859 | 69.9998 | 0.34872 | 0.75 | 0.45 | 0.7 | [25 empty] | 215
Roofing felt - 1/8 in. | StandardOpaqueMaterial | VeryRough | 0.13 | 8.3004 | 0.01566189581 | 141 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Building Membrane | Roofing felt - 1/8 in. | [5 empty] | 345
Rubber tile - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 0.3396 | 2.944640754 | 119 | 0.48 | [19 empty] | CEC Title24-2013 | AEC | Finish Materials | Rubber tile - 1 in. | [5 empty] | 402
Sand aggregate - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 5.4504 | 0.09173638632 | 105 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Sand aggregate - 1/2 in. | [5 empty] | 675
Sand aggregate - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 5.0796 | 0.1476494212 | 116 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Sand aggregate - 3/4 in. | [5 empty] | 677
Sand aggregate - 3/8 in. | StandardOpaqueMaterial | Smooth | 0.38 | 5.1504 | 0.07378067723 | 116 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Sand aggregate - 3/8 in. | [5 empty] | 674
Sand aggregate - 5/8 in. | StandardOpaqueMaterial | Smooth | 0.63 | 5.6004 | 0.1124919649 | 105 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Sand aggregate - 5/8 in. | [5 empty] | 676
Sand aggregate on metal lath - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 5.7696 | 0.1299916805 | 105 | 0.2 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Sand aggregate on metal lath - 3/4 in. | [5 empty] | 678
Shingles - Asbestos cement - lapped - 1/4 in. | StandardOpaqueMaterial | VeryRough | 0.25 | 1.1904 | 0.2100134409 | 120 | 0.24 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Shingles - Asbestos cement - lapped - 1/4 in. | [5 empty] | 335
Shingles - Asphalt roll siding - 1/4 in. | StandardOpaqueMaterial | VeryRough | 0.25 | 1.6704 | 0.149664751 | 70 | 0.36 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Shingles - Asphalt roll siding - 1/4 in. | [5 empty] | 336
Shingles - Wood - 16 in. - 7 1/2 in. exposure - 1/2 in. | StandardOpaqueMaterial | MediumRough | 0.5 | 0.57 | 0.8771929825 | 22 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Shingles - Wood - 16 in. - 7 1/2 in. exposure - 1/2 in. | [5 empty] | 337
Shingles - Wood - plus insulated backer board Siding - 5/16 in. | StandardOpaqueMaterial | MediumRough | 0.31 | 0.2196 | 1.411657559 | 22 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Shingles - Wood - plus insulated backer board Siding - 5/16 in. | [5 empty] | 338
Siding - Asphalt insulating siding - 1/2 in. bed - 1/2 in. | StandardOpaqueMaterial | VeryRough | 0.5 | 0.3396 | 1.472320377 | 70 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Siding - Asphalt insulating siding - 1/2 in. bed - 1/2 in. | [5 empty] | 341
Siding - Wood - bevel - 10 in. - lapped - 3/4 in. | StandardOpaqueMaterial | Rough | 0.75 | 0.7104 | 1.055743243 | 22 | 0.28 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Siding - Wood - bevel - 10 in. - lapped - 3/4 in. | [5 empty] | 342
SIPS - Crawl Space - R22 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.24768 | 26.24354005 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R22 - Double 2x Spline - 6 1/2 in. | [5 empty] | 711
SIPS - Crawl Space - R22 - I Joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.23148 | 28.08017971 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R22 - I Joist Spline - 6 1/2 in. | [5 empty] | 703
SIPS - Crawl Space - R22 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.23952 | 27.13760855 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R22 - Single 2x Spline - 6 1/2 in. | [5 empty] | 707
SIPS - Crawl Space - R28 - Double 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.25356 | 32.53667771 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R28 - Double 2x Spline - 8 1/4 in. | [5 empty] | 713
SIPS - Crawl Space - R28 - I Joist Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.2436 | 33.86699507 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R28 - I Joist Spline - 8 1/4 in. | [5 empty] | 705
SIPS - Crawl Space - R28 - Single 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.2436 | 33.86699507 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R28 - Single 2x Spline - 8 1/4 in. | [5 empty] | 709
SIPS - Crawl Space - R33 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.1842 | 35.28773073 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R33 - Double 2x Spline - 6 1/2 in. | [5 empty] | 712
SIPS - Crawl Space - R33 - I Joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.16884 | 38.49798626 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R33 - I Joist Spline - 6 1/2 in. | [5 empty] | 704
SIPS - Crawl Space - R33 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.16884 | 38.49798626 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R33 - Single 2x Spline - 6 1/2 in. | [5 empty] | 708
SIPS - Crawl Space - R36 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.26628 | 38.49331531 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R36 - Double 2x Spline - 10 1/4 in. | [5 empty] | 714
SIPS - Crawl Space - R36 - I Joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.2424 | 42.28547855 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R36 - I Joist Spline - 10 1/4 in. | [5 empty] | 706
SIPS - Crawl Space - R36 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.25428 | 40.3098946 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R36 - Single 2x Spline - 10 1/4 in. | [5 empty] | 710
SIPS - No Crawl Space - R22 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.32364 | 20.084044 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R22 - Double 2x Spline - 6 1/2 in. | [5 empty] | 723
SIPS - No Crawl Space - R22 - I Joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.29772 | 21.83259438 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R22 - I Joist Spline - 6 1/2 in. | [5 empty] | 715
SIPS - No Crawl Space - R22 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.30636 | 21.21686904 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R22 - Single 2x Spline - 6 1/2 in. | [5 empty] | 719
SIPS - No Crawl Space - R28 - Double 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.3144 | 26.24045802 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R28 - Double 2x Spline - 8 1/4 in. | [5 empty] | 725
SIPS - No Crawl Space - R28 - I Joist Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.29376 | 28.08415033 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R28 - I Joist Spline - 8 1/4 in. | [5 empty] | 717
SIPS - No Crawl Space - R28 - Single 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.30408 | 27.13101815 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R28 - Single 2x Spline - 8 1/4 in. | [5 empty] | 721
SIPS - No Crawl Space - R33 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.23148 | 28.08017971 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R33 - Double 2x Spline - 6 1/2 in. | [5 empty] | 724
SIPS - No Crawl Space - R33 - I Joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.19968 | 32.55208333 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R33 - I Joist Spline - 6 1/2 in. | [5 empty] | 716
SIPS - No Crawl Space - R33 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.2076 | 31.31021195 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R33 - Single 2x Spline - 6 1/2 in. | [5 empty] | 720
SIPS - No Crawl Space - R36 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.315 | 32.53968254 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R36 - Double 2x Spline - 10 1/4 in. | [5 empty] | 726
SIPS - No Crawl Space - R36 - I Joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.2904 | 35.29614325 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R36 - I Joist Spline - 10 1/4 in. | [5 empty] | 718
SIPS - No Crawl Space - R36 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.2904 | 35.29614325 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R36 - Single 2x Spline - 10 1/4 in. | [5 empty] | 722
SIPS - R14 - Double 2x Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.39312 | 11.44688645 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R14 - Double 2x Spline - 4 1/2 in. | [5 empty] | 771
SIPS - R14 - I joist Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.35304 | 12.746431 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R14 - I joist Spline - 4 1/2 in. | [5 empty] | 755
SIPS - R14 - Metal Spline - 48 in. | StandardOpaqueMaterial | Smooth | 48 | 4.14 | 11.5942029 | 1.83 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R14 - Metal Spline - 48 in. | [5 empty] | 751
SIPS - R14 - OSB Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.303 | 14.85148515 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R14 - OSB Spline - 4 1/2 in. | [5 empty] | 779
SIPS - R14 - Single 2x Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.35868 | 12.54600201 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R14 - Single 2x Spline - 4 1/2 in. | [5 empty] | 763
SIPS - R18 - Double 2x Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.3306 | 13.61161525 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R18 - Double 2x Spline - 4 1/2 in. | [5 empty] | 772
SIPS - R18 - I joist Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.29208 | 15.40673788 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R18 - I joist Spline - 4 1/2 in. | [5 empty] | 756
SIPS - R18 - OSB Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.25968 | 17.32902033 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R18 - OSB Spline - 4 1/2 in. | [5 empty] | 780
SIPS - R18 - Single 2x Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.303 | 14.85148515 | 9.89 | 0.31 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R18 - Single 2x Spline - 4 1/2 in. | [5 empty] | 764
SIPS - R22 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.32496 | 20.00246184 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R22 - Double 2x Spline - 6 1/2 in. | [5 empty] | 739
SIPS - R22 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.3828 | 16.98014629 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R22 - Double 2x Spline - 6 1/2 in. | [5 empty] | 773
SIPS - R22 - I joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.30216 | 21.51178184 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R22 - I joist Spline - 6 1/2 in. | [5 empty] | 727
SIPS - R22 - I joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.33696 | 19.29012346 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R22 - I joist Spline - 6 1/2 in. | [5 empty] | 757
SIPS - R22 - Metal Spline - 48 in. | StandardOpaqueMaterial | Smooth | 48 | 3.0396 | 15.79155152 | 1.83 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R22 - Metal Spline - 48 in. | [5 empty] | 752
SIPS - R22 - OSB Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.28692 | 22.65439844 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R22 - OSB Spline - 6 1/2 in. | [5 empty] | 745
SIPS - R22 - OSB Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.28452 | 22.84549417 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R22 - OSB Spline - 6 1/2 in. | [5 empty] | 781
SIPS - R22 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.3096 | 20.99483204 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R22 - Single 2x Spline - 6 1/2 in. | [5 empty] | 733
SIPS - R22 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.35208 | 18.46171325 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R22 - Single 2x Spline - 6 1/2 in. | [5 empty] | 765
SIPS - R28 - Double 2x Spline - 8 1/2 in. | StandardOpaqueMaterial | Smooth | 8.5 | 0.33612 | 25.28858741 | 5.71 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R28 - Double 2x Spline - 8 1/2 in. | [5 empty] | 741
SIPS - R28 - Double 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.37992 | 21.71509792 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R28 - Double 2x Spline - 8 1/4 in. | [5 empty] | 775
SIPS - R28 - I joist Spline - 8 1/2 in. | StandardOpaqueMaterial | Smooth | 8.5 | 0.2976 | 28.56182796 | 5.71 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R28 - I joist Spline - 8 1/2 in. | [5 empty] | 729
SIPS - R28 - I joist Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.32364 | 25.49128661 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R28 - I joist Spline - 8 1/4 in. | [5 empty] | 759
SIPS - R28 - Metal Spline - 48 in. | StandardOpaqueMaterial | Smooth | 48 | 2.4569 | 19.53697372 | 1.83 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R28 - Metal Spline - 48 in. | [5 empty] | 753
SIPS - R28 - OSB Spline - 8 1/2 in. | StandardOpaqueMaterial | Smooth | 8.5 | 0.2976 | 28.56182796 | 5.71 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R28 - OSB Spline - 8 1/2 in. | [5 empty] | 747
SIPS - R28 - OSB Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.27768 | 29.71045808 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R28 - OSB Spline - 8 1/4 in. | [5 empty] | 783
SIPS - R28 - Single 2x Spline - 8 1/2 in. | StandardOpaqueMaterial | Smooth | 8.5 | 0.3072 | 27.66927083 | 5.71 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R28 - Single 2x Spline - 8 1/2 in. | [5 empty] | 735
SIPS - R28 - Single 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.34236 | 24.09744129 | 5.85 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R28 - Single 2x Spline - 8 1/4 in. | [5 empty] | 767
SIPS - R33 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.23484 | 27.67841935 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R33 - Double 2x Spline - 6 1/2 in. | [5 empty] | 740
SIPS - R33 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.29928 | 21.71879177 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R33 - Double 2x Spline - 6 1/2 in. | [5 empty] | 774
SIPS - R33 - I joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.213 | 30.51643192 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R33 - I joist Spline - 6 1/2 in. | [5 empty] | 728
SIPS - R33 - I joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.24768 | 26.24354005 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R33 - I joist Spline - 6 1/2 in. | [5 empty] | 758
SIPS - R33 - OSB Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.2058 | 31.5840622 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R33 - OSB Spline - 6 1/2 in. | [5 empty] | 746
SIPS - R33 - OSB Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.21876 | 29.71292741 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R33 - OSB Spline - 6 1/2 in. | [5 empty] | 782
SIPS - R33 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.213 | 30.51643192 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R33 - Single 2x Spline - 6 1/2 in. | [5 empty] | 734
SIPS - R33 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.26232 | 24.778896 | 7.15 | 0.3 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R33 - Single 2x Spline - 6 1/2 in. | [5 empty] | 766
SIPS - R36 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.31308 | 32.73923598 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R36 - Double 2x Spline - 10 1/4 in. | [5 empty] | 742
SIPS - R36 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.3792 | 27.03059072 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R36 - Double 2x Spline - 10 1/4 in. | [5 empty] | 776
SIPS - R36 - I joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.2904 | 35.29614325 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R36 - I joist Spline - 10 1/4 in. | [5 empty] | 730
SIPS - R36 - I joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.32244 | 31.78885994 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R36 - I joist Spline - 10 1/4 in. | [5 empty] | 760
SIPS - R36 - Metal Spline - 48 in. | StandardOpaqueMaterial | Smooth | 48 | 2.2296 | 21.5285253 | 1.83 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R36 - Metal Spline - 48 in. | [5 empty] | 754
SIPS - R36 - OSB Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.27912 | 36.72255661 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R36 - OSB Spline - 10 1/4 in. | [5 empty] | 748
SIPS - R36 - OSB Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.27756 | 36.9289523 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R36 - OSB Spline - 10 1/4 in. | [5 empty] | 784
SIPS - R36 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.30168 | 33.97639883 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R36 - Single 2x Spline - 10 1/4 in. | [5 empty] | 736
SIPS - R36 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.345 | 29.71014493 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R36 - Single 2x Spline - 10 1/4 in. | [5 empty] | 768
SIPS - R44 - Double 2x Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.32016 | 38.26211894 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R44 - Double 2x Spline - 12 1/4 in. | [5 empty] | 744
SIPS - R44 - Double 2x Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.35844 | 34.17587323 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R44 - Double 2x Spline - 12 1/4 in. | [5 empty] | 778
SIPS - R44 - I joist Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.2802 | 43.71877231 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R44 - I joist Spline - 12 1/4 in. | [5 empty] | 732
SIPS - R44 - I joist Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.31848 | 38.46395378 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R44 - I joist Spline - 12 1/4 in. | [5 empty] | 762
SIPS - R44 - OSB Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.267 | 45.88014981 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R44 - OSB Spline - 12 1/4 in. | [5 empty] | 750
SIPS - R44 - OSB Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.279 | 43.90681004 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R44 - OSB Spline - 12 1/4 in. | [5 empty] | 786
SIPS - R44 - Single 2x Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.29352 | 41.73480512 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R44 - Single 2x Spline - 12 1/4 in. | [5 empty] | 738
SIPS - R44 - Single 2x Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.34512 | 35.49490032 | 4.27 | 0.28 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R44 - Single 2x Spline - 12 1/4 in. | [5 empty] | 770
SIPS - R55 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.22344 | 45.8736126 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R55 - Double 2x Spline - 10 1/4 in. | [5 empty] | 743
SIPS - R55 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.3 | 34.16666667 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R55 - Double 2x Spline - 10 1/4 in. | [5 empty] | 777
SIPS - R55 - I joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.19044 | 53.82272632 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R55 - I joist Spline - 10 1/4 in. | [5 empty] | 731
SIPS - R55 - I joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.2334 | 43.91602399 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R55 - I joist Spline - 10 1/4 in. | [5 empty] | 761
SIPS - R55 - OSB Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.17952 | 57.09670232 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R55 - OSB Spline - 10 1/4 in. | [5 empty] | 749
SIPS - R55 - OSB Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.21156 | 48.4496124 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R55 - OSB Spline - 10 1/4 in. | [5 empty] | 785
SIPS - R55 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.20136 | 50.90385379 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R55 - Single 2x Spline - 10 1/4 in. | [5 empty] | 737
SIPS - R55 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.25548 | 40.12055738 | 4.9 | 0.29 | [19 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R55 - Single 2x Spline - 10 1/4 in. | [5 empty] | 769
Slate - 1/2 in. | StandardOpaqueMaterial | VeryRough | 0.5 | 11.0304 | 0.04532927183 | 119.81 | 0.3 | [19 empty] | CEC Title24-2013 | CEC Doug | Roofing | Slate - 1/2 in. | [5 empty] | 699
Slate or tile - 1/2 in. | StandardOpaqueMaterial | VeryRough | 0.5 | 11.0304 | 0.04532927183 | 119.81 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Finish Materials | Slate or tile - 1/2 in. | [5 empty] | 403
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 3 1/2 in. | StandardOpaqueMaterial | Rough | 3.5 | 0.3204 | 10.92384519 | 4.6 | 0.34 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 3 1/2 in. | [5 empty] | 563
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 4 1/2 in. | StandardOpaqueMaterial | Rough | 4.5 | 0.3204 | 14.04494382 | 4.6 | 0.34 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 4 1/2 in. | [5 empty] | 565
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 4 in. | StandardOpaqueMaterial | Rough | 4 | 0.3204 | 12.48439451 | 4.6 | 0.34 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 4 in. | [5 empty] | 564
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 5 1/2 in. | StandardOpaqueMaterial | Rough | 5.5 | 0.3204 | 17.16604245 | 4.6 | 0.34 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 5 1/2 in. | [5 empty] | 567
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 5 in. | StandardOpaqueMaterial | Rough | 5 | 0.3204 | 15.60549313 | 4.6 | 0.34 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 5 in. | [5 empty] | 566
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 6 1/2 in. | StandardOpaqueMaterial | Rough | 6.5 | 0.3204 | 20.28714107 | 4.6 | 0.34 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 6 1/2 in. | [5 empty] | 569
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 6 in. | StandardOpaqueMaterial | Rough | 6 | 0.3204 | 18.72659176 | 4.6 | 0.34 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 6 in. | [5 empty] | 568
Spray applied - Glass fiber - 3.9 lb/ft3 - 3 1/2 in. | StandardOpaqueMaterial | MediumRough | 3.5 | 0.27 | 12.96296296 | 3.9 | 0.23 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 3 1/2 in. | [5 empty] | 570
Spray applied - Glass fiber - 3.9 lb/ft3 - 4 1/2 in. | StandardOpaqueMaterial | MediumRough | 4.5 | 0.27 | 16.66666667 | 3.9 | 0.23 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 4 1/2 in. | [5 empty] | 572
Spray applied - Glass fiber - 3.9 lb/ft3 - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 0.27 | 14.81481481 | 3.9 | 0.23 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 4 in. | [5 empty] | 571
Spray applied - Glass fiber - 3.9 lb/ft3 - 5 1/2 in. | StandardOpaqueMaterial | MediumRough | 5.5 | 0.27 | 20.37037037 | 3.9 | 0.23 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 5 1/2 in. | [5 empty] | 574
Spray applied - Glass fiber - 3.9 lb/ft3 - 5 in. | StandardOpaqueMaterial | MediumRough | 5 | 0.27 | 18.51851852 | 3.9 | 0.23 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 5 in. | [5 empty] | 573
Spray applied - Glass fiber - 3.9 lb/ft3 - 6 1/2 in. | StandardOpaqueMaterial | MediumRough | 6.5 | 0.27 | 24.07407407 | 3.9 | 0.23 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 6 1/2 in. | [5 empty] | 576
Spray applied - Glass fiber - 3.9 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 0.27 | 22.22222222 | 3.9 | 0.23 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 6 in. | [5 empty] | 575
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 3 1/2 in. | StandardOpaqueMaterial | Rough | 3.5 | 0.3 | 11.66666667 | 0.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 3 1/2 in. | [5 empty] | 577
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 4 1/2 in. | StandardOpaqueMaterial | Rough | 4.5 | 0.3 | 15 | 0.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 4 1/2 in. | [5 empty] | 579
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 4 in. | StandardOpaqueMaterial | Rough | 4 | 0.3 | 13.33333333 | 0.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 4 in. | [5 empty] | 578
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 5 1/2 in. | StandardOpaqueMaterial | Rough | 5.5 | 0.3 | 18.33333333 | 0.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 5 1/2 in. | [5 empty] | 581
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 5 in. | StandardOpaqueMaterial | Rough | 5 | 0.3 | 16.66666667 | 0.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 5 in. | [5 empty] | 580
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 6 1/2 in. | StandardOpaqueMaterial | Rough | 6.5 | 0.3 | 21.66666667 | 0.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 6 1/2 in. | [5 empty] | 583
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 6 in. | StandardOpaqueMaterial | Rough | 6 | 0.3 | 20 | 0.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 6 in. | [5 empty] | 582
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 3 1/2 in. | StandardOpaqueMaterial | Rough | 3.5 | 0.20004 | 17.4965007 | 3 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 3 1/2 in. | [5 empty] | 584
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 4 1/2 in. | StandardOpaqueMaterial | Rough | 4.5 | 0.20004 | 22.4955009 | 3 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 4 1/2 in. | [5 empty] | 586
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 4 in. | StandardOpaqueMaterial | Rough | 4 | 0.20004 | 19.9960008 | 3 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 4 in. | [5 empty] | 585
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 5 1/2 in. | StandardOpaqueMaterial | Rough | 5.5 | 0.20004 | 27.4945011 | 3 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 5 1/2 in. | [5 empty] | 588
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 5 in. | StandardOpaqueMaterial | Rough | 5 | 0.20004 | 24.995001 | 3 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 5 in. | [5 empty] | 587
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 6 1/2 in. | StandardOpaqueMaterial | Rough | 6.5 | 0.20004 | 32.4935013 | 3 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 6 1/2 in. | [5 empty] | 590
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 6 in. | StandardOpaqueMaterial | Rough | 6 | 0.20004 | 29.9940012 | 3 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 6 in. | [5 empty] | 589
Std Wood 6 in. | StandardOpaqueMaterial | MediumSmooth | 5.9055 | 0.83202 | 7.097829176 | 33.7111 | 0.289 | 0.9 | 0.7 | 0.7 | [25 empty] | 1210
Steel Frame NonRes Wall Insulation-0.73 | StandardOpaqueMaterial | MediumRough | 0.79836 | 0.33974 | 2.34990258 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 216
Steel Frame Wall Insulation R-1.02 IP | StandardOpaqueMaterial | MediumRough | 0.34789 | 0.33974 | 1.023991182 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 243
Steel Frame/Cavity | StandardOpaqueMaterial | MediumRough | 3.5 | 0.58322 | 6.001206697 | 40.04 | 0.11992 | 0.9 | 0.7 | 0.7 | [25 empty] | 1211
Stone - 1 in. | StandardOpaqueMaterial | MediumRough | 1 | 12.504 | 0.07997440819 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | CEC Doug | Masonry Materials | Stone - 1 in. | [5 empty] | 604
Straw Bale - Int and Ext Stucco - 18 in. | StandardOpaqueMaterial | Smooth | 19.5 | 0.6504 | 29.98154982 | 12.95 | 0.11 | [19 empty] | CEC Title24-2013 | JA4-10 | Straw Bale Wall | Straw Bale - Int and Ext Stucco - 18 in. | [5 empty] | 883
Structural Glazing - Double glass with no low e coatings - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.81 | 2.802469136 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - No Ins. | [5 empty] | 867
Structural Glazing - Double glass with no low e coatings - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.5304 | 6.165158371 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R10 Ins. | [5 empty] | 870
Structural Glazing - Double glass with no low e coatings - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.64764 | 6.901982583 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R15 Ins. | [5 empty] | 871
Structural Glazing - Double glass with no low e coatings - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.7704 | 7.359813084 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R20 Ins. | [5 empty] | 872
Structural Glazing - Double glass with no low e coatings - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 0.8904 | 7.715633423 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R25 Ins. | [5 empty] | 873
Structural Glazing - Double glass with no low e coatings - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.02 | 7.911764706 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R30 Ins. | [5 empty] | 874
Structural Glazing - Double glass with no low e coatings - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.39 | 4.692307692 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R4 Ins. | [5 empty] | 868
Structural Glazing - Double glass with no low e coatings - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.4596 | 5.548302872 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R7 Ins. | [5 empty] | 869
Structural Glazing - Single glass pane. stone. or metal pane - No Ins. | StandardOpaqueMaterial | Smooth | 2.52 | 1.2804 | 1.968134958 | 41.9 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - No Ins. | [5 empty] | 859
Structural Glazing - Single glass pane. stone. or metal pane - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.52 | 0.5904 | 5.962059621 | 30.2 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R10 Ins. | [5 empty] | 862
Structural Glazing - Single glass pane. stone. or metal pane - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.72 | 0.6996 | 6.746712407 | 22.79 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R15 Ins. | [5 empty] | 863
Structural Glazing - Single glass pane. stone. or metal pane - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.92 | 0.81324 | 7.27952388 | 18.37 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R20 Ins. | [5 empty] | 864
Structural Glazing - Single glass pane. stone. or metal pane - R25 Ins. | StandardOpaqueMaterial | Smooth | 7.12 | 0.93372 | 7.625412329 | 15.45 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R25 Ins. | [5 empty] | 865
Structural Glazing - Single glass pane. stone. or metal pane - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.32 | 1.05 | 7.923809524 | 13.37 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R30 Ins. | [5 empty] | 866
Structural Glazing - Single glass pane. stone. or metal pane - R4 Ins. | StandardOpaqueMaterial | Smooth | 2.08 | 0.48624 | 4.277722935 | 50.36 | 0.25 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R4 Ins. | [5 empty] | 860
Structural Glazing - Single glass pane. stone. or metal pane - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.8 | 0.5304 | 5.279034691 | 37.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R7 Ins. | [5 empty] | 861
Structural Glazing - Triple or low e glass - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.6504 | 3.490159902 | 29.09 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - No Ins. | [5 empty] | 875
Structural Glazing - Triple or low e glass - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.51 | 6.411764706 | 20.44 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R10 Ins. | [5 empty] | 878
Structural Glazing - Triple or low e glass - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.63636 | 7.024325853 | 15.23 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R15 Ins. | [5 empty] | 879
Structural Glazing - Triple or low e glass - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.76476 | 7.414090695 | 12.22 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R20 Ins. | [5 empty] | 880
Structural Glazing - Triple or low e glass - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 0.88404 | 7.771141577 | 10.26 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R25 Ins. | [5 empty] | 881
Structural Glazing - Triple or low e glass - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.0104 | 7.986935867 | 8.88 | 0.27 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R30 Ins. | [5 empty] | 882
Structural Glazing - Triple or low e glass - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.36 | 5.083333333 | 35.69 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R4 Ins. | [5 empty] | 876
Structural Glazing - Triple or low e glass - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.43836 | 5.8171366 | 25.92 | 0.26 | [19 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R7 Ins. | [5 empty] | 877
Stucco - 3/8 in. | StandardOpaqueMaterial | Smooth | 0.38 | 5.0004 | 0.07599392049 | 115.81 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Stucco - 3/8 in. | [5 empty] | 680
Stucco - 7/8 in. | StandardOpaqueMaterial | Smooth | 0.88 | 4.86 | 0.1810699588 | 115.81 | 0.2 | [19 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Stucco - 7/8 in. | [5 empty] | 681
Synthetic Stucco - EIFS finish - 1 in. | StandardOpaqueMaterial | Smooth | 1 | 0.2496 | 4.006410256 | 1.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Synthetic Stucco - EIFS finish - 1 in. | [5 empty] | 343
Synthetic Stucco - EIFS finish - 1 in. | StandardOpaqueMaterial | Smooth | 1 | 0.2496 | 4.006410256 | 1.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Masonry Materials | Synthetic Stucco - EIFS finish - 1 in. | [5 empty] | 607
Synthetic Stucco - EIFS finish - 1 in. | StandardOpaqueMaterial | Smooth | 1 | 0.2496 | 4.006410256 | 1.5 | 0.35 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Synthetic Stucco - EIFS finish - 1 in. | [5 empty] | 682
Terrazzo - 1 in. | StandardOpaqueMaterial | Rough | 1 | 12.5004 | 0.07999744008 | 160 | 0.19 | [19 empty] | CEC Title24-2013 | AEC | Finish Materials | Terrazzo - 1 in. | [5 empty] | 404
Terrazzo - 1 in. | StandardOpaqueMaterial | MediumRough | 1 | 12.504 | 0.07997440819 | 139.78 | 0.22 | [19 empty] | CEC Title24-2013 | CEC Doug | Masonry Materials | Terrazzo - 1 in. | [5 empty] | 608
Theoretical Glass [167] | StandardGlazing |  | 0.11811 | 14.6109 | 0.068442 | [9 empty] | SpectralAverage | 0.2374 | 0.7126 | 0.7126 | 0.2512 | 0.6988 | 0.6988 | 0 | 0.985 | 0.985 | 1 | FALSE | [9 empty] | 249
Theoretical Glass [197] | StandardGlazing |  | 0.11811 | 0.28774 | 3.4754 | [9 empty] | SpectralAverage | 0.2349 | 0.7151 | 0.7151 | 0.2512 | 0.6988 | 0.6988 | 0 | 0.9 | 0.9 | 1 | FALSE | [9 empty] | 250
Theoretical Glass [202] | StandardGlazing |  | 0.11811 | 0.13312 | 7.5119 | [9 empty] | SpectralAverage | 0.2325 | 0.7175 | 0.7175 | 0.3192 | 0.6308 | 0.6308 | 0 | 0.9 | 0.9 | 1 | FALSE | [9 empty] | 251
Theoretical Glass [207] | StandardGlazing |  | 0.11811 | 0.092215 | 10.8442 | [9 empty] | SpectralAverage | 0.3311 | 0.6189 | 0.6189 | 0.44 | 0.51 | 0.51 | 0 | 0.9 | 0.9 | 1 | FALSE | [9 empty] | 252
Theoretical Glass [216] | StandardGlazing |  | 0.11811 | 0.092215 | 10.8442 | [9 empty] | SpectralAverage | 0.3801 | 0.5699 | 0.5699 | 0.5079 | 0.4421 | 0.4421 | 0 | 0.9 | 0.9 | 1 | FALSE | [9 empty] | 253
Theoretical Glass [221] | StandardGlazing |  | 0.11811 | 0.061708 | 16.2054 | [9 empty] | SpectralAverage | 0.4296 | 0.5204 | 0.5204 | 0.4503 | 0.4997 | 0.4997 | 0 | 0.9 | 0.9 | 1 | FALSE | [9 empty] | 254
Theoretical Glass 297 | StandardGlazing |  | 0.11811 | 0.071804 | 13.9269 | [9 empty] | SpectralAverage | 0.37504 | 0.57496 | 0.57496 | 0.5297 | 0.4203 | 0.4203 | 0 | 0.9 | 0.9 | 1 | FALSE | [9 empty] | 1348
Theoretical Glass 347 | StandardGlazing |  | 0.11811 | 0.071817 | 13.9243 | [9 empty] | SpectralAverage | 0.31586 | 0.63414 | 0.63414 | 0.47991 | 0.47009 | 0.47009 | 0 | 0.9 | 0.9 | 1 | FALSE | [9 empty] | 1349
Tile Gap - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 0.6612 | 1.13430127 | 70 | 0.24 | [19 empty] | CEC Title24-2013 | CEC Bruce | Roofing | Tile Gap - 3/4 in. | [5 empty] | 700
Typical Air Wall | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7 | [25 empty] | 1212
Typical Carpet Pad | MasslessOpaqueMaterial | VeryRough |  |  | 1.2292 |  |  | 0.9 | 0.7 | 0.8 | [25 empty] | 1213
Typical Insulation | MasslessOpaqueMaterial | MediumSmooth |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7 | [25 empty] | 1214
U 0.52 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 0.52 | 0.39 | 0.31
U 0.52 SHGC 0.49 Simple Glazing | SimpleGlazing | [10 empty] | 0.52 | 0.49 | 0.41
U 0.52 SHGC 0.615 Simple Glazing | SimpleGlazing | [10 empty] | 0.52 | 0.615 | 0.41
U 0.58 SHGC 0.19 Simple Glazing | SimpleGlazing | [10 empty] | 0.58 | 0.19 | 0.15
U 0.58 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 0.58 | 0.36 | 0.25
U 0.59 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 0.59 | 0.36 | 0.27
U 0.59 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 0.59 | 0.39 | 0.31
U 0.61 SHGC 0.77 Simple Glazing | SimpleGlazing | [10 empty] | 0.61 | 0.77 | 0.6
U 0.62 SHGC 0.41 Simple Glazing | SimpleGlazing | 1.22 | 0.54 | 0.38 | [7 empty] | 0.62 | 0.41 | 0.32
U 0.65 SHGC 0.35 Simple Glazing | SimpleGlazing | [10 empty] | 0.65 | 0.35 | 0.25
U 0.69 SHGC 0.19 Simple Glazing | SimpleGlazing | [10 empty] | 0.69 | 0.19 | 0.15
U 0.69 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 0.69 | 0.36 | 0.23
U 0.69 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 0.69 | 0.39 | 0.23
U 0.69 SHGC 0.49 Simple Glazing | SimpleGlazing | [10 empty] | 0.69 | 0.49 | 0.38
U 0.69 SHGC 0.64 Simple Glazing | SimpleGlazing | [10 empty] | 0.69 | 0.64 | 0.55
U 0.69 SHGC 0.68 Simple Glazing | SimpleGlazing | [10 empty] | 0.69 | 0.68 | 0.55
U 0.72 SHGC 0.25 Simple Glazing | SimpleGlazing | [10 empty] | 0.72 | 0.25 | 0.13
U 0.72 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 0.72 | 0.36 | 0.23
U 0.72 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 0.72 | 0.39 | 0.23
U 0.74 SHGC 0.55 Simple Glazing | SimpleGlazing | [10 empty] | 0.74 | 0.55 | 0.4
U 0.74 SHGC 0.65 Simple Glazing | SimpleGlazing | [10 empty] | 0.74 | 0.65 | 0.55
U 0.75 SHGC 0.35 Simple Glazing | SimpleGlazing | [10 empty] | 0.75 | 0.35 | 0.23
U 0.81 SHGC 0.65 Simple Glazing | SimpleGlazing | [10 empty] | 0.81 | 0.65 | 0.55
U 0.85 SHGC 0.65 Simple Glazing | SimpleGlazing | [10 empty] | 0.85 | 0.65 | 0.55
U 0.87 SHGC 0.58 Simple Glazing | SimpleGlazing | [10 empty] | 0.87 | 0.58 | 0.55
U 0.87 SHGC 0.71 Simple Glazing | SimpleGlazing | [10 empty] | 0.87 | 0.71 | 0.6
U 0.87 SHGC 0.77 Simple Glazing | SimpleGlazing | [10 empty] | 0.87 | 0.77 | 0.6
U 0.98 SHGC 0.19 Simple Glazing | SimpleGlazing | [10 empty] | 0.98 | 0.19 | 0.15
U 0.98 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 0.98 | 0.36 | 0.25
U 1.10 SHGC 0.62 Simple Glazing | SimpleGlazing | [10 empty] | 1.1 | 0.62 | 0.55
U 1.10 SHGC 0.77 Simple Glazing | SimpleGlazing | [10 empty] | 1.1 | 0.77 | 0.6
U 1.15 SHGC 0.77 Simple Glazing | SimpleGlazing | [10 empty] | 1.15 | 0.77 | 0.6
U 1.17 SHGC 0.19 Simple Glazing | SimpleGlazing | [10 empty] | 1.17 | 0.19 | 0.15
U 1.17 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 1.17 | 0.36 | 0.23
U 1.17 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 1.17 | 0.39 | 0.23
U 1.17 SHGC 0.49 Simple Glazing | SimpleGlazing | [10 empty] | 1.17 | 0.49 | 0.38
U 1.17 SHGC 0.64 Simple Glazing | SimpleGlazing | [10 empty] | 1.17 | 0.64 | 0.55
U 1.17 SHGC 0.68 Simple Glazing | SimpleGlazing | [10 empty] | 1.17 | 0.68 | 0.55
U 1.22 SHGC 0.25 Simple Glazing | SimpleGlazing | [10 empty] | 1.22 | 0.25 | 0.11
U 1.22 SHGC 0.54 Simple Glazing | SimpleGlazing | [10 empty] | 1.22 | 0.54 | 0.38
U 1.30 SHGC 0.27 Simple Glazing | SimpleGlazing | [10 empty] | 1.3 | 0.27 | 0.25
U 1.30 SHGC 0.34 Simple Glazing | SimpleGlazing | [10 empty] | 1.3 | 0.34 | 0.25
U 1.30 SHGC 0.62 Simple Glazing | SimpleGlazing | [10 empty] | 1.3 | 0.62 | 0.55
U 1.30 SHGC 0.65 Simple Glazing | SimpleGlazing | [10 empty] | 1.3 | 0.65 | 0.55
U 1.36 SHGC 0.19 Simple Glazing | SimpleGlazing | [10 empty] | 1.36 | 0.19 | 0.15
U 1.36 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 1.36 | 0.36 | 0.23
U 1.36 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 1.36 | 0.39 | 0.23
U 1.36 SHGC 0.61 Simple Glazing | SimpleGlazing | [10 empty] | 1.36 | 0.61 | 0.23
U 1.70 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 1.7 | 0.36 | 0.23
U 1.80 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 1.8 | 0.36 | 0.23
U 1.90 SHGC 0.27 Simple Glazing | SimpleGlazing | [10 empty] | 1.9 | 0.27 | 0.25
U 1.90 SHGC 0.34 Simple Glazing | SimpleGlazing | [10 empty] | 1.9 | 0.34 | 0.25
U 1.90 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 1.9 | 0.39 | 0.25
U 1.90 SHGC 0.65 Simple Glazing | SimpleGlazing | [10 empty] | 1.9 | 0.65 | 0.25
U 1.98 SHGC 0.16 Simple Glazing | SimpleGlazing | [10 empty] | 1.98 | 0.16 | 0.15
U 1.98 SHGC 0.19 Simple Glazing | SimpleGlazing | [10 empty] | 1.98 | 0.19 | 0.15
U 1.98 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 1.98 | 0.36 | 0.25
U 1.98 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 1.98 | 0.39 | 0.25
U 1.98 SHGC 0.61 Simple Glazing | SimpleGlazing | [10 empty] | 1.98 | 0.61 | 0.25
Vapor permeable felt - 1/8 in. | StandardOpaqueMaterial | Rough | 0.13 | 2.0796 | 0.06251202154 | 22 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Building Membrane | Vapor permeable felt - 1/8 in. | [5 empty] | 346
Vapor seal - 2 layers of mopped 15 lb felt - 1/4 in. | StandardOpaqueMaterial | Rough | 0.25 | 2.0796 | 0.120215426 | 22 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Building Membrane | Vapor seal - 2 layers of mopped 15 lb felt - 1/4 in. | [5 empty] | 347
Vapor seal - plastic film - 1/16 in. | StandardOpaqueMaterial | Rough | 0.63 | 62.4996 | 0.01008006451 | 30 | 0.3 | [19 empty] | CEC Title24-2013 | AEC | Building Membrane | Vapor seal - plastic film - 1/16 in. | [5 empty] | 348
Vermiculite aggregate - 45 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 1.7004 | 0.2940484592 | 45 | 0.32 | [19 empty] | CEC Title24-2013 | AEC | Plastering Materials | Vermiculite aggregate - 45 lb/ft3 - 1/2 in. | [5 empty] | 679
Wall Insulation [31] | StandardOpaqueMaterial | MediumRough | 1.3268 | 0.29953 | 4.429571171 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5 | [25 empty] | 255
Wood - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.0404 | 0.9611687812 | 37.94 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Wood - 1 in. | [5 empty] | 894
Wood - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 1.0404 | 0.4805843906 | 37.94 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Wood - 1/2 in. | [5 empty] | 895
Wood - 2 in. | StandardOpaqueMaterial | MediumSmooth | 2 | 1.0404 | 1.922337562 | 37.94 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Wood - 2 in. | [5 empty] | 896
Wood - 4 in. | StandardOpaqueMaterial | MediumSmooth | 4 | 1.0404 | 3.844675125 | 37.94 | 0.39 | [19 empty] | CEC Title24-2013 | AEC | Woods | Wood - 4 in. | [5 empty] | 897
Wood Frame NonRes Wall Insulation-0.73 | StandardOpaqueMaterial | MediumRough | 0.79836 | 0.33974 | 2.34990258 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 270
Wood Frame Wall Insulation R-1.61 IP | StandardOpaqueMaterial | MediumRough | 0.54621 | 0.33974 | 1.607739625 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7 | [25 empty] | 284
Wood Framed Attic Floor - 16inOC - 2x10 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.783 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 11 | 1112
Wood Framed Attic Floor - 16inOC - 2x10 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.4765 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 13 | 1113
Wood Framed Attic Floor - 16inOC - 2x10 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.1561 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 19 | 1114
Wood Framed Attic Floor - 16inOC - 2x10 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 18.5953 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 21 | 1115
Wood Framed Attic Floor - 16inOC - 2x10 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 19.2942 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 22 | 1116
Wood Framed Attic Floor - 16inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 21.3129 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 25 | 1117
Wood Framed Attic Floor - 16inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 24.4379 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 30 | 1118
Wood Framed Attic Floor - 16inOC - 2x10 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 28.8982 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 38 | 1119
Wood Framed Attic Floor - 16inOC - 2x10 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 31.873 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 44 | 1120
Wood Framed Attic Floor - 16inOC - 2x10 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 34.1444 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 49 | 1121
Wood Framed Attic Floor - 16inOC - 2x10 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 38.5802 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 60 | 1122
Wood Framed Attic Floor - 16inOC - 2x12 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 11.0136 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 11 | 1134
Wood Framed Attic Floor - 16inOC - 2x12 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.7862 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 13 | 1135
Wood Framed Attic Floor - 16inOC - 2x12 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.7471 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 19 | 1136
Wood Framed Attic Floor - 16inOC - 2x12 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 19.2917 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 21 | 1137
Wood Framed Attic Floor - 16inOC - 2x12 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 20.045 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 22 | 1138
Wood Framed Attic Floor - 16inOC - 2x12 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 22.2328 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 25 | 1139
Wood Framed Attic Floor - 16inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 25.6551 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 30 | 1140
Wood Framed Attic Floor - 16inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 30.6158 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 38 | 1141
Wood Framed Attic Floor - 16inOC - 2x12 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 33.9752 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 44 | 1142
Wood Framed Attic Floor - 16inOC - 2x12 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 36.5684 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 49 | 1143
Wood Framed Attic Floor - 16inOC - 2x12 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 41.7037 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 60 | 1144
Wood Framed Attic Floor - 16inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.0352 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 11 | 1046
Wood Framed Attic Floor - 16inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 10.1946 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 13 | 1047
Wood Framed Attic Floor - 16inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 13.1185 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 19 | 1048
Wood Framed Attic Floor - 16inOC - 2x4 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 13.9437 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 21 | 1049
Wood Framed Attic Floor - 16inOC - 2x4 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 14.333 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 22 | 1050
Wood Framed Attic Floor - 16inOC - 2x4 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 15.4178 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 25 | 1051
Wood Framed Attic Floor - 16inOC - 2x4 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 16.9895 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 30 | 1052
Wood Framed Attic Floor - 16inOC - 2x4 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 19.0316 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 38 | 1053
Wood Framed Attic Floor - 16inOC - 2x4 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 20.278 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 44 | 1054
Wood Framed Attic Floor - 16inOC - 2x4 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 21.1742 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 49 | 1055
Wood Framed Attic Floor - 16inOC - 2x4 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 22.7998 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 60 | 1056
Wood Framed Attic Floor - 16inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.9817 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 11 | 1068
Wood Framed Attic Floor - 16inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.416 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 13 | 1069
Wood Framed Attic Floor - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 15.2129 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 19 | 1070
Wood Framed Attic Floor - 16inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 16.3338 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 21 | 1071
Wood Framed Attic Floor - 16inOC - 2x6 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 16.8706 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 22 | 1072
Wood Framed Attic Floor - 16inOC - 2x6 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 18.394 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 25 | 1073
Wood Framed Attic Floor - 16inOC - 2x6 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 20.6759 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 30 | 1074
Wood Framed Attic Floor - 16inOC - 2x6 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 23.7814 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 38 | 1075
Wood Framed Attic Floor - 16inOC - 2x6 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 25.7599 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 44 | 1076
Wood Framed Attic Floor - 16inOC - 2x6 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 27.2236 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 49 | 1077
Wood Framed Attic Floor - 16inOC - 2x6 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 29.9711 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 60 | 1078
Wood Framed Attic Floor - 16inOC - 2x8 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.4438 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 11 | 1090
Wood Framed Attic Floor - 16inOC - 2x8 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.0246 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 13 | 1091
Wood Framed Attic Floor - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.313 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 19 | 1092
Wood Framed Attic Floor - 16inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 17.6089 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 21 | 1093
Wood Framed Attic Floor - 16inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 18.2344 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 22 | 1094
Wood Framed Attic Floor - 16inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 20.0271 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 25 | 1095
Wood Framed Attic Floor - 16inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 22.7622 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 30 | 1096
Wood Framed Attic Floor - 16inOC - 2x8 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 26.584 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 38 | 1097
Wood Framed Attic Floor - 16inOC - 2x8 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 29.0808 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 44 | 1098
Wood Framed Attic Floor - 16inOC - 2x8 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 30.96 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 49 | 1099
Wood Framed Attic Floor - 16inOC - 2x8 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 34.5633 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 60 | 1100
Wood Framed Attic Floor - 24inOC - 2x10 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.8472 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 11 | 1123
Wood Framed Attic Floor - 24inOC - 2x10 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.6291 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 13 | 1124
Wood Framed Attic Floor - 24inOC - 2x10 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.6705 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 19 | 1125
Wood Framed Attic Floor - 24inOC - 2x10 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 19.2568 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 21 | 1126
Wood Framed Attic Floor - 24inOC - 2x10 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 20.0334 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 22 | 1127
Wood Framed Attic Floor - 24inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 22.2995 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 25 | 1128
Wood Framed Attic Floor - 24inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 25.8772 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 30 | 1129
Wood Framed Attic Floor - 24inOC - 2x10 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 31.1355 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 38 | 1130
Wood Framed Attic Floor - 24inOC - 2x10 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 34.7459 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 44 | 1131
Wood Framed Attic Floor - 24inOC - 2x10 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 37.5607 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 49 | 1132
Wood Framed Attic Floor - 24inOC - 2x10 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 43.2077 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 60 | 1133
Wood Framed Attic Floor - 24inOC - 2x12 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 11.0095 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 11 | 1145
Wood Framed Attic Floor - 24inOC - 2x12 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.8496 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 13 | 1146
Wood Framed Attic Floor - 24inOC - 2x12 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 18.1053 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 19 | 1147
Wood Framed Attic Floor - 24inOC - 2x12 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 19.7743 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 21 | 1148
Wood Framed Attic Floor - 24inOC - 2x12 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 20.594 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 22 | 1149
Wood Framed Attic Floor - 24inOC - 2x12 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 22.9964 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 25 | 1150
Wood Framed Attic Floor - 24inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 26.8204 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 30 | 1151
Wood Framed Attic Floor - 24inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 32.5111 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 38 | 1152
Wood Framed Attic Floor - 24inOC - 2x12 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 36.4678 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 44 | 1153
Wood Framed Attic Floor - 24inOC - 2x12 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 39.581 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 49 | 1154
Wood Framed Attic Floor - 24inOC - 2x12 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 45.903 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 60 | 1155
Wood Framed Attic Floor - 24inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.5468 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 11 | 1057
Wood Framed Attic Floor - 24inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 10.9003 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 13 | 1058
Wood Framed Attic Floor - 24inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 14.4614 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 19 | 1059
Wood Framed Attic Floor - 24inOC - 2x4 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 15.5068 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 21 | 1060
Wood Framed Attic Floor - 24inOC - 2x4 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 16.0065 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 22 | 1061
Wood Framed Attic Floor - 24inOC - 2x4 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 17.421 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 25 | 1062
Wood Framed Attic Floor - 24inOC - 2x4 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 19.5305 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 30 | 1063
Wood Framed Attic Floor - 24inOC - 2x4 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 22.3835 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 38 | 1064
Wood Framed Attic Floor - 24inOC - 2x4 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 24.1906 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 44 | 1065
Wood Framed Attic Floor - 24inOC - 2x4 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 25.5222 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 49 | 1066
Wood Framed Attic Floor - 24inOC - 2x4 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 28.0096 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 60 | 1067
Wood Framed Attic Floor - 24inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.2668 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 11 | 1079
Wood Framed Attic Floor - 24inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.8491 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 13 | 1080
Wood Framed Attic Floor - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.1804 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 19 | 1081
Wood Framed Attic Floor - 24inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 17.5004 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 21 | 1082
Wood Framed Attic Floor - 24inOC - 2x6 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 18.1394 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 22 | 1083
Wood Framed Attic Floor - 24inOC - 2x6 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 19.9777 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 25 | 1084
Wood Framed Attic Floor - 24inOC - 2x6 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 22.802 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 30 | 1085
Wood Framed Attic Floor - 24inOC - 2x6 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 26.7885 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 38 | 1086
Wood Framed Attic Floor - 24inOC - 2x6 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 29.4185 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 44 | 1087
Wood Framed Attic Floor - 24inOC - 2x6 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 31.4116 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 49 | 1088
Wood Framed Attic Floor - 24inOC - 2x6 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 35.2661 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 60 | 1089
Wood Framed Attic Floor - 24inOC - 2x8 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.6047 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 11 | 1101
Wood Framed Attic Floor - 24inOC - 2x8 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.3015 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 13 | 1102
Wood Framed Attic Floor - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.0358 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 19 | 1103
Wood Framed Attic Floor - 24inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 18.5054 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 21 | 1104
Wood Framed Attic Floor - 24inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 19.2214 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 22 | 1105
Wood Framed Attic Floor - 24inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 21.298 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 25 | 1106
Wood Framed Attic Floor - 24inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 24.5383 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 30 | 1107
Wood Framed Attic Floor - 24inOC - 2x8 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 29.2172 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 38 | 1108
Wood Framed Attic Floor - 24inOC - 2x8 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 32.3739 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 44 | 1109
Wood Framed Attic Floor - 24inOC - 2x8 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 34.804 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 49 | 1110
Wood Framed Attic Floor - 24inOC - 2x8 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 39.5997 | [21 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 60 | 1111
Wood Framed Floor - 16inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 21.3129 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 9_25In | 2x10 | 25 | 1035
Wood Framed Floor - 16inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 24.4379 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 9_25In | 2x10 | 30 | 1036
Wood Framed Floor - 16inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 30.6158 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 11_25In | 2x12 | 38 | 1037
Wood Framed Floor - 16inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.9817 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 5_5In | 2x6 | 11 | 1030
Wood Framed Floor - 16inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.416 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 5_5In | 2x6 | 13 | 1031
Wood Framed Floor - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 15.2129 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 5_5In | 2x6 | 19 | 1032
Wood Framed Floor - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.313 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 7_25In | 2x8 | 19 | 1033
Wood Framed Floor - 16inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 18.2344 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 7_25In | 2x8 | 22 | 1034
Wood Framed Floor - 24inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 22.2995 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 9_25In | 2x10 | 25 | 1043
Wood Framed Floor - 24inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 25.8772 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 9_25In | 2x10 | 30 | 1044
Wood Framed Floor - 24inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 32.5111 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 11_25In | 2x12 | 38 | 1045
Wood Framed Floor - 24inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.2668 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 5_5In | 2x6 | 11 | 1038
Wood Framed Floor - 24inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.8491 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 5_5In | 2x6 | 13 | 1039
Wood Framed Floor - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.1804 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 5_5In | 2x6 | 19 | 1040
Wood Framed Floor - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.0358 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 7_25In | 2x8 | 19 | 1041
Wood Framed Floor - 24inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 19.2214 | [21 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 7_25In | 2x8 | 22 | 1042
Wood Framed Rafter Roof - 16inOC - 2x10 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 19.2942 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 9_25In | 2x10 | 22 | 1167
Wood Framed Rafter Roof - 16inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 21.3129 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 9_25In | 2x10 | 25 | 1168
Wood Framed Rafter Roof - 16inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 24.4379 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 9_25In | 2x10 | 30 | 1169
Wood Framed Rafter Roof - 16inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 25.6551 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 11_25In | 2x12 | 30 | 1170
Wood Framed Rafter Roof - 16inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 30.6158 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 11_25In | 2x12 | 38 | 1171
Wood Framed Rafter Roof - 16inOC - 2x14 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 30.6158 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 11_25In | 2x14 | 38 | 1172
Wood Framed Rafter Roof - 16inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.0352 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 3_5In | 2x4 | 11 | 1156
Wood Framed Rafter Roof - 16inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 10.1946 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 3_5In | 2x4 | 13 | 1157
Wood Framed Rafter Roof - 16inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 11.2537 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 3_5In | 2x4 | 15 | 1158
Wood Framed Rafter Roof - 16inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 13.1185 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 3_5In | 2x4 | 19 | 1159
Wood Framed Rafter Roof - 16inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.9817 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 5_5In | 2x6 | 11 | 1160
Wood Framed Rafter Roof - 16inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.416 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 5_5In | 2x6 | 13 | 1161
Wood Framed Rafter Roof - 16inOC - 2x6 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 12.7607 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 5_5In | 2x6 | 15 | 1162
Wood Framed Rafter Roof - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 15.2129 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 5_5In | 2x6 | 19 | 1163
Wood Framed Rafter Roof - 16inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 16.3338 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 5_5In | 2x6 | 21 | 1164
Wood Framed Rafter Roof - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.313 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 7_25In | 2x8 | 19 | 1165
Wood Framed Rafter Roof - 16inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 17.6089 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 7_25In | 2x8 | 21 | 1166
Wood Framed Rafter Roof - 24inOC - 2x10 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 20.0334 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 9_25In | 2x10 | 22 | 1184
Wood Framed Rafter Roof - 24inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 22.2995 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 9_25In | 2x10 | 25 | 1185
Wood Framed Rafter Roof - 24inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 25.8772 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 9_25In | 2x10 | 30 | 1186
Wood Framed Rafter Roof - 24inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 26.8204 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 11_25In | 2x12 | 30 | 1187
Wood Framed Rafter Roof - 24inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 32.5111 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 11_25In | 2x12 | 38 | 1188
Wood Framed Rafter Roof - 24inOC - 2x14 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 32.5111 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 11_25In | 2x14 | 38 | 1189
Wood Framed Rafter Roof - 24inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.5468 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 3_5In | 2x4 | 11 | 1173
Wood Framed Rafter Roof - 24inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 10.9003 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 3_5In | 2x4 | 13 | 1174
Wood Framed Rafter Roof - 24inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 12.1652 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 3_5In | 2x4 | 15 | 1175
Wood Framed Rafter Roof - 24inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 14.4614 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 3_5In | 2x4 | 19 | 1176
Wood Framed Rafter Roof - 24inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.2668 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 5_5In | 2x6 | 11 | 1177
Wood Framed Rafter Roof - 24inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.8491 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 5_5In | 2x6 | 13 | 1178
Wood Framed Rafter Roof - 24inOC - 2x6 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 13.359 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 5_5In | 2x6 | 15 | 1179
Wood Framed Rafter Roof - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.1804 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 5_5In | 2x6 | 19 | 1180
Wood Framed Rafter Roof - 24inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 17.5004 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 5_5In | 2x6 | 21 | 1181
Wood Framed Rafter Roof - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.0358 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 7_25In | 2x8 | 19 | 1182
Wood Framed Rafter Roof - 24inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 18.5054 | [21 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 7_25In | 2x8 | 21 | 1183
Wood Framed Wall - 16inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 7.126 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 3_5In | 2x4 | 11 | 990
Wood Framed Wall - 16inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 7.7016 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 3_5In | 2x4 | 13 | 991
Wood Framed Wall - 16inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 8.1867 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 3_5In | 2x4 | 15 | 992
Wood Framed Wall - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 11.7113 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 5_5In | 2x6 | 19 | 993
Wood Framed Wall - 16inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 12.2507 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 5_5In | 2x6 | 21 | 994
Wood Framed Wall - 16inOC - 2x6 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 12.4993 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 5_5In | 2x6 | 22 | 995
Wood Framed Wall - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 13.4581 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 7_25In | 2x8 | 19 | 996
Wood Framed Wall - 16inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 14.5092 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 7_25In | 2x8 | 22 | 997
Wood Framed Wall - 16inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 15.4247 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 7_25In | 2x8 | 25 | 998
Wood Framed Wall - 16inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 16.7137 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 7_25In | 2x8 | 30 | 999
Wood Framed Wall - 24inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 7.4404 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 3_5In | 2x4 | 11 | 1000
Wood Framed Wall - 24inOC - 2x4 - R11 ins. AWS | MasslessOpaqueMaterial |  |  |  | 8.0311 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 3_5In | 2x4 | 11 | 1010
Wood Framed Wall - 24inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 8.0977 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 3_5In | 2x4 | 13 | 1001
Wood Framed Wall - 24inOC - 2x4 - R13 ins. AWS | MasslessOpaqueMaterial |  |  |  | 8.8567 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 3_5In | 2x4 | 13 | 1011
Wood Framed Wall - 24inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 8.6586 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 3_5In | 2x4 | 15 | 1002
Wood Framed Wall - 24inOC - 2x4 - R15 ins. AWS | MasslessOpaqueMaterial |  |  |  | 9.579 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 3_5In | 2x4 | 15 | 1012
Wood Framed Wall - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 12.2765 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 5_5In | 2x6 | 19 | 1003
Wood Framed Wall - 24inOC - 2x6 - R19 ins. AWS | MasslessOpaqueMaterial |  |  |  | 13.3502 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 5_5In | 2x6 | 19 | 1013
Wood Framed Wall - 24inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 12.8954 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 5_5In | 2x6 | 21 | 1004
Wood Framed Wall - 24inOC - 2x6 - R21 ins. AWS | MasslessOpaqueMaterial |  |  |  | 14.1353 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 5_5In | 2x6 | 21 | 1014
Wood Framed Wall - 24inOC - 2x6 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 13.1824 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 5_5In | 2x6 | 22 | 1005
Wood Framed Wall - 24inOC - 2x6 - R22 ins. AWS | MasslessOpaqueMaterial |  |  |  | 14.5036 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 5_5In | 2x6 | 22 | 1015
Wood Framed Wall - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 13.9462 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 7_25In | 2x8 | 19 | 1006
Wood Framed Wall - 24inOC - 2x8 - R19 ins. AWS | MasslessOpaqueMaterial |  |  |  | 14.8435 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 7_25In | 2x8 | 19 | 1016
Wood Framed Wall - 24inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 15.1272 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 7_25In | 2x8 | 22 | 1007
Wood Framed Wall - 24inOC - 2x8 - R22 ins. AWS | MasslessOpaqueMaterial |  |  |  | 16.2834 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 7_25In | 2x8 | 22 | 1017
Wood Framed Wall - 24inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 16.1678 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 7_25In | 2x8 | 25 | 1008
Wood Framed Wall - 24inOC - 2x8 - R25 ins. AWS | MasslessOpaqueMaterial |  |  |  | 17.5793 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 7_25In | 2x8 | 25 | 1018
Wood Framed Wall - 24inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 17.6518 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 7_25In | 2x8 | 30 | 1009
Wood Framed Wall - 24inOC - 2x8 - R30 ins. AWS | MasslessOpaqueMaterial |  |  |  | 19.4735 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 7_25In | 2x8 | 30 | 1019
Wood Framed Wall - 48inOC - 2x4 - R11 ins. AWS | MasslessOpaqueMaterial |  |  |  | 10.1197 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 3_5In | 2x4 | 11 | 1020
Wood Framed Wall - 48inOC - 2x4 - R13 ins. AWS | MasslessOpaqueMaterial |  |  |  | 11.711 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 3_5In | 2x4 | 13 | 1021
Wood Framed Wall - 48inOC - 2x4 - R15 ins. AWS | MasslessOpaqueMaterial |  |  |  | 13.2373 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 3_5In | 2x4 | 15 | 1022
Wood Framed Wall - 48inOC - 2x6 - R19 ins. AWS | MasslessOpaqueMaterial |  |  |  | 17.2794 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 5_5In | 2x6 | 19 | 1023
Wood Framed Wall - 48inOC - 2x6 - R21 ins. AWS | MasslessOpaqueMaterial |  |  |  | 18.8464 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 5_5In | 2x6 | 21 | 1024
Wood Framed Wall - 48inOC - 2x6 - R22 ins. AWS | MasslessOpaqueMaterial |  |  |  | 19.6146 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 5_5In | 2x6 | 22 | 1025
Wood Framed Wall - 48inOC - 2x8 - R19 ins. AWS | MasslessOpaqueMaterial |  |  |  | 17.8255 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 7_25In | 2x8 | 19 | 1026
Wood Framed Wall - 48inOC - 2x8 - R22 ins. AWS | MasslessOpaqueMaterial |  |  |  | 20.3213 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 7_25In | 2x8 | 22 | 1027
Wood Framed Wall - 48inOC - 2x8 - R25 ins. AWS | MasslessOpaqueMaterial |  |  |  | 22.7412 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 7_25In | 2x8 | 25 | 1028
Wood Framed Wall - 48inOC - 2x8 - R30 ins. AWS | MasslessOpaqueMaterial |  |  |  | 26.6149 | [21 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 7_25In | 2x8 | 30 | 1029
Wood shingles - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 0.8304 | 0.9031791908 | 36.94 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Wood shingles - 3/4 in. | [5 empty] | 339
Wood shingles - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 0.8304 | 0.9031791908 | 36.94 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Wood shingles - 3/4 in. | [5 empty] | 701
Wood shingles - plain and plastic film faced - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 0.8004 | 0.9370314843 | 22 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Wood shingles - plain and plastic film faced - 3/4 in. | [5 empty] | 340
Wood shingles - plain and plastic film faced - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 0.8004 | 0.9370314843 | 22 | 0.31 | [19 empty] | CEC Title24-2013 | AEC | Roofing | Wood shingles - plain and plastic film faced - 3/4 in. | [5 empty] | 702
Wood Siding | StandardOpaqueMaterial | MediumSmooth | 0.3937 | 0.76268 | 0.5162057583 | 33.9995 | 0.289 | 0.9 | 0.78 | 0.78 | [25 empty] | 289
Wood siding - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.6204 | 0.805931657 | 36.94 | 0.28 | [19 empty] | CEC Title24-2013 | AEC | Woods | Wood siding - 1/2 in. | [5 empty] | 898

## Schedules
Each row represents the efficiency standards for a specificy type of chiller
Day Type choices: Default, Wkdy, Wknd, Mon, Tue, Wed, Thu, Fri, Sat, Sun, WntrDsn, SmrDsn, Hol
Name | Category | Units | Day Types | Start Date | End Date | Type | Hr 1 | Hr 2 | Hr 3 | Hr 4 | Hr 5 | Hr 6 | Hr 7 | Hr 8 | Hr 9 | Hr 10 | Hr 11 | Hr 12 | Hr 13 | Hr 14 | Hr 15 | Hr 16 | Hr 17 | Hr 18 | Hr 19 | Hr 20 | Hr 21 | Hr 22 | Hr 23 | Hr 24 | Notes
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Always Off | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 95 | [23 empty] | From DOE Prototype Buildings
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Always Off | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29 | From DOE Prototype Buildings
Always Off | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
Always Off | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Always Off | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 29.4 | [23 empty] | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 23.9 | [23 empty] | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 29.4 | [23 empty] | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 29.4 | [23 empty] | From DOE Prototype Buildings
Always Off | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Always Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Always On | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise COMPACT HVAC-ALWAYS 4 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
ApartmentHighRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise EQP_APT_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58 | From DOE Prototype Buildings
ApartmentHighRise EQP_OFF_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise EQP_OFF_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | From DOE Prototype Buildings
ApartmentHighRise Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise Exterior_Ltg_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_DESIGN_OFF_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_No_Optimum | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_No_Optimum | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentHighRise INF_APT_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise INF_COR_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise INF_OFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0 | From DOE Prototype Buildings
ApartmentHighRise LTG_APT_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.06 | 0.13 | 0.14 | 0.13 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.14 | 0.2 | 0.27 | 0.32 | 0.32 | 0.22 | 0.12 | 0.05 | From DOE Prototype Buildings
ApartmentHighRise LTG_COR_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise LTG_OFF_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.18 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise LTG_OFF_SCH | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise LTG_OFF_SCH | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise LTG_OFF_SCH | Unknown |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | From DOE Prototype Buildings
ApartmentHighRise N CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise N HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise OCC_APT_SCH | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1 | From DOE Prototype Buildings
ApartmentHighRise OCC_OFF_SCH | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise OCC_OFF_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
ApartmentHighRise PLANT LOOP HIGH TEMP SCHEDULE | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANT LOOP LOW TEMP SCHEDULE | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 20 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown |  | Wknd¦Wkdy | 2014-10-18 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown |  | Wknd¦Wkdy | 2014-01-01 | 2014-05-08 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTHEATINGONSCHED | Unknown |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTHEATINGONSCHED | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTHEATINGONSCHED | Unknown |  | Wknd¦Wkdy | 2014-10-18 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PLANTHEATINGONSCHED | Unknown |  | Wknd¦Wkdy | 2014-01-01 | 2014-05-08 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise S CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise S HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SHW Latent fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SHW Sensible fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SHW SUPPLY TEMP SCHED | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SHW TARGET TEMP SCHED | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
ApartmentHighRise Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise SupplyFanSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 2 | [23 empty] | From DOE Prototype Buildings
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown |  | Wkdy | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise Activity Schedule | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 95 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise All Off | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise All On | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise APT_DHW_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29 | From DOE Prototype Buildings
ApartmentMidRise BLDG_ELEVATORS Pre2004 | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
ApartmentMidRise BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
ApartmentMidRise BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24.4 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.4 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_No_Setback | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.9 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_No_Setback | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.4 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise CLGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Prototype Buildings
ApartmentMidRise COMPACT HVAC-ALWAYS 0 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise COMPACT HVAC-ALWAYS 1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise COMPACT HVAC-ALWAYS 18.3333338190008 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.3333 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise COMPACT HVAC-ALWAYS 4 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise Constant Mains Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
ApartmentMidRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise EQP_APT_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58 | From DOE Prototype Buildings
ApartmentMidRise EQP_OFF_SCH_Pre2004 | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise EQP_OFF_SCH_Pre2004 | Equipment |  | Wkdy¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | From DOE Prototype Buildings
ApartmentMidRise EQP_OFF_SCH_2004_2007 | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise EQP_OFF_SCH_2004_2007 | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | From DOE Prototype Buildings
ApartmentMidRise EQP_OFF_SCH_2010_2013 | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.21863 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise EQP_OFF_SCH_2010_2013 | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.21863 | 0.21863 | 0.21863 | 0.21863 | 0.21863 | 0.21863 | 0.21863 | 0.33125 | 0.92575 | 0.92575 | 0.92575 | 0.92575 | 0.87021 | 0.92575 | 0.92575 | 0.92575 | 0.92575 | 0.33125 | 0.21863 | 0.21863 | 0.21863 | 0.21863 | 0.21863 | 0.21863 | From DOE Prototype Buildings
ApartmentMidRise Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise Exterior_Ltg_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
ApartmentMidRise Hot Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.7 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentMidRise HTGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
ApartmentMidRise INF_APT_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise INF_COR_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise INF_OFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise INFIL_Door_Opening_SCH_2004_2007 | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0 | From DOE Prototype Buildings
ApartmentMidRise INFIL_Door_Opening_SCH_2010_2013 | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 1 | 0.131 | 0.131 | 0.131 | 0.131 | 0.131 | 0.131 | 0.131 | 0.131 | 0.131 | 1 | 0.131 | 0.131 | 0.131 | 0.131 | 0 | 0 | From DOE Prototype Buildings
ApartmentMidRise LTG_APT_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.06 | 0.13 | 0.14 | 0.13 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.14 | 0.2 | 0.27 | 0.32 | 0.32 | 0.22 | 0.12 | 0.05 | From DOE Prototype Buildings
ApartmentMidRise LTG_COR_SCH_2004_2007 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise LTG_COR_SCH_2010 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.8176 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise LTG_COR_SCH_2013 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.53144 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise LTG_OFF_SCH_2004_2007 | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.18 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise LTG_OFF_SCH_2004_2007 | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise LTG_OFF_SCH_2004_2007 | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise LTG_OFF_SCH_2004_2007 | Unknown |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.76932 | 0.76932 | 0.76932 | 0.76932 | 0.68384 | 0.76932 | 0.76932 | 0.76932 | 0.76932 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | From DOE Prototype Buildings
ApartmentMidRise LTG_OFF_SCH_2010_2013 | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.18 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise LTG_OFF_SCH_2010_2013 | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise LTG_OFF_SCH_2010_2013 | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise LTG_OFF_SCH_2010_2013 | Unknown |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | From DOE Prototype Buildings
ApartmentMidRise N CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise N HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise OCC_APT_SCH | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1 | From DOE Prototype Buildings
ApartmentMidRise OCC_OFF_SCH | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise OCC_OFF_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
ApartmentMidRise S CLGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise S HTGSETP_APT_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
ApartmentMidRise Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
ApartmentMidRise Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
FullServiceRestaurant Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Bldg Equip | Equipment |  | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
FullServiceRestaurant Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | From DOE Reference Buildings
FullServiceRestaurant Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | From DOE Reference Buildings
FullServiceRestaurant Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2 | From DOE Reference Buildings
FullServiceRestaurant Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35 | From DOE Reference Buildings
FullServiceRestaurant Bldg Swh | Service Water Heating |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | From DOE Reference Buildings
FullServiceRestaurant Bldg Swh | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | From DOE Reference Buildings
FullServiceRestaurant Bldg Swh | Service Water Heating |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | From DOE Reference Buildings
FullServiceRestaurant ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Reference Buildings
FullServiceRestaurant ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Reference Buildings
FullServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Gas Equip | Equipment |  | Default¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | From DOE Reference Buildings
FullServiceRestaurant Gas Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Gas Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | From DOE Reference Buildings
FullServiceRestaurant HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | From DOE Reference Buildings
FullServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 19 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
FullServiceRestaurant Infil Half On | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
FullServiceRestaurant Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Hospital Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
Hospital ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
Hospital AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital Bldg ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Reference Buildings
Hospital Bldg ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Reference Buildings
Hospital Bldg ClgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | 25 | [23 empty] | From DOE Reference Buildings
Hospital BLDG ELEVATORS | Elevator |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | From DOE Reference Buildings
Hospital BLDG ELEVATORS | Elevator |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Reference Buildings
Hospital BLDG ELEVATORS | Elevator |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Reference Buildings
Hospital Bldg Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Hospital Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Reference Buildings
Hospital Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Hospital Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Hospital Bldg HtgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Reference Buildings
Hospital Bldg HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Reference Buildings
Hospital Bldg HtgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | 18.3 | [23 empty] | From DOE Reference Buildings
Hospital Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Reference Buildings
Hospital Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Hospital Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Hospital Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Hospital Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Hospital Bldg Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
Hospital Bldg Occ | Occupancy |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Hospital Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Hospital BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_ELEVATORS | Elevator |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital BLDG_ELEVATORS | Elevator |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_EXTD_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_EXTD_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_EQUIP_EXTD_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_EQUIP_EXTD_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_EXTD_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXAM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXAM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXAM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXAM_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXAM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXTD_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXTD_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXTD_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXTD_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_EXTD_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | From DOE Prototype Buildings
Hospital BLDG_OA_FRAC_SCH | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_OA_FRAC_SCH | OA Air |  | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_OCC_EXTD_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_OCC_EXTD_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_OCC_EXTD_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_OCC_EXTD_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_OCC_EXTD_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
Hospital BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_SWH_EXTD_SCH | Service Water Heating |  | Default¦WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
Hospital BLDG_SWH_EXTD_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
Hospital BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0 | 0 | From DOE Prototype Buildings
Hospital CLGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
Hospital Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Hospital Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Hospital Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Hospital Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Hospital CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
Hospital CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital Cool-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
Hospital CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital Critical ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22.2 | [23 empty] | From DOE Reference Buildings
Hospital Critical Equip | Equipment |  | Default¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
Hospital Critical Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Reference Buildings
Hospital Critical HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.1 | [23 empty] | From DOE Reference Buildings
Hospital Critical Light | Lighting |  | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | From DOE Reference Buildings
Hospital Critical Occ | Occupancy |  | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | From DOE Reference Buildings
Hospital CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
Hospital Dishwashing Booster Setpoint Temp Schedule | Service Water Heating | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
Hospital Dishwashing Booster Water Inlet Temp Schedule | Service Water Heating | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital ER_Exam1_Mult4_Flr_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Exam1_Mult4_Flr_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Exam1_Mult4_Flr_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Exam1_Mult4_Flr_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Exam3_Mult4_Flr_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Exam3_Mult4_Flr_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Exam3_Mult4_Flr_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Exam3_Mult4_Flr_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital ER_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital ER_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma1_Flr_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma1_Flr_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma1_Flr_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma1_Flr_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma2_Flr_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma2_Flr_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma2_Flr_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Trauma2_Flr_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Triage_Mult4_Flr_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Triage_Mult4_Flr_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Triage_Mult4_Flr_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital ER_Triage_Mult4_Flr_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital Heat-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
Hospital Hours_of_operation | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital HTGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
Hospital Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50 | [23 empty] | From DOE Prototype Buildings
Hospital HVACOperationSchd | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82 | [23 empty] | From DOE Prototype Buildings
Hospital ICU_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital ICU_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital Infil Quarter On | Infiltration |  | Default¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
Hospital Infil Quarter On | Infiltration |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Hospital INFIL_SCH_PNNL | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
Hospital Kitchen ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
Hospital Kitchen ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
Hospital Kitchen ClgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
Hospital Kitchen Exhaust | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Hospital Kitchen Exhaust | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Hospital Kitchen Exhaust | Equipment |  | Wknd | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Hospital Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | From DOE Prototype Buildings
Hospital Kitchen Gas | Equipment |  | Default¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | From DOE Reference Buildings
Hospital Kitchen Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Hospital Kitchen Gas | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
Hospital Kitchen HtgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Hospital Kitchen HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Hospital Kitchen HtgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
Hospital Kitchen_Exhaust_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
Hospital Kitchen_Flr_5 sub cat Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital Kitchen_Flr_5 sub cat Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital Kitchen_Flr_5 sub cat Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital Kitchen_Flr_5 sub catHot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
Hospital Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital Kitchen_SAT_SCH | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital Lab_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital Labs_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital Labs_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital Laundry Setpoint Temp Schedule | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
Hospital LAUNDRY_SWH_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Hospital MaxRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital MinRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 40 | [23 empty] | From DOE Prototype Buildings
Hospital MinRelHumSetSch_addDI | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
Hospital MinRelHumSetSch_addDI_ICU | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 35 | [23 empty] | From DOE Prototype Buildings
Hospital OR ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | From DOE Reference Buildings
Hospital OR HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.3 | [23 empty] | From DOE Reference Buildings
Hospital OR_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital OR_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital OR_MinSA_Sched | Unknown |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital OR_MinSA_Sched | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital OR_MinSA_Sched | Unknown |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital OR_MinSA_Sched | Unknown |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
Hospital OR1_Flr_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital OR1_Flr_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital OR1_Flr_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital OR1_Flr_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital OR2_Mult5_Flr_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital OR2_Mult5_Flr_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital OR2_Mult5_Flr_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital OR2_Mult5_Flr_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital OR3_Flr_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital OR3_Flr_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital OR3_Flr_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital OR3_Flr_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital OR4_Flr_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital OR4_Flr_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital OR4_Flr_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital OR4_Flr_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital Patrms_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital Patrms_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom1_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom2_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom3_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom4_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom5_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom6_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom7_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PatRoom8_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PhysTherapy_Flr_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital PhysTherapy_Flr_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital PhysTherapy_Flr_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital PhysTherapy_Flr_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital Radiology_Flr_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
Hospital Radiology_Flr_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
Hospital Radiology_Flr_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital Radiology_Flr_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
Hospital ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital scheduleOSCBasementFloorTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital scheduleOSCBasementLowerWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital scheduleOSCBasementUpperWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital scheduleOSCBasementWallSurfaceTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
Hospital SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Hospital Tower-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.1 | [23 empty] | From DOE Prototype Buildings
Hospital VAV_ER_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Prototype Buildings
Hospital VAV_ICU_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Prototype Buildings
Hospital VAV_LABS_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital VAV_OR_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Prototype Buildings
Hospital VAV_PATRMS_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Prototype Buildings
Hospital VAV_SAT_SCH | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
Hospital walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
Hospital walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Hospital walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Hospital walkin_occ_lght_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.104 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Hospital walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.26 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.156 | 0.156 | 0.156 | 0.156 | 0.156 | 0.156 | 0.156 | 0.1 | From DOE Prototype Buildings
Hospital Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Hospital WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
HotelLarge Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
HotelLarge Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
HotelLarge Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
HotelLarge Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
HotelLarge Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
HotelLarge Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
HotelLarge Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
HotelLarge Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
HotelLarge AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Base_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
HotelLarge Base_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH_2010 | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.38414 | 0.38414 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.38414 | 0.48018 | 0.48018 | 0.38414 | 0.38414 | 0.38414 | 0.38414 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.57621 | 0.76829 | 0.86432 | 0.67225 | 0.57621 | 0.38414 | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH_2010 | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH_2010 | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH_2010 | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.28811 | 0.28811 | 0.19207 | 0.19207 | 0.19207 | 0.19207 | 0.38414 | 0.38414 | 0.48018 | 0.48018 | 0.38414 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.67225 | 0.76829 | 0.76829 | 0.76829 | 0.67225 | 0.38414 | From DOE Prototype Buildings
HotelLarge BASEMENT_EQUIP_SCH_2010 | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.28811 | 0.24009 | 0.19207 | 0.19207 | 0.19207 | 0.28811 | 0.48018 | 0.57621 | 0.48018 | 0.48018 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.67225 | 0.86432 | 0.91234 | 0.86432 | 0.67225 | 0.38414 | From DOE Prototype Buildings
HotelLarge BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
HotelLarge BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | From DOE Prototype Buildings
HotelLarge BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | From DOE Prototype Buildings
HotelLarge BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH_2010 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.25029 | 0.25029 | 0.16686 | 0.16686 | 0.16686 | 0.16686 | 0.25029 | 0.33372 | 0.33372 | 0.25029 | 0.25029 | 0.25029 | 0.25029 | 0.16686 | 0.16686 | 0.16686 | 0.16686 | 0.16686 | 0.41715 | 0.58401 | 0.66744 | 0.50058 | 0.41715 | 0.25029 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH_2010 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH_2010 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH_2010 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.16686 | 0.16686 | 0.08343 | 0.08343 | 0.08343 | 0.08343 | 0.25029 | 0.25029 | 0.33372 | 0.33372 | 0.25029 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.50058 | 0.58401 | 0.58401 | 0.58401 | 0.50058 | 0.25029 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_CORRIDOR_SCH_2010 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.16686 | 0.12515 | 0.08343 | 0.08343 | 0.08343 | 0.16686 | 0.33372 | 0.41715 | 0.33372 | 0.33372 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.20858 | 0.50058 | 0.66744 | 0.75087 | 0.66744 | 0.50058 | 0.25029 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2197 | 0.2197 | 0.0945 | 0.0945 | 0.0945 | 0.0945 | 0.3852 | 0.3852 | 0.5259 | 0.44427 | 0.30216 | 0.2432 | 0.2432 | 0.2432 | 0.2432 | 0.2432 | 0.2432 | 0.25327 | 0.7973 | 0.938 | 0.938 | 0.938 | 0.7973 | 0.3852 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1859 | 0.1452 | 0.0945 | 0.0945 | 0.0945 | 0.1859 | 0.4121 | 0.5259 | 0.4121 | 0.4121 | 0.2087 | 0.2087 | 0.2087 | 0.2087 | 0.2087 | 0.2087 | 0.21304 | 0.2149 | 0.6297 | 0.8342 | 0.938 | 0.8342 | 0.6297 | 0.3083 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH_2010 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.28125 | 0.28125 | 0.1875 | 0.1875 | 0.1875 | 0.1875 | 0.28125 | 0.375 | 0.375 | 0.28125 | 0.28125 | 0.28125 | 0.28125 | 0.1875 | 0.1875 | 0.1875 | 0.1875 | 0.1875 | 0.46875 | 0.65625 | 0.75 | 0.5625 | 0.46875 | 0.28125 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH_2010 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH_2010 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH_2010 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1875 | 0.1875 | 0.09375 | 0.09375 | 0.09375 | 0.09375 | 0.28125 | 0.28125 | 0.375 | 0.375 | 0.28125 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.5625 | 0.65625 | 0.65625 | 0.65625 | 0.5625 | 0.28125 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH_2010 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1875 | 0.14062 | 0.09375 | 0.09375 | 0.09375 | 0.1875 | 0.375 | 0.46875 | 0.375 | 0.375 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.23438 | 0.5625 | 0.75 | 0.84375 | 0.75 | 0.5625 | 0.28125 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH_2010 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.17565 | 0.17565 | 0.1171 | 0.1171 | 0.1171 | 0.1171 | 0.17565 | 0.2342 | 0.2342 | 0.17565 | 0.17565 | 0.17565 | 0.17565 | 0.1171 | 0.1171 | 0.1171 | 0.1171 | 0.1171 | 0.29275 | 0.40985 | 0.4684 | 0.3513 | 0.29275 | 0.17565 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH_2010 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH_2010 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH_2010 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1171 | 0.1171 | 0.05855 | 0.05855 | 0.05855 | 0.05855 | 0.17565 | 0.17565 | 0.2342 | 0.2342 | 0.17565 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.3513 | 0.40985 | 0.40985 | 0.40985 | 0.3513 | 0.17565 | From DOE Prototype Buildings
HotelLarge BLDG_LIGHT_STORAGE_SCH_2010 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1171 | 0.087825 | 0.05855 | 0.05855 | 0.05855 | 0.1171 | 0.2342 | 0.29275 | 0.2342 | 0.2342 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.14638 | 0.3513 | 0.4684 | 0.52695 | 0.4684 | 0.3513 | 0.17565 | From DOE Prototype Buildings
HotelLarge BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | From DOE Prototype Buildings
HotelLarge BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | From DOE Prototype Buildings
HotelLarge BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | From DOE Prototype Buildings
HotelLarge BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | From DOE Prototype Buildings
HotelLarge BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | From DOE Prototype Buildings
HotelLarge BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | From DOE Prototype Buildings
HotelLarge Booster Water Inlet Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Booster Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
HotelLarge CLGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
HotelLarge CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
HotelLarge CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Cool-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
HotelLarge CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
HotelLarge Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
HotelLarge ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Eqp_Sch | Equipment |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Eqp_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Eqp_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge EmployeeLounge_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge ExerciseRoom_Eqp_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | From DOE Prototype Buildings
HotelLarge ExerciseRoom_Occ_Sch | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | From DOE Prototype Buildings
HotelLarge Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Exterior_Ltg_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
HotelLarge FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge FLR_3_DOAS_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.3 | 0.62 | 0.9 | 0.62 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.21 | 0.4 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.17 | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.62 | 0.9 | 0.43 | 0.43 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.19 | 0.48 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.17 | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Prototype Buildings
HotelLarge GuestRoom_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
HotelLarge GuestRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge GuestRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge GuestRoom_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | From DOE Prototype Buildings
HotelLarge GuestRoom_SWH_Sch | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | From DOE Prototype Buildings
HotelLarge GuestRoom_SWH_Sch | Service Water Heating |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | From DOE Prototype Buildings
HotelLarge Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Prototype Buildings
HotelLarge Hours_of_operation | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge HTGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
HotelLarge Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50 | [23 empty] | From DOE Prototype Buildings
HotelLarge HVACOperationSchd | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge INFIL_HALF_ON_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
HotelLarge INFIL_QUARTER_ON_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
HotelLarge INFIL_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | From DOE Prototype Buildings
HotelLarge Kitchen_Elec_Equip_SCH | Equipment |  | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
HotelLarge Kitchen_Elec_Equip_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen_Elec_Equip_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen_Exhaust_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Kitchen_Gas_Equip_SCH | Equipment |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | From DOE Prototype Buildings
HotelLarge Kitchen_Gas_Equip_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Kitchen_Gas_Equip_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
HotelLarge Laundry Setpoint Temp Schedule | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
HotelLarge LAUNDRY_SWH_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Elec_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Elec_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Elec_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Gas_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Gas_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge LaundryRoom_Eqp_Gas_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge LaundryRoom_Occ_Sch | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge LaundryRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge LaundryRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge LaundryRoom_SWH_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Lobby_Eqp_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21 | From DOE Prototype Buildings
HotelLarge Lobby_Eqp_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Lobby_Eqp_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Lobby_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelLarge Lobby_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Lobby_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Lobby_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelLarge MaxRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge MeetingRoom_Eqp_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge MeetingRoom_Occ_Sch | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge MeetingRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge MeetingRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge MinOA_MotorizedDamper_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge MinRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
HotelLarge N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelLarge N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelLarge N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelLarge N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelLarge Off During Unoccupied Period | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Office_Eqp_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Prototype Buildings
HotelLarge Office_Eqp_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Office_Eqp_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Office_Eqp_Sch | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Prototype Buildings
HotelLarge Office_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
HotelLarge Office_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Office_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Office_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
HotelLarge PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_6 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_6 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_1_Flr_6 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_6 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_6 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_2_Flr_6 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_5_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_5_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_5_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_5_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_6_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_6_Flr_3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_6_Flr_3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelLarge Room_6_Flr_3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelLarge S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelLarge S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelLarge S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelLarge scheduleOSCBasementFloorTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge scheduleOSCBasementLowerWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge scheduleOSCBasementUpperWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge scheduleOSCBasementWallSurfaceTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
HotelLarge Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
HotelLarge Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
HotelLarge SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
HotelLarge Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge SWHSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
HotelLarge SWHSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge SWHSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelLarge walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.156 | 0.156 | 0.104 | 0.104 | 0.104 | 0.104 | 0.156 | 0.208 | 0.208 | 0.156 | 0.156 | 0.156 | 0.156 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.26 | 0.364 | 0.416 | 0.312 | 0.26 | 0.156 | From DOE Prototype Buildings
HotelLarge walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelLarge walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelLarge walkin_occ_lght_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.104 | 0.104 | 0.052 | 0.052 | 0.052 | 0.052 | 0.156 | 0.156 | 0.208 | 0.208 | 0.156 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.312 | 0.364 | 0.364 | 0.364 | 0.312 | 0.156 | From DOE Prototype Buildings
HotelLarge walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.104 | 0.078 | 0.052 | 0.052 | 0.052 | 0.104 | 0.208 | 0.26 | 0.208 | 0.208 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.312 | 0.416 | 0.468 | 0.416 | 0.312 | 0.156 | From DOE Prototype Buildings
HotelLarge WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall Activity_Sch | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 132 | [23 empty] | From DOE Prototype Buildings
HotelSmall Adva_EmployeeLounge_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 26.667 | 26.667 | 26.667 | 26.667 | From DOE Prototype Buildings
HotelSmall Adva_EmployeeLounge_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.333 | 18.333 | 18.333 | 18.333 | From DOE Prototype Buildings
HotelSmall Adva_ExerciseCenter_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 26.667 | From DOE Prototype Buildings
HotelSmall Adva_ExerciseCenter_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.333 | From DOE Prototype Buildings
HotelSmall Adva_MeetingRoom_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | From DOE Prototype Buildings
HotelSmall Adva_MeetingRoom_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | From DOE Prototype Buildings
HotelSmall Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall AlwaysOff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall AlwaysOff_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall AlwaysOn | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall AlwaysOn_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall Base_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall Base_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
HotelSmall BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_CORRIDOR_SCH_2013 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.65 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_EXERCENTER_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2197 | 0.2197 | 0.0945 | 0.0945 | 0.0945 | 0.0945 | 0.3852 | 0.3852 | 0.5259 | 0.44427 | 0.30216 | 0.2432 | 0.2432 | 0.2432 | 0.2432 | 0.2432 | 0.2432 | 0.25327 | 0.7973 | 0.939 | 0.939 | 0.939 | 0.7973 | 0.3852 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2010 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1859 | 0.1452 | 0.0945 | 0.0945 | 0.0945 | 0.1859 | 0.4121 | 0.5259 | 0.4121 | 0.4121 | 0.2087 | 0.2087 | 0.2087 | 0.2087 | 0.2087 | 0.2087 | 0.21304 | 0.2149 | 0.6297 | 0.8342 | 0.938 | 0.8342 | 0.6297 | 0.3083 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2013 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.13 | 0.13 | 0.06 | 0.06 | 0.06 | 0.06 | 0.33 | 0.33 | 0.45 | 0.18667 | 0.062121 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0825 | 0.68 | 0.8 | 0.8 | 0.8 | 0.68 | 0.33 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2013 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2013 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_GUESTROOM_SCH_2013 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.09 | 0.06 | 0.06 | 0.06 | 0.11 | 0.35 | 0.45 | 0.45 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.05 | 0.064 | 0.07 | 0.54 | 0.71 | 0.8 | 0.71 | 0.54 | 0.26 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_LAUNDRY_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MECHROOM_SCH | Lighting |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MECHROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MECHROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.50935 | 0.7515 | 0.7515 | 0.7515 | 0.7515 | 0.668 | 0.7515 | 0.7515 | 0.7515 | 0.7515 | 0.50935 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | 0.4175 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_RESTROOM_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.66 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_STAIR_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.55 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_STORAGE_SCH | Lighting |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05418 | 0.05418 | 0.05418 | 0.05418 | 0.05418 | 0.05418 | 0.05418 | 0.10836 | 0.21672 | 0.21672 | 0.21672 | 0.21672 | 0.21672 | 0.21672 | 0.21672 | 0.21672 | 0.21672 | 0.21672 | 0.10836 | 0.10836 | 0.10836 | 0.10836 | 0.05418 | 0.05418 | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_STORAGE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall BLDG_LIGHT_STORAGE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall CommonArea_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.889 | [23 empty] | From DOE Prototype Buildings
HotelSmall CommonArea_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall CommonArea_Infil_Sch | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
HotelSmall CommonArea_Infil_Sch | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall CommonArea_Infil_Sch | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall COMPACT HVAC-ALWAYS 0 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall COMPACT HVAC-ALWAYS 1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall COMPACT HVAC-ALWAYS 4 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
HotelSmall ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
HotelSmall ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelSmall ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Eqp_Sch | Equipment |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Eqp_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Eqp_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall EmployeeLounge_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall ExerciseCenter_Eqp_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | From DOE Prototype Buildings
HotelSmall ExerciseCenter_Occ_Sch | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | From DOE Prototype Buildings
HotelSmall Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall Exterior_Ltg_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.3 | 0.62 | 0.9 | 0.62 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.21 | 0.4 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.09 | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.62 | 0.9 | 0.43 | 0.43 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.19 | 0.48 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.09 | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | From DOE Prototype Buildings
HotelSmall GuestRoom_Infil_Sch | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Infil_Sch | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Infil_Sch | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77 | From DOE Prototype Buildings
HotelSmall GuestRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall GuestRoom_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1 | From DOE Prototype Buildings
HotelSmall GuestRoom_SHW_Sch | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | From DOE Prototype Buildings
HotelSmall GuestRoom_SHW_Sch | Service Water Heating |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | From DOE Prototype Buildings
HotelSmall Heat Exchanger Supply Air Temp Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 14 | [23 empty] | From DOE Prototype Buildings
HotelSmall INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0 | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Elec_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Elec_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Elec_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Gas_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Gas_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall LaundryRoom_Eqp_Gas_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall LaundryRoom_Occ_Sch | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall LaundryRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall LaundryRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall LaundryRoom_SHW_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall Lobby_Eqp_Sch | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21 | From DOE Prototype Buildings
HotelSmall Lobby_Eqp_Sch | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall Lobby_Eqp_Sch | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall Lobby_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelSmall Lobby_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall Lobby_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall Lobby_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Prototype Buildings
HotelSmall MeetingRoom_Eqp_Sch | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall MeetingRoom_Occ_Sch | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall MeetingRoom_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall MeetingRoom_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall MinOA_MotorizedDamper_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall Off During Unoccupied Period | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
HotelSmall OFF_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Prototype Buildings
HotelSmall OFF_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall OFF_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall OFF_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Prototype Buildings
HotelSmall Office_Occ_Sch | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
HotelSmall Office_Occ_Sch | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall Office_Occ_Sch | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall Office_Occ_Sch | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
HotelSmall PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
HotelSmall S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | From DOE Prototype Buildings
HotelSmall S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111 | [23 empty] | From DOE Prototype Buildings
HotelSmall SAC_Econ_MaxOAFrac_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.7
HotelSmall SemiHeated_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 7.2 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHW Latent fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHW Laundry Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHW Sensible fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHW Shower Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHWSys Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.1 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHWSysLaundry Water Heater Setpoint Temperature Schedule | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHWSysLaundry-Loop-Temp-Schedule | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHWSysShower Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelSmall SHWSysShower-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
HotelSmall Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
HotelSmall Sliding_Doors_Ventilation_Availability_SCH | Unknown |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
HotelSmall VacGuestRoom_ClgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.333 | [23 empty] | From DOE Prototype Buildings
HotelSmall VacGuestRoom_HtgSP_Sch | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.889 | [23 empty] | From DOE Prototype Buildings
Large Office Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
Large Office BLDG ELEVATORS | Elevator |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Reference Buildings
Large Office Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | From DOE Reference Buildings
Large Office Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Large Office Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Large Office Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Reference Buildings
Large Office Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Large Office Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | From DOE Reference Buildings
Large Office Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Large Office Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Large Office Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Reference Buildings
Large Office Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Large Office Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
Large Office Bldg Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Large Office Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Reference Buildings
Large Office Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Large Office ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Reference Buildings
Large Office ClgSetp | Thermostat Setpoint | C | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Reference Buildings
Large Office ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Reference Buildings
Large Office Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Large Office Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Large Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Large Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Large Office HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
Large Office HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
Large Office HtgSetp | Thermostat Setpoint | C | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
Large Office HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Large Office Infil Quarter On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Reference Buildings
Large Office Infil Quarter On | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
Large Office Infil Quarter On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Large Office Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
LargeHotel BLDG ELEVATORS | Elevator |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Reference Buildings
LargeHotel Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | From DOE Reference Buildings
LargeHotel Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | From DOE Reference Buildings
LargeHotel Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | From DOE Reference Buildings
LargeHotel Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Reference Buildings
LargeHotel Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Reference Buildings
LargeHotel Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Reference Buildings
LargeHotel Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | From DOE Reference Buildings
LargeHotel Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | From DOE Reference Buildings
LargeHotel Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | From DOE Reference Buildings
LargeHotel ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Reference Buildings
LargeHotel Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
LargeHotel Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
LargeHotel Common Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel Common Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
LargeHotel Common Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Reference Buildings
LargeHotel Common Occ | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Reference Buildings
LargeHotel Corridor ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
LargeHotel Corridor HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Reference Buildings
LargeHotel GuestRoom Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom Equip | Equipment |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Reference Buildings
LargeHotel GuestRoom HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom Occ | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | From DOE Reference Buildings
LargeHotel GuestRoom Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
LargeHotel GuestRoom_Ltg_Sch_Base | Lighting |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom_Ltg_Sch_Base | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel GuestRoom_Ltg_Sch_Base | Lighting |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | From DOE Reference Buildings
LargeHotel GuestRoom_Ltg_Sch_Base | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | From DOE Reference Buildings
LargeHotel HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | From DOE Reference Buildings
LargeHotel Infil Quarter On | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
LargeHotel Kitchen ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Reference Buildings
LargeHotel Kitchen Equip | Equipment |  | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
LargeHotel Kitchen Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel Kitchen Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
LargeHotel Kitchen Exhaust | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
LargeHotel Kitchen Gas | Equipment |  | Default¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | From DOE Reference Buildings
LargeHotel Kitchen Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel Kitchen Gas | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
LargeHotel Kitchen HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | From DOE Reference Buildings
LargeHotel Kitchen_Elec_Equip_SCH | Equipment |  | Default¦Wkdy¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
LargeHotel Kitchen_Elec_Equip_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
LargeHotel Kitchen_Elec_Equip_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel LaundryRoom Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
LargeHotel LaundryRoom Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel LaundryRoom Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel LaundryRoom Gas | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
LargeHotel LaundryRoom Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel LaundryRoom Gas | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel Lobby Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Reference Buildings
LargeHotel Lobby Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
LargeHotel Lobby Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
LargeHotel Lobby Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Reference Buildings
LargeHotel Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Medium Office Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
Medium Office BLDG ELEVATORS | Elevator |  | Wkdy¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | From DOE Reference Buildings
Medium Office BLDG ELEVATORS | Elevator |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Medium Office BLDG ELEVATORS | Elevator |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Equip | Equipment |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | From DOE Reference Buildings
Medium Office Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Medium Office Bldg Light | Lighting |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Occ | Occupancy |  | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Medium Office Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Medium Office Bldg Swh | Service Water Heating |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Swh | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | From DOE Reference Buildings
Medium Office Bldg Swh | Service Water Heating |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | From DOE Reference Buildings
Medium Office ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Reference Buildings
Medium Office ClgSetp | Thermostat Setpoint | C | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Reference Buildings
Medium Office ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Reference Buildings
Medium Office Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Medium Office Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Medium Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Medium Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Medium Office HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
Medium Office HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
Medium Office HtgSetp | Thermostat Setpoint | C | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
Medium Office HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Medium Office Infil Quarter On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Reference Buildings
Medium Office Infil Quarter On | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
Medium Office Infil Quarter On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Medium Office Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
MidriseApartment Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
MidriseApartment Apartment ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.9 | [23 empty] | From DOE Reference Buildings
MidriseApartment Apartment DHW | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29 | From DOE Reference Buildings
MidriseApartment Apartment Equip | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58 | From DOE Reference Buildings
MidriseApartment Apartment HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.1 | [23 empty] | From DOE Reference Buildings
MidriseApartment Apartment Light | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.067 | 0.067 | 0.067 | 0.067 | 0.187 | 0.394 | 0.44 | 0.393 | 0.172 | 0.119 | 0.119 | 0.119 | 0.119 | 0.119 | 0.119 | 0.206 | 0.439 | 0.616 | 0.829 | 0.986 | 1 | 0.692 | 0.384 | 0.16 | From DOE Reference Buildings
MidriseApartment Apartment Occ | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1 | From DOE Reference Buildings
MidriseApartment Apartment Operation | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
MidriseApartment BLDG ELEVATORS | Elevator |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Reference Buildings
MidriseApartment Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
MidriseApartment Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
MidriseApartment Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
MidriseApartment Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
MidriseApartment Corridor ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 40 | [23 empty] | From DOE Reference Buildings
MidriseApartment Corridor HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
MidriseApartment Corridor Light | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
MidriseApartment Infil | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
MidriseApartment Office ClgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Reference Buildings
MidriseApartment Office ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.4 | [23 empty] | From DOE Reference Buildings
MidriseApartment Office ClgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | From DOE Reference Buildings
MidriseApartment Office Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | From DOE Reference Buildings
MidriseApartment Office Equip | Equipment |  | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Reference Buildings
MidriseApartment Office HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
MidriseApartment Office HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
MidriseApartment Office HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
MidriseApartment OFFICE Infil | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
MidriseApartment OFFICE Infil | Infiltration |  | WntrDsn¦SmrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
MidriseApartment Office Light | Lighting |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | From DOE Reference Buildings
MidriseApartment Office Light | Lighting |  | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 0.18 | [23 empty] | From DOE Reference Buildings
MidriseApartment Office Occ | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
MidriseApartment Office Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
MidriseApartment Office Operation | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
MidriseApartment Office Operation | Operation |  | Wknd | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
MidriseApartment UnitHeater ClgSP Sch | Thermostat Setpoint |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 40 | [23 empty] | From DOE Reference Buildings
MidriseApartment UnitHeater HtgSP Sch | Thermostat Setpoint |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
MidriseApartment Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
NECB-A-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2
NECB-A-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
NECB-A-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
NECB-A-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
NECB-A-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-A-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-A-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.5 | 0.3 | 0.3 | 0.1 | 0.1 | 0.05
NECB-A-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-A-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-A-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.7 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.7 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0
NECB-A-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-A-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-A-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2
NECB-A-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
NECB-A-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
NECB-A-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05
NECB-A-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-A-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-A-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 35 | 35
NECB-A-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
NECB-A-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
NECB-A-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18
NECB-A-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NECB-A-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NECB-B-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-B-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-B-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5
NECB-B-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-B-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-B-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
NECB-B-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-B-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-B-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5
NECB-B-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.9 | 0.8 | 0.5 | 0.2 | 0.2 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.6 | 0.4
NECB-B-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.9 | 0.8 | 0.5 | 0.2 | 0.2 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6
NECB-B-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.4 | 0.5 | 0.5 | 0.4 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.7 | 0.5 | 0.3 | 0.1
NECB-B-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-B-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-B-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5
NECB-B-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.6 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 0.7 | 0.4 | 0.5 | 0.6 | 0.6 | 0.4 | 0.3 | 0.3 | 0.4 | 0.5 | 0.8 | 0.8 | 0.9 | 0.9
NECB-B-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.6 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 0.7 | 0.4 | 0.5 | 0.6 | 0.6 | 0.4 | 0.3 | 0.3 | 0.4 | 0.5 | 0.8 | 0.8 | 0.9 | 0.9
NECB-B-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.6 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.7 | 0.7 | 0.4 | 0.5 | 0.6 | 0.6 | 0.4 | 0.3 | 0.3 | 0.4 | 0.5 | 0.8 | 0.8 | 0.5 | 0.5
NECB-B-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-B-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-B-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35
NECB-B-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-B-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-B-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 18 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18
NECB-C-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.5 | 0.05 | 0.05 | 0.05
NECB-C-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.5 | 0.05 | 0.05 | 0.05
NECB-C-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-C-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
NECB-C-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
NECB-C-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
NECB-C-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.5 | 0.05 | 0.05 | 0.05
NECB-C-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.5 | 0.05 | 0.05 | 0.05
NECB-C-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-C-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
NECB-C-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.7 | 0.5 | 0.2 | 0.2 | 0 | 0 | 0
NECB-C-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0 | 0 | 0 | 0 | 0
NECB-C-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.5 | 0.05 | 0.05 | 0.05
NECB-C-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.5 | 0.05 | 0.05 | 0.05
NECB-C-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-C-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.3 | 0.4 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.3 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05
NECB-C-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.3 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05
NECB-C-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.8 | 0.8 | 0.6 | 0.4 | 0.3 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-C-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 35 | 35
NECB-C-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 35 | 35
NECB-C-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 35 | 35 | 35 | 35
NECB-C-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18
NECB-C-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18
NECB-C-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 18
NECB-D-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.3 | 0.05
NECB-D-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
NECB-D-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-D-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-D-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.3 | 0.05
NECB-D-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.2 | 0.1 | 0.3 | 0.3 | 0.3 | 0.1 | 0
NECB-D-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-D-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-D-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.3 | 0.05
NECB-D-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.3 | 0.5 | 0.5 | 0.5 | 0.3 | 0.05 | 0.05
NECB-D-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-D-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35
NECB-D-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
NECB-D-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
NECB-D-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18
NECB-D-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NECB-D-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NECB-E-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
NECB-E-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-E-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-E-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.9 | 0.8 | 0.8 | 0.2 | 0 | 0 | 0 | 0 | 0
NECB-E-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-E-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-E-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.5 | 0.5 | 0.7 | 0.9 | 0.8 | 0.7 | 0.8 | 0.3 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.4 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-E-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 35 | 35 | 35 | 35
NECB-E-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35
NECB-E-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
NECB-E-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 18
NECB-E-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NECB-E-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NECB-F-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6
NECB-F-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6
NECB-F-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5
NECB-F-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-F-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-F-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-F-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6
NECB-F-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6
NECB-F-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5
NECB-F-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9
NECB-F-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7
NECB-F-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8
NECB-F-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6
NECB-F-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6
NECB-F-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5
NECB-F-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.3 | 0.2 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.9 | 0.7 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7
NECB-F-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.3 | 0.2 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.8 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.3 | 0.3 | 0.3 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7
NECB-F-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.3 | 0.2 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.6 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6
NECB-F-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-F-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-F-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-F-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-F-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-F-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-G-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.2 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5
NECB-G-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.2 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5
NECB-G-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.2 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5
NECB-G-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-G-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-G-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-G-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6
NECB-G-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6
NECB-G-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6
NECB-G-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-G-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-G-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-G-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.2 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5
NECB-G-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.2 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5
NECB-G-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.2 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.5
NECB-G-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.8 | 0.7 | 0.5 | 0.4 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.1
NECB-G-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.7 | 0.6 | 0.5 | 0.4 | 0.3 | 0.2
NECB-G-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.3 | 0.3 | 0.2 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2
NECB-G-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-G-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-G-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-G-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-G-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-G-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-H-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-H-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-H-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-H-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-H-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-H-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-H-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-H-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-H-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-H-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-I-Electric-Equipment | Equipment | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
NECB-I-Electric-Equipment | Equipment | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
NECB-I-Electric-Equipment | Equipment | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
NECB-I-Fan | Fan | ON_OFF | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-I-Fan | Fan | ON_OFF | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NECB-I-Fan | Fan | ON_OFF | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-I-Lighting | Lighting | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.5 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NECB-I-Lighting | Lighting | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.5 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9
NECB-I-Lighting | Lighting | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-I-Occupancy | Occupancy | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.4 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4
NECB-I-Occupancy | Occupancy | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.4 | 0.6 | 0.8 | 0.6 | 0.4 | 0.2 | 0.4 | 0.8 | 0.8 | 0.6 | 0.4
NECB-I-Occupancy | Occupancy | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.4 | 0.8 | 0.8 | 0.4 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NECB-I-Processes | Processes | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
NECB-I-Processes | Processes | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
NECB-I-Processes | Processes | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
NECB-I-Service Water Heating | Service Water Heating | FRACTION | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6
NECB-I-Service Water Heating | Service Water Heating | FRACTION | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.2 | 0.4 | 0.8 | 0.9 | 0.8 | 0.6 | 0.4 | 0.4 | 0.9 | 0.9 | 0.8 | 0.6
NECB-I-Service Water Heating | Service Water Heating | FRACTION | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.4 | 0.2 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NECB-I-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-I-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
NECB-I-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
NECB-I-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-I-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sat | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
NECB-I-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Sun¦Hol | 2014-01-01 | 2014-12-31 | Hourly | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
NECB-Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 130 | [23 empty] | From DOE Reference Buildings
NECB-*-Lighting | Lighting | FRACTION | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
NECB-*-Occupancy | Occupancy | FRACTION | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
NECB-*-Electric-Equipment | Equipment | FRACTION | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
NECB-*-Thermostat Setpoint-Heating | Thermostat Setpoint | TEMPERATURE | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18
NECB-*-Thermostat Setpoint-Cooling | Thermostat Setpoint | TEMPERATURE | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 35
NECB-*-Service Water Heating | Service Water Heating | FRACTION | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
NECB-*-FAN | Fan | ON_OFF | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Office Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 132 | [23 empty] | From DOE Reference Buildings
Office Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | From DOE Reference Buildings
Office Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Office Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Office Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Reference Buildings
Office Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Office Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | From DOE Reference Buildings
Office Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Office Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Office Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Reference Buildings
Office Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Office Infil Quarter On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Reference Buildings
Office Infil Quarter On | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
Office Infil Quarter On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Office Misc Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
Office Misc Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Office Misc Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Reference Buildings
Office Misc Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Office Work Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.85 | 0.85 | 0.85 | 0.85 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
Office Work Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Office Work Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Reference Buildings
Office Work Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
OfficeLarge ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
OfficeLarge AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeLarge ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
OfficeLarge BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OfficeLarge BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
OfficeLarge BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | From DOE Prototype Buildings
OfficeLarge BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeLarge BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeLarge CLGSETP_DC_SCH | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLGSETP_DC_SCH | Thermostat Setpoint | C | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 27 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦WntrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeLarge CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Cool-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_bottom sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_bottom sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_bottom sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_bottom sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_mid sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_mid sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_mid sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_mid sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_top sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_top sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_top sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Core_top sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeLarge CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
OfficeLarge DataCenter_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge DataCenter_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge DC_MinRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
OfficeLarge ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Prototype Buildings
OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
OfficeLarge Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge EXTERIOR_LIGHT_SCH | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | From DOE Prototype Buildings
OfficeLarge FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Heat-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Hours_of_operation | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Hours_of_operation | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge Hours_of_operation | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge HTGSETP_DC_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeLarge HVACOperationSchd | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge HVACOperationSchd | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge HVACOperationSchd | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82 | [23 empty] | From DOE Prototype Buildings
OfficeLarge INFIL_HALF_ON_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge INFIL_HALF_ON_SCH | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge INFIL_HALF_ON_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge INFIL_SCH | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge INFIL_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge INFIL_SCH_PNNL | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge INFIL_SCH_PNNL | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge INFIL_SCH_PNNL | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Prototype Buildings
OfficeLarge MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge MinOA_MotorizedDamper_Sched | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeLarge MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge PLANT LOOP HIGH TEMP SCHEDULE | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.33 | [23 empty] | From DOE Prototype Buildings
OfficeLarge PLANT LOOP LOW TEMP SCHEDULE | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 5 | [23 empty] | From DOE Prototype Buildings
OfficeLarge PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge scheduleOSCBasementFloorTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge scheduleOSCBasementLowerWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge scheduleOSCBasementUpperWallTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge scheduleOSCBasementWallSurfaceTemp | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeLarge SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
OfficeLarge SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeLarge SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeLarge SupplyFanSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge Tower-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.1 | [23 empty] | From DOE Prototype Buildings
OfficeLarge WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
OfficeMedium AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_ELEVATORS | Elevator |  | Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.69 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_ELEVATORS | Elevator |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_ELEVATORS | Elevator |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2004 | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2004 | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2004 | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2004 | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2004 | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2010 | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2010 | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2010 | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2010 | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.38414 | 0.38414 | 0.48018 | 0.48018 | 0.48018 | 0.48018 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.28811 | 0.28811 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2010 | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.38414 | 0.38414 | 0.86432 | 0.86432 | 0.86432 | 0.86432 | 0.76829 | 0.86432 | 0.86432 | 0.86432 | 0.86432 | 0.48018 | 0.38414 | 0.38414 | 0.38414 | 0.38414 | 0.38414 | 0.38414 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2013 | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2013 | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2013 | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.23076 | 0.23076 | 0.23076 | 0.23076 | 0.23076 | 0.23076 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2013 | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.23076 | 0.23076 | 0.23076 | 0.23076 | 0.23076 | 0.23076 | 0.38123 | 0.38123 | 0.47654 | 0.47654 | 0.47654 | 0.47654 | 0.33358 | 0.33358 | 0.33358 | 0.33358 | 0.33358 | 0.28593 | 0.28593 | 0.23076 | 0.23076 | 0.23076 | 0.23076 | 0.23076 | From DOE Prototype Buildings
OfficeMedium BLDG_EQUIP_SCH_2013 | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.30767 | 0.30767 | 0.30767 | 0.30767 | 0.30767 | 0.30767 | 0.38123 | 0.38123 | 0.85778 | 0.85778 | 0.85778 | 0.85778 | 0.76247 | 0.85778 | 0.85778 | 0.85778 | 0.85778 | 0.47654 | 0.38123 | 0.38123 | 0.38123 | 0.38123 | 0.38123 | 0.38123 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2004 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2004 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2004 | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2004 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2004 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2010 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2010 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2010 | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2010 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0904 | 0.0904 | 0.2712 | 0.2712 | 0.2712 | 0.2712 | 0.1356 | 0.1356 | 0.1356 | 0.1356 | 0.1356 | 0.0452 | 0.0452 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2010 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.0904 | 0.2712 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.452 | 0.2712 | 0.2712 | 0.1808 | 0.1808 | 0.0904 | 0.0452 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2013 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2013 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2013 | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.043116 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2013 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.086233 | 0.086233 | 0.2587 | 0.2587 | 0.2587 | 0.2587 | 0.12935 | 0.12935 | 0.12935 | 0.12935 | 0.12935 | 0.043116 | 0.043116 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_LIGHT_SCH_2013 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.086233 | 0.2587 | 0.77609 | 0.77609 | 0.77609 | 0.77609 | 0.77609 | 0.77609 | 0.77609 | 0.77609 | 0.77609 | 0.43116 | 0.2587 | 0.2587 | 0.17247 | 0.17247 | 0.086233 | 0.043116 | From DOE Prototype Buildings
OfficeMedium BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦WntrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Prototype Buildings
OfficeMedium CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Cool-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_bottom sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_bottom sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_bottom sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_bottom sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_mid sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_mid sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_mid sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_mid sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_top sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_top sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_top sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Core_top sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.69 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium Exterior_Lgt_189_1 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
OfficeMedium Exterior_Lgt_ALWAYS_ON | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeMedium Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeMedium FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Heat-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Hours_of_operation | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Hours_of_operation | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium Hours_of_operation | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Prototype Buildings
OfficeMedium Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HVACOperationSchd | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium HVACOperationSchd | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium HVACOperationSchd | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium INFIL_SCH_PNNL | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium INFIL_SCH_PNNL | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeMedium INFIL_SCH_PNNL | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Prototype Buildings
OfficeMedium MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium MinOA_MotorizedDamper_Sched | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
OfficeMedium MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_bot_ZN_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_mid_ZN_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_1 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_1 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_1 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_1 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_2 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_2 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_2 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_2 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_3 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_3 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_3 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_3 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_4 sub cat Latent fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_4 sub cat Sensible fract sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_4 sub cat Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium Perimeter_top_ZN_4 sub catHot Supply Temp Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeMedium PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeMedium SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeMedium SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
OfficeMedium SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeMedium VAV OA Damper | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0%
OfficeMedium VAV OA Damper | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0%
OfficeMedium VAV Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0%
OfficeMedium VAV Operation | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0%
OfficeMedium WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
OfficeSmall AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeSmall ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
OfficeSmall BLDG_LIGHT_SCH | Lighting |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.23 | 0.42 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.42 | 0.42 | 0.32 | 0.32 | 0.23 | 0.18 | From DOE Prototype Buildings
OfficeSmall BLDG_OCC_SCH | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0.11 | 0.11 | 0.11 | 0.11 | 0.05 | 0 | From DOE Prototype Buildings
OfficeSmall BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 0.55 | 0.64 | 0.64 | 0.82 | 1 | 0.91 | 0.55 | 0.55 | 0.73 | 0.37 | 0.37 | 0.18 | 0.27 | 0.09 | 0 | 0 | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
OfficeSmall CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Core_ZN Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Core_ZN Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Core_ZN Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Core_ZN Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 48.8 | [23 empty] | From DOE Prototype Buildings
OfficeSmall CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeSmall Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeSmall Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
OfficeSmall Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HVACOperationSchd | Operation |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall HVACOperationSchd | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeSmall HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeSmall INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeSmall INFIL_QUARTER_ON_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall INFIL_QUARTER_ON_SCH | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeSmall INFIL_QUARTER_ON_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OfficeSmall MinOA_MotorizedDamper_Sched | OA Air |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall MinOA_MotorizedDamper_Sched | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OfficeSmall MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
OfficeSmall Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
OfficeSmall SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OfficeSmall SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
OfficeSmall SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeSmall SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OfficeSmall WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Outpatient Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
Outpatient BLDG ELEVATORS | Elevator |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient BLDG ELEVATORS | Elevator |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient BLDG ELEVATORS | Elevator |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient Bldg Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Outpatient Bldg Equip | Equipment |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Outpatient Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Outpatient Bldg Light | Lighting |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Reference Buildings
Outpatient Bldg Light | Lighting |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Outpatient Bldg Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient Bldg Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Outpatient Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Outpatient ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Reference Buildings
Outpatient ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Reference Buildings
Outpatient ClgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | 25 | [23 empty] | From DOE Reference Buildings
Outpatient Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Outpatient Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Outpatient Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Outpatient Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Outpatient HtgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Reference Buildings
Outpatient HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Reference Buildings
Outpatient HtgSetp | Thermostat Setpoint | C | Wknd | 2014-01-01 | 2014-12-31 | Constant | 18.3 | [23 empty] | From DOE Reference Buildings
Outpatient Infil | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Outpatient Infil | Infiltration |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Outpatient OR ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | From DOE Reference Buildings
Outpatient OR HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.3 | [23 empty] | From DOE Reference Buildings
Outpatient Radiology Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | From DOE Reference Buildings
Outpatient Radiology Equip | Equipment |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0.01 | [23 empty] | From DOE Reference Buildings
Outpatient Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
OutPatientHealthCare ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare AHU-1_ExtraElecHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare AHU-1_ExtraWaterHeatC_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare AHU-1_OAminOAFracSchedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare BLDG_CAV_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_CAV_SCH_HUMID | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_ELEVATORS | Elevator |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare BLDG_ELEVATORS | Elevator |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_ELEVATORS | Elevator |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH | Equipment |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH | Equipment |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH_BASE | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH_BASE | Equipment |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_EQUIP_SCH_BASE | Equipment |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_TOILET_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_TOILET_SCH | Lighting |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_LIGHT_TOILET_SCH | Lighting |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OA_FRAC_SCH | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OA_FRAC_SCH | OA Air |  | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OA_SCH | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OA_SCH | OA Air |  | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OCC_SCH | Occupancy |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_OCC_SCH | Occupancy |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | From DOE Prototype Buildings
OutPatientHealthCare BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | From DOE Prototype Buildings
OutPatientHealthCare CAV_SAT_SCH | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 11.1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 25 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 22.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 25 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 23.9 | 23.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 25 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 23.9 | 23.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | From DOE Prototype Buildings
OutPatientHealthCare CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05 | From DOE Prototype Buildings
OutPatientHealthCare Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
OutPatientHealthCare Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OutPatientHealthCare Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
OutPatientHealthCare FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Room Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Room Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Room Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 MRI Room Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 1 humidity sched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 PACU Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 PACU Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 PACU Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 PACU Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Step Down Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Step Down Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Step Down Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 1 Step Down Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 2 X-Ray Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 2 X-Ray Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 2 X-Ray Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 2 X-Ray Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare HeatSys1 Loop Setpoint Sched | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Hours_of_operation | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 18.3 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Constant | 18.3 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Prototype Buildings
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 19.4 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | From DOE Prototype Buildings
OutPatientHealthCare Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare HVACOperationSchd | Operation |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
OutPatientHealthCare INFIL_HALF_ON_SCH | Infiltration |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare INFIL_HALF_ON_SCH | Infiltration |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare INFIL_SCH | Infiltration |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare INFIL_SCH | Infiltration |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare MaxRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare MinOA_MotorizedDamper_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare MinRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 40 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare MinRelHumSetSch_addDI | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare OR_CLGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | From DOE Prototype Buildings
OutPatientHealthCare OR_HTGSETP_SCH | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.3 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare OR_MinSA_Sched | Unknown |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare OR_MinSA_Sched | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare OR_MinSA_Sched | Unknown |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
OutPatientHealthCare PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 11.1 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare SWHSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare SWHSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare SWHSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare VAV_SAT_SCH | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
OutPatientHealthCare WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
PrimarySchool Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
PrimarySchool BathCorrMechKitchen ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 27 | [23 empty] | From DOE Reference Buildings
PrimarySchool BathCorrMechKitchen ClgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
PrimarySchool BathCorrMechKitchen HtgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Reference Buildings
PrimarySchool BathCorrMechKitchen HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
PrimarySchool Bldg Equip | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
PrimarySchool Bldg Light | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Bldg Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Cafeteria Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool ClgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
PrimarySchool ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 27 | [23 empty] | From DOE Reference Buildings
PrimarySchool ClgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Reference Buildings
PrimarySchool ClgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
PrimarySchool ClgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27 | From DOE Reference Buildings
PrimarySchool Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Reference Buildings
PrimarySchool Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.6 | [23 empty] | From DOE Reference Buildings
PrimarySchool Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Reference Buildings
PrimarySchool Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.6 | [23 empty] | From DOE Reference Buildings
PrimarySchool Exterior Lights | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
PrimarySchool Exterior Lights Always On | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
PrimarySchool Gym Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Gym Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
PrimarySchool HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
PrimarySchool HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Reference Buildings
PrimarySchool HtgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
PrimarySchool HtgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | From DOE Reference Buildings
PrimarySchool Infil | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13 | 0.13 | 0.2 | 0.2 | 0.2 | 0.13 | 0.13 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
PrimarySchool Kitchen Equip | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Exhaust | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Kitchen Exhaust | Equipment |  | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
PrimarySchool Kitchen Gas | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
PrimarySchool Offices Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
PrimarySchool PSZ-AC OA Damper | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
PrimarySchool PSZ-AC OA Damper | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
PrimarySchool PSZ-AC Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
PrimarySchool PSZ-AC Operation | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
PrimarySchool VAV OA Damper | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
PrimarySchool VAV OA Damper | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
PrimarySchool VAV Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
PrimarySchool VAV Operation | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
PrimarySchool Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Bldg Equip | Equipment |  | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.35 | 0.35 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.3 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.2 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Bldg Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.2 | 0.45 | 0.6 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.2 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Swh | Service Water Heating |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Swh | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | From DOE Reference Buildings
QuickServiceRestaurant Bldg Swh | Service Water Heating |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | From DOE Reference Buildings
QuickServiceRestaurant ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Reference Buildings
QuickServiceRestaurant ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Reference Buildings
QuickServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Gas Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.09 | 0.14 | 0.1 | 0.1 | 0.22 | 0.27 | 0.24 | 0.21 | 0.14 | 0.13 | 0.15 | 0.17 | 0.17 | 0.17 | 0.15 | 0.14 | 0.12 | 0.02 | From DOE Reference Buildings
QuickServiceRestaurant Gas Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Gas Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 19 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
QuickServiceRestaurant Infil Half On | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
QuickServiceRestaurant Kitchen Exhaust | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
QuickServiceRestaurant Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
RestaurantFastFood ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_EQUIP_SCH | Equipment |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | From DOE Prototype Buildings
RestaurantFastFood BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.29 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2010 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.19034 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.28551 | 0.28551 | 0.47585 | 0.47585 | 0.66619 | 0.66619 | 0.66619 | 0.66619 | 0.66619 | 0.66619 | 0.57102 | 0.57102 | 0.57102 | 0.57102 | 0.57102 | 0.57102 | 0.47585 | 0.28551 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2010 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.14275 | 0.15 | 0.15 | 0.15 | 0.15 | 0.19034 | 0.38068 | 0.38068 | 0.57102 | 0.57102 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.47585 | 0.28551 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2010 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2010 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2010 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.19034 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.28551 | 0.28551 | 0.57102 | 0.57102 | 0.76136 | 0.76136 | 0.76136 | 0.76136 | 0.76136 | 0.76136 | 0.76136 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.85653 | 0.47585 | 0.28551 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2013 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1865 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2797 | 0.2797 | 0.4662 | 0.4662 | 0.6527 | 0.6527 | 0.6527 | 0.6527 | 0.6527 | 0.6527 | 0.5594 | 0.5594 | 0.5594 | 0.5594 | 0.5594 | 0.5594 | 0.4662 | 0.2797 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2013 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1399 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1865 | 0.373 | 0.373 | 0.5594 | 0.5594 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.4662 | 0.2797 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2013 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2013 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_DINING_SCH_2013 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1865 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2797 | 0.2797 | 0.5594 | 0.5594 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.7459 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.8391 | 0.4662 | 0.2797 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2004_2007 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2004_2007 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2004_2007 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2004_2007 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2004_2007 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2010_2013 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.17776 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.26664 | 0.26664 | 0.4444 | 0.4444 | 0.62216 | 0.62216 | 0.62216 | 0.62216 | 0.62216 | 0.62216 | 0.53328 | 0.53328 | 0.53328 | 0.53328 | 0.53328 | 0.53328 | 0.4444 | 0.26664 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2010_2013 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.13332 | 0.15 | 0.15 | 0.15 | 0.15 | 0.17776 | 0.35552 | 0.35552 | 0.53328 | 0.53328 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.4444 | 0.26664 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2010_2013 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2010_2013 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH_2010_2013 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.17776 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.26664 | 0.26664 | 0.53328 | 0.53328 | 0.71104 | 0.71104 | 0.71104 | 0.71104 | 0.71104 | 0.71104 | 0.71104 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.79992 | 0.4444 | 0.26664 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_LIGHT_SCH | Lighting |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantFastFood BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2 | From DOE Prototype Buildings
RestaurantFastFood BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35 | From DOE Prototype Buildings
RestaurantFastFood BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | From DOE Prototype Buildings
RestaurantFastFood BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.1 | 0.72 | 0.6 | 0.98 | 0.92 | 0.25 | 0.25 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0 | From DOE Prototype Buildings
RestaurantFastFood BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.1 | 0.72 | 0.6 | 0.98 | 0.92 | 0.25 | 0.25 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0.15 | From DOE Prototype Buildings
RestaurantFastFood BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.33 | 0.13 | 0.1 | 0.72 | 0.31 | 0.98 | 0.92 | 0.22 | 0.31 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0.15 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 28.33 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 26.11 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 28.33 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 28.9 | 27.8 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 28.33 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RestaurantFastFood CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood DOOR_INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.258 | 0.258 | 0.363 | 0.558 | 0.558 | 0.363 | 0.258 | 0.363 | 0.462 | 0.558 | 0.65 | 0.74 | 0.462 | 0.258 | 0.258 | From DOE Prototype Buildings
RestaurantFastFood DOOR_INFIL_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood DOOR_INFIL_SCH | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood DOOR_INFIL_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.462 | 0.258 | 0.462 | 0.558 | 0.558 | 0.462 | 0.363 | 0.363 | 0.363 | 0.74 | 0.915 | 0.74 | 0.65 | 0.558 | 0.363 | From DOE Prototype Buildings
RestaurantFastFood DOOR_INFIL_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.462 | 0.462 | 0.462 | 0.258 | 0.558 | 0.829 | 0.74 | 0.462 | 0.258 | 0.363 | 0.558 | 0.829 | 0.829 | 0.829 | 0.558 | 0.363 | 0.258 | From DOE Prototype Buildings
RestaurantFastFood Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood FF_GAS_EQUIP_SCH | Equipment |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | From DOE Prototype Buildings
RestaurantFastFood FF_GAS_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood FF_GAS_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.29 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Hours_of_operation | Operation |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.22 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 16.7 | 17.8 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.22 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RestaurantFastFood HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood HVACOperationSchd | Operation |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood INFIL_SCH_PNNL | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
RestaurantFastFood Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule_2004 | Equipment |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.53051 | 0 | 0 | 0 | 0 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | From DOE Prototype Buildings
RestaurantFastFood Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule_2007_2010_2013 | Equipment |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.53051 | 0 | 0 | 0 | 0 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | From DOE Prototype Buildings
RestaurantFastFood Kitchen Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Kitchen Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Kitchen Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Kitchen Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RestaurantFastFood Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
RestaurantFastFood Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RestaurantFastFood Kitchen_Exhaust_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood MinOA_FFKitch_Sched | OA Air |  | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood MinOA_FFKitch_Sched | OA Air |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood MinOA_MotorizedDamper_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantFastFood MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood SHWSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood SHWSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.241 | 0.241 | 0.345 | 0.542 | 0.542 | 0.345 | 0.241 | 0.345 | 0.445 | 0.542 | 0.637 | 0.73 | 0.445 | 0.241 | 0.241 | From DOE Prototype Buildings
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.445 | 0.241 | 0.445 | 0.542 | 0.542 | 0.445 | 0.345 | 0.345 | 0.345 | 0.73 | 0.911 | 0.73 | 0.637 | 0.542 | 0.345 | From DOE Prototype Buildings
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.445 | 0.445 | 0.445 | 0.241 | 0.542 | 0.821 | 0.73 | 0.445 | 0.241 | 0.345 | 0.542 | 0.821 | 0.821 | 0.821 | 0.542 | 0.345 | 0.241 | From DOE Prototype Buildings
RestaurantFastFood walkin_occ_lght_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.312 | 0.312 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.26 | 0.156 | From DOE Prototype Buildings
RestaurantFastFood walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantFastFood walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.26 | 0.26 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.26 | 0.156 | From DOE Prototype Buildings
RestaurantFastFood walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.104 | 0.208 | 0.208 | 0.312 | 0.312 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.26 | 0.156 | From DOE Prototype Buildings
RestaurantFastFood WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_EQUIP_SCH | Equipment |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | From DOE Prototype Buildings
RestaurantSitDown BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.29 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH_2013 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1877 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2816 | 0.2816 | 0.4693 | 0.4693 | 0.657 | 0.657 | 0.657 | 0.657 | 0.657 | 0.657 | 0.5631 | 0.5631 | 0.5631 | 0.5631 | 0.5631 | 0.5631 | 0.4693 | 0.2816 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH_2013 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1408 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1877 | 0.3754 | 0.3754 | 0.5631 | 0.5631 | 0.8447 | 0.8447 | 0.8447 | 0.8447 | 0.8447 | 0.8447 | 0.8447 | 0.8447 | 0.8447 | 0.8447 | 0.8447 | 0.8447 | 0.4693 | 0.2816 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH_2013 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH_2013 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH_2013 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1877 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2816 | 0.2816 | 0.5631 | 0.5631 | 0.7509 | 0.7509 | 0.7509 | 0.7509 | 0.7509 | 0.7509 | 0.7509 | 0.8447 | 0.8447 | 0.8447 | 0.8447 | 0.8447 | 0.4693 | 0.2816 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH_2010 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1944 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2916 | 0.2916 | 0.4861 | 0.4861 | 0.6805 | 0.6805 | 0.6805 | 0.6805 | 0.6805 | 0.6805 | 0.5833 | 0.5833 | 0.5833 | 0.5833 | 0.5833 | 0.5833 | 0.4861 | 0.2916 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH_2010 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1458 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1944 | 0.3888 | 0.3888 | 0.5833 | 0.5833 | 0.8749 | 0.8749 | 0.8749 | 0.8749 | 0.8749 | 0.8749 | 0.8749 | 0.8749 | 0.8749 | 0.8749 | 0.8749 | 0.8749 | 0.4861 | 0.2916 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH_2010 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH_2010 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_DINING_SCH_2010 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1944 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2916 | 0.2916 | 0.5833 | 0.5833 | 0.7777 | 0.7777 | 0.7777 | 0.7777 | 0.7777 | 0.7777 | 0.7777 | 0.8749 | 0.8749 | 0.8749 | 0.8749 | 0.8749 | 0.4861 | 0.2916 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2010_2013 | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.16446 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.24669 | 0.24669 | 0.41115 | 0.41115 | 0.57561 | 0.57561 | 0.57561 | 0.57561 | 0.57561 | 0.57561 | 0.49338 | 0.49338 | 0.49338 | 0.49338 | 0.49338 | 0.49338 | 0.41115 | 0.24669 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2010_2013 | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.12334 | 0.15 | 0.15 | 0.15 | 0.15 | 0.16446 | 0.32892 | 0.32892 | 0.49338 | 0.49338 | 0.74007 | 0.74007 | 0.74007 | 0.74007 | 0.74007 | 0.74007 | 0.74007 | 0.74007 | 0.74007 | 0.74007 | 0.74007 | 0.74007 | 0.41115 | 0.24669 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2010_2013 | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2010_2013 | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2010_2013 | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.16446 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.24669 | 0.24669 | 0.49338 | 0.49338 | 0.65784 | 0.65784 | 0.65784 | 0.65784 | 0.65784 | 0.65784 | 0.65784 | 0.74007 | 0.74007 | 0.74007 | 0.74007 | 0.74007 | 0.41115 | 0.24669 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_LIGHT_SCH | Lighting |  | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2 | From DOE Prototype Buildings
RestaurantSitDown BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35 | From DOE Prototype Buildings
RestaurantSitDown BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2 | From DOE Prototype Buildings
RestaurantSitDown BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | From DOE Prototype Buildings
RestaurantSitDown BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | From DOE Prototype Buildings
RestaurantSitDown BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | From DOE Prototype Buildings
RestaurantSitDown Booster Water Inlet Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Booster Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 26 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 28.9 | 27.8 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | From DOE Prototype Buildings
RestaurantSitDown CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown DOOR_INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.258 | 0.258 | 0.363 | 0.558 | 0.558 | 0.363 | 0.258 | 0.363 | 0.462 | 0.558 | 0.65 | 0.74 | 0.462 | 0.258 | 0.258 | From DOE Prototype Buildings
RestaurantSitDown DOOR_INFIL_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown DOOR_INFIL_SCH | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown DOOR_INFIL_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.462 | 0.258 | 0.462 | 0.558 | 0.558 | 0.462 | 0.363 | 0.363 | 0.363 | 0.74 | 0.915 | 0.74 | 0.65 | 0.558 | 0.363 | From DOE Prototype Buildings
RestaurantSitDown DOOR_INFIL_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.462 | 0.462 | 0.462 | 0.258 | 0.558 | 0.829 | 0.74 | 0.462 | 0.258 | 0.363 | 0.558 | 0.829 | 0.829 | 0.829 | 0.558 | 0.363 | 0.258 | From DOE Prototype Buildings
RestaurantSitDown Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Hours_of_operation | Operation |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 19 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 16.7 | 17.8 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 19 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown HVACOperationSchd | Operation |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown INFIL_HALF_ON_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
RestaurantSitDown INFIL_SCH_PNNL | Infiltration |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
RestaurantSitDown Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.93371 | 0 | 0 | 0 | 0 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | From DOE Prototype Buildings
RestaurantSitDown Kitchen Water Equipment Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Kitchen Water Equipment Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Kitchen Water Equipment Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Kitchen Water Equipment Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RestaurantSitDown Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
RestaurantSitDown Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RestaurantSitDown Kitchen_Exhaust_SCH | Equipment |  | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown MaxRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown MinOA_FFKitch_Sched | OA Air |  | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | From DOE Prototype Buildings
RestaurantSitDown MinOA_FFKitch_Sched | OA Air |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.65 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown MinOA_MotorizedDamper_Sched | OA Air |  | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown MinOA_SDKitch_Sched | OA Air |  | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RestaurantSitDown MinOA_SDKitch_Sched | OA Air |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown MinRelHumSetSch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Rest_GAS_EQUIP_SCH | Equipment |  | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03 | From DOE Prototype Buildings
RestaurantSitDown Rest_GAS_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Rest_GAS_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.29 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown SWHSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown SWHSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown SWHSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.241 | 0.241 | 0.345 | 0.542 | 0.542 | 0.345 | 0.241 | 0.345 | 0.445 | 0.542 | 0.637 | 0.73 | 0.445 | 0.241 | 0.241 | From DOE Prototype Buildings
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.445 | 0.241 | 0.445 | 0.542 | 0.542 | 0.445 | 0.345 | 0.345 | 0.345 | 0.73 | 0.911 | 0.73 | 0.637 | 0.542 | 0.345 | From DOE Prototype Buildings
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.445 | 0.445 | 0.445 | 0.241 | 0.542 | 0.821 | 0.73 | 0.445 | 0.241 | 0.345 | 0.542 | 0.821 | 0.821 | 0.821 | 0.542 | 0.345 | 0.241 | From DOE Prototype Buildings
RestaurantSitDown walkin_occ_lght_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.312 | 0.312 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.26 | 0.156 | From DOE Prototype Buildings
RestaurantSitDown walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RestaurantSitDown walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.26 | 0.26 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.26 | 0.156 | From DOE Prototype Buildings
RestaurantSitDown walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.104 | 0.208 | 0.208 | 0.312 | 0.312 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.26 | 0.156 | From DOE Prototype Buildings
RestaurantSitDown WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Retail Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
Retail Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | From DOE Reference Buildings
Retail Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Retail Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Retail Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | From DOE Reference Buildings
Retail Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | From DOE Reference Buildings
Retail Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
Retail Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Retail Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Retail Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Retail Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
Retail Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | From DOE Reference Buildings
Retail Bldg Occ | Occupancy |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Retail Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Retail Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | From DOE Reference Buildings
Retail ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | From DOE Reference Buildings
Retail ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
Retail ClgSetp | Thermostat Setpoint | C | Sun | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
Retail ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | From DOE Reference Buildings
Retail Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Retail Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Retail Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Retail Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Retail FRONT ENTRY COOLING | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 90 | [23 empty] | From DOE Reference Buildings
Retail HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Retail HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
Retail HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
Retail HtgSetp | Thermostat Setpoint | C | Sun | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Retail HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
Retail INFIL FRONT | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
Retail INFIL FRONT | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Retail INFIL FRONT | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
Retail INFIL FRONT | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | From DOE Reference Buildings
Retail Infil Half On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Reference Buildings
Retail Infil Half On | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Retail Infil Half On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
Retail Infil Half On | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | From DOE Reference Buildings
Retail Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
RetailStandalone ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
RetailStandalone AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
RetailStandalone ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_ELEVATORS | Elevator |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_ELEVATORS | Elevator |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_ELEVATORS | Elevator |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | From DOE Prototype Buildings
RetailStandalone BLDG_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | From DOE Prototype Buildings
RetailStandalone BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH_2010 | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH_2010 | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH_2010 | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH_2010 | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_OCC_SCH_2010 | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone BLDG_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStandalone CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CoolingCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Prototype Buildings
RetailStandalone Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone FAN_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone FRONT_ENTRY_COOLING | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 100 | [23 empty] | From DOE Prototype Buildings
RetailStandalone FrontEntry_CoilSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone FrontEntry_FanSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Hot Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Hours_of_operation | Operation |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone Hours_of_operation | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone Hours_of_operation | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | C | WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStandalone Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50 | [23 empty] | From DOE Prototype Buildings
RetailStandalone HVACOperationSchd | Operation |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone HVACOperationSchd | Operation |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone HVACOperationSchd | Operation |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RetailStandalone INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone INFIL_HALF_ON_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_HALF_ON_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone INFIL_HALF_ON_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_HALF_ON_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone INFIL_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH_PNNL | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH_PNNL | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone INFIL_SCH_PNNL | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
RetailStandalone MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone PlantOnSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone ReheatCoilAvailSched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
RetailStandalone Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
RetailStandalone SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStandalone WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
RetailStripmall AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
RetailStripmall ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
RetailStripmall CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Hot Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
RetailStripmall INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Fri¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | From DOE Prototype Buildings
RetailStripmall Type1_EQUIP_SCH | Equipment |  | Default¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | From DOE Prototype Buildings
RetailStripmall Type1_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_EQUIP_SCH | Equipment |  | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | From DOE Prototype Buildings
RetailStripmall Type1_FAN_SCH | Unknown |  | Default¦SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type1_FAN_SCH | Unknown |  | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | From DOE Prototype Buildings
RetailStripmall Type1_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_Infil_SCH | Infiltration |  | Default¦SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
RetailStripmall Type1_Infil_SCH | Infiltration |  | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
RetailStripmall Type1_LIGHT_SCH | Lighting |  | Default¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | From DOE Prototype Buildings
RetailStripmall Type1_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_LIGHT_SCH | Lighting |  | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | From DOE Prototype Buildings
RetailStripmall Type1_MinOA_MotorizedDamper_SCH | OA Air |  | Default¦SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type1_MinOA_MotorizedDamper_SCH | OA Air |  | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type1_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.6 | 0.4 | 0.4 | 0.3 | 0.6 | 0.6 | 0.4 | 0.4 | 0.3 | 0.2 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type1_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type1_OCC_SCH | Occupancy |  | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.2 | 0.6 | 0.4 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.2 | From DOE Prototype Buildings
RetailStripmall Type1_OCC_SCH | Occupancy |  | Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type1_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.16 | 0.1 | From DOE Prototype Buildings
RetailStripmall Type1_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.23 | 0.32 | 0.41 | 0.65 | 0.6 | 0.55 | 0.45 | 0.5 | 0.46 | 0.47 | 0.34 | 0.33 | 0.23 | 0.13 | From DOE Prototype Buildings
RetailStripmall Type1_SWH_SCH | Service Water Heating |  | SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.62 | 0.6 | 0.55 | 0.45 | 0.5 | 0.46 | 0.47 | 0.34 | 0.33 | 0.23 | 0.13 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type2_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_FAN_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_FAN_SCH | Unknown |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_FAN_SCH | Unknown |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type2_Infil_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type2_Infil_SCH | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type2_Infil_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type2_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type2_MinOA_MotorizedDamper_SCH | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_MinOA_MotorizedDamper_SCH | OA Air |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_MinOA_MotorizedDamper_SCH | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.2 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type2_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.4 | 0.3 | 0.3 | 0.3 | 0.05 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.3 | 0.2 | 0.2 | 0.5 | 0.5 | 0.2 | 0.05 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.14 | 0.29 | 0.33 | 0.4 | 0.36 | 0.37 | 0.35 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.62 | 0.6 | 0.5 | 0.48 | 0.47 | 0.34 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type2_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 23.89 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
RetailStripmall Type3_EQUIP_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_EQUIP_SCH | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_EQUIP_SCH | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_FAN_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_FAN_SCH | Unknown |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_FAN_SCH | Unknown |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | From DOE Prototype Buildings
RetailStripmall Type3_Infil_SCH | Infiltration |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type3_Infil_SCH | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type3_Infil_SCH | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
RetailStripmall Type3_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_LIGHT_SCH | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | From DOE Prototype Buildings
RetailStripmall Type3_MinOA_MotorizedDamper_SCH | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_MinOA_MotorizedDamper_SCH | OA Air |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_MinOA_MotorizedDamper_SCH | OA Air |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.43 | 0.46 | 0.5 | 0.69 | 0.34 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_OCC_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
RetailStripmall Type3_OCC_SCH | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.58 | 0.71 | 0.74 | 0.77 | 0.8 | 0.74 | 0.54 | 0.11 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.43 | 0.46 | 0.71 | 0.5 | 0.69 | 0.54 | 0.71 | 0.34 | 0.26 | 0.11 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_SWH_SCH | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall Type3_SWH_SCH | Service Water Heating |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.25 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0 | 0 | 0 | From DOE Prototype Buildings
RetailStripmall WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Schedule:Compact 1 | Unknown |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | From DOE Reference Buildings
Schedule:Compact 1 | Unknown |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Schedule:Compact 1 | Unknown |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
SchoolPrimary ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Latent fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Sensible fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.35 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Wknd | 2014-06-16 | 2014-09-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Wknd | 2014-01-01 | 2014-06-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Sat | 2014-09-16 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Sun¦Sat | 2014-06-16 | 2014-09-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Sun¦Sat | 2014-01-01 | 2014-06-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Booster Water Inlet Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Booster Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_Setup | Thermostat Setpoint | C | Default¦WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_Setup | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | From DOE Prototype Buildings
SchoolPrimary CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1.1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CoolingCoilAvailSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolPrimary Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolPrimary FAN_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Hours_of_operation | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Hours_of_operation | Operation |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_Setback | Thermostat Setpoint | C | Default¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_Setback | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_OTHER | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolPrimary Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 65 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HVACOperationSchd | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary HVACOperationSchd | Operation |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary INFIL_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolPrimary INFIL_SCH_PNNL | Infiltration |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary INFIL_SCH_PNNL | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.02 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.02 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.02 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary MinOA_Kitchen_Sched | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary MinOA_Kitchen_Sched | Equipment |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolPrimary MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary PlantOnSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary ReheatCoilAvailSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary SHWSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary SHWSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary VAV-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolPrimary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolPrimary WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ACTIVITY_SCH | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary AIR_VELO_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Latent fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Sensible fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Hot Supply Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Latent fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Sensible fract sched | Service Water Heating |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Temp Sched | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_ELEVATORS | Elevator |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_ELEVATORS | Elevator |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_ELEVATORS | Elevator |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.25 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.35 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_LIGHT_SCH | Lighting |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Wknd | 2014-06-16 | 2014-09-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Wknd | 2014-01-01 | 2014-06-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Sat | 2014-09-16 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Sun¦Sat | 2014-06-16 | 2014-09-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Sun¦Sat | 2014-01-01 | 2014-06-15 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary BLDG_SWH_SCH | Service Water Heating |  | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Booster Water Inlet Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Booster Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_PSZ_AC | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_Setback | Thermostat Setpoint | C | Default¦WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_Setback | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44 | From DOE Prototype Buildings
SchoolSecondary CLOTHING_SCH | Clothing | W | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLOTHING_SCH | Clothing | W | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CLOTHING_SCH | Clothing | W | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1.1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CoolingCoilAvailSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary CW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Dual Zone Control Type Sched | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7 | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolSecondary Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolSecondary FAN_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Heating-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Hours_of_operation | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Hours_of_operation | Operation |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_PSZ_AC | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_Setback | Thermostat Setpoint | C | Default¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_Setback | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HTGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | C | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Prototype Buildings
SchoolSecondary Humidity Setpoint Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 65 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HVACOperationSchd | Operation |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary HVACOperationSchd | Operation |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary HW-Loop-Temp-Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary INFIL_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolSecondary INFIL_SCH_PNNL | Infiltration |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary INFIL_SCH_PNNL | Infiltration |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_Exhaust_SCH_DCV | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.02 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.02 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.02 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Equipment | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | W | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
SchoolSecondary MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary PlantOnSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary ReheatCoilAvailSched | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | C | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary SHADING_SCH | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary SHWSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary SHWSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary SHWSys1-Loop-Temp-Schedule | Service Water Heating | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary VAV-Supply-Air-Temp-Sch | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Prototype Buildings
SchoolSecondary walkin_occ_lght_SCH | Occupancy |  | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773 | From DOE Prototype Buildings
SchoolSecondary WORK_EFF_SCH | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
SecondarySchool Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Wkdy¦SmrDsn | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Auditorium Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool BLDG ELEVATORS | Elevator |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool BLDG ELEVATORS | Elevator |  | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.25 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Wkdy¦SmrDsn | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | From DOE Reference Buildings
SecondarySchool Bldg Equip | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.35 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Wkdy¦SmrDsn | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | From DOE Reference Buildings
SecondarySchool Bldg Light | Lighting |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Wkdy¦SmrDsn | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Bldg Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Wkdy¦SmrDsn | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Cafeteria Bldg Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool ClgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
SecondarySchool ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 27 | [23 empty] | From DOE Reference Buildings
SecondarySchool ClgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Reference Buildings
SecondarySchool ClgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
SecondarySchool ClgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27 | From DOE Reference Buildings
SecondarySchool ClgSetp BathCorrMechKitchen | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 27 | [23 empty] | From DOE Reference Buildings
SecondarySchool ClgSetp BathCorrMechKitchen | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | From DOE Reference Buildings
SecondarySchool Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Reference Buildings
SecondarySchool Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.6 | [23 empty] | From DOE Reference Buildings
SecondarySchool Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1.1 | [23 empty] | From DOE Reference Buildings
SecondarySchool Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.6 | [23 empty] | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Wkdy¦SmrDsn | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Extend Bldg Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Exterior Lights | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SecondarySchool Exterior Lights Always On | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SecondarySchool Gym Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Wkdy¦SmrDsn | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Gym Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
SecondarySchool HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
SecondarySchool HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Reference Buildings
SecondarySchool HtgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
SecondarySchool HtgSetp | Thermostat Setpoint | C | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | From DOE Reference Buildings
SecondarySchool HtgSetp BathCorrMechKitchen | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16 | [23 empty] | From DOE Reference Buildings
SecondarySchool HtgSetp BathCorrMechKitchen | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | From DOE Reference Buildings
SecondarySchool Infil | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Wkdy¦SmrDsn | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13 | 0.13 | 0.2 | 0.2 | 0.2 | 0.13 | 0.13 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
SecondarySchool Kitchen Equip | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Exhaust | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Kitchen Exhaust | Equipment |  | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Wkdy¦SmrDsn | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | From DOE Reference Buildings
SecondarySchool Kitchen Gas | Equipment |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.02 | [23 empty] | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Wkdy¦SmrDsn | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SecondarySchool Office Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SecondarySchool PSZ-AC OA Damper | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
SecondarySchool PSZ-AC OA Damper | Operation | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
SecondarySchool PSZ-AC OA Damper | Operation | Dimensionless | Sat¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool PSZ-AC Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
SecondarySchool PSZ-AC Operation | Operation | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
SecondarySchool PSZ-AC Operation | Operation | Dimensionless | Sat¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool VAV OA Damper | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
SecondarySchool VAV OA Damper | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool VAV Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
SecondarySchool VAV Operation | Operation | Dimensionless | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
SecondarySchool VAV Operation | Operation | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Small Office Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | From DOE Reference Buildings
Small Office Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Reference Buildings
Small Office Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | From DOE Reference Buildings
Small Office Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.05 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Small Office Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
Small Office Bldg Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Small Office Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | From DOE Reference Buildings
Small Office Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Small Office ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | From DOE Reference Buildings
Small Office ClgSetp | Thermostat Setpoint | C | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Reference Buildings
Small Office ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | From DOE Reference Buildings
Small Office Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Small Office Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Small Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Small Office Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Small Office HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
Small Office HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
Small Office HtgSetp | Thermostat Setpoint | C | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
Small Office HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
Small Office Infil Quarter On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | From DOE Reference Buildings
Small Office Infil Quarter On | Infiltration |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
Small Office Infil Quarter On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Small Office Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
SmallHotel BLDG ELEVATORS | Elevator |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | From DOE Reference Buildings
SmallHotel Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | From DOE Reference Buildings
SmallHotel Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | From DOE Reference Buildings
SmallHotel Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | From DOE Reference Buildings
SmallHotel Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | From DOE Reference Buildings
SmallHotel Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | From DOE Reference Buildings
SmallHotel Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | From DOE Reference Buildings
SmallHotel Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | From DOE Reference Buildings
SmallHotel Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | From DOE Reference Buildings
SmallHotel Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | From DOE Reference Buildings
SmallHotel ClgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24 | [23 empty] | From DOE Reference Buildings
SmallHotel Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
SmallHotel Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
SmallHotel Corridor Light | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Exercise Equip | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | From DOE Reference Buildings
SmallHotel Exercise Light | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | From DOE Reference Buildings
SmallHotel Exercise Occ | Occupancy |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | From DOE Reference Buildings
SmallHotel Exterior Lights | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel GuestRoom Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Reference Buildings
SmallHotel GuestRoom Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel GuestRoom Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel GuestRoom Equip | Equipment |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | From DOE Reference Buildings
SmallHotel GuestRoom Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | From DOE Reference Buildings
SmallHotel GuestRoom Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel GuestRoom Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel GuestRoom Light | Lighting |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | From DOE Reference Buildings
SmallHotel GuestRoom Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | From DOE Reference Buildings
SmallHotel GuestRoom Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel GuestRoom Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel GuestRoom Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
SmallHotel HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
SmallHotel Infil | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Infil Half On | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
SmallHotel Laundry Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Laundry Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Laundry Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Laundry Gas | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Laundry Gas | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Laundry Gas | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Laundry Light | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Laundry Occ | Occupancy |  | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Laundry Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Laundry Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Meeting Equip | Equipment |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Meeting Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | From DOE Reference Buildings
SmallHotel Meeting Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Meeting Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Meeting Occ | Occupancy |  | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Meeting Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Meeting Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Office Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Reference Buildings
SmallHotel Office Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Office Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Office Equip | Equipment |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | From DOE Reference Buildings
SmallHotel Office Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | From DOE Reference Buildings
SmallHotel Office Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Office Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Office Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Reference Buildings
SmallHotel Office Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Office Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel Office Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | From DOE Reference Buildings
SmallHotel PSZ-AC OA Damper | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel PSZ-AC Operation | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel PTAC OA Damper | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel PTAC Operation | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Split-AC OA Damper | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Split-AC Operation | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel StaffLounge Equip | Equipment |  | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | From DOE Reference Buildings
SmallHotel StaffLounge Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel StaffLounge Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel StaffLounge Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05 | From DOE Reference Buildings
SmallHotel StaffLounge Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel StaffLounge Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel StaffLounge Light | Lighting |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05 | From DOE Reference Buildings
SmallHotel StaffLounge Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel StaffLounge Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel StaffLounge Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel StaffLounge Occ | Occupancy |  | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
SmallHotel Storage Light | Lighting |  | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | From DOE Reference Buildings
SmallHotel Storage Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallHotel Storage Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SmallHotel UnitHeater ClgSP Sch | Thermostat Setpoint |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 40 | [23 empty] | From DOE Reference Buildings
SmallHotel UnitHeater HtgSP Sch | Thermostat Setpoint |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
SmallHotel Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SmallOffice Exterior Lights | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SmallOffice Exterior Lights Always On | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallOffice PSZ-AC OA Damper | Operation | Dimensionless | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
SmallOffice PSZ-AC OA Damper | Operation | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0
SmallOffice PSZ-AC Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
SmallOffice PSZ-AC Operation | Operation | Dimensionless | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallOffice PSZ-AC Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
StripMall Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
StripMall Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | From DOE Reference Buildings
StripMall Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
StripMall Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
StripMall Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | From DOE Reference Buildings
StripMall Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | From DOE Reference Buildings
StripMall Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
StripMall Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
StripMall Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
StripMall Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | From DOE Reference Buildings
StripMall Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
StripMall Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | From DOE Reference Buildings
StripMall Bldg Occ | Occupancy |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
StripMall Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
StripMall Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | From DOE Reference Buildings
StripMall ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | From DOE Reference Buildings
StripMall ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
StripMall ClgSetp | Thermostat Setpoint | C | Sun | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
StripMall ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | From DOE Reference Buildings
StripMall Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
StripMall Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
StripMall Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
StripMall Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
StripMall HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
StripMall HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
StripMall HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
StripMall HtgSetp | Thermostat Setpoint | C | Sun | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | From DOE Reference Buildings
StripMall HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
StripMall Infil Half On | Infiltration |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | From DOE Reference Buildings
StripMall Infil Half On | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
StripMall Infil Half On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
StripMall Infil Half On | Infiltration |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | From DOE Reference Buildings
StripMall Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SuperMarket Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
SuperMarket Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | From DOE Reference Buildings
SuperMarket Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SuperMarket Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SuperMarket Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.15 | 0.15 | From DOE Reference Buildings
SuperMarket Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | From DOE Reference Buildings
SuperMarket Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
SuperMarket Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SuperMarket Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SuperMarket Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | From DOE Reference Buildings
SuperMarket Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | From DOE Reference Buildings
SuperMarket Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0 | 0 | From DOE Reference Buildings
SuperMarket Bldg Occ | Occupancy |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
SuperMarket Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SuperMarket Bldg Occ | Occupancy |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | From DOE Reference Buildings
SuperMarket Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | From DOE Reference Buildings
SuperMarket Bldg Swh | Service Water Heating |  | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | From DOE Reference Buildings
SuperMarket Bldg Swh | Service Water Heating |  | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | From DOE Reference Buildings
SuperMarket Bldg Swh | Service Water Heating |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | From DOE Reference Buildings
SuperMarket ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | From DOE Reference Buildings
SuperMarket ClgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
SuperMarket Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SuperMarket Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
SuperMarket Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SuperMarket Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
SuperMarket HtgSetp | Thermostat Setpoint | C | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | From DOE Reference Buildings
SuperMarket HtgSetp | Thermostat Setpoint | C | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
SuperMarket Infil Half On | Infiltration |  | Default¦SmrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | From DOE Reference Buildings
SuperMarket Infil Half On | Infiltration |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
SuperMarket Infil Half On | Infiltration |  | Sun | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Reference Buildings
SuperMarket Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Warehouse Activity | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120 | [23 empty] | From DOE Reference Buildings
Warehouse Always Off Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse Always On Schedule | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse ALWAYS_OFF | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse Bldg Equip | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Warehouse Bldg Equip | Equipment |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Equip | Equipment |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Equip | Equipment |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Equip | Equipment |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Warehouse Bldg Light | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Warehouse Bldg Light | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Light | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Light | Lighting |  | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Light | Lighting |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.24 | 0.24 | 0.24 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Reference Buildings
Warehouse Bldg Occ | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Warehouse Bldg Occ | Occupancy |  | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Occ | Occupancy |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Warehouse Bldg Occ | Occupancy |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Reference Buildings
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.18 | [23 empty] | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.42 | 0.77 | 0.77 | 0.77 | 0.77 | 0.68 | 0.77 | 0.77 | 0.77 | 0.77 | 0.61 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1 | [23 empty] | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.6 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | From DOE Prototype Buildings
Warehouse BLDG_OCC_SCH | Occupancy |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse BLDG_OCC_SCH | Occupancy |  | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Warehouse Bulk Storage Heating Setpoint Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 10 | [23 empty] | From DOE Prototype Buildings
Warehouse ClgSetp | Thermostat Setpoint | C | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
Warehouse ClgSetp | Thermostat Setpoint | C | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 30 | [23 empty] | From DOE Reference Buildings
Warehouse ClgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | From DOE Reference Buildings
Warehouse ClgSetp FineStorage | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Reference Buildings
Warehouse Clothing | Clothing |  | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Warehouse Clothing | Clothing |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Warehouse Clothing | Clothing |  | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Reference Buildings
Warehouse Clothing | Clothing |  | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5 | [23 empty] | From DOE Reference Buildings
Warehouse COMPACT HVAC-ALWAYS 1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse COMPACT HVAC-ALWAYS 4 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4 | [23 empty] | From DOE Prototype Buildings
Warehouse Exterior_Lgt_189_1 | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5 | [23 empty] | From DOE Prototype Buildings
Warehouse Exterior_Lgt_ALWAYS_ON | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse Exterior_lighting_schedule_a | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
Warehouse Exterior_lighting_schedule_b | Lighting |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
Warehouse Exterior_Ltg_Sch | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | From DOE Prototype Buildings
Warehouse FanSched | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse FanSched | Unknown |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse FanSched | Unknown |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Warehouse Fine Storage Cooling Setpoint Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7 | [23 empty] | From DOE Prototype Buildings
Warehouse Fine Storage Heating Setpoint Schedule | Unknown | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56 | [23 empty] | From DOE Prototype Buildings
Warehouse Hot Water Setpoint Temp Schedule | Unknown | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60 | [23 empty] | From DOE Prototype Buildings
Warehouse HtgSetp | Thermostat Setpoint | C | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | From DOE Reference Buildings
Warehouse HtgSetp | Thermostat Setpoint | C | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21 | [23 empty] | From DOE Reference Buildings
Warehouse HtgSetp | Thermostat Setpoint | C | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 15.5 | [23 empty] | From DOE Reference Buildings
Warehouse HtgSetp | Thermostat Setpoint | C | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | From DOE Reference Buildings
Warehouse HtgSetp BulkStorage | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 7.2 | [23 empty] | From DOE Reference Buildings
Warehouse HtgSetp FineStorage | Thermostat Setpoint | C | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6 | [23 empty] | From DOE Reference Buildings
Warehouse INFIL_Door_Opening_SCH | Infiltration |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse INFIL_Door_Opening_SCH | Infiltration |  | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Warehouse MinOA_MotorizedDamper_Sched | OA Air |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse MinOA_MotorizedDamper_Sched | OA Air |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse MinOA_MotorizedDamper_Sched | OA Air |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Warehouse MinOA_Sched | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse OA Damper Always ON Schedule | OA Air |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse OA Damper Off during off hrs Schedule | OA Air |  | Default¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse OA Damper Off during off hrs Schedule | OA Air |  | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse OA Damper Off during off hrs Schedule | OA Air |  | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Warehouse Office Activity Schedule | Activity | W | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 131.85 | [23 empty] | From DOE Prototype Buildings
Warehouse Office_Plug_SCH | Unknown |  | Default | 2014-01-01 | 2014-12-31 | Constant | 0.3 | [23 empty] | From DOE Prototype Buildings
Warehouse Office_Plug_SCH | Unknown |  | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Prototype Buildings
Warehouse Office_Plug_SCH | Unknown |  | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Warehouse Office_Plug_SCH | Unknown |  | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | From DOE Prototype Buildings
Warehouse Work Eff | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0 | [23 empty] | From DOE Reference Buildings
Warehouse ZoneControlSchedule | Unknown |  | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1 | [23 empty] | From DOE Prototype Buildings
Stripmall HVACOperationSchd | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Stripmall HVACOperationSchd | Equipment |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
Stripmall HVACOperationSchd | Equipment |  | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings
Stripmall MinOA_Sched | Equipment |  | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | From DOE Prototype Buildings
Stripmall MinOA_Sched | Equipment |  | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | From DOE Prototype Buildings
Stripmall MinOA_Sched | Equipment |  | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | From DOE Prototype Buildings

## Chillers
Each row represents the efficiency standards for a specificy type of chiller
Template | Cooling Type | Condenser Type | Compressor Type | Absorption Type | Minimum Capacity (Tons) | Maximum Capacity (Tons) | Minimum Full Load Efficiency (kW/ton) | Minimum Integrated Part Load Value (kW/ton) | CAPFT | EIRFT | EIRFPLR | Notes
90.1-2004 | AirCooled | WithCondenser |  |  | 0 | 9999 | 1.256 | 1.153 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR
90.1-2004 | AirCooled | WithoutCondenser |  |  | 0 | 9999 | 1.135 | 1.019
90.1-2004 | AirCooled |  |  | Single Effect | 0 | 9999 | 5.862
90.1-2007 | AirCooled | WithCondenser |  |  | 0 | 9999 | 1.29 | 1.164 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR | Form 90.1-2007 Table 6.8.1A
90.1-2010 | AirCooled | WithCondenser |  |  | 0 | 149.99 | 1.255 | 0.941 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR
90.1-2010 | AirCooled | WithCondenser |  |  | 150 | 9999 | 1.255 | 0.941 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR
90.1-2010 | AirCooled | WithoutCondenser |  |  | 0 | 9999 | 1.255 | 0.941 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR
90.1-2010 | AirCooled |  |  | Single Effect | 0 | 9999 | 5.862
90.1-2013 | AirCooled | WithCondenser |  |  | 0 | 149.99 | 1.188 | 0.876 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR
90.1-2013 | AirCooled | WithCondenser |  |  | 150 | 9999 | 1.188 | 0.857 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR
90.1-2013 | AirCooled | WithoutCondenser |  |  | 0 | 149.99 | 1.188 | 0.876
90.1-2013 | AirCooled | WithoutCondenser |  |  | 150 | 9999 | 1.188 | 0.857
90.1-2013 | AirCooled |  |  | Single Effect | 0 | 9999 | 5.862
DOE Ref 1980-2004 | AirCooled | WithCondenser |  |  | 150 | 9999 | 1.407 | 1.407 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | WithoutCondenser |  |  | 0 | 9999 | 1.135 | 1.099 |  |  |  | From 90.1-1989
DOE Ref Pre-1980 | AirCooled | WithCondenser |  |  | 0 | 149.99 | 1.303 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled | WithCondenser |  |  | 150 | 299.99 | 1.332 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled | WithCondenser |  |  | 300 | 9999 | 1.332 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled | WithoutCondenser |  |  | 0 | 149.99 | 1.303 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled | WithoutCondenser |  |  | 150 | 299.99 | 1.332 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled | WithoutCondenser |  |  | 300 | 9999 | 1.332 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled |  |  | Single Effect | 0 | 9999 | 6.395 |  |  |  |  | From DOE Reference Buildings
90.1-2004 | WaterCooled |  | Reciprocating |  | 0 | 149.99 | 0.837 | 0.696
90.1-2004 | WaterCooled |  | Reciprocating |  | 150 | 9999 | 0.837 | 0.696
90.1-2004 | WaterCooled |  | Rotary Screw |  | 0 | 149.99 | 0.79 | 0.676
90.1-2004 | WaterCooled |  | Rotary Screw |  | 150 | 299.99 | 0.718 | 0.628
90.1-2004 | WaterCooled |  | Rotary Screw |  | 300 | 9999 | 0.639 | 0.572
90.1-2004 | WaterCooled |  | Scroll |  | 0 | 149.99 | 0.79 | 0.676
90.1-2004 | WaterCooled |  | Scroll |  | 150 | 299.99 | 0.718 | 0.628
90.1-2004 | WaterCooled |  | Scroll |  | 300 | 9999 | 0.639 | 0.572
90.1-2004 | WaterCooled |  | Centrifugal |  | 0 | 149.99 | 0.703 | 0.67
90.1-2004 | WaterCooled |  | Centrifugal |  | 150 | 299.99 | 0.634 | 0.596
90.1-2004 | WaterCooled |  | Centrifugal |  | 300 | 9999 | 0.577 | 0.55
90.1-2004 | WaterCooled |  |  | Single Effect | 0 | 9999 | 5.024
90.1-2010 | WaterCooled |  | Reciprocating |  | 0 | 74.99 | 0.78 | 0.63 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Reciprocating |  | 75 | 149.99 | 0.775 | 0.615 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Reciprocating |  | 150 | 299.99 | 0.68 | 0.58 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Reciprocating |  | 300 | 9999 | 0.62 | 0.54 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Scroll |  | 0 | 74.99 | 0.78 | 0.63 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Scroll |  | 75 | 149.99 | 0.775 | 0.615 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Scroll |  | 150 | 299.99 | 0.68 | 0.58 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Scroll |  | 300 | 9999 | 0.62 | 0.54 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Rotary Screw |  | 0 | 74.99 | 0.78 | 0.63 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Rotary Screw |  | 75 | 149.99 | 0.775 | 0.615 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Rotary Screw |  | 150 | 299.99 | 0.68 | 0.58 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Rotary Screw |  | 300 | 9999 | 0.62 | 0.54 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Centrifugal |  | 0 | 149.99 | 0.634 | 0.596 |  |  |  | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Centrifugal |  | 150 | 299.99 | 0.634 | 0.596 |  |  |  | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Centrifugal |  | 300 | 599.99 | 0.576 | 0.549 |  |  |  | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Centrifugal |  | 600 | 9999 | 0.57 | 0.539 |  |  |  | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  |  | Single Effect | 0 | 9999 | 5.024
90.1-2013 | WaterCooled |  | Reciprocating |  | 0 | 74.99 | 0.75 | 0.6
90.1-2013 | WaterCooled |  | Reciprocating |  | 75 | 149.99 | 0.72 | 0.56
90.1-2013 | WaterCooled |  | Reciprocating |  | 150 | 299.99 | 0.66 | 0.54
90.1-2013 | WaterCooled |  | Reciprocating |  | 300 | 599.99 | 0.61 | 0.52
90.1-2013 | WaterCooled |  | Reciprocating |  | 600 | 9999 | 0.56 | 0.5
90.1-2013 | WaterCooled |  | Scroll |  | 0 | 74.99 | 0.75 | 0.6
90.1-2013 | WaterCooled |  | Scroll |  | 75 | 149.99 | 0.72 | 0.56
90.1-2013 | WaterCooled |  | Scroll |  | 150 | 299.99 | 0.66 | 0.54
90.1-2013 | WaterCooled |  | Scroll |  | 300 | 599.99 | 0.61 | 0.52
90.1-2013 | WaterCooled |  | Scroll |  | 600 | 9999 | 0.56 | 0.5
90.1-2013 | WaterCooled |  | Rotary Screw |  | 0 | 74.99 | 0.75 | 0.6
90.1-2013 | WaterCooled |  | Rotary Screw |  | 75 | 149.99 | 0.72 | 0.56
90.1-2013 | WaterCooled |  | Rotary Screw |  | 150 | 299.99 | 0.66 | 0.54
90.1-2013 | WaterCooled |  | Rotary Screw |  | 300 | 599.99 | 0.61 | 0.52
90.1-2013 | WaterCooled |  | Rotary Screw |  | 600 | 9999 | 0.56 | 0.5
90.1-2013 | WaterCooled |  | Centrifugal |  | 0 | 149.99 | 0.61 | 0.55
90.1-2013 | WaterCooled |  | Centrifugal |  | 150 | 299.99 | 0.61 | 0.55
90.1-2013 | WaterCooled |  | Centrifugal |  | 300 | 399.99 | 0.56 | 0.52
90.1-2013 | WaterCooled |  | Centrifugal |  | 400 | 599.99 | 0.56 | 0.5
90.1-2013 | WaterCooled |  | Centrifugal |  | 600 | 9999 | 0.56 | 0.5
90.1-2013 | WaterCooled |  |  | Single Effect | 0 | 9999 | 5.024
DOE Ref 1980-2004 | WaterCooled |  | Reciprocating |  | 0 | 149.99 | 0.926 | 0.902 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Reciprocating |  | 150 | 299.99 | 0.837 | 0.782 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Reciprocating |  | 300 | 9999 | 0.676 | 0.664 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Rotary Screw |  | 0 | 149.99 | 0.926 | 0.902 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Rotary Screw |  | 150 | 299.99 | 0.837 | 0.782 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Rotary Screw |  | 300 | 9999 | 0.676 | 0.664 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Scroll |  | 0 | 149.99 | 0.926 | 0.902 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Scroll |  | 150 | 299.99 | 0.837 | 0.782 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Scroll |  | 300 | 9999 | 0.676 | 0.664 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Centrifugal |  | 0 | 149.99 | 0.926 | 0.902 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Centrifugal |  | 150 | 299.99 | 0.837 | 0.782 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Centrifugal |  | 300 | 9999 | 0.676 | 0.664 |  |  |  | From 90.1-1989
DOE Ref Pre-1980 | WaterCooled |  | Reciprocating |  | 0 | 149.99 | 0.884 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Reciprocating |  | 150 | 299.99 | 0.884 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Reciprocating |  | 300 | 9999 | 0.884 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Rotary Screw |  | 0 | 149.99 | 0.852 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Rotary Screw |  | 150 | 299.99 | 0.782 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Rotary Screw |  | 300 | 9999 | 0.688 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Scroll |  | 0 | 149.99 | 0.852 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Scroll |  | 150 | 299.99 | 0.782 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Scroll |  | 300 | 9999 | 0.688 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Centrifugal |  | 0 | 149.99 | 0.776 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Centrifugal |  | 150 | 299.99 | 0.713 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Centrifugal |  | 300 | 9999 | 0.635 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  |  | Single Effect | 0 | 9999 | 5.097 |  |  |  |  | From DOE Reference Buildings
90.1-2004 |  |  |  | Double Effect Indirect Fired | 0 | 9999 | 3.517 | 3.35
90.1-2004 |  |  |  | Double Effect Direct Fired | 0 | 9999 | 3.517 | 3.517
90.1-2010 |  |  |  | Double Effect Indirect Fired | 0 | 9999 | 3.517 | 3.35
90.1-2010 |  |  |  | Double Effect Direct Fired | 0 | 9999 | 3.517 | 3.517
90.1-2013 |  |  |  | Double Effect Indirect Fired | 0 | 9999 | 3.517 | 3.35
90.1-2013 |  |  |  | Double Effect Direct Fired | 0 | 9999 | 3.517 | 3.517
DOE Ref Pre-1980 |  |  |  | Double Effect Indirect Fired | 0 | 9999 | 3.589 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 |  |  |  | Double Effect Direct Fired | 0 | 9999 | 3.589 |  |  |  |  | From DOE Reference Buildings
NECB 2011 | WaterCooled |  | Scroll |  | 0 | 9999 | 1.406 |  | WaterCooled_Scroll_CAPFT_NECB2011 | WaterCooled_Scroll_EIRFT_NECB2011 | WaterCooled_Scroll_EIRFPLR_NECB2011
NECB 2011 | WaterCooled |  | Reciprocating |  | 0 | 9999 | 1.406 |  | WaterCooled_Reciprocating_CAPFT_NECB2011 | WaterCooled_Reciprocating_EIRFT_NECB2011 | WaterCooled_Reciprocating_EIRFPLR_NECB2011
NECB 2011 | WaterCooled |  | Rotary Screw |  | 0 | 9999 | 1.406 |  | WaterCooled_Screw_CAPFT_NECB2011 | WaterCooled_Screw_EIRFT_NECB2011 | WaterCooled_Screw_EIRFPLR_NECB2011
NECB 2011 | WaterCooled |  | Centrifugal |  | 0 | 9999 | 1.406 |  | WaterCooled_Centrifugal_CAPFT_NECB2011 | WaterCooled_Centrifugal_EIRFT_NECB2011 | WaterCooled_Centrifugal_EIRFPLR_NECB2011

## Unitary ACs
Each row represents the efficiency standards for a specificy type of unitary AC
Template | Cooling Type | Heating Type | Subcategory | Minimum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Minimum Seasonal Energy Efficiency Ratio (SEER) | Minimum Energy Efficiency Ratio (EER) | Minimum Integrated Part Load Value (kW/ton) | Minimum Integrated Energy Efficiency Ratio (IEER) | PTAC_EER_Coefficient_1 | PTAC_EER_Coefficient_2 | COOL CAP FT | COOL CAP FFLOW | COOL EIR FT | COOL EIR FFLOW | COOL PLF FPLR | Notes
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 11.09 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 0 | 64999 | 11.09 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 11.06 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 0 | 64999 | 11.06 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 |  |  |  |  | 10 | -0.00016 | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | PTAC | 0 | 9999999 |  |  |  |  | 10 | -0.00016 | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 |  | 9.63 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 |  | 9.63 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 65000 | 134999 |  | 9.63 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 65000 | 134999 |  | 9.63 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 |  | 9.28 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 |  | 9.28 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 135000 | 239999 |  | 9.28 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 135000 | 239999 |  | 9.28 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 |  | 8.92 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 |  | 8.92 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 240000 | 759999 |  | 8.92 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 240000 | 759999 |  | 8.92 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 |  | 8.63 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 |  | 8.63 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 760000 | 9999999 |  | 8.63 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 760000 | 9999999 |  | 8.63 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 0 | 64999 | 10 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 10 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 0 | 64999 | 9.7 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 9.7 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | PTAC | 0 | 9999999 |  |  |  |  | 10 | -0.00016 | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 |  |  |  |  | 10 | -0.00016 | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 65000 | 134999 |  | 8.9 | 8.3 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 |  | 8.9 | 8.3 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 65000 | 134999 |  | 8.9 | 8.3 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 |  | 8.9 | 8.3 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 135000 | 759999 |  | 8.5 | 7.5 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 135000 | 759999 |  | 8.5 | 7.5 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 135000 | 759999 |  | 8.5 | 7.5 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 135000 | 759999 |  | 8.5 | 7.5 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 760000 | 9999999 |  | 8.2 | 7.5 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 |  | 8.2 | 7.5 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 760000 | 9999999 |  | 8.2 | 7.5 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 |  | 8.2 | 7.5 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 10
90.1-2004 | AirCooled | All Other | Split System | 0 | 64999 | 10
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 9.7
90.1-2004 | AirCooled | All Other | Single Package | 0 | 64999 | 9.7
90.1-2004 | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 |  |  |  |  | 12.5 | -0.000213 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2004 | AirCooled | All Other | PTAC | 0 | 9999999 |  |  |  |  | 12.5 | -0.000213 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 |  | 10.3
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 |  | 10.3
90.1-2004 | AirCooled | All Other | Split System | 65000 | 134999 |  | 10.1
90.1-2004 | AirCooled | All Other | Single Package | 65000 | 134999 |  | 10.1
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 |  | 9.7
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 |  | 9.7
90.1-2004 | AirCooled | All Other | Split System | 135000 | 239999 |  | 9.5
90.1-2004 | AirCooled | All Other | Single Package | 135000 | 239999 |  | 9.5
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 |  | 9.5 | 9.7
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 |  | 9.5 | 9.7
90.1-2004 | AirCooled | All Other | Split System | 240000 | 759999 |  | 9.3 | 9.5
90.1-2004 | AirCooled | All Other | Single Package | 240000 | 759999 |  | 9.3 | 9.5
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 |  | 9.2 | 9.4
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 |  | 9.2 | 9.4
90.1-2004 | AirCooled | All Other | Split System | 760000 | 9999999 |  | 9 | 9.2
90.1-2004 | AirCooled | All Other | Single Package | 760000 | 9999999 |  | 9 | 9.2
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 13
90.1-2007 | AirCooled | All Other | Split System | 0 | 64999 | 13
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 13
90.1-2007 | AirCooled | All Other | Single Package | 0 | 64999 | 13
90.1-2007 | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 |  |  |  |  | 12.5 | -0.000213 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2007 | AirCooled | All Other | PTAC | 0 | 9999999 |  |  |  |  | 12.5 | -0.000213 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 |  | 10.3
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 |  | 10.3
90.1-2007 | AirCooled | All Other | Split System | 65000 | 134999 |  | 10.1
90.1-2007 | AirCooled | All Other | Single Package | 65000 | 134999 |  | 10.1
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 |  | 9.7
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 |  | 9.7
90.1-2007 | AirCooled | All Other | Split System | 135000 | 239999 |  | 9.5
90.1-2007 | AirCooled | All Other | Single Package | 135000 | 239999 |  | 9.5
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 |  | 9.5 | 9.7
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 |  | 9.5 | 9.7
90.1-2007 | AirCooled | All Other | Split System | 240000 | 759999 |  | 9.3 | 9.5
90.1-2007 | AirCooled | All Other | Single Package | 240000 | 759999 |  | 9.3 | 9.5
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 |  | 9.2 | 9.4
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 |  | 9.2 | 9.4
90.1-2007 | AirCooled | All Other | Split System | 760000 | 9999999 |  | 9 | 9.2
90.1-2007 | AirCooled | All Other | Single Package | 760000 | 9999999 |  | 9 | 9.2
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 13 | [5 empty] | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | All Other | Split System | 0 | 64999 | 13 | [5 empty] | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 13 | [5 empty] | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | All Other | Single Package | 0 | 64999 | 13 | [5 empty] | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 |  |  |  |  | 13.8 | -0.0003 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | All Other | PTAC | 0 | 9999999 |  |  |  |  | 13.8 | -0.0003 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 |  | 11.2 |  |  |  |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 |  | 11.2 |  |  |  |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | All Other | Split System | 65000 | 134999 |  | 11 |  |  |  |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | All Other | Single Package | 65000 | 134999 |  | 11 |  |  |  |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 |  | 11 |  |  |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 |  | 11 |  |  |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Split System | 135000 | 239999 |  | 10.8 |  |  |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Single Package | 135000 | 239999 |  | 10.8 |  |  |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 |  | 10 |  | 9.7 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 |  | 10 |  | 9.7 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Split System | 240000 | 759999 |  | 9.8 |  | 9.7 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Single Package | 240000 | 759999 |  | 9.8 |  | 9.7 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 |  | 9.7 |  | 9.4 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 |  | 9.7 |  | 9.4 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Split System | 760000 | 9999999 |  | 9.5 |  | 9.2 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Single Package | 760000 | 9999999 |  | 9.5 |  | 9.2 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 13
90.1-2013 | AirCooled | All Other | Split System | 0 | 64999 | 13
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 14
90.1-2013 | AirCooled | All Other | Single Package | 0 | 64999 | 14
90.1-2013 | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 |  |  |  |  | 14 | -0.0003 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2013 | AirCooled | All Other | PTAC | 0 | 9999999 |  |  |  |  | 14 | -0.0003 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 |  | 11.2 |  | 11.4
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 |  | 11.2 |  | 11.4
90.1-2013 | AirCooled | All Other | Split System | 65000 | 134999 |  | 11 |  | 11.2
90.1-2013 | AirCooled | All Other | Single Package | 65000 | 134999 |  | 11 |  | 11.2
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 |  | 11 |  | 11.2
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 |  | 11 |  | 11.2
90.1-2013 | AirCooled | All Other | Split System | 135000 | 239999 |  | 10.8 |  | 11
90.1-2013 | AirCooled | All Other | Single Package | 135000 | 239999 |  | 10.8 |  | 11
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 |  | 10 |  | 10.1
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 |  | 10 |  | 10.1
90.1-2013 | AirCooled | All Other | Split System | 240000 | 759999 |  | 9.8 |  | 9.9
90.1-2013 | AirCooled | All Other | Single Package | 240000 | 759999 |  | 9.8 |  | 9.9
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 |  | 9.7 |  | 9.8
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 |  | 9.7 |  | 9.8
90.1-2013 | AirCooled | All Other | Split System | 760000 | 9999999 |  | 9.5 |  | 9.6
90.1-2013 | AirCooled | All Other | Single Package | 760000 | 9999999 |  | 9.5 |  | 9.6
NECB 2011 | AirCooled | Electric Resistance or None | Single Package | - | 65000 | 14 | [5 empty] | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | All Other | Single Package | - | 65000 | 14 | [5 empty] | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | Electric Resistance or None | Split System | - | 65000 | 15 | [5 empty] | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | All Other | Split System | - | 65000 | 15 | [5 empty] | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | Electric Resistance or None | Single Package | 65001 | 249999 |  | 9.7 |  |  |  |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | All Other | Single Package | 65001 | 249999 |  | 9.7 |  |  |  |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | Electric Resistance or None | Split System | 65001 | 249999 |  | 9.7 |  |  |  |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | All Other | Split System | 65001 | 249999 |  | 9.7 |  |  |  |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | Electric Resistance or None | Single Package | 250000 | 759999 |  | 8.39 |  |  |  |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1: CHECK THIS
NECB 2011 | AirCooled | All Other | Single Package | 250000 | 759999 |  | 8.21 |  |  |  |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1: CHECK THIS
NECB 2011 | AirCooled | Electric Resistance or None | Split System | 250000 | 759999 |  | 8.39 |  |  |  |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1: CHECK THIS
NECB 2011 | AirCooled | All Other | Split System | 250000 | 759999 |  | 8.21 |  |  |  |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1: CHECK THIS
NECB 2011 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 |  | 8.12 |  |  |  |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | All Other | Single Package | 760000 | 9999999 |  | 7.94 |  |  |  |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 |  | 8.12 |  |  |  |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | All Other | Split System | 760000 | 9999999 |  | 7.94 |  |  |  |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | Electric Resistance or None | PTAC | - | 9999999 |  |  |  |  | 12.5 | -0.000213 | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | All Other | PTAC | - | 9999999 |  |  |  |  | 10.9 | -0.000213 | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1

## Heat Pumps Heating
Each row represents the efficiency standards for a specific type of heat pump
Template | Cooling Type | Subcategory | Minimum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Minimum Seasonal Efficiency (SEER) | Minimum Energy Efficiency Ratio (EER) | Minimum IPLV | HEAT CAP FT | HEAT CAP FFLOW | HEAT EIR FT | HEAT EIR FFLOW | HEAT PLF FPLR | Notes
NECB 2011 | AirCooled | Single Package | - | 65000 |  | 8.9 |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | Split System | - | 65000 |  | 8.9 |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | Single Package | 65001 | 238840 |  | 9.5 |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | Split System | 65001 | 238840 |  | 9.5 |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | Single Package | 238841 | 9999999 |  | 9.2 |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | Split System | 238841 | 9999999 |  | 9.2 |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From NECB 2011, Table 5.2.12.1

## Heat Pumps
Each row represents the efficiency standards for a specific type of heat pump
Template | Cooling Type | Heating Type | Subcategory | Minimum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Minimum Seasonal Efficiency (SEER) | Minimum Full Load Efficiency (EER) | Minimum IPLV | COOL CAP FT | COOL CAP FFLOW | COOL EIR FT | COOL EIR FFLOW | COOL PLF FPLR | Notes
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 0 | 9999999 | 13 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | All Other | Split System | 0 | 9999999 | 13 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 0 | 9999999 | 13 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | All Other | Single Package | 0 | 9999999 | 13 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR
NECB 2011 | AirCooled | Electric Resistance or None | Single Package | - | 65000 |  | 10 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | All Other | Single Package | - | 65000 |  | 10 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR
NECB 2011 | AirCooled | Electric Resistance or None | Split System | - | 65000 |  | 10 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | All Other | Split System | - | 65000 |  | 10 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR
NECB 2011 | AirCooled | Electric Resistance or None | Single Package | 65001 | 136480 |  | 9.26 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | All Other | Single Package | 65001 | 136480 |  | 9.08 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR
NECB 2011 | AirCooled | Electric Resistance or None | Split System | 65001 | 136480 |  | 9.26 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | All Other | Split System | 65001 | 136480 |  | 9.08 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR
NECB 2011 | AirCooled | Electric Resistance or None | Single Package | 136481 | 238840 |  | 8.9 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | All Other | Single Package | 136481 | 238840 |  | 8.72 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR
NECB 2011 | AirCooled | Electric Resistance or None | Split System | 136841 | 238840 |  | 8.9 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | All Other | Split System | 136841 | 238840 |  | 8.72 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR
NECB 2011 | AirCooled | Electric Resistance or None | Single Package | 238841 | 9999999 |  | 7.94 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | All Other | Single Package | 238841 | 9999999 |  | 7.76 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR
NECB 2011 | AirCooled | Electric Resistance or None | Split System | 238841 | 9999999 |  | 7.94 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR | From NECB 2011, Table 5.2.12.1
NECB 2011 | AirCooled | All Other | Split System | 238841 | 9999999 |  | 7.76 |  | DXCOOL-NECB2011-REF-CAPFT | DXCOOL-NECB2011-REF-CAPFFLOW | DXCOOL-NECB2011-REF-COOLEIRFT | DXCOOL-NECB2011-REF-COOLEIRFFLOW | DXCOOL-NECB2011-REF-COOLPLFFPLR

## Boilers
Each row represents the efficiency standards for a specific type of boiler
Template | Fluid Type | Fuel Type | Minimum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Minimum Annual Fuel Utilization Efficiency (AFUE) | Minimum Thermal Efficiency (%) | Minimum Combustion Efficiency (%) | EFFFPLR | Notes
DOE Ref Pre-1980 | Hot Water | Gas | 0 | 299999 |  | 0.73 |  | Boiler Constant Efficiency Curve | From DOE Reference Buildings
DOE Ref Pre-1980 | Hot Water | Gas | 300000 | 9999999999 |  | 0.74 |  | Boiler Constant Efficiency Curve | From DOE Reference Buildings
DOE Ref Pre-1980 | Hot Water | Gas | 250000000 | 9999999999 |  | 0.76 |  | Boiler Constant Efficiency Curve | From DOE Reference Buildings
DOE Ref 1980-2004 | Hot Water | Gas | 0 | 299999 | 0.8 |  |  | Boiler Constant Efficiency Curve | From 90.1-1989
DOE Ref 1980-2004 | Hot Water | Gas | 300000 | 249999999 |  |  | 0.8 | Boiler Constant Efficiency Curve | From 90.1-1989
90.1-2004 | Hot Water | Gas | 0 | 299999 | 0.8 |  |  | Boiler with No Minimum Turndown | From 90.1-2004
90.1-2004 | Hot Water | Gas | 300000 | 249999999 |  | 0.75 |  | Boiler with No Minimum Turndown | From 90.1-2004
90.1-2004 | Hot Water | Gas | 250000000 | 9999999999 |  |  | 0.8 | Boiler with No Minimum Turndown | From 90.1-2004
90.1-2007 | Hot Water | Gas | 0 | 299999 | 0.8 |  |  | Boiler with No Minimum Turndown | From 90.1-2007
90.1-2007 | Hot Water | Gas | 300000 | 249999999 |  | 0.8 |  | Boiler with No Minimum Turndown | From 90.1-2007
90.1-2007 | Hot Water | Gas | 250000000 | 9999999999 |  |  | 0.82 | Boiler with No Minimum Turndown | From 90.1-2007
90.1-2010 | Hot Water | Gas | 0 | 299999 | 0.8 |  |  | Boiler with No Minimum Turndown | From 90.1-2010
90.1-2010 | Hot Water | Gas | 300000 | 249999999 |  | 0.8 |  | Boiler with No Minimum Turndown | From 90.1-2010
90.1-2010 | Hot Water | Gas | 250000000 | 9999999999 |  |  | 0.82 | Boiler with No Minimum Turndown | From 90.1-2010
90.1-2013 | Hot Water | Gas | 0 | 299999 | 0.8 |  |  | Boiler with No Minimum Turndown | From 90.1-2013
90.1-2013 | Hot Water | Gas | 300000 | 999999 |  | 0.8 |  | Boiler with No Minimum Turndown | From 90.1-2013
90.1-2013 | Hot Water | Gas | 1000000 | 249999999 |  | 0.8 |  | Boiler with Minimum Turndown | From 90.1-2013
90.1-2013 | Hot Water | Gas | 250000000 | 9999999999 |  |  | 0.82 | Boiler with Minimum Turndown | From 90.1-2013
NECB 2011 | Hot Water | Gas | - | 299999 | 0.85 |  |  | BOILER-EFFFPLR-NECB2011 | From NECB 2011
NECB 2011 | Hot Water | Gas | 300000 | 2499999 |  | 0.83 |  | BOILER-EFFFPLR-NECB2011 | From NECB 2011
NECB 2011 | Hot Water | Gas | 2500000 | ########### |  |  | 0.833 | BOILER-EFFFPLR-NECB2011 | From NECB 2011
NECB 2011 | Hot Water | Electric | - | ########### |  | 1 |  | BOILER-EFFFPLR-NECB2011 | From NECB 2011
NECB 2011 | Hot Water | Oil | - | 299999 | 0.847 |  |  | BOILER-EFFFPLR-NECB2011 | From NECB 2011
NECB 2011 | Hot Water | Oil | 300000 | 2499999 |  | 0.834 |  | BOILER-EFFFPLR-NECB2011 | From NECB 2011
NECB 2011 | Hot Water | Oil | 2500000 | 9999999999 |  |  | 0.858 | BOILER-EFFFPLR-NECB2011 | From NECB 2011

## Motors
Each row represents the efficiency standards for a specificy type of motor
Template | Number of Poles | Type | Synchronous Speed (RPM) | Minimum Capacity (HP) | Maximum Capacity (HP) | Nominal Full Load Efficiency (%) | Notes
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 0 | 0.999 | 29% | Motors below 1 HP assumed to be PSC, with average typical efficiency of 29% per PNNL
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 1 | 1.499 | 82.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 1.5 | 1.999 | 84% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 2 | 2.999 | 84% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 3 | 4.999 | 87.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 5 | 7.499 | 87.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 7.5 | 9.999 | 89.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 10 | 14.999 | 89.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 15 | 19.999 | 91% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 20 | 24.999 | 91% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 25 | 29.999 | 92.4% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 30 | 39.999 | 92.4% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 40 | 49.999 | 93% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 50 | 59.999 | 93% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 60 | 74.999 | 93.6% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 75 | 99.999 | 94.1% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 100 | 124.999 | 94.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 125 | 149.999 | 94.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 150 | 199.999 | 95% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 200 | 9999 | 95% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 0 | 0.999 | 29% | Motors below 1 HP assumed to be PSC, with average typical efficiency of 29% per PNNL
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 1 | 1.499 | 82.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 1.5 | 1.999 | 84% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 2 | 2.999 | 84% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 3 | 4.999 | 87.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 5 | 7.499 | 87.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 7.5 | 9.999 | 89.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 10 | 14.999 | 89.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 15 | 19.999 | 91% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 20 | 24.999 | 91% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 25 | 29.999 | 92.4% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 30 | 39.999 | 92.4% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 40 | 49.999 | 93% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 50 | 59.999 | 93% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 60 | 74.999 | 93.6% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 75 | 99.999 | 94.1% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 100 | 124.999 | 94.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 125 | 149.999 | 94.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 150 | 199.999 | 95% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 200 | 9999 | 95% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 0 | 0.999 | 29% | Motors below 1 HP assumed to be PSC, with average typical efficiency of 29% per PNNL
90.1-2004 | 4 | Enclosed | 1800 | 1 | 1.499 | 82.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 1.5 | 1.999 | 84% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 2 | 2.999 | 84% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 3 | 4.999 | 87.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 5 | 7.499 | 87.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 7.5 | 9.999 | 89.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 10 | 14.999 | 89.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 15 | 19.999 | 91% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 20 | 24.999 | 91% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 25 | 29.999 | 92.4% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 30 | 39.999 | 92.4% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 40 | 49.999 | 93% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 50 | 59.999 | 93% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 60 | 74.999 | 93.6% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 75 | 99.999 | 94.1% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 100 | 124.999 | 94.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 125 | 149.999 | 94.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 150 | 199.999 | 95% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 200 | 9999 | 95% | From 90.1-2004 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 0 | 0.999 | 29% | Motors below 1 HP assumed to be PSC, with average typical efficiency of 29% per PNNL
90.1-2007 | 4 | Enclosed | 1800 | 1 | 1.499 | 82.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 1.5 | 1.999 | 84% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 2 | 2.999 | 84% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 3 | 4.999 | 87.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 5 | 7.499 | 87.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 7.5 | 9.999 | 89.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 10 | 14.999 | 89.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 15 | 19.999 | 91% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 20 | 24.999 | 91% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 25 | 29.999 | 92.4% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 30 | 39.999 | 92.4% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 40 | 49.999 | 93% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 50 | 59.999 | 93% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 60 | 74.999 | 93.6% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 75 | 99.999 | 94.1% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 100 | 124.999 | 94.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 125 | 149.999 | 94.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 150 | 199.999 | 95% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 200 | 9999 | 95% | From 90.1-2007 Table 10.8
90.1-2010 | 4 | Enclosed | 1800 | 0 | 0.999 | 29% | Motors below 1 HP assumed to be PSC, with average typical efficiency of 29% per PNNL
90.1-2010 | 4 | Enclosed | 1800 | 1 | 1.499 | 85.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 1.5 | 1.999 | 86.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 2 | 2.999 | 86.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 3 | 4.999 | 89.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 5 | 7.499 | 89.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 7.5 | 9.999 | 91.7% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 10 | 14.999 | 91.7% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 15 | 19.999 | 92.4% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 20 | 24.9999 | 93% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 25 | 29.999 | 93.6% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 30 | 39.999 | 93.6% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 40 | 49.999 | 94.1% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 50 | 59.999 | 94.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 60 | 74.999 | 95% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 75 | 99.999 | 95.4% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 100 | 124.999 | 95.4% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 125 | 149.999 | 95.4% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 150 | 199.999 | 95.8% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 200 | 249.999 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 250 | 299.999 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 300 | 349.999 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 350 | 399.999 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 400 | 449.999 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 450 | 499.999 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 500 | 9999 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2013 | 4 | Enclosed | 1800 | 0 | 0.08333 | 29% | Motors below 1/12 HP assumed to be PSC, with average typical efficiency of 29% per PNNL
90.1-2013 | 4 | Enclosed | 1800 | 0.08334 | 0.999 | 70% | Motors between 1/12 and 1 HP must be EC, with minimum efficiency of 70% per PNNL
90.1-2013 | 4 | Enclosed | 1800 | 1 | 1.499 | 85.5%
90.1-2013 | 4 | Enclosed | 1800 | 1.5 | 1.999 | 86.5%
90.1-2013 | 4 | Enclosed | 1800 | 2 | 2.999 | 86.5%
90.1-2013 | 4 | Enclosed | 1800 | 3 | 4.999 | 89.5%
90.1-2013 | 4 | Enclosed | 1800 | 5 | 7.499 | 89.5%
90.1-2013 | 4 | Enclosed | 1800 | 7.5 | 9.999 | 91.7%
90.1-2013 | 4 | Enclosed | 1800 | 10 | 14.999 | 91.7%
90.1-2013 | 4 | Enclosed | 1800 | 15 | 19.999 | 92.4%
90.1-2013 | 4 | Enclosed | 1800 | 20 | 24.999 | 93%
90.1-2013 | 4 | Enclosed | 1800 | 25 | 29.999 | 93.6%
90.1-2013 | 4 | Enclosed | 1800 | 30 | 39.999 | 93.6%
90.1-2013 | 4 | Enclosed | 1800 | 40 | 49.999 | 94.1%
90.1-2013 | 4 | Enclosed | 1800 | 50 | 59.999 | 94.5%
90.1-2013 | 4 | Enclosed | 1800 | 60 | 74.999 | 95%
90.1-2013 | 4 | Enclosed | 1800 | 75 | 99.999 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 100 | 124.999 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 125 | 149.999 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 150 | 199.999 | 95.8%
90.1-2013 | 4 | Enclosed | 1800 | 200 | 249.999 | 96.2%
90.1-2013 | 4 | Enclosed | 1800 | 250 | 299.999 | 95%
90.1-2013 | 4 | Enclosed | 1800 | 300 | 349.999 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 350 | 399.999 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 400 | 449.999 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 450 | 499.999 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 500 | 9999 | 95.4%
NECB 2011-CONSTANT | 4 | Enclosed | 1800 | 0 | 9999 | 61.5% | To get total fan efficiency of 40% (0.4/0.65)
NECB 2011-VARIABLE | 4 | Enclosed | 1800 | 0 | 9999 | 84.61% | To get total fan efficiency of 55% (0.55/0.65)

## Curve Biquadratics
Each row represents a biquadratic curve used to describe HVAC component performance
Name | coeff_1 | coeff_2 | coeff_3 | coeff_4 | coeff_5 | coeff_6 | min_x | max_x | min_y | max_y | notes
WaterCooled_PositiveDisplacement_Chiller_2004_CAPFT | 0.90612 | 0.029227 | -0.0003647 | -0.0009709 | -9.05e-05 | 0.0002527 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_2004_EIRFT | 0.36171 | -0.022983 | 0.0009519 | 0.013189 | 0.0003752 | -0.0007059 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | 0.90612 | 0.029228 | -0.0003647 | -0.0009709 | -9.05e-05 | 0.0002527 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | 0.36171 | -0.022983 | 0.0009519 | 0.013189 | 0.0003752 | -0.0007059 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | 0.90612 | 0.029228 | -0.0003647 | -0.0009709 | -9.05e-05 | 0.0002527 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | 0.37731 | -0.022903 | 0.0016504 | 0.011816 | 0.0004345 | -0.0010132 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_2010_PathB_CAPFT | 0.90612 | 0.029227 | -0.0003665 | -0.0009698 | -9.07e-05 | 0.0002535 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_2010_PathB_EIRFT | 0.36178 | -0.023002 | 0.0009672 | 0.01318 | 0.0003761 | -0.0007121 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_LT150_2004_CAPFT | 0.74465 | 0.011486 | 1.48e-05 | 0.022401 | -0.000688 | 0.0009839 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_LT150_2004_EIRFT | 0.77288 | 0.022101 | -7.99e-05 | -0.0070045 | 0.0004763 | -0.0010612 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_GT150_2004_CAPFT | 0.76002 | 0.014743 | 0.0002144 | 0.020722 | -0.0006425 | 0.0008007 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_GT150_2004_EIRFT | 0.67726 | 0.011786 | -0.0001967 | 0.0014414 | 0.0003005 | -0.0006807 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | 0.76002 | 0.014743 | 0.0002144 | 0.020722 | -0.0006425 | 0.0008007 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | 0.67726 | 0.011786 | -0.0001967 | 0.0014414 | 0.0003005 | -0.0006807 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_2010_PathB_CAPFT | 0.53623 | 0.005581 | -0.0013654 | 0.048897 | -0.0012018 | 0.0010523 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_2010_PathB_EIRFT | 1.0822 | 0.0042977 | -0.0013182 | -0.026078 | 0.0008256 | -0.0006013 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_2004_CAPFT | 1.0434 | 0.040708 | 0.0004506 | -0.0041514 | -8.86e-05 | -0.0003467 | 5 | 10 | 12.7 | 51.67 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_2004_EIRFT | 0.59619 | -0.0099496 | 0.0007888 | 0.0004506 | 0.0004875 | -0.0007623 | 5 | 10 | 12.7 | 51.67 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_2010_PathA_CAPFT | 1.0434 | 0.040707 | 0.0004506 | -0.0041514 | -8.86e-05 | -0.0003467 | 5 | 10 | 12.7 | 51.67 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_2010_PathA_EIRFT | 0.59619 | -0.0099496 | 0.0007888 | 0.0004506 | 0.0004875 | -0.0007623 | 5 | 10 | 12.7 | 51.67 | Based on Dick Lord's study dated January 17, 2010.
ChillerCentCapFT | 0.74465 | 0.011486 | 1.48e-05 | 0.022401 | -0.000688 | 0.0009839 | 5 | 10 | 24 | 35 | From Dick Lord's Chiller Model study for ASHRAE 2007 baseline
ChillerCentEIRFT | 0.77288 | 0.022101 | -7.99e-05 | -0.0070045 | 0.0004763 | -0.0010612 | 5 | 10 | 24 | 35 | From Dick Lord's Chiller Model study for ASHRAE 2007 baseline
DOE Ref DX Clg Coil Cool-Cap-fT | 0.97121 | -0.015276 | 0.0014435 | -0.00039321 | -6.8364e-06 | -0.0002906 | -100 | 100 | -100 | 100 | From DOE Pre-1980 Reference Building
DOE Ref DX Clg Coil Cool-EIR-fT | 0.28687 | 0.023902 | -0.00081065 | 0.013459 | 0.00033894 | -0.000487 | -100 | 100 | -100 | 100 | From DOE Pre-1980 Reference Building
HPACCoolCapFT | 0.76696 | 0.010776 | -4.147e-05 | 0.0013496 | -0.00026114 | 0.00045749 | 12.7778 | 23.8889 | 21.1111 | 46.1111
HPACCOOLEIRFT | 0.29714 | 0.043093 | -0.00074877 | 0.0059773 | 0.00048211 | -0.00095645 | 12.7778 | 23.8889 | 21.1111 | 46.1111
PSZ-AC DX Unitary Package EIRFT | 0.29714 | 0.043093 | -0.00074877 | 0.0059773 | 0.00048211 | -0.00095645 | 12.7778 | 23.8889 | 21.1111 | 46.1111 | From PNNL Prototype Buildings RetailStandAlone, RetailStripMall,SchoolPrimary
PSZ-AC DX Coil EIR-FT | 0.34241 | 0.034885 | -0.0006237 | 0.0049772 | 0.00043795 | -0.00072803 | 12.7778 | 23.8889 | 23.8889 | 46.1111 | From PNNL Prototype Buildings HotelSmall, Warehouse
PTACHPACEIRFT | 0.34241 | 0.034885 | -0.0006237 | 0.0049772 | 0.00043795 | -0.00072803 | 12.7778 | 23.8889 | 18.3 | 46.1111 | From DOE Reference Buildings SmallHotel
FURNACE_PACU_VAV_CoolCCarrier48TM014_12tons_EIRFT | -0.53616 | 0.10514 | -0.0017266 | 0.014985 | 0.00065995 | -0.0017385 | 16.5556 | 22.1111 | 23.7778 | 47.66 | From PNNL Prototype Buildings OfficeMedium
PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | 0.42415 | 0.04426 | -0.00042 | 0.00333 | -8e-05 | -0.00021 | 17 | 22 | 29 | 46 | From PNNL Prototype Buildings OutPatientHealtCare, RestaurantFastFood, RestaurantSitDown, SchoolPrimary, SchoolSecondary
WC_PD_2010_PB_EIRFT | 0.36178 | -0.023002 | 0.0009672 | 0.01318 | 0.0003761 | -0.0007121 | 5 | 10 | 17.78 | 46.11 | From PNNL Prototype OfficeLarge
PSZ-AC_Unitary_PackagecoolCapFT | 0.76696 | 0.010776 | -4.147e-05 | 0.0013496 | -0.00026114 | 0.00045749 | 12.7778 | 23.8889 | 21.1111 | 46.1111 | From PNNL Prototype Buildings RetailStandalone, RetailStripMall, SchoolPrimary
WC_PD_2010_PB_CAPFT | 0.90612 | 0.029227 | -0.0003665 | -0.0009698 | -9.07e-05 | 0.0002535 | 5 | 10 | 17.78 | 46.11 | From PNNL Prototype OfficeLarge
WC_PD_2004_CAPFT | 0.90612 | 0.029228 | -0.0003647 | -0.0009709 | -9.05e-05 | 0.0002527 | 5 | 10 | 17.78 | 46.11 | From PNNL Prototype Hospital
PSZ-AC_CoolCStandard10Ton_EIRFT | 1.2365 | -0.02431 | 0.00057 | -0.01434 | 0.00063 | -0.00038 | 17 | 22 | 29 | 46 | From PNNL Prototype Buildings OutPatientHealtCare, RestaurantFastFood, RestaurantSitDown, SchoolPrimary, SchoolSecondary
PSZ-Fine Storage DX Coil Cap-FT | 0.94259 | 0.0095433 | 0.00068377 | -0.011043 | 5.249e-06 | -9.72e-06 | 12.7778 | 23.8889 | 23.8889 | 46.1111 | From PNNL Prototype Buildings HotelSmall, Warehouse
DXCOOL-NECB2011-REF-CAPFT | 0.86791 | 0.014246 | 0.00055436 | -0.0075575 | 3.3e-05 | -0.0001918 | 13 | 24 | 24 | 46 | From NECB 2011
DXCOOL-NECB2011-REF-COOLEIRFT | 0.11694 | 0.028493 | -0.0004112 | 0.021411 | 0.00016103 | -0.0006791 | 13 | 24 | 24 | 46 | From NECB 2011
WaterCooled_Scroll_CAPFT_NECB2011 | 0.94418 | 0.03371 | 9.7556e-05 | -0.0032211 | -4.918e-05 | -0.0001776 | 5 | 10 | 24 | 35 | From NECB 2011
WaterCooled_Scroll_EIRFT_NECB2011 | 0.727 | -0.0119 | 0.000541 | 0.00188 | 0.000473 | -0.000711 | 5 | 10 | 24 | 35 | From NECB 2011
WaterCooled_Reciprocating_CAPFT_NECB2011 | 1.0303 | 0.03347 | 0.00023639 | -0.0072959 | -2.317e-05 | -0.0001489 | 5 | 10 | 24 | 35 | From NECB 2011
WaterCooled_Reciprocating_EIRFT_NECB2011 | 0.5 | -0.0131 | 0.000266 | 0.0166 | 0.000185 | -0.000376 | 5 | 10 | 24 | 35 | From NECB 2011
WaterCooled_Screw_CAPFT_NECB2011 | 0.813 | -0.014253 | -0.001618 | 0.026384 | -0.0009154 | 0.001696 | 5 | 10 | 24 | 35 | From NECB 2011
WaterCooled_Screw_EIRFT_NECB2011 | 0.638 | 0.0063 | 0.000923 | -0.00455 | 0.000826 | -0.00156 | 5 | 10 | 24 | 35 | From NECB 2011
WaterCooled_Centrifugal_CAPFT_NECB2011 | 0.70791 | -0.0020066 | -0.0025961 | 0.030059 | -0.0010564 | 0.0020457 | 5 | 10 | 24 | 35 | From NECB 2011
WaterCooled_Centrifugal_EIRFT_NECB2011 | 0.561 | -0.0138 | 6.56e-05 | 0.0132 | 0.000269 | -0.000501 | 5 | 10 | 24 | 35 | From NECB 2011

## Curve Bicubics
Each row represents a bicubic curve used to describe HVAC component performance
Name | coeff_1 | coeff_2 | coeff_3 | coeff_4 | coeff_5 | coeff_6 | coeff_7 | coeff_8 | coeff_9 | coeff_10 | min_x | max_x | min_y | max_y | notes
WaterCooled_PositiveDisplacement_Chiller_LT75_2004_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_75TO150_2004_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_150TO300_2004_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_GT300_2004_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_LT75_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_75TO150_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_150TO300_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_GT300_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_LT75_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_75TO150_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_150TO300_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_GT300_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_LT150_2004_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_150TO300_2004_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_GT300_2004_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_LT150_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_150TO300_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_300TO600_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_GT600_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_LT150_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_150TO300_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_300TO600_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_GT600_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
ChillerCentEIRPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | From Dick Lord's Chiller Model study for ASHRAE 2007 baseline
WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010. EIRFPLR curve is identical for all WaterCooled Chillers

## Curve Quadratics
Each row represents a bicubic curve used to describe HVAC component performance
Name | coeff_1 | coeff_2 | coeff_3 | min_x | max_x | notes
AirCooled_Chiller_LT150_2004_EIRFPLR | 0.141 | 0.655 | 0.203 | 0 | 1 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_GT150_2004_EIRFPLR | 0.141 | 0.655 | 0.203 | 0 | 1 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_LT150_2010_PathA_EIRFPLR | 0.141 | 0.655 | 0.203 | 0 | 1 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_GT150_2010_PathA_EIRFPLR | 0.141 | 0.655 | 0.203 | 0 | 1 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR | 0.141 | 0.655 | 0.203 | 0 | 1 | Based on Dick Lord's study dated January 17, 2010. EIRFPLR curve is identical for all AirCooled Chillers
DOE Ref DX Clg Coil Cool-PLF-fPLR | 0.9095 | 0.098648 | -0.0081949 | 0 | 1
HPACCoolCapFFF | 0.8 | 0.2 | 0 | 0.5 | 1.5
HPACCOOLEIRFFF | 1.156 | -0.1816 | 0.0256 | 0.5 | 1.5
HPACCOOLPLFFPLR | 0.85 | 0.15 | 0 | 0 | 1
PSZ-AC_Unitary_PackagecoolPLR | 0.75 | 0.25 | 0 | 0 | 1 | From PNNL Prototype Buildings RetailStandAlone, RetailStripMall, SchoolPrimary
PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR | 0.771 | 0.229 | 0 | 0 | 1 | From PNNL Prototype Buildings OutPatientHealtCare, RestaurantFastFood, RestaurantSitDown, SchoolPrimary, SchoolSecondary
AHU-1_CoolCStandard10Ton_CapFF | 0.77136 | 0.34053 | -0.11088 | 0.75918 | 1.1388 | From PNNL Prototype Buildings OutPatientHealtCare, RestaurantFastFood, RestaurantSitDown, SchoolPrimary, SchoolSecondary
DX Coil Cap-FF | 0.8 | 0.2 | 0 | 0.5 | 1.5 | From PNNL Prototype Buildings ApartmentMidRise, HotelSmall, OfficeSmall, RetailStandAlone, RetailStripmall, SchoolPrimary, Warehouse
Split DX Coil EIR-FF | 1.1552 | -0.1808 | 0.0256 | 0.5 | 1.5 | From PNNL Prototype Buildings ApartmentMidRise, HotelSmall, Warehouse
Cool-PLF-fPLR | 0.9095 | 0.098648 | -0.0081949 | 0 | 1 | From PNNL Prototype FullServiceRestaurant
PSZ-AC:1_Unitary_PackagecoolEIRFFF | 1.156 | -0.1816 | 0.0256 | 0.5 | 1.5 | From PNNL Prototype Buildings RetailStandAlone, RetailStripMall, SchoolPrimary
Measured_CoolCStandard10Ton_EIRFFF | 1.192 | -0.1917 | 0 | 0.776 | 1.197 | From PNNL Prototype FullServiceRestaurant
FURNACE_PACU_VAV_CoolCCarrier48TM014_12tons_EIRFFF | 1.1952 | -0.30614 | 0.11097 | 0.75 | 1.25 | From PNNL OfficeMedium
CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | 1.2055 | -0.32953 | 0.12308 | 0.75918 | 1.1388 | From PNNL Prototype Buildings OutPatientHealtCare, RestaurantFastFood, RestaurantSitDown, SchoolPrimary, SchoolSecondary
WaterCooled_Scroll_EIRFPLR_NECB2011 | 0.04412 | 0.64037 | 0.31956 | 0 | 1 | From NECB 2011
WaterCooled_Reciprocating_EIRFPLR_NECB2011 | 0.081441 | 0.41927 | 0.4994 | 0 | 1 | From NECB 2011
WaterCooled_Screw_EIRFPLR_NECB2011 | 0.33019 | 0.23554 | 0.46071 | 0 | 1 | From NECB 2011
WaterCooled_Centrifugal_EIRFPLR_NECB2011 | 0.17149 | 0.5882 | 0.23737 | 0 | 1 | From NECB 2011
DXCOOL-NECB2011-REF-CAPFFLOW | 1 | 0 | 0 | 0 | 1 | From NECB 2011
DXCOOL-NECB2011-REF-COOLEIRFFLOW | 1 | 0 | 0 | 0 | 1 | From NECB 2011
DXHEAT-NECB2011-REF-EIRFFLOW | 1.3824 | -0.4336 | 0.0512 | 0 | 1 | From NECB 2011

## Curve Cubics
Each row represents a cubic curve used to describe HVAC component performance
Name | coeff_1 | coeff_2 | coeff_3 | coeff_4 | min_x | max_x | notes
DOE Ref DX Clg Coil Cool-EIR-fFlow | 1 | 0 | 0 | 0 | -100 | 100 | From DOE Pre-1980 Reference Building
DOE Ref DX Clg Coil Cool-CAP-fFlow | 1 | 0 | 0 | 0 | -100 | 100 | From DOE Pre-1980 Reference Building
Boiler with Minimum Turndown | 0.7791 | 1.4745 | -2.5795 | 1.3467 | 0 | 1.3 | From Regression of Prototype Building EMS
Boiler with No Minimum Turndown | 0.7463 | 1.3196 | -2.2154 | 1.1674 | 0 | 1.3 | From Regression of Prototype Building EMS
Boiler Constant Efficiency Curve | 1 | 0 | 0 | 0 | 0 | 1 | From DOE Reference Building
Hospital Kitchen_Flr_5_Case:1_WALKINFREEZERSingleShelfHorizontal_LatentEnergyMult | 0.0236 | 0.0006 | 0 | 0 | -35 | 20 | From Prototype Buildings
Hospital Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASEMultiShelfVertical_LatentEnergyMult | 0.026526 | 0.001078 | 6.0256e-05 | 1.2373e-06 | -35 | 20 | From Prototype Buildings
Tower_Fan_Curve | 0 | 0 | 0 | 1 | 0 | 1 | From Prototype Buildings
HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZERSingleShelfHorizontal_LatentEnergyMult | 0.0236 | 0.0006 | 0 | 0 | -35 | 20 | From Prototype Buildings
HotelLarge Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASEMultiShelfVertical_LatentEnergyMult | 0.026526 | 0.001078 | 6.0256e-05 | 1.2373e-06 | -35 | 20 | From Prototype Buildings
SAC Heating Coil PLF-FPLR | 0.8 | 0.2 | 0 | 0 | 0 | 1 | From Prototype Buildings
HPACHeatCapFT | 0.75875 | 0.027626 | 0.00014872 | 3.4992e-06 | -20 | 20 | From Prototype Buildings
HPACHeatCapFFF | 0.84 | 0.16 | 0 | 0 | 0.5 | 1.5 | From Prototype Buildings
HPACHeatEIRFT | 1.1925 | -0.030044 | 0.0010375 | -2.3328e-05 | -20 | 20 | From Prototype Buildings
HeatSys1 Boiler Non-Condensing Boiler Curve | 0.62643 | 0.64564 | -0.77721 | 0.31381 | 0.1 | 1 | From Prototype Buildings
RestaurantFastFood Kitchen_Case:1_WALKINFREEZERSingleShelfHorizontal_LatentEnergyMult | 0.0236 | 0.0006 | 0 | 0 | -35 | 20 | From Prototype Buildings
RestaurantFastFood Kitchen_Case:2_SELFCONTAINEDDISPLAYCASEMultiShelfVertical_LatentEnergyMult | 0.026526 | 0.001078 | 6.0256e-05 | 1.2373e-06 | -35 | 20 | From Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZERSingleShelfHorizontal_LatentEnergyMult | 0.0236 | 0.0006 | 0 | 0 | -35 | 20 | From Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASEMultiShelfVertical_LatentEnergyMult | 0.026526 | 0.001078 | 6.0256e-05 | 1.2373e-06 | -35 | 20 | From Prototype Buildings
PSZ-Office Heating Coil PLF-FPLR | 0.8 | 0.2 | 0 | 0 | 0 | 1 | From Prototype Buildings
PSZ-Fine Storage Heating Coil PLF-FPLR | 0.8 | 0.2 | 0 | 0 | 0 | 1 | From Prototype Buildings
ConstantCubic | 1 | 0 | 0 | 0 | -100 | 100 | From Reference Buildings
Single Shelf Horizontal Latent Energy Multiplier_Pre2004 | 0.020376 | 0.00024378 | 1.14e-05 | 1.811e-07 | -35 | 20 | From Reference Buildings
Single Shelf Horizontal Latent Energy Multiplier_After2004 | 0.0236 | 0.0006 | 0 | 0 | -35 | 20 | From Reference Buildings
Multi Shelf Vertical Latent Energy Multiplier | 0.026526 | 0.001078 | -6.0256e-05 | 1.2373e-06 | -35 | 20 | From Reference Buildings
BOILER-EFFFPLR-NECB2011 | 0.2901 | 2.6664 | -3.764 | 1.82 | 0 | 1 | From NECB 2011
DXCOOL-NECB2011-REF-COOLPLFFPLR | 0.0277 | 4.9151 | -8.184 | 4.2702 | 0.7 | 1 | From NECB, curve modified to take into account how PLF is used in E+, and PLF ranges (> 0.7)
DXHEAT-NECB2011-REF-CAPFT | 0.729 | 0.0319 | 0.000136 | -8.75e-06 | -20 | 20 | From NECB 2011
DXHEAT-NECB2011-REF-CAPFFLOW | 0.84 | 0.16 | 0 | 0 | 0.5 | 1.5 | From NECB 2011
DXHEAT-NECB2011-REF-EIRFT | 1.2183 | -0.03612 | 0.00142 | -2.68e-05 | -20 | 20 | From NECB 2011
DXHEAT-NECB2011-REF-PLFFPLR | 0.3696 | 2.3362 | -2.9577 | 1.2596 | 0.7 | 1 | From NECB 2011

## Ground Temperatures
Ground temperatures at the building surface, created using the slab preprocessor with climate-specific slab insulation
Building Type | Template | Climate Zone | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-1A | 21 | 21 | 21.03 | 21.11 | 21.16 | 23.38 | 23.69 | 23.76 | 23.76 | 21.49 | 21.21 | 21.07
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Hospital | 90.1-2004 | ASHRAE 169-2006-1A
LargeHotel | 90.1-2004 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
LargeOffice | 90.1-2004 | ASHRAE 169-2006-1A
MediumOffice | 90.1-2004 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.04 | 21.06 | 23.22 | 23.57 | 23.64 | 23.66 | 21.46 | 21.16 | 21.05
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Outpatient | 90.1-2004 | ASHRAE 169-2006-1A | 20.96 | 20.96 | 20.99 | 21.06 | 21.1 | 21.99 | 22.14 | 22.18 | 22.17 | 21.28 | 21.11 | 21.01
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.05 | 23.26 | 23.58 | 23.64 | 23.66 | 21.4 | 21.14 | 21.05
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-1A | 21.01 | 21.01 | 21.06 | 21.19 | 21.26 | 23.48 | 23.8 | 23.87 | 23.85 | 21.58 | 21.27 | 21.1
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.04 | 23.26 | 23.57 | 23.64 | 23.66 | 21.4 | 21.13 | 21.04
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
SmallHotel | 90.1-2004 | ASHRAE 169-2006-1A | 20.94 | 20.95 | 20.99 | 21.07 | 21.11 | 21.16 | 21.19 | 21.21 | 21.18 | 21.14 | 21.08 | 20.99
SmallOffice | 90.1-2004 | ASHRAE 169-2006-1A | 20.96 | 20.94 | 20.97 | 21.09 | 21.16 | 23.13 | 23.6 | 23.73 | 23.75 | 21.75 | 21.3 | 21.09
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-1A | 21 | 20.99 | 21 | 21.05 | 21.08 | 23.29 | 23.61 | 23.67 | 23.69 | 21.42 | 21.16 | 21.05
Warehouse | 90.1-2004 | ASHRAE 169-2006-1A | 20.19 | 20.72 | 21.39 | 23.77 | 25.14 | 26.54 | 27.33 | 27.4 | 26.65 | 25.11 | 23.37 | 20.99
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-1A | 21 | 21 | 21.03 | 21.11 | 21.16 | 23.38 | 23.69 | 23.76 | 23.76 | 21.49 | 21.21 | 21.07
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Hospital | 90.1-2007 | ASHRAE 169-2006-1A
LargeHotel | 90.1-2007 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
LargeOffice | 90.1-2007 | ASHRAE 169-2006-1A
MediumOffice | 90.1-2007 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.04 | 21.06 | 23.22 | 23.57 | 23.64 | 23.66 | 21.46 | 21.16 | 21.05
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Outpatient | 90.1-2007 | ASHRAE 169-2006-1A | 20.96 | 20.96 | 20.99 | 21.06 | 21.1 | 21.99 | 22.14 | 22.18 | 22.17 | 21.28 | 21.11 | 21.01
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.05 | 23.26 | 23.58 | 23.64 | 23.66 | 21.4 | 21.14 | 21.05
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-1A | 21.01 | 21.01 | 21.06 | 21.19 | 21.26 | 23.48 | 23.8 | 23.87 | 23.85 | 21.58 | 21.27 | 21.1
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.04 | 23.26 | 23.57 | 23.64 | 23.66 | 21.4 | 21.13 | 21.04
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
SmallHotel | 90.1-2007 | ASHRAE 169-2006-1A | 20.94 | 20.95 | 20.99 | 21.07 | 21.11 | 21.16 | 21.19 | 21.21 | 21.18 | 21.14 | 21.08 | 20.99
SmallOffice | 90.1-2007 | ASHRAE 169-2006-1A | 20.96 | 20.94 | 20.97 | 21.09 | 21.16 | 23.13 | 23.6 | 23.73 | 23.75 | 21.75 | 21.3 | 21.09
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-1A | 21 | 20.99 | 21 | 21.05 | 21.08 | 23.29 | 23.61 | 23.67 | 23.69 | 21.42 | 21.16 | 21.05
Warehouse | 90.1-2007 | ASHRAE 169-2006-1A | 20.19 | 20.72 | 21.39 | 23.77 | 25.14 | 26.54 | 27.33 | 27.4 | 26.65 | 25.11 | 23.37 | 20.99
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-1A | 21 | 21 | 21.03 | 21.11 | 21.16 | 23.38 | 23.69 | 23.76 | 23.76 | 21.49 | 21.21 | 21.07
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Hospital | 90.1-2010 | ASHRAE 169-2006-1A
LargeHotel | 90.1-2010 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
LargeOffice | 90.1-2010 | ASHRAE 169-2006-1A
MediumOffice | 90.1-2010 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.04 | 21.06 | 23.22 | 23.57 | 23.64 | 23.66 | 21.46 | 21.16 | 21.05
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Outpatient | 90.1-2010 | ASHRAE 169-2006-1A | 20.96 | 20.96 | 20.99 | 21.06 | 21.1 | 21.99 | 22.14 | 22.18 | 22.17 | 21.28 | 21.11 | 21.01
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.05 | 23.26 | 23.58 | 23.64 | 23.66 | 21.4 | 21.14 | 21.05
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-1A | 21.01 | 21.01 | 21.06 | 21.19 | 21.26 | 23.48 | 23.8 | 23.87 | 23.85 | 21.58 | 21.27 | 21.1
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.04 | 23.26 | 23.57 | 23.64 | 23.66 | 21.4 | 21.13 | 21.04
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
SmallHotel | 90.1-2010 | ASHRAE 169-2006-1A | 20.94 | 20.95 | 20.99 | 21.07 | 21.11 | 21.16 | 21.19 | 21.21 | 21.18 | 21.14 | 21.08 | 20.99
SmallOffice | 90.1-2010 | ASHRAE 169-2006-1A | 20.96 | 20.94 | 20.97 | 21.09 | 21.16 | 23.13 | 23.6 | 23.73 | 23.75 | 21.75 | 21.3 | 21.09
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-1A | 21 | 20.99 | 21 | 21.05 | 21.08 | 23.29 | 23.61 | 23.67 | 23.69 | 21.42 | 21.16 | 21.05
Warehouse | 90.1-2010 | ASHRAE 169-2006-1A | 20.19 | 20.72 | 21.39 | 23.77 | 25.14 | 26.54 | 27.33 | 27.4 | 26.65 | 25.11 | 23.37 | 20.99
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-1A | 21 | 21 | 21.03 | 21.11 | 21.16 | 23.38 | 23.69 | 23.76 | 23.76 | 21.49 | 21.21 | 21.07
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Hospital | 90.1-2013 | ASHRAE 169-2006-1A
LargeHotel | 90.1-2013 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
LargeOffice | 90.1-2013 | ASHRAE 169-2006-1A
MediumOffice | 90.1-2013 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.04 | 21.06 | 23.22 | 23.57 | 23.64 | 23.66 | 21.46 | 21.16 | 21.05
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Outpatient | 90.1-2013 | ASHRAE 169-2006-1A | 20.96 | 20.96 | 20.99 | 21.06 | 21.1 | 21.99 | 22.14 | 22.18 | 22.17 | 21.28 | 21.11 | 21.01
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.05 | 23.26 | 23.58 | 23.64 | 23.66 | 21.4 | 21.14 | 21.05
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-1A | 21.01 | 21.01 | 21.06 | 21.19 | 21.26 | 23.48 | 23.8 | 23.87 | 23.85 | 21.58 | 21.27 | 21.1
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.04 | 23.26 | 23.57 | 23.64 | 23.66 | 21.4 | 21.13 | 21.04
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
SmallHotel | 90.1-2013 | ASHRAE 169-2006-1A | 20.94 | 20.95 | 20.99 | 21.07 | 21.11 | 21.16 | 21.19 | 21.21 | 21.18 | 21.14 | 21.08 | 20.99
SmallOffice | 90.1-2013 | ASHRAE 169-2006-1A | 20.96 | 20.94 | 20.97 | 21.09 | 21.16 | 23.13 | 23.6 | 23.73 | 23.75 | 21.75 | 21.3 | 21.09
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-1A | 21 | 20.99 | 21 | 21.05 | 21.08 | 23.29 | 23.61 | 23.67 | 23.69 | 21.42 | 21.16 | 21.05
Warehouse | 90.1-2013 | ASHRAE 169-2006-1A | 20.19 | 20.72 | 21.39 | 23.77 | 25.14 | 26.54 | 27.33 | 27.4 | 26.65 | 25.11 | 23.37 | 20.99
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 10.7 | 10.54 | 11.61 | 13.26 | 16.58 | 19.47 | 22.27 | 24.29 | 21.8 | 17.54 | 14.44 | 11.6
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 10.7 | 10.54 | 11.61 | 13.26 | 16.58 | 19.47 | 22.27 | 24.29 | 21.8 | 17.54 | 14.44 | 11.6
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.64 | 23.98 | 24.09 | 24.07 | 21.71 | 21.29 | 21.01
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Hospital | 90.1-2004 | ASHRAE 169-2006-1B
LargeHotel | 90.1-2004 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
LargeOffice | 90.1-2004 | ASHRAE 169-2006-1B
MediumOffice | 90.1-2004 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.95 | 21.05 | 21.16 | 23.39 | 23.75 | 23.85 | 23.86 | 21.6 | 21.22 | 21.02
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Outpatient | 90.1-2004 | ASHRAE 169-2006-1B | 20.85 | 20.87 | 20.94 | 21.07 | 21.23 | 22.21 | 22.38 | 22.46 | 22.44 | 21.47 | 21.2 | 20.97
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-1B | 20.92 | 20.92 | 20.96 | 21.03 | 21.13 | 23.4 | 23.72 | 23.81 | 23.82 | 21.51 | 21.18 | 21.02
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-1B | 20.79 | 20.83 | 20.96 | 21.19 | 21.48 | 23.87 | 24.21 | 24.34 | 24.3 | 21.9 | 21.39 | 21
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-1B | 20.93 | 20.92 | 20.96 | 21.03 | 21.12 | 23.39 | 23.71 | 23.79 | 23.81 | 21.5 | 21.18 | 21.02
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
SmallHotel | 90.1-2004 | ASHRAE 169-2006-1B | 20.82 | 20.85 | 20.93 | 21.08 | 21.26 | 21.41 | 21.45 | 21.51 | 21.47 | 21.35 | 21.17 | 20.94
SmallOffice | 90.1-2004 | ASHRAE 169-2006-1B | 20.78 | 20.76 | 20.87 | 21.08 | 21.36 | 23.5 | 24.02 | 24.21 | 24.22 | 22.1 | 21.48 | 21.05
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.96 | 21.05 | 21.17 | 23.46 | 23.78 | 23.88 | 23.88 | 21.56 | 21.21 | 21.02
Warehouse | 90.1-2004 | ASHRAE 169-2006-1B | 14.79 | 16.72 | 19.78 | 24.59 | 30.22 | 33.53 | 34.88 | 35.37 | 32.81 | 28.11 | 22.6 | 16.33
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.64 | 23.98 | 24.09 | 24.07 | 21.71 | 21.29 | 21.01
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Hospital | 90.1-2007 | ASHRAE 169-2006-1B
LargeHotel | 90.1-2007 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
LargeOffice | 90.1-2007 | ASHRAE 169-2006-1B
MediumOffice | 90.1-2007 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.95 | 21.05 | 21.16 | 23.39 | 23.75 | 23.85 | 23.86 | 21.6 | 21.22 | 21.02
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Outpatient | 90.1-2007 | ASHRAE 169-2006-1B | 20.85 | 20.87 | 20.94 | 21.07 | 21.23 | 22.21 | 22.38 | 22.46 | 22.44 | 21.47 | 21.2 | 20.97
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-1B | 20.92 | 20.92 | 20.96 | 21.03 | 21.13 | 23.4 | 23.72 | 23.81 | 23.82 | 21.51 | 21.18 | 21.02
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-1B | 20.79 | 20.83 | 20.96 | 21.19 | 21.48 | 23.87 | 24.21 | 24.34 | 24.3 | 21.9 | 21.39 | 21
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-1B | 20.93 | 20.92 | 20.96 | 21.03 | 21.12 | 23.39 | 23.71 | 23.79 | 23.81 | 21.5 | 21.18 | 21.02
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
SmallHotel | 90.1-2007 | ASHRAE 169-2006-1B | 20.82 | 20.85 | 20.93 | 21.08 | 21.26 | 21.41 | 21.45 | 21.51 | 21.47 | 21.35 | 21.17 | 20.94
SmallOffice | 90.1-2007 | ASHRAE 169-2006-1B | 20.78 | 20.76 | 20.87 | 21.08 | 21.36 | 23.5 | 24.02 | 24.21 | 24.22 | 22.1 | 21.48 | 21.05
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.96 | 21.05 | 21.17 | 23.46 | 23.78 | 23.88 | 23.88 | 21.56 | 21.21 | 21.02
Warehouse | 90.1-2007 | ASHRAE 169-2006-1B | 14.79 | 16.72 | 19.78 | 24.59 | 30.22 | 33.53 | 34.88 | 35.37 | 32.81 | 28.11 | 22.6 | 16.33
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.64 | 23.98 | 24.09 | 24.07 | 21.71 | 21.29 | 21.01
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Hospital | 90.1-2010 | ASHRAE 169-2006-1B
LargeHotel | 90.1-2010 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
LargeOffice | 90.1-2010 | ASHRAE 169-2006-1B
MediumOffice | 90.1-2010 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.95 | 21.05 | 21.16 | 23.39 | 23.75 | 23.85 | 23.86 | 21.6 | 21.22 | 21.02
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Outpatient | 90.1-2010 | ASHRAE 169-2006-1B | 20.85 | 20.87 | 20.94 | 21.07 | 21.23 | 22.21 | 22.38 | 22.46 | 22.44 | 21.47 | 21.2 | 20.97
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-1B | 20.92 | 20.92 | 20.96 | 21.03 | 21.13 | 23.4 | 23.72 | 23.81 | 23.82 | 21.51 | 21.18 | 21.02
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-1B | 20.79 | 20.83 | 20.96 | 21.19 | 21.48 | 23.87 | 24.21 | 24.34 | 24.3 | 21.9 | 21.39 | 21
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-1B | 20.93 | 20.92 | 20.96 | 21.03 | 21.12 | 23.39 | 23.71 | 23.79 | 23.81 | 21.5 | 21.18 | 21.02
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
SmallHotel | 90.1-2010 | ASHRAE 169-2006-1B | 20.82 | 20.85 | 20.93 | 21.08 | 21.26 | 21.41 | 21.45 | 21.51 | 21.47 | 21.35 | 21.17 | 20.94
SmallOffice | 90.1-2010 | ASHRAE 169-2006-1B | 20.78 | 20.76 | 20.87 | 21.08 | 21.36 | 23.5 | 24.02 | 24.21 | 24.22 | 22.1 | 21.48 | 21.05
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.96 | 21.05 | 21.17 | 23.46 | 23.78 | 23.88 | 23.88 | 21.56 | 21.21 | 21.02
Warehouse | 90.1-2010 | ASHRAE 169-2006-1B | 14.79 | 16.72 | 19.78 | 24.59 | 30.22 | 33.53 | 34.88 | 35.37 | 32.81 | 28.11 | 22.6 | 16.33
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.64 | 23.98 | 24.09 | 24.07 | 21.71 | 21.29 | 21.01
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Hospital | 90.1-2013 | ASHRAE 169-2006-1B
LargeHotel | 90.1-2013 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
LargeOffice | 90.1-2013 | ASHRAE 169-2006-1B
MediumOffice | 90.1-2013 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.95 | 21.05 | 21.16 | 23.39 | 23.75 | 23.85 | 23.86 | 21.6 | 21.22 | 21.02
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Outpatient | 90.1-2013 | ASHRAE 169-2006-1B | 20.85 | 20.87 | 20.94 | 21.07 | 21.23 | 22.21 | 22.38 | 22.46 | 22.44 | 21.47 | 21.2 | 20.97
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-1B | 20.92 | 20.92 | 20.96 | 21.03 | 21.13 | 23.4 | 23.72 | 23.81 | 23.82 | 21.51 | 21.18 | 21.02
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-1B | 20.79 | 20.83 | 20.96 | 21.19 | 21.48 | 23.87 | 24.21 | 24.34 | 24.3 | 21.9 | 21.39 | 21
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-1B | 20.93 | 20.92 | 20.96 | 21.03 | 21.12 | 23.39 | 23.71 | 23.79 | 23.81 | 21.5 | 21.18 | 21.02
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
SmallHotel | 90.1-2013 | ASHRAE 169-2006-1B | 20.82 | 20.85 | 20.93 | 21.08 | 21.26 | 21.41 | 21.45 | 21.51 | 21.47 | 21.35 | 21.17 | 20.94
SmallOffice | 90.1-2013 | ASHRAE 169-2006-1B | 20.78 | 20.76 | 20.87 | 21.08 | 21.36 | 23.5 | 24.02 | 24.21 | 24.22 | 22.1 | 21.48 | 21.05
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.96 | 21.05 | 21.17 | 23.46 | 23.78 | 23.88 | 23.88 | 21.56 | 21.21 | 21.02
Warehouse | 90.1-2013 | ASHRAE 169-2006-1B | 14.79 | 16.72 | 19.78 | 24.59 | 30.22 | 33.53 | 34.88 | 35.37 | 32.81 | 28.11 | 22.6 | 16.33
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-2A | 20.59 | 20.53 | 20.67 | 20.8 | 20.96 | 23.24 | 23.6 | 23.68 | 23.67 | 21.35 | 20.98 | 20.69
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Hospital | 90.1-2004 | ASHRAE 169-2006-2A
LargeHotel | 90.1-2004 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
LargeOffice | 90.1-2004 | ASHRAE 169-2006-2A
MediumOffice | 90.1-2004 | ASHRAE 169-2006-2A | 20.73 | 20.68 | 20.76 | 20.84 | 20.94 | 23.13 | 23.5 | 23.58 | 23.6 | 21.36 | 21.01 | 20.81
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Outpatient | 90.1-2004 | ASHRAE 169-2006-2A | 20.62 | 20.57 | 20.68 | 20.8 | 20.93 | 21.87 | 22.06 | 22.11 | 22.1 | 21.15 | 20.91 | 20.69
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-2A | 20.78 | 20.74 | 20.81 | 20.87 | 20.95 | 23.19 | 23.53 | 23.6 | 23.61 | 21.33 | 21.02 | 20.85
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-2A | 20.41 | 20.33 | 20.54 | 20.74 | 20.98 | 23.29 | 23.67 | 23.76 | 23.73 | 21.38 | 20.94 | 20.54
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-2A | 20.79 | 20.75 | 20.81 | 20.87 | 20.95 | 23.19 | 23.52 | 23.59 | 23.61 | 21.33 | 21.02 | 20.86
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-2A | 20.84 | 20.81 | 20.85 | 20.89 | 20.94 | 23.18 | 23.51 | 23.57 | 23.6 | 21.32 | 21.03 | 20.9
SmallHotel | 90.1-2004 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
SmallOffice | 90.1-2004 | ASHRAE 169-2006-2A | 20.38 | 20.28 | 20.43 | 20.62 | 20.85 | 22.92 | 23.46 | 23.6 | 23.62 | 21.54 | 20.98 | 20.57
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-2A | 20.74 | 20.69 | 20.77 | 20.85 | 20.95 | 23.2 | 23.54 | 23.62 | 23.63 | 21.33 | 21.01 | 20.81
Warehouse | 90.1-2004 | ASHRAE 169-2006-2A | 13.19 | 13.04 | 15.76 | 19.5 | 22.75 | 25.31 | 26.94 | 26.7 | 25.13 | 21.35 | 17.77 | 13.7
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-2A | 20.59 | 20.53 | 20.67 | 20.8 | 20.96 | 23.24 | 23.6 | 23.68 | 23.67 | 21.35 | 20.98 | 20.69
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Hospital | 90.1-2007 | ASHRAE 169-2006-2A
LargeHotel | 90.1-2007 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
LargeOffice | 90.1-2007 | ASHRAE 169-2006-2A
MediumOffice | 90.1-2007 | ASHRAE 169-2006-2A | 20.73 | 20.68 | 20.76 | 20.84 | 20.94 | 23.13 | 23.5 | 23.58 | 23.6 | 21.36 | 21.01 | 20.81
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Outpatient | 90.1-2007 | ASHRAE 169-2006-2A | 20.62 | 20.57 | 20.68 | 20.8 | 20.93 | 21.87 | 22.06 | 22.11 | 22.1 | 21.15 | 20.91 | 20.69
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-2A | 20.78 | 20.74 | 20.81 | 20.87 | 20.95 | 23.19 | 23.53 | 23.6 | 23.61 | 21.33 | 21.02 | 20.85
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-2A | 20.41 | 20.33 | 20.54 | 20.74 | 20.98 | 23.29 | 23.67 | 23.76 | 23.73 | 21.38 | 20.94 | 20.54
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-2A | 20.79 | 20.75 | 20.81 | 20.87 | 20.95 | 23.19 | 23.52 | 23.59 | 23.61 | 21.33 | 21.02 | 20.86
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-2A | 20.84 | 20.81 | 20.85 | 20.89 | 20.94 | 23.18 | 23.51 | 23.57 | 23.6 | 21.32 | 21.03 | 20.9
SmallHotel | 90.1-2007 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
SmallOffice | 90.1-2007 | ASHRAE 169-2006-2A | 20.38 | 20.28 | 20.43 | 20.62 | 20.85 | 22.92 | 23.46 | 23.6 | 23.62 | 21.54 | 20.98 | 20.57
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-2A | 20.74 | 20.69 | 20.77 | 20.85 | 20.95 | 23.2 | 23.54 | 23.62 | 23.63 | 21.33 | 21.01 | 20.81
Warehouse | 90.1-2007 | ASHRAE 169-2006-2A | 13.19 | 13.04 | 15.76 | 19.5 | 22.75 | 25.31 | 26.94 | 26.7 | 25.13 | 21.35 | 17.77 | 13.7
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-2A | 20.59 | 20.53 | 20.67 | 20.8 | 20.96 | 23.24 | 23.6 | 23.68 | 23.67 | 21.35 | 20.98 | 20.69
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Hospital | 90.1-2010 | ASHRAE 169-2006-2A
LargeHotel | 90.1-2010 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
LargeOffice | 90.1-2010 | ASHRAE 169-2006-2A
MediumOffice | 90.1-2010 | ASHRAE 169-2006-2A | 20.73 | 20.68 | 20.76 | 20.84 | 20.94 | 23.13 | 23.5 | 23.58 | 23.6 | 21.36 | 21.01 | 20.81
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Outpatient | 90.1-2010 | ASHRAE 169-2006-2A | 20.62 | 20.57 | 20.68 | 20.8 | 20.93 | 21.87 | 22.06 | 22.11 | 22.1 | 21.15 | 20.91 | 20.69
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-2A | 20.78 | 20.74 | 20.81 | 20.87 | 20.95 | 23.19 | 23.53 | 23.6 | 23.61 | 21.33 | 21.02 | 20.85
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-2A | 20.41 | 20.33 | 20.54 | 20.74 | 20.98 | 23.29 | 23.67 | 23.76 | 23.73 | 21.38 | 20.94 | 20.54
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-2A | 20.79 | 20.75 | 20.81 | 20.87 | 20.95 | 23.19 | 23.52 | 23.59 | 23.61 | 21.33 | 21.02 | 20.86
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-2A | 20.84 | 20.81 | 20.85 | 20.89 | 20.94 | 23.18 | 23.51 | 23.57 | 23.6 | 21.32 | 21.03 | 20.9
SmallHotel | 90.1-2010 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
SmallOffice | 90.1-2010 | ASHRAE 169-2006-2A | 20.38 | 20.28 | 20.43 | 20.62 | 20.85 | 22.92 | 23.46 | 23.6 | 23.62 | 21.54 | 20.98 | 20.57
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-2A | 20.74 | 20.69 | 20.77 | 20.85 | 20.95 | 23.2 | 23.54 | 23.62 | 23.63 | 21.33 | 21.01 | 20.81
Warehouse | 90.1-2010 | ASHRAE 169-2006-2A | 13.19 | 13.04 | 15.76 | 19.5 | 22.75 | 25.31 | 26.94 | 26.7 | 25.13 | 21.35 | 17.77 | 13.7
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-2A | 20.59 | 20.53 | 20.67 | 20.8 | 20.96 | 23.24 | 23.6 | 23.68 | 23.67 | 21.35 | 20.98 | 20.69
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Hospital | 90.1-2013 | ASHRAE 169-2006-2A
LargeHotel | 90.1-2013 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
LargeOffice | 90.1-2013 | ASHRAE 169-2006-2A
MediumOffice | 90.1-2013 | ASHRAE 169-2006-2A | 20.73 | 20.68 | 20.76 | 20.84 | 20.94 | 23.13 | 23.5 | 23.58 | 23.6 | 21.36 | 21.01 | 20.81
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Outpatient | 90.1-2013 | ASHRAE 169-2006-2A | 20.62 | 20.57 | 20.68 | 20.8 | 20.93 | 21.87 | 22.06 | 22.11 | 22.1 | 21.15 | 20.91 | 20.69
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-2A | 20.78 | 20.74 | 20.81 | 20.87 | 20.95 | 23.19 | 23.53 | 23.6 | 23.61 | 21.33 | 21.02 | 20.85
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-2A | 20.41 | 20.33 | 20.54 | 20.74 | 20.98 | 23.29 | 23.67 | 23.76 | 23.73 | 21.38 | 20.94 | 20.54
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-2A | 20.79 | 20.75 | 20.81 | 20.87 | 20.95 | 23.19 | 23.52 | 23.59 | 23.61 | 21.33 | 21.02 | 20.86
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-2A | 20.84 | 20.81 | 20.85 | 20.89 | 20.94 | 23.18 | 23.51 | 23.57 | 23.6 | 21.32 | 21.03 | 20.9
SmallHotel | 90.1-2013 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
SmallOffice | 90.1-2013 | ASHRAE 169-2006-2A | 20.38 | 20.28 | 20.43 | 20.62 | 20.85 | 22.92 | 23.46 | 23.6 | 23.62 | 21.54 | 20.98 | 20.57
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-2A | 20.74 | 20.69 | 20.77 | 20.85 | 20.95 | 23.2 | 23.54 | 23.62 | 23.63 | 21.33 | 21.01 | 20.81
Warehouse | 90.1-2013 | ASHRAE 169-2006-2A | 13.19 | 13.04 | 15.76 | 19.5 | 22.75 | 25.31 | 26.94 | 26.7 | 25.13 | 21.35 | 17.77 | 13.7
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 10.61 | 10.45 | 11.54 | 13.27 | 16.58 | 19.44 | 22.24 | 24.28 | 21.77 | 17.49 | 14.43 | 11.56
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 10.61 | 10.45 | 11.54 | 13.27 | 16.58 | 19.44 | 22.24 | 24.28 | 21.77 | 17.49 | 14.43 | 11.56
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-2B | 20.67 | 20.66 | 20.81 | 20.97 | 21.11 | 23.49 | 23.9 | 23.96 | 23.93 | 21.53 | 21.11 | 20.79
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Hospital | 90.1-2004 | ASHRAE 169-2006-2B
LargeHotel | 90.1-2004 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
LargeOffice | 90.1-2004 | ASHRAE 169-2006-2B
MediumOffice | 90.1-2004 | ASHRAE 169-2006-2B | 20.78 | 20.76 | 20.85 | 20.95 | 21.03 | 23.29 | 23.69 | 23.76 | 23.76 | 21.48 | 21.09 | 20.87
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Outpatient | 90.1-2004 | ASHRAE 169-2006-2B | 20.68 | 20.68 | 20.8 | 20.94 | 21.05 | 22.07 | 22.31 | 22.34 | 22.31 | 21.3 | 21.03 | 20.78
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-2B | 20.83 | 20.81 | 20.88 | 20.96 | 21.03 | 23.32 | 23.68 | 23.74 | 23.75 | 21.42 | 21.09 | 20.9
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-2B | 20.52 | 20.51 | 20.74 | 20.98 | 21.19 | 23.65 | 24.1 | 24.16 | 24.11 | 21.63 | 21.12 | 20.69
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-2B | 20.83 | 20.82 | 20.88 | 20.96 | 21.02 | 23.31 | 23.67 | 23.73 | 23.74 | 21.42 | 21.09 | 20.91
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
SmallHotel | 90.1-2004 | ASHRAE 169-2006-2B | 20.64 | 20.64 | 20.78 | 20.93 | 21.07 | 21.26 | 21.37 | 21.38 | 21.33 | 21.17 | 20.98 | 20.73
SmallOffice | 90.1-2004 | ASHRAE 169-2006-2B | 20.48 | 20.44 | 20.6 | 20.84 | 21.04 | 23.23 | 23.85 | 23.99 | 23.98 | 21.81 | 21.17 | 20.72
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-2B | 20.79 | 20.78 | 20.86 | 20.96 | 21.05 | 23.36 | 23.73 | 23.79 | 23.79 | 21.45 | 21.09 | 20.88
Warehouse | 90.1-2004 | ASHRAE 169-2006-2B | 13.33 | 13.17 | 17.7 | 20.9 | 24.62 | 30.29 | 31.97 | 31.6 | 29.42 | 23.49 | 18.35 | 13.91
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-2B | 20.67 | 20.66 | 20.81 | 20.97 | 21.11 | 23.49 | 23.9 | 23.96 | 23.93 | 21.53 | 21.11 | 20.79
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Hospital | 90.1-2007 | ASHRAE 169-2006-2B
LargeHotel | 90.1-2007 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
LargeOffice | 90.1-2007 | ASHRAE 169-2006-2B
MediumOffice | 90.1-2007 | ASHRAE 169-2006-2B | 20.78 | 20.76 | 20.85 | 20.95 | 21.03 | 23.29 | 23.69 | 23.76 | 23.76 | 21.48 | 21.09 | 20.87
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Outpatient | 90.1-2007 | ASHRAE 169-2006-2B | 20.68 | 20.68 | 20.8 | 20.94 | 21.05 | 22.07 | 22.31 | 22.34 | 22.31 | 21.3 | 21.03 | 20.78
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-2B | 20.83 | 20.81 | 20.88 | 20.96 | 21.03 | 23.32 | 23.68 | 23.74 | 23.75 | 21.42 | 21.09 | 20.9
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-2B | 20.52 | 20.51 | 20.74 | 20.98 | 21.19 | 23.65 | 24.1 | 24.16 | 24.11 | 21.63 | 21.12 | 20.69
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-2B | 20.83 | 20.82 | 20.88 | 20.96 | 21.02 | 23.31 | 23.67 | 23.73 | 23.74 | 21.42 | 21.09 | 20.91
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
SmallHotel | 90.1-2007 | ASHRAE 169-2006-2B | 20.64 | 20.64 | 20.78 | 20.93 | 21.07 | 21.26 | 21.37 | 21.38 | 21.33 | 21.17 | 20.98 | 20.73
SmallOffice | 90.1-2007 | ASHRAE 169-2006-2B | 20.48 | 20.44 | 20.6 | 20.84 | 21.04 | 23.23 | 23.85 | 23.99 | 23.98 | 21.81 | 21.17 | 20.72
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-2B | 20.79 | 20.78 | 20.86 | 20.96 | 21.05 | 23.36 | 23.73 | 23.79 | 23.79 | 21.45 | 21.09 | 20.88
Warehouse | 90.1-2007 | ASHRAE 169-2006-2B | 13.33 | 13.17 | 17.7 | 20.9 | 24.62 | 30.29 | 31.97 | 31.6 | 29.42 | 23.49 | 18.35 | 13.91
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-2B | 20.67 | 20.66 | 20.81 | 20.97 | 21.11 | 23.49 | 23.9 | 23.96 | 23.93 | 21.53 | 21.11 | 20.79
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Hospital | 90.1-2010 | ASHRAE 169-2006-2B
LargeHotel | 90.1-2010 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
LargeOffice | 90.1-2010 | ASHRAE 169-2006-2B
MediumOffice | 90.1-2010 | ASHRAE 169-2006-2B | 20.78 | 20.76 | 20.85 | 20.95 | 21.03 | 23.29 | 23.69 | 23.76 | 23.76 | 21.48 | 21.09 | 20.87
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Outpatient | 90.1-2010 | ASHRAE 169-2006-2B | 20.68 | 20.68 | 20.8 | 20.94 | 21.05 | 22.07 | 22.31 | 22.34 | 22.31 | 21.3 | 21.03 | 20.78
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-2B | 20.83 | 20.81 | 20.88 | 20.96 | 21.03 | 23.32 | 23.68 | 23.74 | 23.75 | 21.42 | 21.09 | 20.9
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-2B | 20.52 | 20.51 | 20.74 | 20.98 | 21.19 | 23.65 | 24.1 | 24.16 | 24.11 | 21.63 | 21.12 | 20.69
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-2B | 20.83 | 20.82 | 20.88 | 20.96 | 21.02 | 23.31 | 23.67 | 23.73 | 23.74 | 21.42 | 21.09 | 20.91
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
SmallHotel | 90.1-2010 | ASHRAE 169-2006-2B | 20.64 | 20.64 | 20.78 | 20.93 | 21.07 | 21.26 | 21.37 | 21.38 | 21.33 | 21.17 | 20.98 | 20.73
SmallOffice | 90.1-2010 | ASHRAE 169-2006-2B | 20.48 | 20.44 | 20.6 | 20.84 | 21.04 | 23.23 | 23.85 | 23.99 | 23.98 | 21.81 | 21.17 | 20.72
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-2B | 20.79 | 20.78 | 20.86 | 20.96 | 21.05 | 23.36 | 23.73 | 23.79 | 23.79 | 21.45 | 21.09 | 20.88
Warehouse | 90.1-2010 | ASHRAE 169-2006-2B | 13.33 | 13.17 | 17.7 | 20.9 | 24.62 | 30.29 | 31.97 | 31.6 | 29.42 | 23.49 | 18.35 | 13.91
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-2B | 20.67 | 20.66 | 20.81 | 20.97 | 21.11 | 23.49 | 23.9 | 23.96 | 23.93 | 21.53 | 21.11 | 20.79
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Hospital | 90.1-2013 | ASHRAE 169-2006-2B
LargeHotel | 90.1-2013 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
LargeOffice | 90.1-2013 | ASHRAE 169-2006-2B
MediumOffice | 90.1-2013 | ASHRAE 169-2006-2B | 20.78 | 20.76 | 20.85 | 20.95 | 21.03 | 23.29 | 23.69 | 23.76 | 23.76 | 21.48 | 21.09 | 20.87
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Outpatient | 90.1-2013 | ASHRAE 169-2006-2B | 20.68 | 20.68 | 20.8 | 20.94 | 21.05 | 22.07 | 22.31 | 22.34 | 22.31 | 21.3 | 21.03 | 20.78
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-2B | 20.83 | 20.81 | 20.88 | 20.96 | 21.03 | 23.32 | 23.68 | 23.74 | 23.75 | 21.42 | 21.09 | 20.9
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-2B | 20.52 | 20.51 | 20.74 | 20.98 | 21.19 | 23.65 | 24.1 | 24.16 | 24.11 | 21.63 | 21.12 | 20.69
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-2B | 20.83 | 20.82 | 20.88 | 20.96 | 21.02 | 23.31 | 23.67 | 23.73 | 23.74 | 21.42 | 21.09 | 20.91
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
SmallHotel | 90.1-2013 | ASHRAE 169-2006-2B | 20.64 | 20.64 | 20.78 | 20.93 | 21.07 | 21.26 | 21.37 | 21.38 | 21.33 | 21.17 | 20.98 | 20.73
SmallOffice | 90.1-2013 | ASHRAE 169-2006-2B | 20.48 | 20.44 | 20.6 | 20.84 | 21.04 | 23.23 | 23.85 | 23.99 | 23.98 | 21.81 | 21.17 | 20.72
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-2B | 20.79 | 20.78 | 20.86 | 20.96 | 21.05 | 23.36 | 23.73 | 23.79 | 23.79 | 21.45 | 21.09 | 20.88
Warehouse | 90.1-2013 | ASHRAE 169-2006-2B | 13.33 | 13.17 | 17.7 | 20.9 | 24.62 | 30.29 | 31.97 | 31.6 | 29.42 | 23.49 | 18.35 | 13.91
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-3A | 20.28 | 20.26 | 20.41 | 20.61 | 20.83 | 23.15 | 23.54 | 23.63 | 23.58 | 21.18 | 20.75 | 20.45
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-3A | 20.28 | 20.25 | 20.39 | 20.59 | 20.82 | 23.07 | 23.5 | 23.59 | 23.55 | 21.21 | 20.75 | 20.45
Hospital | 90.1-2004 | ASHRAE 169-2006-3A
LargeHotel | 90.1-2004 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
LargeOffice | 90.1-2004 | ASHRAE 169-2006-3A
MediumOffice | 90.1-2004 | ASHRAE 169-2006-3A | 20.53 | 20.51 | 20.6 | 20.72 | 20.85 | 23.07 | 23.47 | 23.55 | 23.54 | 21.25 | 20.86 | 20.65
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-3A | 20.28 | 20.25 | 20.39 | 20.59 | 20.82 | 23.07 | 23.5 | 23.59 | 23.55 | 21.21 | 20.75 | 20.45
Outpatient | 90.1-2004 | ASHRAE 169-2006-3A | 20.36 | 20.35 | 20.47 | 20.64 | 20.82 | 21.79 | 22.02 | 22.07 | 22.02 | 21 | 20.72 | 20.49
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-3A | 20.63 | 20.6 | 20.67 | 20.77 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.9 | 20.73
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-3A | 19.96 | 19.93 | 20.16 | 20.46 | 20.79 | 23.16 | 23.6 | 23.69 | 23.6 | 21.13 | 20.61 | 20.19
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-3A | 20.64 | 20.62 | 20.69 | 20.78 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.91 | 20.74
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
SmallHotel | 90.1-2004 | ASHRAE 169-2006-3A | 20.29 | 20.27 | 20.42 | 20.6 | 20.81 | 20.95 | 21.06 | 21.09 | 21.02 | 20.83 | 20.65 | 20.42
SmallOffice | 90.1-2004 | ASHRAE 169-2006-3A | 19.96 | 19.9 | 20.07 | 20.34 | 20.66 | 22.79 | 23.38 | 23.54 | 23.51 | 21.31 | 20.68 | 20.24
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-3A | 20.55 | 20.52 | 20.61 | 20.73 | 20.87 | 23.14 | 23.51 | 23.58 | 23.57 | 21.23 | 20.87 | 20.66
Warehouse | 90.1-2004 | ASHRAE 169-2006-3A | 12.94 | 12.86 | 12.86 | 16.47 | 21.05 | 24.57 | 26.19 | 26.03 | 23.11 | 17.55 | 13.67 | 13.12
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-3A | 20.28 | 20.26 | 20.41 | 20.61 | 20.83 | 23.15 | 23.54 | 23.63 | 23.58 | 21.18 | 20.75 | 20.45
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-3A | 20.28 | 20.25 | 20.39 | 20.59 | 20.82 | 23.07 | 23.5 | 23.59 | 23.55 | 21.21 | 20.75 | 20.45
Hospital | 90.1-2007 | ASHRAE 169-2006-3A
LargeHotel | 90.1-2007 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
LargeOffice | 90.1-2007 | ASHRAE 169-2006-3A
MediumOffice | 90.1-2007 | ASHRAE 169-2006-3A | 20.53 | 20.51 | 20.6 | 20.72 | 20.85 | 23.07 | 23.47 | 23.55 | 23.54 | 21.25 | 20.86 | 20.65
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-3A | 20.28 | 20.25 | 20.39 | 20.59 | 20.82 | 23.07 | 23.5 | 23.59 | 23.55 | 21.21 | 20.75 | 20.45
Outpatient | 90.1-2007 | ASHRAE 169-2006-3A | 20.36 | 20.35 | 20.47 | 20.64 | 20.82 | 21.79 | 22.02 | 22.07 | 22.02 | 21 | 20.72 | 20.49
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-3A | 20.63 | 20.6 | 20.67 | 20.77 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.9 | 20.73
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-3A | 19.96 | 19.93 | 20.16 | 20.46 | 20.79 | 23.16 | 23.6 | 23.69 | 23.6 | 21.13 | 20.61 | 20.19
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-3A | 20.64 | 20.62 | 20.69 | 20.78 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.91 | 20.74
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
SmallHotel | 90.1-2007 | ASHRAE 169-2006-3A | 20.29 | 20.27 | 20.42 | 20.6 | 20.81 | 20.95 | 21.06 | 21.09 | 21.02 | 20.83 | 20.65 | 20.42
SmallOffice | 90.1-2007 | ASHRAE 169-2006-3A | 19.96 | 19.9 | 20.07 | 20.34 | 20.66 | 22.79 | 23.38 | 23.54 | 23.51 | 21.31 | 20.68 | 20.24
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-3A | 20.55 | 20.52 | 20.61 | 20.73 | 20.87 | 23.14 | 23.51 | 23.58 | 23.57 | 21.23 | 20.87 | 20.66
Warehouse | 90.1-2007 | ASHRAE 169-2006-3A | 12.94 | 12.86 | 12.86 | 16.47 | 21.05 | 24.57 | 26.19 | 26.03 | 23.11 | 17.55 | 13.67 | 13.12
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-3A | 20.28 | 20.26 | 20.41 | 20.61 | 20.83 | 23.15 | 23.54 | 23.63 | 23.58 | 21.18 | 20.75 | 20.45
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-3A | 20.28 | 20.25 | 20.39 | 20.59 | 20.82 | 23.07 | 23.5 | 23.59 | 23.55 | 21.21 | 20.75 | 20.45
Hospital | 90.1-2010 | ASHRAE 169-2006-3A
LargeHotel | 90.1-2010 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
LargeOffice | 90.1-2010 | ASHRAE 169-2006-3A
MediumOffice | 90.1-2010 | ASHRAE 169-2006-3A | 20.53 | 20.51 | 20.6 | 20.72 | 20.85 | 23.07 | 23.47 | 23.55 | 23.54 | 21.25 | 20.86 | 20.65
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-3A | 20.28 | 20.25 | 20.39 | 20.59 | 20.82 | 23.07 | 23.5 | 23.59 | 23.55 | 21.21 | 20.75 | 20.45
Outpatient | 90.1-2010 | ASHRAE 169-2006-3A | 20.36 | 20.35 | 20.47 | 20.64 | 20.82 | 21.79 | 22.02 | 22.07 | 22.02 | 21 | 20.72 | 20.49
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-3A | 20.63 | 20.6 | 20.67 | 20.77 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.9 | 20.73
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-3A | 19.96 | 19.93 | 20.16 | 20.46 | 20.79 | 23.16 | 23.6 | 23.69 | 23.6 | 21.13 | 20.61 | 20.19
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-3A | 20.64 | 20.62 | 20.69 | 20.78 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.91 | 20.74
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
SmallHotel | 90.1-2010 | ASHRAE 169-2006-3A | 20.29 | 20.27 | 20.42 | 20.6 | 20.81 | 20.95 | 21.06 | 21.09 | 21.02 | 20.83 | 20.65 | 20.42
SmallOffice | 90.1-2010 | ASHRAE 169-2006-3A | 19.96 | 19.9 | 20.07 | 20.34 | 20.66 | 22.79 | 23.38 | 23.54 | 23.51 | 21.31 | 20.68 | 20.24
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-3A | 20.55 | 20.52 | 20.61 | 20.73 | 20.87 | 23.14 | 23.51 | 23.58 | 23.57 | 21.23 | 20.87 | 20.66
Warehouse | 90.1-2010 | ASHRAE 169-2006-3A | 12.94 | 12.86 | 12.86 | 16.47 | 21.05 | 24.57 | 26.19 | 26.03 | 23.11 | 17.55 | 13.67 | 13.12
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-3A | 20.28 | 20.26 | 20.41 | 20.61 | 20.83 | 23.15 | 23.54 | 23.63 | 23.58 | 21.18 | 20.75 | 20.45
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-3A | 20.51 | 20.47 | 20.53 | 20.63 | 20.76 | 23.01 | 23.42 | 23.52 | 23.54 | 21.26 | 20.88 | 20.67
Hospital | 90.1-2013 | ASHRAE 169-2006-3A
LargeHotel | 90.1-2013 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
LargeOffice | 90.1-2013 | ASHRAE 169-2006-3A
MediumOffice | 90.1-2013 | ASHRAE 169-2006-3A | 20.53 | 20.51 | 20.6 | 20.72 | 20.85 | 23.07 | 23.47 | 23.55 | 23.54 | 21.25 | 20.86 | 20.65
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-3A | 20.51 | 20.47 | 20.53 | 20.63 | 20.76 | 23.01 | 23.42 | 23.52 | 23.54 | 21.26 | 20.88 | 20.67
Outpatient | 90.1-2013 | ASHRAE 169-2006-3A | 20.36 | 20.35 | 20.47 | 20.64 | 20.82 | 21.79 | 22.02 | 22.07 | 22.02 | 21 | 20.72 | 20.49
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-3A | 20.63 | 20.6 | 20.67 | 20.77 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.9 | 20.73
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-3A | 19.96 | 19.93 | 20.16 | 20.46 | 20.79 | 23.16 | 23.6 | 23.69 | 23.6 | 21.13 | 20.61 | 20.19
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-3A | 20.64 | 20.62 | 20.69 | 20.78 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.91 | 20.74
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
SmallHotel | 90.1-2013 | ASHRAE 169-2006-3A | 20.29 | 20.27 | 20.42 | 20.6 | 20.81 | 20.95 | 21.06 | 21.09 | 21.02 | 20.83 | 20.65 | 20.42
SmallOffice | 90.1-2013 | ASHRAE 169-2006-3A | 19.96 | 19.9 | 20.07 | 20.34 | 20.66 | 22.79 | 23.38 | 23.54 | 23.51 | 21.31 | 20.68 | 20.24
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-3A | 20.55 | 20.52 | 20.61 | 20.73 | 20.87 | 23.14 | 23.51 | 23.58 | 23.57 | 21.23 | 20.87 | 20.66
Warehouse | 90.1-2013 | ASHRAE 169-2006-3A | 12.94 | 12.86 | 12.86 | 16.47 | 21.05 | 24.57 | 26.19 | 26.03 | 23.11 | 17.55 | 13.67 | 13.12
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 10.51 | 10.33 | 11.44 | 13.16 | 16.48 | 19.37 | 22.18 | 24.28 | 21.77 | 17.43 | 14.32 | 11.46
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 10.51 | 10.33 | 11.44 | 13.16 | 16.48 | 19.37 | 22.18 | 24.28 | 21.77 | 17.43 | 14.32 | 11.46
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-3B | 20.41 | 20.43 | 20.57 | 20.67 | 20.88 | 23.27 | 23.66 | 23.69 | 23.65 | 21.29 | 20.81 | 20.56
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-3B | 20.41 | 20.42 | 20.56 | 20.65 | 20.87 | 23.19 | 23.62 | 23.66 | 23.62 | 21.32 | 20.81 | 20.56
Hospital | 90.1-2004 | ASHRAE 169-2006-3B
LargeHotel | 90.1-2004 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
LargeOffice | 90.1-2004 | ASHRAE 169-2006-3B
MediumOffice | 90.1-2004 | ASHRAE 169-2006-3B | 20.62 | 20.61 | 20.7 | 20.75 | 20.89 | 23.14 | 23.54 | 23.59 | 23.58 | 21.32 | 20.9 | 20.72
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-3B | 20.41 | 20.42 | 20.56 | 20.65 | 20.87 | 23.19 | 23.62 | 23.66 | 23.62 | 21.32 | 20.81 | 20.56
Outpatient | 90.1-2004 | ASHRAE 169-2006-3B | 20.47 | 20.48 | 20.6 | 20.69 | 20.86 | 21.89 | 22.11 | 22.12 | 22.08 | 21.1 | 20.77 | 20.58
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-3B | 20.69 | 20.69 | 20.76 | 20.8 | 20.91 | 23.2 | 23.56 | 23.61 | 23.6 | 21.3 | 20.93 | 20.78
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-3B | 20.15 | 20.18 | 20.4 | 20.55 | 20.87 | 23.33 | 23.76 | 23.78 | 23.7 | 21.28 | 20.69 | 20.35
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-3B | 20.71 | 20.71 | 20.77 | 20.81 | 20.91 | 23.2 | 23.55 | 23.6 | 23.6 | 21.3 | 20.94 | 20.79
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
SmallHotel | 90.1-2004 | ASHRAE 169-2006-3B | 20.4 | 20.43 | 20.56 | 20.66 | 20.86 | 21.06 | 21.16 | 21.14 | 21.08 | 20.94 | 20.7 | 20.52
SmallOffice | 90.1-2004 | ASHRAE 169-2006-3B | 20.13 | 20.1 | 20.29 | 20.43 | 20.73 | 22.94 | 23.54 | 23.63 | 23.6 | 21.46 | 20.77 | 20.38
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-3B | 20.63 | 20.63 | 20.71 | 20.77 | 20.9 | 23.22 | 23.58 | 23.63 | 23.61 | 21.29 | 20.91 | 20.73
Warehouse | 90.1-2004 | ASHRAE 169-2006-3B | 13 | 12.93 | 13.51 | 16.19 | 21.28 | 26.23 | 27.17 | 25.64 | 23.19 | 18.61 | 13.81 | 13.19
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-3B | 20.41 | 20.43 | 20.57 | 20.67 | 20.88 | 23.27 | 23.66 | 23.69 | 23.65 | 21.29 | 20.81 | 20.56
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-3B | 20.41 | 20.42 | 20.56 | 20.65 | 20.87 | 23.19 | 23.62 | 23.66 | 23.62 | 21.32 | 20.81 | 20.56
Hospital | 90.1-2007 | ASHRAE 169-2006-3B
LargeHotel | 90.1-2007 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
LargeOffice | 90.1-2007 | ASHRAE 169-2006-3B
MediumOffice | 90.1-2007 | ASHRAE 169-2006-3B | 20.62 | 20.61 | 20.7 | 20.75 | 20.89 | 23.14 | 23.54 | 23.59 | 23.58 | 21.32 | 20.9 | 20.72
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-3B | 20.41 | 20.42 | 20.56 | 20.65 | 20.87 | 23.19 | 23.62 | 23.66 | 23.62 | 21.32 | 20.81 | 20.56
Outpatient | 90.1-2007 | ASHRAE 169-2006-3B | 20.47 | 20.48 | 20.6 | 20.69 | 20.86 | 21.89 | 22.11 | 22.12 | 22.08 | 21.1 | 20.77 | 20.58
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-3B | 20.69 | 20.69 | 20.76 | 20.8 | 20.91 | 23.2 | 23.56 | 23.61 | 23.6 | 21.3 | 20.93 | 20.78
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-3B | 20.15 | 20.18 | 20.4 | 20.55 | 20.87 | 23.33 | 23.76 | 23.78 | 23.7 | 21.28 | 20.69 | 20.35
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-3B | 20.71 | 20.71 | 20.77 | 20.81 | 20.91 | 23.2 | 23.55 | 23.6 | 23.6 | 21.3 | 20.94 | 20.79
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
SmallHotel | 90.1-2007 | ASHRAE 169-2006-3B | 20.4 | 20.43 | 20.56 | 20.66 | 20.86 | 21.06 | 21.16 | 21.14 | 21.08 | 20.94 | 20.7 | 20.52
SmallOffice | 90.1-2007 | ASHRAE 169-2006-3B | 20.13 | 20.1 | 20.29 | 20.43 | 20.73 | 22.94 | 23.54 | 23.63 | 23.6 | 21.46 | 20.77 | 20.38
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-3B | 20.63 | 20.63 | 20.71 | 20.77 | 20.9 | 23.22 | 23.58 | 23.63 | 23.61 | 21.29 | 20.91 | 20.73
Warehouse | 90.1-2007 | ASHRAE 169-2006-3B | 13 | 12.93 | 13.51 | 16.19 | 21.28 | 26.23 | 27.17 | 25.64 | 23.19 | 18.61 | 13.81 | 13.19
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-3B | 20.41 | 20.43 | 20.57 | 20.67 | 20.88 | 23.27 | 23.66 | 23.69 | 23.65 | 21.29 | 20.81 | 20.56
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-3B | 20.41 | 20.42 | 20.56 | 20.65 | 20.87 | 23.19 | 23.62 | 23.66 | 23.62 | 21.32 | 20.81 | 20.56
Hospital | 90.1-2010 | ASHRAE 169-2006-3B
LargeHotel | 90.1-2010 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
LargeOffice | 90.1-2010 | ASHRAE 169-2006-3B
MediumOffice | 90.1-2010 | ASHRAE 169-2006-3B | 20.62 | 20.61 | 20.7 | 20.75 | 20.89 | 23.14 | 23.54 | 23.59 | 23.58 | 21.32 | 20.9 | 20.72
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-3B | 20.41 | 20.42 | 20.56 | 20.65 | 20.87 | 23.19 | 23.62 | 23.66 | 23.62 | 21.32 | 20.81 | 20.56
Outpatient | 90.1-2010 | ASHRAE 169-2006-3B | 20.47 | 20.48 | 20.6 | 20.69 | 20.86 | 21.89 | 22.11 | 22.12 | 22.08 | 21.1 | 20.77 | 20.58
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-3B | 20.69 | 20.69 | 20.76 | 20.8 | 20.91 | 23.2 | 23.56 | 23.61 | 23.6 | 21.3 | 20.93 | 20.78
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-3B | 20.15 | 20.18 | 20.4 | 20.55 | 20.87 | 23.33 | 23.76 | 23.78 | 23.7 | 21.28 | 20.69 | 20.35
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-3B | 20.71 | 20.71 | 20.77 | 20.81 | 20.91 | 23.2 | 23.55 | 23.6 | 23.6 | 21.3 | 20.94 | 20.79
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
SmallHotel | 90.1-2010 | ASHRAE 169-2006-3B | 20.4 | 20.43 | 20.56 | 20.66 | 20.86 | 21.06 | 21.16 | 21.14 | 21.08 | 20.94 | 20.7 | 20.52
SmallOffice | 90.1-2010 | ASHRAE 169-2006-3B | 20.13 | 20.1 | 20.29 | 20.43 | 20.73 | 22.94 | 23.54 | 23.63 | 23.6 | 21.46 | 20.77 | 20.38
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-3B | 20.63 | 20.63 | 20.71 | 20.77 | 20.9 | 23.22 | 23.58 | 23.63 | 23.61 | 21.29 | 20.91 | 20.73
Warehouse | 90.1-2010 | ASHRAE 169-2006-3B | 13 | 12.93 | 13.51 | 16.19 | 21.28 | 26.23 | 27.17 | 25.64 | 23.19 | 18.61 | 13.81 | 13.19
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-3B | 20.41 | 20.43 | 20.57 | 20.67 | 20.88 | 23.27 | 23.66 | 23.69 | 23.65 | 21.29 | 20.81 | 20.56
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-3B | 20.61 | 20.57 | 20.64 | 20.69 | 20.81 | 23.09 | 23.51 | 23.58 | 23.59 | 21.34 | 20.93 | 20.74
Hospital | 90.1-2013 | ASHRAE 169-2006-3B
LargeHotel | 90.1-2013 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
LargeOffice | 90.1-2013 | ASHRAE 169-2006-3B
MediumOffice | 90.1-2013 | ASHRAE 169-2006-3B | 20.62 | 20.61 | 20.7 | 20.75 | 20.89 | 23.14 | 23.54 | 23.59 | 23.58 | 21.32 | 20.9 | 20.72
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-3B | 20.61 | 20.57 | 20.64 | 20.69 | 20.81 | 23.09 | 23.51 | 23.58 | 23.59 | 21.34 | 20.93 | 20.74
Outpatient | 90.1-2013 | ASHRAE 169-2006-3B | 20.47 | 20.48 | 20.6 | 20.69 | 20.86 | 21.89 | 22.11 | 22.12 | 22.08 | 21.1 | 20.77 | 20.58
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-3B | 20.69 | 20.69 | 20.76 | 20.8 | 20.91 | 23.2 | 23.56 | 23.61 | 23.6 | 21.3 | 20.93 | 20.78
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-3B | 20.15 | 20.18 | 20.4 | 20.55 | 20.87 | 23.33 | 23.76 | 23.78 | 23.7 | 21.28 | 20.69 | 20.35
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-3B | 20.71 | 20.71 | 20.77 | 20.81 | 20.91 | 23.2 | 23.55 | 23.6 | 23.6 | 21.3 | 20.94 | 20.79
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
SmallHotel | 90.1-2013 | ASHRAE 169-2006-3B | 20.4 | 20.43 | 20.56 | 20.66 | 20.86 | 21.06 | 21.16 | 21.14 | 21.08 | 20.94 | 20.7 | 20.52
SmallOffice | 90.1-2013 | ASHRAE 169-2006-3B | 20.13 | 20.1 | 20.29 | 20.43 | 20.73 | 22.94 | 23.54 | 23.63 | 23.6 | 21.46 | 20.77 | 20.38
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-3B | 20.63 | 20.63 | 20.71 | 20.77 | 20.9 | 23.22 | 23.58 | 23.63 | 23.61 | 21.29 | 20.91 | 20.73
Warehouse | 90.1-2013 | ASHRAE 169-2006-3B | 13 | 12.93 | 13.51 | 16.19 | 21.28 | 26.23 | 27.17 | 25.64 | 23.19 | 18.61 | 13.81 | 13.19
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 10.57 | 10.43 | 11.51 | 13.2 | 16.53 | 19.43 | 22.22 | 24.26 | 21.73 | 17.45 | 14.36 | 11.51
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 20.133 | 20.114 | 20.098 | 20.195 | 20.555 | 20.958 | 22.367 | 22.7 | 22.775 | 21.957 | 20.592 | 20.216
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 10.57 | 10.43 | 11.51 | 13.2 | 16.53 | 19.43 | 22.22 | 24.26 | 21.73 | 17.45 | 14.36 | 11.51
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-3C | 20.33 | 20.37 | 20.38 | 20.44 | 20.51 | 22.71 | 23.07 | 23.13 | 23.16 | 20.95 | 20.61 | 20.42
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-3C | 20.32 | 20.37 | 20.36 | 20.43 | 20.49 | 22.64 | 23.02 | 23.09 | 23.13 | 20.98 | 20.61 | 20.42
Hospital | 90.1-2004 | ASHRAE 169-2006-3C
LargeHotel | 90.1-2004 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
LargeOffice | 90.1-2004 | ASHRAE 169-2006-3C
MediumOffice | 90.1-2004 | ASHRAE 169-2006-3C | 20.56 | 20.58 | 20.57 | 20.61 | 20.65 | 22.79 | 23.17 | 23.23 | 23.27 | 21.11 | 20.77 | 20.63
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-3C | 20.32 | 20.37 | 20.36 | 20.43 | 20.49 | 22.64 | 23.02 | 23.09 | 23.13 | 20.98 | 20.61 | 20.42
Outpatient | 90.1-2004 | ASHRAE 169-2006-3C | 20.4 | 20.44 | 20.44 | 20.5 | 20.55 | 21.44 | 21.63 | 21.66 | 21.68 | 20.8 | 20.6 | 20.47
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-3C | 20.65 | 20.66 | 20.66 | 20.68 | 20.72 | 22.92 | 23.26 | 23.32 | 23.35 | 21.12 | 20.83 | 20.71
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-3C | 20.04 | 20.11 | 20.12 | 20.22 | 20.33 | 22.53 | 22.9 | 22.96 | 22.99 | 20.8 | 20.4 | 20.16
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-3C | 20.66 | 20.68 | 20.67 | 20.7 | 20.73 | 22.93 | 23.27 | 23.33 | 23.36 | 21.13 | 20.84 | 20.72
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
SmallHotel | 90.1-2004 | ASHRAE 169-2006-3C | 20.33 | 20.38 | 20.39 | 20.45 | 20.51 | 20.57 | 20.64 | 20.64 | 20.65 | 20.61 | 20.52 | 20.39
SmallOffice | 90.1-2004 | ASHRAE 169-2006-3C | 20.04 | 20.07 | 20.07 | 20.15 | 20.24 | 22.19 | 22.71 | 22.82 | 22.88 | 20.95 | 20.47 | 20.19
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-3C | 20.57 | 20.59 | 20.59 | 20.63 | 20.67 | 22.87 | 23.21 | 23.27 | 23.31 | 21.08 | 20.77 | 20.64
Warehouse | 90.1-2004 | ASHRAE 169-2006-3C | 12.76 | 12.76 | 12.75 | 12.76 | 13.58 | 14.42 | 15.67 | 15.85 | 16.37 | 15.08 | 13.09 | 12.83
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-3C | 20.33 | 20.37 | 20.38 | 20.44 | 20.51 | 22.71 | 23.07 | 23.13 | 23.16 | 20.95 | 20.61 | 20.42
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-3C | 20.32 | 20.37 | 20.36 | 20.43 | 20.49 | 22.64 | 23.02 | 23.09 | 23.13 | 20.98 | 20.61 | 20.42
Hospital | 90.1-2007 | ASHRAE 169-2006-3C
LargeHotel | 90.1-2007 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
LargeOffice | 90.1-2007 | ASHRAE 169-2006-3C
MediumOffice | 90.1-2007 | ASHRAE 169-2006-3C | 20.56 | 20.58 | 20.57 | 20.61 | 20.65 | 22.79 | 23.17 | 23.23 | 23.27 | 21.11 | 20.77 | 20.63
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-3C | 20.32 | 20.37 | 20.36 | 20.43 | 20.49 | 22.64 | 23.02 | 23.09 | 23.13 | 20.98 | 20.61 | 20.42
Outpatient | 90.1-2007 | ASHRAE 169-2006-3C | 20.4 | 20.44 | 20.44 | 20.5 | 20.55 | 21.44 | 21.63 | 21.66 | 21.68 | 20.8 | 20.6 | 20.47
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-3C | 20.65 | 20.66 | 20.66 | 20.68 | 20.72 | 22.92 | 23.26 | 23.32 | 23.35 | 21.12 | 20.83 | 20.71
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-3C | 20.04 | 20.11 | 20.12 | 20.22 | 20.33 | 22.53 | 22.9 | 22.96 | 22.99 | 20.8 | 20.4 | 20.16
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-3C | 20.66 | 20.68 | 20.67 | 20.7 | 20.73 | 22.93 | 23.27 | 23.33 | 23.36 | 21.13 | 20.84 | 20.72
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
SmallHotel | 90.1-2007 | ASHRAE 169-2006-3C | 20.33 | 20.38 | 20.39 | 20.45 | 20.51 | 20.57 | 20.64 | 20.64 | 20.65 | 20.61 | 20.52 | 20.39
SmallOffice | 90.1-2007 | ASHRAE 169-2006-3C | 20.04 | 20.07 | 20.07 | 20.15 | 20.24 | 22.19 | 22.71 | 22.82 | 22.88 | 20.95 | 20.47 | 20.19
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-3C | 20.57 | 20.59 | 20.59 | 20.63 | 20.67 | 22.87 | 23.21 | 23.27 | 23.31 | 21.08 | 20.77 | 20.64
Warehouse | 90.1-2007 | ASHRAE 169-2006-3C | 12.76 | 12.76 | 12.75 | 12.76 | 13.58 | 14.42 | 15.67 | 15.85 | 16.37 | 15.08 | 13.09 | 12.83
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-3C | 20.33 | 20.37 | 20.38 | 20.44 | 20.51 | 22.71 | 23.07 | 23.13 | 23.16 | 20.95 | 20.61 | 20.42
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-3C | 20.32 | 20.37 | 20.36 | 20.43 | 20.49 | 22.64 | 23.02 | 23.09 | 23.13 | 20.98 | 20.61 | 20.42
Hospital | 90.1-2010 | ASHRAE 169-2006-3C
LargeHotel | 90.1-2010 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
LargeOffice | 90.1-2010 | ASHRAE 169-2006-3C
MediumOffice | 90.1-2010 | ASHRAE 169-2006-3C | 20.56 | 20.58 | 20.57 | 20.61 | 20.65 | 22.79 | 23.17 | 23.23 | 23.27 | 21.11 | 20.77 | 20.63
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-3C | 20.32 | 20.37 | 20.36 | 20.43 | 20.49 | 22.64 | 23.02 | 23.09 | 23.13 | 20.98 | 20.61 | 20.42
Outpatient | 90.1-2010 | ASHRAE 169-2006-3C | 20.4 | 20.44 | 20.44 | 20.5 | 20.55 | 21.44 | 21.63 | 21.66 | 21.68 | 20.8 | 20.6 | 20.47
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-3C | 20.65 | 20.66 | 20.66 | 20.68 | 20.72 | 22.92 | 23.26 | 23.32 | 23.35 | 21.12 | 20.83 | 20.71
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-3C | 20.04 | 20.11 | 20.12 | 20.22 | 20.33 | 22.53 | 22.9 | 22.96 | 22.99 | 20.8 | 20.4 | 20.16
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-3C | 20.66 | 20.68 | 20.67 | 20.7 | 20.73 | 22.93 | 23.27 | 23.33 | 23.36 | 21.13 | 20.84 | 20.72
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
SmallHotel | 90.1-2010 | ASHRAE 169-2006-3C | 20.33 | 20.38 | 20.39 | 20.45 | 20.51 | 20.57 | 20.64 | 20.64 | 20.65 | 20.61 | 20.52 | 20.39
SmallOffice | 90.1-2010 | ASHRAE 169-2006-3C | 20.04 | 20.07 | 20.07 | 20.15 | 20.24 | 22.19 | 22.71 | 22.82 | 22.88 | 20.95 | 20.47 | 20.19
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-3C | 20.57 | 20.59 | 20.59 | 20.63 | 20.67 | 22.87 | 23.21 | 23.27 | 23.31 | 21.08 | 20.77 | 20.64
Warehouse | 90.1-2010 | ASHRAE 169-2006-3C | 12.76 | 12.76 | 12.75 | 12.76 | 13.58 | 14.42 | 15.67 | 15.85 | 16.37 | 15.08 | 13.09 | 12.83
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-3C | 20.33 | 20.37 | 20.38 | 20.44 | 20.51 | 22.71 | 23.07 | 23.13 | 23.16 | 20.95 | 20.61 | 20.42
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-3C | 20.51 | 20.51 | 20.5 | 20.53 | 20.57 | 22.72 | 23.1 | 23.17 | 23.21 | 21.06 | 20.73 | 20.59
Hospital | 90.1-2013 | ASHRAE 169-2006-3C
LargeHotel | 90.1-2013 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
LargeOffice | 90.1-2013 | ASHRAE 169-2006-3C
MediumOffice | 90.1-2013 | ASHRAE 169-2006-3C | 20.56 | 20.58 | 20.57 | 20.61 | 20.65 | 22.79 | 23.17 | 23.23 | 23.27 | 21.11 | 20.77 | 20.63
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-3C | 20.51 | 20.51 | 20.5 | 20.53 | 20.57 | 22.72 | 23.1 | 23.17 | 23.21 | 21.06 | 20.73 | 20.59
Outpatient | 90.1-2013 | ASHRAE 169-2006-3C | 20.4 | 20.44 | 20.44 | 20.5 | 20.55 | 21.44 | 21.63 | 21.66 | 21.68 | 20.8 | 20.6 | 20.47
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-3C | 20.65 | 20.66 | 20.66 | 20.68 | 20.72 | 22.92 | 23.26 | 23.32 | 23.35 | 21.12 | 20.83 | 20.71
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-3C | 20.04 | 20.11 | 20.12 | 20.22 | 20.33 | 22.53 | 22.9 | 22.96 | 22.99 | 20.8 | 20.4 | 20.16
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-3C | 20.66 | 20.68 | 20.67 | 20.7 | 20.73 | 22.93 | 23.27 | 23.33 | 23.36 | 21.13 | 20.84 | 20.72
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
SmallHotel | 90.1-2013 | ASHRAE 169-2006-3C | 20.33 | 20.38 | 20.39 | 20.45 | 20.51 | 20.57 | 20.64 | 20.64 | 20.65 | 20.61 | 20.52 | 20.39
SmallOffice | 90.1-2013 | ASHRAE 169-2006-3C | 20.04 | 20.07 | 20.07 | 20.15 | 20.24 | 22.19 | 22.71 | 22.82 | 22.88 | 20.95 | 20.47 | 20.19
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-3C | 20.57 | 20.59 | 20.59 | 20.63 | 20.67 | 22.87 | 23.21 | 23.27 | 23.31 | 21.08 | 20.77 | 20.64
Warehouse | 90.1-2013 | ASHRAE 169-2006-3C | 12.76 | 12.76 | 12.75 | 12.76 | 13.58 | 14.42 | 15.67 | 15.85 | 16.37 | 15.08 | 13.09 | 12.83
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 10.56 | 10.42 | 11.49 | 13.19 | 16.48 | 19.37 | 22.14 | 24.19 | 21.68 | 17.4 | 14.34 | 11.52
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 10.56 | 10.42 | 11.49 | 13.19 | 16.48 | 19.37 | 22.14 | 24.19 | 21.68 | 17.4 | 14.34 | 11.52
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-4A | 20 | 19.93 | 20.11 | 20.26 | 20.49 | 22.89 | 23.33 | 23.44 | 23.36 | 21 | 20.52 | 20.17
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-4A | 19.99 | 19.92 | 20.1 | 20.24 | 20.48 | 22.81 | 23.29 | 23.4 | 23.33 | 21.03 | 20.52 | 20.17
Hospital | 90.1-2004 | ASHRAE 169-2006-4A
LargeHotel | 90.1-2004 | ASHRAE 169-2006-4A | 20.62 | 20.59 | 20.64 | 20.69 | 20.77 | 23.05 | 23.41 | 23.48 | 23.48 | 21.19 | 20.87 | 20.71
LargeOffice | 90.1-2004 | ASHRAE 169-2006-4A
MediumOffice | 90.1-2004 | ASHRAE 169-2006-4A | 20.35 | 20.3 | 20.41 | 20.49 | 20.64 | 22.9 | 23.33 | 23.43 | 23.4 | 21.14 | 20.72 | 20.48
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-4A | 19.99 | 19.92 | 20.1 | 20.24 | 20.48 | 22.81 | 23.29 | 23.4 | 23.33 | 21.03 | 20.52 | 20.17
Outpatient | 90.1-2004 | ASHRAE 169-2006-4A | 20.12 | 20.07 | 20.22 | 20.34 | 20.54 | 21.58 | 21.84 | 21.91 | 21.84 | 20.85 | 20.53 | 20.26
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-4A | 20.48 | 20.43 | 20.52 | 20.59 | 20.71 | 23.01 | 23.39 | 23.47 | 23.45 | 21.15 | 20.79 | 20.58
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-4A | 19.55 | 19.46 | 19.73 | 19.96 | 20.31 | 22.79 | 23.29 | 23.42 | 23.29 | 20.87 | 20.28 | 19.79
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-4A | 20.5 | 20.46 | 20.54 | 20.61 | 20.72 | 23.01 | 23.39 | 23.47 | 23.46 | 21.16 | 20.8 | 20.61
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-4A | 20.62 | 20.59 | 20.64 | 20.69 | 20.77 | 23.05 | 23.41 | 23.48 | 23.48 | 21.19 | 20.87 | 20.71
SmallHotel | 90.1-2004 | ASHRAE 169-2006-4A | 20.03 | 19.97 | 20.15 | 20.28 | 20.5 | 20.73 | 20.87 | 20.92 | 20.83 | 20.66 | 20.44 | 20.17
SmallOffice | 90.1-2004 | ASHRAE 169-2006-4A | 19.58 | 19.45 | 19.66 | 19.86 | 20.19 | 22.4 | 23.07 | 23.28 | 23.21 | 21.07 | 20.38 | 19.87
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-4A | 20.36 | 20.31 | 20.42 | 20.51 | 20.65 | 22.98 | 23.37 | 23.46 | 23.43 | 21.11 | 20.72 | 20.49
Warehouse | 90.1-2004 | ASHRAE 169-2006-4A | 12.74 | 12.67 | 12.7 | 12.74 | 16.14 | 21 | 23.32 | 23.64 | 19.96 | 14.91 | 13.22 | 12.88
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-4A | 20 | 19.93 | 20.11 | 20.26 | 20.49 | 22.89 | 23.33 | 23.44 | 23.36 | 21 | 20.52 | 20.17
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-4A | 20.31 | 20.22 | 20.3 | 20.38 | 20.51 | 22.79 | 23.24 | 23.36 | 23.36 | 21.12 | 20.71 | 20.46
Hospital | 90.1-2007 | ASHRAE 169-2006-4A
LargeHotel | 90.1-2007 | ASHRAE 169-2006-4A | 20.62 | 20.59 | 20.64 | 20.69 | 20.77 | 23.05 | 23.41 | 23.48 | 23.48 | 21.19 | 20.87 | 20.71
LargeOffice | 90.1-2007 | ASHRAE 169-2006-4A
MediumOffice | 90.1-2007 | ASHRAE 169-2006-4A | 20.35 | 20.3 | 20.41 | 20.49 | 20.64 | 22.9 | 23.33 | 23.43 | 23.4 | 21.14 | 20.72 | 20.48
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-4A | 20.31 | 20.22 | 20.3 | 20.38 | 20.51 | 22.79 | 23.24 | 23.36 | 23.36 | 21.12 | 20.71 | 20.46
Outpatient | 90.1-2007 | ASHRAE 169-2006-4A | 20.12 | 20.07 | 20.22 | 20.34 | 20.54 | 21.58 | 21.84 | 21.91 | 21.84 | 20.85 | 20.53 | 20.26
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-4A | 20.48 | 20.43 | 20.52 | 20.59 | 20.71 | 23.01 | 23.39 | 23.47 | 23.45 | 21.15 | 20.79 | 20.58
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-4A | 19.55 | 19.46 | 19.73 | 19.96 | 20.31 | 22.79 | 23.29 | 23.42 | 23.29 | 20.87 | 20.28 | 19.79
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-4A | 20.5 | 20.46 | 20.54 | 20.61 | 20.72 | 23.01 | 23.39 | 23.47 | 23.46 | 21.16 | 20.8 | 20.61
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-4A | 20.62 | 20.59 | 20.64 | 20.69 | 20.77 | 23.05 | 23.41 | 23.48 | 23.48 | 21.19 | 20.87 | 20.71
SmallHotel | 90.1-2007 | ASHRAE 169-2006-4A | 20.03 | 19.97 | 20.15 | 20.28 | 20.5 | 20.73 | 20.87 | 20.92 | 20.83 | 20.66 | 20.44 | 20.17
SmallOffice | 90.1-2007 | ASHRAE 169-2006-4A | 19.58 | 19.45 | 19.66 | 19.86 | 20.19 | 22.4 | 23.07 | 23.28 | 23.21 | 21.07 | 20.38 | 19.87
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-4A | 20.36 | 20.31 | 20.42 | 20.51 | 20.65 | 22.98 | 23.37 | 23.46 | 23.43 | 21.11 | 20.72 | 20.49
Warehouse | 90.1-2007 | ASHRAE 169-2006-4A | 12.74 | 12.67 | 12.7 | 12.74 | 16.14 | 21 | 23.32 | 23.64 | 19.96 | 14.91 | 13.22 | 12.88
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-4A | 20 | 19.93 | 20.11 | 20.26 | 20.49 | 22.89 | 23.33 | 23.44 | 23.36 | 21 | 20.52 | 20.17
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-4A | 20.31 | 20.22 | 20.3 | 20.38 | 20.51 | 22.79 | 23.24 | 23.36 | 23.36 | 21.12 | 20.71 | 20.46
Hospital | 90.1-2010 | ASHRAE 169-2006-4A
LargeHotel | 90.1-2010 | ASHRAE 169-2006-4A | 20.62 | 20.59 | 20.64 | 20.69 | 20.77 | 23.05 | 23.41 | 23.48 | 23.48 | 21.19 | 20.87 | 20.71
LargeOffice | 90.1-2010 | ASHRAE 169-2006-4A
MediumOffice | 90.1-2010 | ASHRAE 169-2006-4A | 20.35 | 20.3 | 20.41 | 20.49 | 20.64 | 22.9 | 23.33 | 23.43 | 23.4 | 21.14 | 20.72 | 20.48
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-4A | 20.31 | 20.22 | 20.3 | 20.38 | 20.51 | 22.79 | 23.24 | 23.36 | 23.36 | 21.12 | 20.71 | 20.46
Outpatient | 90.1-2010 | ASHRAE 169-2006-4A | 20.12 | 20.07 | 20.22 | 20.34 | 20.54 | 21.58 | 21.84 | 21.91 | 21.84 | 20.85 | 20.53 | 20.26
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-4A | 20.48 | 20.43 | 20.52 | 20.59 | 20.71 | 23.01 | 23.39 | 23.47 | 23.45 | 21.15 | 20.79 | 20.58
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-4A | 19.55 | 19.46 | 19.73 | 19.96 | 20.31 | 22.79 | 23.29 | 23.42 | 23.29 | 20.87 | 20.28 | 19.79
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-4A | 20.5 | 20.46 | 20.54 | 20.61 | 20.72 | 23.01 | 23.39 | 23.47 | 23.46 | 21.16 | 20.8 | 20.61
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-4A | 20.62 | 20.59 | 20.64 | 20.69 | 20.77 | 23.05 | 23.41 | 23.48 | 23.48 | 21.19 | 20.87 | 20.71
SmallHotel | 90.1-2010 | ASHRAE 169-2006-4A | 20.03 | 19.97 | 20.15 | 20.28 | 20.5 | 20.73 | 20.87 | 20.92 | 20.83 | 20.66 | 20.44 | 20.17
SmallOffice | 90.1-2010 | ASHRAE 169-2006-4A | 19.58 | 19.45 | 19.66 | 19.86 | 20.19 | 22.4 | 23.07 | 23.28 | 23.21 | 21.07 | 20.38 | 19.87
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-4A | 20.36 | 20.31 | 20.42 | 20.51 | 20.65 | 22.98 | 23.37 | 23.46 | 23.43 | 21.11 | 20.72 | 20.49
Warehouse | 90.1-2010 | ASHRAE 169-2006-4A | 12.74 | 12.67 | 12.7 | 12.74 | 16.14 | 21 | 23.32 | 23.64 | 19.96 | 14.91 | 13.22 | 12.88
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-4A | 20.47 | 20.39 | 20.42 | 20.48 | 20.57 | 22.88 | 23.27 | 23.39 | 23.41 | 21.13 | 20.79 | 20.6
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-4A | 20.36 | 20.28 | 20.33 | 20.4 | 20.52 | 22.79 | 23.23 | 23.36 | 23.37 | 21.14 | 20.74 | 20.51
Hospital | 90.1-2013 | ASHRAE 169-2006-4A
LargeHotel | 90.1-2013 | ASHRAE 169-2006-4A | 20.62 | 20.59 | 20.64 | 20.69 | 20.77 | 23.05 | 23.41 | 23.48 | 23.48 | 21.19 | 20.87 | 20.71
LargeOffice | 90.1-2013 | ASHRAE 169-2006-4A
MediumOffice | 90.1-2013 | ASHRAE 169-2006-4A | 20.58 | 20.52 | 20.55 | 20.59 | 20.67 | 22.89 | 23.29 | 23.4 | 23.42 | 21.21 | 20.85 | 20.69
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-4A | 20.36 | 20.28 | 20.33 | 20.4 | 20.52 | 22.79 | 23.23 | 23.36 | 23.37 | 21.14 | 20.74 | 20.51
Outpatient | 90.1-2013 | ASHRAE 169-2006-4A | 20.44 | 20.37 | 20.42 | 20.48 | 20.58 | 21.54 | 21.78 | 21.86 | 21.85 | 20.94 | 20.71 | 20.55
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-4A | 20.71 | 20.66 | 20.68 | 20.7 | 20.74 | 23 | 23.36 | 23.45 | 23.47 | 21.21 | 20.92 | 20.8
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-4A | 20.25 | 20.15 | 20.2 | 20.28 | 20.42 | 22.77 | 23.2 | 23.34 | 23.36 | 21.07 | 20.68 | 20.43
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-4A | 20.73 | 20.68 | 20.69 | 20.71 | 20.75 | 23.01 | 23.36 | 23.45 | 23.48 | 21.22 | 20.92 | 20.81
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-4A | 20.79 | 20.75 | 20.75 | 20.77 | 20.8 | 23.04 | 23.38 | 23.47 | 23.5 | 21.24 | 20.96 | 20.86
SmallHotel | 90.1-2013 | ASHRAE 169-2006-4A | 20.36 | 20.3 | 20.36 | 20.43 | 20.54 | 20.67 | 20.78 | 20.85 | 20.83 | 20.75 | 20.63 | 20.48
SmallOffice | 90.1-2013 | ASHRAE 169-2006-4A | 20.11 | 19.97 | 20.01 | 20.1 | 20.27 | 22.38 | 22.99 | 23.2 | 23.25 | 21.22 | 20.67 | 20.35
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-4A | 20.65 | 20.6 | 20.61 | 20.64 | 20.7 | 22.97 | 23.34 | 23.43 | 23.46 | 21.19 | 20.89 | 20.75
Warehouse | 90.1-2013 | ASHRAE 169-2006-4A | 12.74 | 12.67 | 12.7 | 12.74 | 16.14 | 21 | 23.32 | 23.64 | 19.96 | 14.91 | 13.22 | 12.88
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 10.41 | 10.24 | 11.37 | 13.1 | 16.43 | 19.37 | 22.17 | 24.22 | 21.68 | 17.38 | 14.27 | 11.38
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 10.41 | 10.24 | 11.37 | 13.1 | 16.43 | 19.37 | 22.17 | 24.22 | 21.68 | 17.38 | 14.27 | 11.38
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-4B | 20.11 | 20.14 | 20.23 | 20.4 | 20.65 | 23.01 | 23.46 | 23.53 | 23.47 | 21.08 | 20.54 | 20.25
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-4B | 20.1 | 20.13 | 20.21 | 20.39 | 20.64 | 22.94 | 23.41 | 23.5 | 23.43 | 21.11 | 20.54 | 20.25
Hospital | 90.1-2004 | ASHRAE 169-2006-4B
LargeHotel | 90.1-2004 | ASHRAE 169-2006-4B | 20.67 | 20.66 | 20.69 | 20.74 | 20.83 | 23.09 | 23.45 | 23.52 | 23.52 | 21.22 | 20.87 | 20.74
LargeOffice | 90.1-2004 | ASHRAE 169-2006-4B
MediumOffice | 90.1-2004 | ASHRAE 169-2006-4B | 20.42 | 20.43 | 20.48 | 20.59 | 20.74 | 22.98 | 23.41 | 23.49 | 23.46 | 21.19 | 20.73 | 20.53
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-4B | 20.1 | 20.13 | 20.21 | 20.39 | 20.64 | 22.94 | 23.41 | 23.5 | 23.43 | 21.11 | 20.54 | 20.25
Outpatient | 90.1-2004 | ASHRAE 169-2006-4B | 20.21 | 20.24 | 20.32 | 20.47 | 20.67 | 21.68 | 21.94 | 21.99 | 21.93 | 20.92 | 20.55 | 20.33
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-4B | 20.54 | 20.54 | 20.58 | 20.66 | 20.79 | 23.07 | 23.45 | 23.52 | 23.51 | 21.19 | 20.8 | 20.63
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-4B | 19.71 | 19.77 | 19.9 | 20.17 | 20.54 | 22.97 | 23.47 | 23.55 | 23.44 | 20.99 | 20.3 | 19.91
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-4B | 20.56 | 20.56 | 20.6 | 20.68 | 20.79 | 23.08 | 23.45 | 23.52 | 23.51 | 21.2 | 20.81 | 20.65
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-4B | 20.67 | 20.66 | 20.69 | 20.74 | 20.83 | 23.09 | 23.45 | 23.52 | 23.52 | 21.22 | 20.87 | 20.74
SmallHotel | 90.1-2004 | ASHRAE 169-2006-4B | 20.12 | 20.17 | 20.25 | 20.42 | 20.65 | 20.84 | 20.98 | 21 | 20.92 | 20.74 | 20.46 | 20.24
SmallOffice | 90.1-2004 | ASHRAE 169-2006-4B | 19.71 | 19.71 | 19.82 | 20.06 | 20.41 | 22.58 | 23.24 | 23.4 | 23.34 | 21.19 | 20.41 | 19.97
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-4B | 20.43 | 20.45 | 20.5 | 20.6 | 20.75 | 23.06 | 23.45 | 23.52 | 23.5 | 21.17 | 20.74 | 20.54
Warehouse | 90.1-2004 | ASHRAE 169-2006-4B | 12.78 | 12.75 | 12.75 | 12.8 | 17.63 | 21.41 | 24.22 | 23.02 | 20.59 | 14.35 | 13.17 | 12.91
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-4B | 20.11 | 20.14 | 20.23 | 20.4 | 20.65 | 23.01 | 23.46 | 23.53 | 23.47 | 21.08 | 20.54 | 20.25
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-4B | 20.38 | 20.36 | 20.4 | 20.48 | 20.63 | 22.89 | 23.33 | 23.44 | 23.44 | 21.19 | 20.74 | 20.52
Hospital | 90.1-2007 | ASHRAE 169-2006-4B
LargeHotel | 90.1-2007 | ASHRAE 169-2006-4B | 20.67 | 20.66 | 20.69 | 20.74 | 20.83 | 23.09 | 23.45 | 23.52 | 23.52 | 21.22 | 20.87 | 20.74
LargeOffice | 90.1-2007 | ASHRAE 169-2006-4B
MediumOffice | 90.1-2007 | ASHRAE 169-2006-4B | 20.42 | 20.43 | 20.48 | 20.59 | 20.74 | 22.98 | 23.41 | 23.49 | 23.46 | 21.19 | 20.73 | 20.53
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-4B | 20.38 | 20.36 | 20.4 | 20.48 | 20.63 | 22.89 | 23.33 | 23.44 | 23.44 | 21.19 | 20.74 | 20.52
Outpatient | 90.1-2007 | ASHRAE 169-2006-4B | 20.21 | 20.24 | 20.32 | 20.47 | 20.67 | 21.68 | 21.94 | 21.99 | 21.93 | 20.92 | 20.55 | 20.33
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-4B | 20.54 | 20.54 | 20.58 | 20.66 | 20.79 | 23.07 | 23.45 | 23.52 | 23.51 | 21.19 | 20.8 | 20.63
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-4B | 19.71 | 19.77 | 19.9 | 20.17 | 20.54 | 22.97 | 23.47 | 23.55 | 23.44 | 20.99 | 20.3 | 19.91
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-4B | 20.56 | 20.56 | 20.6 | 20.68 | 20.79 | 23.08 | 23.45 | 23.52 | 23.51 | 21.2 | 20.81 | 20.65
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-4B | 20.67 | 20.66 | 20.69 | 20.74 | 20.83 | 23.09 | 23.45 | 23.52 | 23.52 | 21.22 | 20.87 | 20.74
SmallHotel | 90.1-2007 | ASHRAE 169-2006-4B | 20.12 | 20.17 | 20.25 | 20.42 | 20.65 | 20.84 | 20.98 | 21 | 20.92 | 20.74 | 20.46 | 20.24
SmallOffice | 90.1-2007 | ASHRAE 169-2006-4B | 19.71 | 19.71 | 19.82 | 20.06 | 20.41 | 22.58 | 23.24 | 23.4 | 23.34 | 21.19 | 20.41 | 19.97
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-4B | 20.43 | 20.45 | 20.5 | 20.6 | 20.75 | 23.06 | 23.45 | 23.52 | 23.5 | 21.17 | 20.74 | 20.54
Warehouse | 90.1-2007 | ASHRAE 169-2006-4B | 12.78 | 12.75 | 12.75 | 12.8 | 17.63 | 21.41 | 24.22 | 23.02 | 20.59 | 14.35 | 13.17 | 12.91
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-4B | 20.11 | 20.14 | 20.23 | 20.4 | 20.65 | 23.01 | 23.46 | 23.53 | 23.47 | 21.08 | 20.54 | 20.25
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-4B | 20.38 | 20.36 | 20.4 | 20.48 | 20.63 | 22.89 | 23.33 | 23.44 | 23.44 | 21.19 | 20.74 | 20.52
Hospital | 90.1-2010 | ASHRAE 169-2006-4B
LargeHotel | 90.1-2010 | ASHRAE 169-2006-4B | 20.67 | 20.66 | 20.69 | 20.74 | 20.83 | 23.09 | 23.45 | 23.52 | 23.52 | 21.22 | 20.87 | 20.74
LargeOffice | 90.1-2010 | ASHRAE 169-2006-4B
MediumOffice | 90.1-2010 | ASHRAE 169-2006-4B | 20.42 | 20.43 | 20.48 | 20.59 | 20.74 | 22.98 | 23.41 | 23.49 | 23.46 | 21.19 | 20.73 | 20.53
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-4B | 20.38 | 20.36 | 20.4 | 20.48 | 20.63 | 22.89 | 23.33 | 23.44 | 23.44 | 21.19 | 20.74 | 20.52
Outpatient | 90.1-2010 | ASHRAE 169-2006-4B | 20.21 | 20.24 | 20.32 | 20.47 | 20.67 | 21.68 | 21.94 | 21.99 | 21.93 | 20.92 | 20.55 | 20.33
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-4B | 20.54 | 20.54 | 20.58 | 20.66 | 20.79 | 23.07 | 23.45 | 23.52 | 23.51 | 21.19 | 20.8 | 20.63
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-4B | 19.71 | 19.77 | 19.9 | 20.17 | 20.54 | 22.97 | 23.47 | 23.55 | 23.44 | 20.99 | 20.3 | 19.91
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-4B | 20.56 | 20.56 | 20.6 | 20.68 | 20.79 | 23.08 | 23.45 | 23.52 | 23.51 | 21.2 | 20.81 | 20.65
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-4B | 20.67 | 20.66 | 20.69 | 20.74 | 20.83 | 23.09 | 23.45 | 23.52 | 23.52 | 21.22 | 20.87 | 20.74
SmallHotel | 90.1-2010 | ASHRAE 169-2006-4B | 20.12 | 20.17 | 20.25 | 20.42 | 20.65 | 20.84 | 20.98 | 21 | 20.92 | 20.74 | 20.46 | 20.24
SmallOffice | 90.1-2010 | ASHRAE 169-2006-4B | 19.71 | 19.71 | 19.82 | 20.06 | 20.41 | 22.58 | 23.24 | 23.4 | 23.34 | 21.19 | 20.41 | 19.97
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-4B | 20.43 | 20.45 | 20.5 | 20.6 | 20.75 | 23.06 | 23.45 | 23.52 | 23.5 | 21.17 | 20.74 | 20.54
Warehouse | 90.1-2010 | ASHRAE 169-2006-4B | 12.78 | 12.75 | 12.75 | 12.8 | 17.63 | 21.41 | 24.22 | 23.02 | 20.59 | 14.35 | 13.17 | 12.91
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-4B | 20.53 | 20.5 | 20.51 | 20.56 | 20.66 | 22.96 | 23.36 | 23.46 | 23.48 | 21.19 | 20.82 | 20.65
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-4B | 20.43 | 20.4 | 20.43 | 20.49 | 20.63 | 22.88 | 23.32 | 23.43 | 23.44 | 21.2 | 20.77 | 20.57
Hospital | 90.1-2013 | ASHRAE 169-2006-4B
LargeHotel | 90.1-2013 | ASHRAE 169-2006-4B | 20.67 | 20.66 | 20.69 | 20.74 | 20.83 | 23.09 | 23.45 | 23.52 | 23.52 | 21.22 | 20.87 | 20.74
LargeOffice | 90.1-2013 | ASHRAE 169-2006-4B
MediumOffice | 90.1-2013 | ASHRAE 169-2006-4B | 20.63 | 20.6 | 20.61 | 20.65 | 20.73 | 22.95 | 23.35 | 23.45 | 23.47 | 21.25 | 20.88 | 20.73
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-4B | 20.43 | 20.4 | 20.43 | 20.49 | 20.63 | 22.88 | 23.32 | 23.43 | 23.44 | 21.2 | 20.77 | 20.57
Outpatient | 90.1-2013 | ASHRAE 169-2006-4B | 20.49 | 20.48 | 20.5 | 20.56 | 20.66 | 21.62 | 21.85 | 21.92 | 21.91 | 20.99 | 20.74 | 20.59
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-4B | 20.75 | 20.72 | 20.72 | 20.74 | 20.79 | 23.05 | 23.4 | 23.49 | 23.51 | 21.25 | 20.94 | 20.82
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-4B | 20.34 | 20.3 | 20.32 | 20.4 | 20.55 | 22.89 | 23.32 | 23.44 | 23.45 | 21.15 | 20.73 | 20.5
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-4B | 20.76 | 20.73 | 20.73 | 20.75 | 20.8 | 23.05 | 23.4 | 23.49 | 23.51 | 21.25 | 20.94 | 20.83
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-4B | 20.81 | 20.79 | 20.79 | 20.8 | 20.83 | 23.07 | 23.42 | 23.49 | 23.52 | 21.26 | 20.97 | 20.88
SmallHotel | 90.1-2013 | ASHRAE 169-2006-4B | 20.42 | 20.41 | 20.45 | 20.51 | 20.64 | 20.76 | 20.87 | 20.91 | 20.89 | 20.82 | 20.67 | 20.53
SmallOffice | 90.1-2013 | ASHRAE 169-2006-4B | 20.19 | 20.12 | 20.14 | 20.23 | 20.41 | 22.51 | 23.11 | 23.3 | 23.34 | 21.3 | 20.73 | 20.41
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-4B | 20.69 | 20.67 | 20.67 | 20.7 | 20.76 | 23.03 | 23.39 | 23.48 | 23.5 | 21.23 | 20.91 | 20.78
Warehouse | 90.1-2013 | ASHRAE 169-2006-4B | 12.78 | 12.75 | 12.75 | 12.8 | 17.63 | 21.41 | 24.22 | 23.02 | 20.59 | 14.35 | 13.17 | 12.91
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-4C | 20.07 | 20.09 | 20.13 | 20.22 | 20.37 | 22.68 | 23.1 | 23.22 | 23.19 | 20.84 | 20.38 | 20.21
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-4C | 20.06 | 20.07 | 20.12 | 20.2 | 20.36 | 22.6 | 23.05 | 23.18 | 23.15 | 20.86 | 20.38 | 20.21
Hospital | 90.1-2004 | ASHRAE 169-2006-4C
LargeHotel | 90.1-2004 | ASHRAE 169-2006-4C | 20.65 | 20.64 | 20.65 | 20.68 | 20.73 | 22.97 | 23.32 | 23.4 | 23.42 | 21.13 | 20.81 | 20.72
LargeOffice | 90.1-2004 | ASHRAE 169-2006-4C
MediumOffice | 90.1-2004 | ASHRAE 169-2006-4C | 20.4 | 20.4 | 20.42 | 20.47 | 20.56 | 22.77 | 23.18 | 23.29 | 23.28 | 21.03 | 20.63 | 20.5
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-4C | 20.06 | 20.07 | 20.12 | 20.2 | 20.36 | 22.6 | 23.05 | 23.18 | 23.15 | 20.86 | 20.38 | 20.21
Outpatient | 90.1-2004 | ASHRAE 169-2006-4C | 20.18 | 20.2 | 20.24 | 20.31 | 20.44 | 21.41 | 21.65 | 21.73 | 21.7 | 20.71 | 20.41 | 20.29
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-4C | 20.51 | 20.51 | 20.53 | 20.57 | 20.65 | 22.9 | 23.27 | 23.36 | 23.36 | 21.07 | 20.71 | 20.6
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-4C | 19.65 | 19.69 | 19.77 | 19.9 | 20.13 | 22.49 | 22.95 | 23.1 | 23.03 | 20.63 | 20.08 | 19.86
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-4C | 20.54 | 20.54 | 20.55 | 20.59 | 20.66 | 22.92 | 23.28 | 23.37 | 23.37 | 21.08 | 20.73 | 20.62
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-4C | 20.65 | 20.64 | 20.65 | 20.68 | 20.73 | 22.97 | 23.32 | 23.4 | 23.42 | 21.13 | 20.81 | 20.72
SmallHotel | 90.1-2004 | ASHRAE 169-2006-4C | 20.09 | 20.12 | 20.17 | 20.25 | 20.39 | 20.54 | 20.66 | 20.72 | 20.67 | 20.51 | 20.31 | 20.2
SmallOffice | 90.1-2004 | ASHRAE 169-2006-4C | 19.67 | 19.66 | 19.72 | 19.82 | 20.04 | 22.13 | 22.74 | 22.94 | 22.94 | 20.82 | 20.17 | 19.9
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-4C | 20.41 | 20.41 | 20.44 | 20.48 | 20.58 | 22.85 | 23.23 | 23.32 | 23.32 | 21.01 | 20.63 | 20.51
Warehouse | 90.1-2004 | ASHRAE 169-2006-4C | 12.66 | 12.65 | 12.66 | 12.68 | 12.9 | 15.26 | 17.68 | 18.6 | 16.67 | 13.27 | 12.86 | 12.75
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-4C | 20.07 | 20.09 | 20.13 | 20.22 | 20.37 | 22.68 | 23.1 | 23.22 | 23.19 | 20.84 | 20.38 | 20.21
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-4C | 20.32 | 20.31 | 20.32 | 20.36 | 20.45 | 22.67 | 23.08 | 23.2 | 23.22 | 20.99 | 20.59 | 20.44
Hospital | 90.1-2007 | ASHRAE 169-2006-4C
LargeHotel | 90.1-2007 | ASHRAE 169-2006-4C | 20.65 | 20.64 | 20.65 | 20.68 | 20.73 | 22.97 | 23.32 | 23.4 | 23.42 | 21.13 | 20.81 | 20.72
LargeOffice | 90.1-2007 | ASHRAE 169-2006-4C
MediumOffice | 90.1-2007 | ASHRAE 169-2006-4C | 20.4 | 20.4 | 20.42 | 20.47 | 20.56 | 22.77 | 23.18 | 23.29 | 23.28 | 21.03 | 20.63 | 20.5
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-4C | 20.32 | 20.31 | 20.32 | 20.36 | 20.45 | 22.67 | 23.08 | 23.2 | 23.22 | 20.99 | 20.59 | 20.44
Outpatient | 90.1-2007 | ASHRAE 169-2006-4C | 20.18 | 20.2 | 20.24 | 20.31 | 20.44 | 21.41 | 21.65 | 21.73 | 21.7 | 20.71 | 20.41 | 20.29
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-4C | 20.51 | 20.51 | 20.53 | 20.57 | 20.65 | 22.9 | 23.27 | 23.36 | 23.36 | 21.07 | 20.71 | 20.6
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-4C | 19.65 | 19.69 | 19.77 | 19.9 | 20.13 | 22.49 | 22.95 | 23.1 | 23.03 | 20.63 | 20.08 | 19.86
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-4C | 20.54 | 20.54 | 20.55 | 20.59 | 20.66 | 22.92 | 23.28 | 23.37 | 23.37 | 21.08 | 20.73 | 20.62
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-4C | 20.65 | 20.64 | 20.65 | 20.68 | 20.73 | 22.97 | 23.32 | 23.4 | 23.42 | 21.13 | 20.81 | 20.72
SmallHotel | 90.1-2007 | ASHRAE 169-2006-4C | 20.09 | 20.12 | 20.17 | 20.25 | 20.39 | 20.54 | 20.66 | 20.72 | 20.67 | 20.51 | 20.31 | 20.2
SmallOffice | 90.1-2007 | ASHRAE 169-2006-4C | 19.67 | 19.66 | 19.72 | 19.82 | 20.04 | 22.13 | 22.74 | 22.94 | 22.94 | 20.82 | 20.17 | 19.9
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-4C | 20.41 | 20.41 | 20.44 | 20.48 | 20.58 | 22.85 | 23.23 | 23.32 | 23.32 | 21.01 | 20.63 | 20.51
Warehouse | 90.1-2007 | ASHRAE 169-2006-4C | 12.66 | 12.65 | 12.66 | 12.68 | 12.9 | 15.26 | 17.68 | 18.6 | 16.67 | 13.27 | 12.86 | 12.75
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-4C | 20.07 | 20.09 | 20.13 | 20.22 | 20.37 | 22.68 | 23.1 | 23.22 | 23.19 | 20.84 | 20.38 | 20.21
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-4C | 20.32 | 20.31 | 20.32 | 20.36 | 20.45 | 22.67 | 23.08 | 23.2 | 23.22 | 20.99 | 20.59 | 20.44
Hospital | 90.1-2010 | ASHRAE 169-2006-4C
LargeHotel | 90.1-2010 | ASHRAE 169-2006-4C | 20.65 | 20.64 | 20.65 | 20.68 | 20.73 | 22.97 | 23.32 | 23.4 | 23.42 | 21.13 | 20.81 | 20.72
LargeOffice | 90.1-2010 | ASHRAE 169-2006-4C
MediumOffice | 90.1-2010 | ASHRAE 169-2006-4C | 20.4 | 20.4 | 20.42 | 20.47 | 20.56 | 22.77 | 23.18 | 23.29 | 23.28 | 21.03 | 20.63 | 20.5
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-4C | 20.32 | 20.31 | 20.32 | 20.36 | 20.45 | 22.67 | 23.08 | 23.2 | 23.22 | 20.99 | 20.59 | 20.44
Outpatient | 90.1-2010 | ASHRAE 169-2006-4C | 20.18 | 20.2 | 20.24 | 20.31 | 20.44 | 21.41 | 21.65 | 21.73 | 21.7 | 20.71 | 20.41 | 20.29
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-4C | 20.51 | 20.51 | 20.53 | 20.57 | 20.65 | 22.9 | 23.27 | 23.36 | 23.36 | 21.07 | 20.71 | 20.6
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-4C | 19.65 | 19.69 | 19.77 | 19.9 | 20.13 | 22.49 | 22.95 | 23.1 | 23.03 | 20.63 | 20.08 | 19.86
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-4C | 20.54 | 20.54 | 20.55 | 20.59 | 20.66 | 22.92 | 23.28 | 23.37 | 23.37 | 21.08 | 20.73 | 20.62
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-4C | 20.65 | 20.64 | 20.65 | 20.68 | 20.73 | 22.97 | 23.32 | 23.4 | 23.42 | 21.13 | 20.81 | 20.72
SmallHotel | 90.1-2010 | ASHRAE 169-2006-4C | 20.09 | 20.12 | 20.17 | 20.25 | 20.39 | 20.54 | 20.66 | 20.72 | 20.67 | 20.51 | 20.31 | 20.2
SmallOffice | 90.1-2010 | ASHRAE 169-2006-4C | 19.67 | 19.66 | 19.72 | 19.82 | 20.04 | 22.13 | 22.74 | 22.94 | 22.94 | 20.82 | 20.17 | 19.9
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-4C | 20.41 | 20.41 | 20.44 | 20.48 | 20.58 | 22.85 | 23.23 | 23.32 | 23.32 | 21.01 | 20.63 | 20.51
Warehouse | 90.1-2010 | ASHRAE 169-2006-4C | 12.66 | 12.65 | 12.66 | 12.68 | 12.9 | 15.26 | 17.68 | 18.6 | 16.67 | 13.27 | 12.86 | 12.75
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-4C | 20.47 | 20.44 | 20.44 | 20.46 | 20.52 | 22.79 | 23.16 | 23.27 | 23.3 | 21.03 | 20.69 | 20.57
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-4C | 20.37 | 20.35 | 20.36 | 20.38 | 20.46 | 22.68 | 23.09 | 23.21 | 23.24 | 21.02 | 20.63 | 20.48
Hospital | 90.1-2013 | ASHRAE 169-2006-4C
LargeHotel | 90.1-2013 | ASHRAE 169-2006-4C | 20.65 | 20.64 | 20.65 | 20.68 | 20.73 | 22.97 | 23.32 | 23.4 | 23.42 | 21.13 | 20.81 | 20.72
LargeOffice | 90.1-2013 | ASHRAE 169-2006-4C
MediumOffice | 90.1-2013 | ASHRAE 169-2006-4C | 20.59 | 20.57 | 20.57 | 20.58 | 20.63 | 22.82 | 23.2 | 23.31 | 23.34 | 21.13 | 20.78 | 20.67
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-4C | 20.37 | 20.35 | 20.36 | 20.38 | 20.46 | 22.68 | 23.09 | 23.21 | 23.24 | 21.02 | 20.63 | 20.48
Outpatient | 90.1-2013 | ASHRAE 169-2006-4C | 20.44 | 20.43 | 20.44 | 20.46 | 20.53 | 21.46 | 21.66 | 21.74 | 21.75 | 20.83 | 20.62 | 20.53
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-4C | 20.71 | 20.69 | 20.69 | 20.69 | 20.72 | 22.96 | 23.3 | 23.38 | 23.42 | 21.16 | 20.87 | 20.78
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-4C | 20.25 | 20.22 | 20.23 | 20.26 | 20.35 | 22.64 | 23.04 | 23.17 | 23.2 | 20.92 | 20.54 | 20.39
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-4C | 20.73 | 20.7 | 20.7 | 20.7 | 20.73 | 22.97 | 23.3 | 23.39 | 23.42 | 21.17 | 20.88 | 20.79
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-4C | 20.79 | 20.77 | 20.76 | 20.76 | 20.78 | 23.01 | 23.34 | 23.42 | 23.46 | 21.2 | 20.92 | 20.85
SmallHotel | 90.1-2013 | ASHRAE 169-2006-4C | 20.37 | 20.36 | 20.38 | 20.41 | 20.49 | 20.58 | 20.66 | 20.71 | 20.71 | 20.64 | 20.53 | 20.45
SmallOffice | 90.1-2013 | ASHRAE 169-2006-4C | 20.11 | 20.06 | 20.06 | 20.1 | 20.21 | 22.24 | 22.8 | 22.99 | 23.05 | 21.04 | 20.51 | 20.29
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-4C | 20.65 | 20.63 | 20.63 | 20.64 | 20.67 | 22.92 | 23.26 | 23.35 | 23.39 | 21.13 | 20.82 | 20.73
Warehouse | 90.1-2013 | ASHRAE 169-2006-4C | 12.66 | 12.65 | 12.66 | 12.68 | 12.9 | 15.26 | 17.68 | 18.6 | 16.67 | 13.27 | 12.86 | 12.75
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 10.49 | 10.34 | 11.42 | 13.14 | 16.46 | 19.35 | 22.13 | 24.18 | 21.65 | 17.37 | 14.28 | 11.43
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 10.49 | 10.34 | 11.42 | 13.14 | 16.46 | 19.35 | 22.13 | 24.18 | 21.65 | 17.37 | 14.28 | 11.43
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-5A | 19.77 | 19.74 | 19.84 | 20.08 | 20.34 | 22.78 | 23.24 | 23.3 | 23.25 | 20.85 | 20.35 | 19.99
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-5A | 19.76 | 19.73 | 19.83 | 20.06 | 20.32 | 22.7 | 23.19 | 23.26 | 23.22 | 20.87 | 20.35 | 19.99
Hospital | 90.1-2004 | ASHRAE 169-2006-5A
LargeHotel | 90.1-2004 | ASHRAE 169-2006-5A | 20.54 | 20.52 | 20.55 | 20.63 | 20.72 | 23.01 | 23.37 | 23.43 | 23.44 | 21.14 | 20.8 | 20.64
LargeOffice | 90.1-2004 | ASHRAE 169-2006-5A
MediumOffice | 90.1-2004 | ASHRAE 169-2006-5A | 20.21 | 20.18 | 20.24 | 20.38 | 20.54 | 22.83 | 23.27 | 23.33 | 23.33 | 21.04 | 20.61 | 20.36
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-5A | 19.76 | 19.73 | 19.83 | 20.06 | 20.32 | 22.7 | 23.19 | 23.26 | 23.22 | 20.87 | 20.35 | 19.99
Outpatient | 90.1-2004 | ASHRAE 169-2006-5A | 19.93 | 19.91 | 20 | 20.19 | 20.41 | 21.49 | 21.76 | 21.79 | 21.75 | 20.71 | 20.39 | 20.11
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-5A | 20.36 | 20.34 | 20.38 | 20.5 | 20.63 | 22.95 | 23.34 | 23.4 | 23.39 | 21.07 | 20.7 | 20.49
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-5A | 19.22 | 19.18 | 19.34 | 19.7 | 20.09 | 22.64 | 23.16 | 23.21 | 23.13 | 20.64 | 20.04 | 19.53
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-5A | 20.39 | 20.37 | 20.41 | 20.52 | 20.64 | 22.96 | 23.34 | 23.4 | 23.4 | 21.08 | 20.72 | 20.52
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-5A | 20.54 | 20.52 | 20.55 | 20.63 | 20.72 | 23.01 | 23.37 | 23.43 | 23.44 | 21.14 | 20.8 | 20.64
SmallHotel | 90.1-2004 | ASHRAE 169-2006-5A | 19.82 | 19.8 | 19.9 | 20.12 | 20.36 | 20.63 | 20.78 | 20.79 | 20.73 | 20.51 | 20.29 | 20
SmallOffice | 90.1-2004 | ASHRAE 169-2006-5A | 19.27 | 19.18 | 19.29 | 19.59 | 19.96 | 22.25 | 22.94 | 23.08 | 23.06 | 20.85 | 20.16 | 19.63
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-5A | 20.22 | 20.19 | 20.25 | 20.4 | 20.56 | 22.91 | 23.31 | 23.37 | 23.36 | 21.02 | 20.62 | 20.37
Warehouse | 90.1-2004 | ASHRAE 169-2006-5A | 12.61 | 12.57 | 12.58 | 12.65 | 14.73 | 19.66 | 22.3 | 21.36 | 18.32 | 13.55 | 12.97 | 12.75
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-5A | 19.77 | 19.74 | 19.84 | 20.08 | 20.34 | 22.78 | 23.24 | 23.3 | 23.25 | 20.85 | 20.35 | 19.99
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-5A | 20.14 | 20.08 | 20.11 | 20.23 | 20.39 | 22.7 | 23.15 | 23.25 | 23.27 | 21.01 | 20.59 | 20.33
Hospital | 90.1-2007 | ASHRAE 169-2006-5A
LargeHotel | 90.1-2007 | ASHRAE 169-2006-5A | 20.54 | 20.52 | 20.55 | 20.63 | 20.72 | 23.01 | 23.37 | 23.43 | 23.44 | 21.14 | 20.8 | 20.64
LargeOffice | 90.1-2007 | ASHRAE 169-2006-5A
MediumOffice | 90.1-2007 | ASHRAE 169-2006-5A | 20.21 | 20.18 | 20.24 | 20.38 | 20.54 | 22.83 | 23.27 | 23.33 | 23.33 | 21.04 | 20.61 | 20.36
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-5A | 20.14 | 20.08 | 20.11 | 20.23 | 20.39 | 22.7 | 23.15 | 23.25 | 23.27 | 21.01 | 20.59 | 20.33
Outpatient | 90.1-2007 | ASHRAE 169-2006-5A | 19.93 | 19.91 | 20 | 20.19 | 20.41 | 21.49 | 21.76 | 21.79 | 21.75 | 20.71 | 20.39 | 20.11
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-5A | 20.36 | 20.34 | 20.38 | 20.5 | 20.63 | 22.95 | 23.34 | 23.4 | 23.39 | 21.07 | 20.7 | 20.49
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-5A | 19.22 | 19.18 | 19.34 | 19.7 | 20.09 | 22.64 | 23.16 | 23.21 | 23.13 | 20.64 | 20.04 | 19.53
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-5A | 20.39 | 20.37 | 20.41 | 20.52 | 20.64 | 22.96 | 23.34 | 23.4 | 23.4 | 21.08 | 20.72 | 20.52
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-5A | 20.54 | 20.52 | 20.55 | 20.63 | 20.72 | 23.01 | 23.37 | 23.43 | 23.44 | 21.14 | 20.8 | 20.64
SmallHotel | 90.1-2007 | ASHRAE 169-2006-5A | 19.82 | 19.8 | 19.9 | 20.12 | 20.36 | 20.63 | 20.78 | 20.79 | 20.73 | 20.51 | 20.29 | 20
SmallOffice | 90.1-2007 | ASHRAE 169-2006-5A | 19.27 | 19.18 | 19.29 | 19.59 | 19.96 | 22.25 | 22.94 | 23.08 | 23.06 | 20.85 | 20.16 | 19.63
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-5A | 20.22 | 20.19 | 20.25 | 20.4 | 20.56 | 22.91 | 23.31 | 23.37 | 23.36 | 21.02 | 20.62 | 20.37
Warehouse | 90.1-2007 | ASHRAE 169-2006-5A | 12.61 | 12.57 | 12.58 | 12.65 | 14.73 | 19.66 | 22.3 | 21.36 | 18.32 | 13.55 | 12.97 | 12.75
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-5A | 19.77 | 19.74 | 19.84 | 20.08 | 20.34 | 22.78 | 23.24 | 23.3 | 23.25 | 20.85 | 20.35 | 19.99
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-5A | 20.14 | 20.08 | 20.11 | 20.23 | 20.39 | 22.7 | 23.15 | 23.25 | 23.27 | 21.01 | 20.59 | 20.33
Hospital | 90.1-2010 | ASHRAE 169-2006-5A
LargeHotel | 90.1-2010 | ASHRAE 169-2006-5A | 20.54 | 20.52 | 20.55 | 20.63 | 20.72 | 23.01 | 23.37 | 23.43 | 23.44 | 21.14 | 20.8 | 20.64
LargeOffice | 90.1-2010 | ASHRAE 169-2006-5A
MediumOffice | 90.1-2010 | ASHRAE 169-2006-5A | 20.21 | 20.18 | 20.24 | 20.38 | 20.54 | 22.83 | 23.27 | 23.33 | 23.33 | 21.04 | 20.61 | 20.36
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-5A | 20.14 | 20.08 | 20.11 | 20.23 | 20.39 | 22.7 | 23.15 | 23.25 | 23.27 | 21.01 | 20.59 | 20.33
Outpatient | 90.1-2010 | ASHRAE 169-2006-5A | 19.93 | 19.91 | 20 | 20.19 | 20.41 | 21.49 | 21.76 | 21.79 | 21.75 | 20.71 | 20.39 | 20.11
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-5A | 20.36 | 20.34 | 20.38 | 20.5 | 20.63 | 22.95 | 23.34 | 23.4 | 23.39 | 21.07 | 20.7 | 20.49
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-5A | 19.22 | 19.18 | 19.34 | 19.7 | 20.09 | 22.64 | 23.16 | 23.21 | 23.13 | 20.64 | 20.04 | 19.53
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-5A | 20.39 | 20.37 | 20.41 | 20.52 | 20.64 | 22.96 | 23.34 | 23.4 | 23.4 | 21.08 | 20.72 | 20.52
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-5A | 20.54 | 20.52 | 20.55 | 20.63 | 20.72 | 23.01 | 23.37 | 23.43 | 23.44 | 21.14 | 20.8 | 20.64
SmallHotel | 90.1-2010 | ASHRAE 169-2006-5A | 19.82 | 19.8 | 19.9 | 20.12 | 20.36 | 20.63 | 20.78 | 20.79 | 20.73 | 20.51 | 20.29 | 20
SmallOffice | 90.1-2010 | ASHRAE 169-2006-5A | 19.27 | 19.18 | 19.29 | 19.59 | 19.96 | 22.25 | 22.94 | 23.08 | 23.06 | 20.85 | 20.16 | 19.63
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-5A | 20.22 | 20.19 | 20.25 | 20.4 | 20.56 | 22.91 | 23.31 | 23.37 | 23.36 | 21.02 | 20.62 | 20.37
Warehouse | 90.1-2010 | ASHRAE 169-2006-5A | 12.61 | 12.57 | 12.58 | 12.65 | 14.73 | 19.66 | 22.3 | 21.36 | 18.32 | 13.55 | 12.97 | 12.75
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-5A | 20.34 | 20.27 | 20.28 | 20.35 | 20.46 | 22.79 | 23.2 | 23.3 | 23.33 | 21.05 | 20.69 | 20.5
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-5A | 20.25 | 20.17 | 20.19 | 20.28 | 20.41 | 22.7 | 23.15 | 23.26 | 23.29 | 21.04 | 20.65 | 20.43
Hospital | 90.1-2013 | ASHRAE 169-2006-5A
LargeHotel | 90.1-2013 | ASHRAE 169-2006-5A | 20.54 | 20.52 | 20.55 | 20.63 | 20.72 | 23.01 | 23.37 | 23.43 | 23.44 | 21.14 | 20.8 | 20.64
LargeOffice | 90.1-2013 | ASHRAE 169-2006-5A
MediumOffice | 90.1-2013 | ASHRAE 169-2006-5A | 20.49 | 20.43 | 20.44 | 20.5 | 20.59 | 22.83 | 23.24 | 23.33 | 23.36 | 21.14 | 20.78 | 20.61
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-5A | 20.25 | 20.17 | 20.19 | 20.28 | 20.41 | 22.7 | 23.15 | 23.26 | 23.29 | 21.04 | 20.65 | 20.43
Outpatient | 90.1-2013 | ASHRAE 169-2006-5A | 20.31 | 20.26 | 20.28 | 20.36 | 20.48 | 21.47 | 21.71 | 21.77 | 21.78 | 20.84 | 20.62 | 20.45
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-5A | 20.65 | 20.6 | 20.6 | 20.64 | 20.69 | 22.96 | 23.32 | 23.4 | 23.43 | 21.17 | 20.87 | 20.74
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-5A | 20.07 | 19.98 | 19.99 | 20.11 | 20.26 | 22.65 | 23.1 | 23.22 | 23.25 | 20.94 | 20.55 | 20.28
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-5A | 20.66 | 20.62 | 20.62 | 20.65 | 20.7 | 22.97 | 23.33 | 23.41 | 23.44 | 21.17 | 20.88 | 20.75
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-5A | 20.74 | 20.71 | 20.7 | 20.72 | 20.76 | 23.01 | 23.36 | 23.43 | 23.47 | 21.21 | 20.92 | 20.82
SmallHotel | 90.1-2013 | ASHRAE 169-2006-5A | 20.23 | 20.17 | 20.2 | 20.3 | 20.43 | 20.59 | 20.71 | 20.75 | 20.75 | 20.65 | 20.54 | 20.37
SmallOffice | 90.1-2013 | ASHRAE 169-2006-5A | 19.91 | 19.78 | 19.78 | 19.91 | 20.1 | 22.25 | 22.88 | 23.07 | 23.13 | 21.08 | 20.53 | 20.19
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-5A | 20.57 | 20.52 | 20.52 | 20.57 | 20.63 | 22.92 | 23.29 | 23.38 | 23.41 | 21.14 | 20.82 | 20.68
Warehouse | 90.1-2013 | ASHRAE 169-2006-5A | 12.61 | 12.57 | 12.58 | 12.65 | 14.73 | 19.66 | 22.3 | 21.36 | 18.32 | 13.55 | 12.97 | 12.75
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 10.34 | 10.19 | 11.31 | 13.07 | 16.39 | 19.3 | 22.1 | 24.2 | 21.69 | 17.32 | 14.23 | 11.34
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 10.34 | 10.19 | 11.31 | 13.07 | 16.39 | 19.3 | 22.1 | 24.2 | 21.69 | 17.32 | 14.23 | 11.34
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-5B | 19.85 | 19.95 | 20.01 | 20.17 | 20.39 | 22.75 | 23.29 | 23.36 | 23.24 | 20.84 | 20.31 | 19.98
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-5B | 19.84 | 19.94 | 20 | 20.15 | 20.37 | 22.67 | 23.25 | 23.33 | 23.2 | 20.87 | 20.3 | 19.98
Hospital | 90.1-2004 | ASHRAE 169-2006-5B
LargeHotel | 90.1-2004 | ASHRAE 169-2006-5B | 20.57 | 20.59 | 20.61 | 20.66 | 20.73 | 22.99 | 23.39 | 23.46 | 23.43 | 21.14 | 20.79 | 20.64
LargeOffice | 90.1-2004 | ASHRAE 169-2006-5B
MediumOffice | 90.1-2004 | ASHRAE 169-2006-5B | 20.26 | 20.31 | 20.34 | 20.44 | 20.57 | 22.81 | 23.3 | 23.38 | 23.32 | 21.04 | 20.58 | 20.36
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-5B | 19.84 | 19.94 | 20 | 20.15 | 20.37 | 22.67 | 23.25 | 23.33 | 23.2 | 20.87 | 20.3 | 19.98
Outpatient | 90.1-2004 | ASHRAE 169-2006-5B | 20 | 20.09 | 20.14 | 20.27 | 20.45 | 21.46 | 21.81 | 21.85 | 21.74 | 20.71 | 20.35 | 20.11
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-5B | 20.4 | 20.44 | 20.47 | 20.54 | 20.65 | 22.94 | 23.37 | 23.43 | 23.39 | 21.07 | 20.67 | 20.49
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-5B | 19.33 | 19.49 | 19.59 | 19.83 | 20.16 | 22.58 | 23.24 | 23.31 | 23.11 | 20.64 | 19.97 | 19.51
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-5B | 20.43 | 20.47 | 20.49 | 20.56 | 20.67 | 22.95 | 23.37 | 23.44 | 23.4 | 21.08 | 20.69 | 20.51
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-5B | 20.57 | 20.59 | 20.61 | 20.66 | 20.73 | 22.99 | 23.39 | 23.46 | 23.43 | 21.14 | 20.79 | 20.64
SmallHotel | 90.1-2004 | ASHRAE 169-2006-5B | 19.89 | 19.99 | 20.06 | 20.2 | 20.41 | 20.6 | 20.83 | 20.85 | 20.72 | 20.51 | 20.24 | 19.99
SmallOffice | 90.1-2004 | ASHRAE 169-2006-5B | 19.37 | 19.45 | 19.53 | 19.74 | 20.05 | 22.22 | 23 | 23.17 | 23.04 | 20.86 | 20.09 | 19.61
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-5B | 20.27 | 20.33 | 20.36 | 20.45 | 20.59 | 22.89 | 23.35 | 23.42 | 23.35 | 21.01 | 20.59 | 20.37
Warehouse | 90.1-2004 | ASHRAE 169-2006-5B | 12.62 | 12.63 | 12.64 | 12.68 | 14.11 | 17.43 | 22.96 | 20.8 | 17.41 | 13.44 | 12.92 | 12.72
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-5B | 19.85 | 19.95 | 20.01 | 20.17 | 20.39 | 22.75 | 23.29 | 23.36 | 23.24 | 20.84 | 20.31 | 19.98
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-5B | 20.17 | 20.2 | 20.22 | 20.3 | 20.43 | 22.69 | 23.19 | 23.31 | 23.27 | 21.02 | 20.55 | 20.32
Hospital | 90.1-2007 | ASHRAE 169-2006-5B
LargeHotel | 90.1-2007 | ASHRAE 169-2006-5B | 20.57 | 20.59 | 20.61 | 20.66 | 20.73 | 22.99 | 23.39 | 23.46 | 23.43 | 21.14 | 20.79 | 20.64
LargeOffice | 90.1-2007 | ASHRAE 169-2006-5B
MediumOffice | 90.1-2007 | ASHRAE 169-2006-5B | 20.26 | 20.31 | 20.34 | 20.44 | 20.57 | 22.81 | 23.3 | 23.38 | 23.32 | 21.04 | 20.58 | 20.36
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-5B | 20.17 | 20.2 | 20.22 | 20.3 | 20.43 | 22.69 | 23.19 | 23.31 | 23.27 | 21.02 | 20.55 | 20.32
Outpatient | 90.1-2007 | ASHRAE 169-2006-5B | 20 | 20.09 | 20.14 | 20.27 | 20.45 | 21.46 | 21.81 | 21.85 | 21.74 | 20.71 | 20.35 | 20.11
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-5B | 20.4 | 20.44 | 20.47 | 20.54 | 20.65 | 22.94 | 23.37 | 23.43 | 23.39 | 21.07 | 20.67 | 20.49
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-5B | 19.33 | 19.49 | 19.59 | 19.83 | 20.16 | 22.58 | 23.24 | 23.31 | 23.11 | 20.64 | 19.97 | 19.51
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-5B | 20.43 | 20.47 | 20.49 | 20.56 | 20.67 | 22.95 | 23.37 | 23.44 | 23.4 | 21.08 | 20.69 | 20.51
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-5B | 20.57 | 20.59 | 20.61 | 20.66 | 20.73 | 22.99 | 23.39 | 23.46 | 23.43 | 21.14 | 20.79 | 20.64
SmallHotel | 90.1-2007 | ASHRAE 169-2006-5B | 19.89 | 19.99 | 20.06 | 20.2 | 20.41 | 20.6 | 20.83 | 20.85 | 20.72 | 20.51 | 20.24 | 19.99
SmallOffice | 90.1-2007 | ASHRAE 169-2006-5B | 19.37 | 19.45 | 19.53 | 19.74 | 20.05 | 22.22 | 23 | 23.17 | 23.04 | 20.86 | 20.09 | 19.61
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-5B | 20.27 | 20.33 | 20.36 | 20.45 | 20.59 | 22.89 | 23.35 | 23.42 | 23.35 | 21.01 | 20.59 | 20.37
Warehouse | 90.1-2007 | ASHRAE 169-2006-5B | 12.62 | 12.63 | 12.64 | 12.68 | 14.11 | 17.43 | 22.96 | 20.8 | 17.41 | 13.44 | 12.92 | 12.72
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-5B | 19.85 | 19.95 | 20.01 | 20.17 | 20.39 | 22.75 | 23.29 | 23.36 | 23.24 | 20.84 | 20.31 | 19.98
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-5B | 20.17 | 20.2 | 20.22 | 20.3 | 20.43 | 22.69 | 23.19 | 23.31 | 23.27 | 21.02 | 20.55 | 20.32
Hospital | 90.1-2010 | ASHRAE 169-2006-5B
LargeHotel | 90.1-2010 | ASHRAE 169-2006-5B | 20.57 | 20.59 | 20.61 | 20.66 | 20.73 | 22.99 | 23.39 | 23.46 | 23.43 | 21.14 | 20.79 | 20.64
LargeOffice | 90.1-2010 | ASHRAE 169-2006-5B
MediumOffice | 90.1-2010 | ASHRAE 169-2006-5B | 20.26 | 20.31 | 20.34 | 20.44 | 20.57 | 22.81 | 23.3 | 23.38 | 23.32 | 21.04 | 20.58 | 20.36
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-5B | 20.17 | 20.2 | 20.22 | 20.3 | 20.43 | 22.69 | 23.19 | 23.31 | 23.27 | 21.02 | 20.55 | 20.32
Outpatient | 90.1-2010 | ASHRAE 169-2006-5B | 20 | 20.09 | 20.14 | 20.27 | 20.45 | 21.46 | 21.81 | 21.85 | 21.74 | 20.71 | 20.35 | 20.11
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-5B | 20.4 | 20.44 | 20.47 | 20.54 | 20.65 | 22.94 | 23.37 | 23.43 | 23.39 | 21.07 | 20.67 | 20.49
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-5B | 19.33 | 19.49 | 19.59 | 19.83 | 20.16 | 22.58 | 23.24 | 23.31 | 23.11 | 20.64 | 19.97 | 19.51
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-5B | 20.43 | 20.47 | 20.49 | 20.56 | 20.67 | 22.95 | 23.37 | 23.44 | 23.4 | 21.08 | 20.69 | 20.51
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-5B | 20.57 | 20.59 | 20.61 | 20.66 | 20.73 | 22.99 | 23.39 | 23.46 | 23.43 | 21.14 | 20.79 | 20.64
SmallHotel | 90.1-2010 | ASHRAE 169-2006-5B | 19.89 | 19.99 | 20.06 | 20.2 | 20.41 | 20.6 | 20.83 | 20.85 | 20.72 | 20.51 | 20.24 | 19.99
SmallOffice | 90.1-2010 | ASHRAE 169-2006-5B | 19.37 | 19.45 | 19.53 | 19.74 | 20.05 | 22.22 | 23 | 23.17 | 23.04 | 20.86 | 20.09 | 19.61
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-5B | 20.27 | 20.33 | 20.36 | 20.45 | 20.59 | 22.89 | 23.35 | 23.42 | 23.35 | 21.01 | 20.59 | 20.37
Warehouse | 90.1-2010 | ASHRAE 169-2006-5B | 12.62 | 12.63 | 12.64 | 12.68 | 14.11 | 17.43 | 22.96 | 20.8 | 17.41 | 13.44 | 12.92 | 12.72
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-5B | 20.36 | 20.35 | 20.36 | 20.41 | 20.5 | 22.8 | 23.23 | 23.34 | 23.34 | 21.06 | 20.67 | 20.49
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-5B | 20.27 | 20.27 | 20.29 | 20.35 | 20.45 | 22.7 | 23.17 | 23.31 | 23.29 | 21.06 | 20.62 | 20.42
Hospital | 90.1-2013 | ASHRAE 169-2006-5B
LargeHotel | 90.1-2013 | ASHRAE 169-2006-5B | 20.57 | 20.59 | 20.61 | 20.66 | 20.73 | 22.99 | 23.39 | 23.46 | 23.43 | 21.14 | 20.79 | 20.64
LargeOffice | 90.1-2013 | ASHRAE 169-2006-5B
MediumOffice | 90.1-2013 | ASHRAE 169-2006-5B | 20.5 | 20.5 | 20.51 | 20.55 | 20.62 | 22.83 | 23.26 | 23.37 | 23.37 | 21.14 | 20.76 | 20.61
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-5B | 20.27 | 20.27 | 20.29 | 20.35 | 20.45 | 22.7 | 23.17 | 23.31 | 23.29 | 21.06 | 20.62 | 20.42
Outpatient | 90.1-2013 | ASHRAE 169-2006-5B | 20.33 | 20.34 | 20.36 | 20.42 | 20.51 | 21.47 | 21.73 | 21.81 | 21.79 | 20.86 | 20.6 | 20.44
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-5B | 20.66 | 20.64 | 20.64 | 20.67 | 20.71 | 22.96 | 23.33 | 23.42 | 23.44 | 21.17 | 20.86 | 20.74
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-5B | 20.09 | 20.09 | 20.11 | 20.19 | 20.32 | 22.66 | 23.14 | 23.28 | 23.26 | 20.96 | 20.51 | 20.27
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-5B | 20.67 | 20.66 | 20.66 | 20.68 | 20.72 | 22.97 | 23.34 | 23.43 | 23.44 | 21.18 | 20.87 | 20.75
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-5B | 20.75 | 20.74 | 20.73 | 20.74 | 20.77 | 23.01 | 23.37 | 23.45 | 23.47 | 21.21 | 20.91 | 20.82
SmallHotel | 90.1-2013 | ASHRAE 169-2006-5B | 20.25 | 20.27 | 20.3 | 20.37 | 20.47 | 20.6 | 20.74 | 20.8 | 20.76 | 20.67 | 20.51 | 20.36
SmallOffice | 90.1-2013 | ASHRAE 169-2006-5B | 19.93 | 19.9 | 19.92 | 20.02 | 20.17 | 22.27 | 22.91 | 23.13 | 23.14 | 21.09 | 20.49 | 20.17
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-5B | 20.58 | 20.57 | 20.58 | 20.6 | 20.66 | 22.92 | 23.31 | 23.4 | 23.41 | 21.14 | 20.81 | 20.68
Warehouse | 90.1-2013 | ASHRAE 169-2006-5B | 12.62 | 12.63 | 12.64 | 12.68 | 14.11 | 17.43 | 22.96 | 20.8 | 17.41 | 13.44 | 12.92 | 12.72
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 10.3 | 10.16 | 11.26 | 12.98 | 16.26 | 19.12 | 21.83 | 23.96 | 21.38 | 17.16 | 14.1 | 11.24
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 10.3 | 10.16 | 11.26 | 12.98 | 16.26 | 19.12 | 21.83 | 23.96 | 21.38 | 17.16 | 14.1 | 11.24
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-5C | 19.98 | 20.01 | 20.03 | 20.16 | 20.32 | 22.62 | 23.03 | 23.11 | 23.06 | 20.7 | 20.26 | 20.06
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-5C | 19.97 | 20 | 20.02 | 20.14 | 20.31 | 22.54 | 22.98 | 23.08 | 23.03 | 20.72 | 20.26 | 20.05
Hospital | 90.1-2004 | ASHRAE 169-2006-5C
LargeHotel | 90.1-2004 | ASHRAE 169-2006-5C | 20.62 | 20.61 | 20.61 | 20.65 | 20.71 | 22.95 | 23.29 | 23.37 | 23.37 | 21.08 | 20.77 | 20.66
LargeOffice | 90.1-2004 | ASHRAE 169-2006-5C
MediumOffice | 90.1-2004 | ASHRAE 169-2006-5C | 20.34 | 20.35 | 20.36 | 20.43 | 20.53 | 22.73 | 23.14 | 23.22 | 23.21 | 20.95 | 20.55 | 20.4
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-5C | 19.97 | 20 | 20.02 | 20.14 | 20.31 | 22.54 | 22.98 | 23.08 | 23.03 | 20.72 | 20.26 | 20.05
Outpatient | 90.1-2004 | ASHRAE 169-2006-5C | 20.11 | 20.14 | 20.16 | 20.26 | 20.4 | 21.36 | 21.59 | 21.65 | 21.59 | 20.59 | 20.32 | 20.16
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-5C | 20.47 | 20.47 | 20.48 | 20.54 | 20.62 | 22.87 | 23.23 | 23.31 | 23.3 | 20.99 | 20.65 | 20.52
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-5C | 19.52 | 19.58 | 19.62 | 19.81 | 20.06 | 22.39 | 22.85 | 22.94 | 22.84 | 20.43 | 19.9 | 19.63
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-5C | 20.49 | 20.5 | 20.5 | 20.56 | 20.63 | 22.88 | 23.24 | 23.32 | 23.31 | 21.01 | 20.67 | 20.55
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-5C | 20.62 | 20.61 | 20.61 | 20.65 | 20.71 | 22.95 | 23.29 | 23.37 | 23.37 | 21.08 | 20.77 | 20.66
SmallHotel | 90.1-2004 | ASHRAE 169-2006-5C | 20.01 | 20.05 | 20.08 | 20.19 | 20.35 | 20.49 | 20.6 | 20.63 | 20.56 | 20.38 | 20.2 | 20.06
SmallOffice | 90.1-2004 | ASHRAE 169-2006-5C | 19.55 | 19.56 | 19.59 | 19.75 | 19.98 | 22.06 | 22.66 | 22.82 | 22.78 | 20.65 | 20.02 | 19.69
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-5C | 20.35 | 20.36 | 20.37 | 20.45 | 20.55 | 22.81 | 23.18 | 23.26 | 23.24 | 20.92 | 20.56 | 20.41
Warehouse | 90.1-2004 | ASHRAE 169-2006-5C | 12.59 | 12.59 | 12.6 | 12.64 | 12.69 | 14.57 | 16.37 | 16.72 | 14.09 | 12.92 | 12.73 | 12.64
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-5C | 19.98 | 20.01 | 20.03 | 20.16 | 20.32 | 22.62 | 23.03 | 23.11 | 23.06 | 20.7 | 20.26 | 20.06
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-5C | 20.25 | 20.24 | 20.24 | 20.3 | 20.4 | 22.62 | 23.03 | 23.13 | 23.14 | 20.9 | 20.5 | 20.33
Hospital | 90.1-2007 | ASHRAE 169-2006-5C
LargeHotel | 90.1-2007 | ASHRAE 169-2006-5C | 20.62 | 20.61 | 20.61 | 20.65 | 20.71 | 22.95 | 23.29 | 23.37 | 23.37 | 21.08 | 20.77 | 20.66
LargeOffice | 90.1-2007 | ASHRAE 169-2006-5C
MediumOffice | 90.1-2007 | ASHRAE 169-2006-5C | 20.34 | 20.35 | 20.36 | 20.43 | 20.53 | 22.73 | 23.14 | 23.22 | 23.21 | 20.95 | 20.55 | 20.4
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-5C | 20.25 | 20.24 | 20.24 | 20.3 | 20.4 | 22.62 | 23.03 | 23.13 | 23.14 | 20.9 | 20.5 | 20.33
Outpatient | 90.1-2007 | ASHRAE 169-2006-5C | 20.11 | 20.14 | 20.16 | 20.26 | 20.4 | 21.36 | 21.59 | 21.65 | 21.59 | 20.59 | 20.32 | 20.16
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-5C | 20.47 | 20.47 | 20.48 | 20.54 | 20.62 | 22.87 | 23.23 | 23.31 | 23.3 | 20.99 | 20.65 | 20.52
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-5C | 19.52 | 19.58 | 19.62 | 19.81 | 20.06 | 22.39 | 22.85 | 22.94 | 22.84 | 20.43 | 19.9 | 19.63
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-5C | 20.49 | 20.5 | 20.5 | 20.56 | 20.63 | 22.88 | 23.24 | 23.32 | 23.31 | 21.01 | 20.67 | 20.55
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-5C | 20.62 | 20.61 | 20.61 | 20.65 | 20.71 | 22.95 | 23.29 | 23.37 | 23.37 | 21.08 | 20.77 | 20.66
SmallHotel | 90.1-2007 | ASHRAE 169-2006-5C | 20.01 | 20.05 | 20.08 | 20.19 | 20.35 | 20.49 | 20.6 | 20.63 | 20.56 | 20.38 | 20.2 | 20.06
SmallOffice | 90.1-2007 | ASHRAE 169-2006-5C | 19.55 | 19.56 | 19.59 | 19.75 | 19.98 | 22.06 | 22.66 | 22.82 | 22.78 | 20.65 | 20.02 | 19.69
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-5C | 20.35 | 20.36 | 20.37 | 20.45 | 20.55 | 22.81 | 23.18 | 23.26 | 23.24 | 20.92 | 20.56 | 20.41
Warehouse | 90.1-2007 | ASHRAE 169-2006-5C | 12.59 | 12.59 | 12.6 | 12.64 | 12.69 | 14.57 | 16.37 | 16.72 | 14.09 | 12.92 | 12.73 | 12.64
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-5C | 19.98 | 20.01 | 20.03 | 20.16 | 20.32 | 22.62 | 23.03 | 23.11 | 23.06 | 20.7 | 20.26 | 20.06
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-5C | 20.25 | 20.24 | 20.24 | 20.3 | 20.4 | 22.62 | 23.03 | 23.13 | 23.14 | 20.9 | 20.5 | 20.33
Hospital | 90.1-2010 | ASHRAE 169-2006-5C
LargeHotel | 90.1-2010 | ASHRAE 169-2006-5C | 20.62 | 20.61 | 20.61 | 20.65 | 20.71 | 22.95 | 23.29 | 23.37 | 23.37 | 21.08 | 20.77 | 20.66
LargeOffice | 90.1-2010 | ASHRAE 169-2006-5C
MediumOffice | 90.1-2010 | ASHRAE 169-2006-5C | 20.34 | 20.35 | 20.36 | 20.43 | 20.53 | 22.73 | 23.14 | 23.22 | 23.21 | 20.95 | 20.55 | 20.4
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-5C | 20.25 | 20.24 | 20.24 | 20.3 | 20.4 | 22.62 | 23.03 | 23.13 | 23.14 | 20.9 | 20.5 | 20.33
Outpatient | 90.1-2010 | ASHRAE 169-2006-5C | 20.11 | 20.14 | 20.16 | 20.26 | 20.4 | 21.36 | 21.59 | 21.65 | 21.59 | 20.59 | 20.32 | 20.16
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-5C | 20.47 | 20.47 | 20.48 | 20.54 | 20.62 | 22.87 | 23.23 | 23.31 | 23.3 | 20.99 | 20.65 | 20.52
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-5C | 19.52 | 19.58 | 19.62 | 19.81 | 20.06 | 22.39 | 22.85 | 22.94 | 22.84 | 20.43 | 19.9 | 19.63
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-5C | 20.49 | 20.5 | 20.5 | 20.56 | 20.63 | 22.88 | 23.24 | 23.32 | 23.31 | 21.01 | 20.67 | 20.55
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-5C | 20.62 | 20.61 | 20.61 | 20.65 | 20.71 | 22.95 | 23.29 | 23.37 | 23.37 | 21.08 | 20.77 | 20.66
SmallHotel | 90.1-2010 | ASHRAE 169-2006-5C | 20.01 | 20.05 | 20.08 | 20.19 | 20.35 | 20.49 | 20.6 | 20.63 | 20.56 | 20.38 | 20.2 | 20.06
SmallOffice | 90.1-2010 | ASHRAE 169-2006-5C | 19.55 | 19.56 | 19.59 | 19.75 | 19.98 | 22.06 | 22.66 | 22.82 | 22.78 | 20.65 | 20.02 | 19.69
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-5C | 20.35 | 20.36 | 20.37 | 20.45 | 20.55 | 22.81 | 23.18 | 23.26 | 23.24 | 20.92 | 20.56 | 20.41
Warehouse | 90.1-2010 | ASHRAE 169-2006-5C | 12.59 | 12.59 | 12.6 | 12.64 | 12.69 | 14.57 | 16.37 | 16.72 | 14.09 | 12.92 | 12.73 | 12.64
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-5C | 20.4 | 20.38 | 20.37 | 20.41 | 20.48 | 22.74 | 23.11 | 23.21 | 23.23 | 20.95 | 20.62 | 20.48
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-5C | 20.32 | 20.31 | 20.3 | 20.35 | 20.43 | 22.64 | 23.05 | 23.15 | 23.17 | 20.94 | 20.57 | 20.41
Hospital | 90.1-2013 | ASHRAE 169-2006-5C
LargeHotel | 90.1-2013 | ASHRAE 169-2006-5C | 20.62 | 20.61 | 20.61 | 20.65 | 20.71 | 22.95 | 23.29 | 23.37 | 23.37 | 21.08 | 20.77 | 20.66
LargeOffice | 90.1-2013 | ASHRAE 169-2006-5C
MediumOffice | 90.1-2013 | ASHRAE 169-2006-5C | 20.54 | 20.52 | 20.52 | 20.55 | 20.6 | 22.79 | 23.17 | 23.26 | 23.29 | 21.07 | 20.73 | 20.61
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-5C | 20.32 | 20.31 | 20.3 | 20.35 | 20.43 | 22.64 | 23.05 | 23.15 | 23.17 | 20.94 | 20.57 | 20.41
Outpatient | 90.1-2013 | ASHRAE 169-2006-5C | 20.38 | 20.37 | 20.37 | 20.42 | 20.49 | 21.42 | 21.62 | 21.68 | 21.69 | 20.76 | 20.55 | 20.44
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-5C | 20.68 | 20.66 | 20.65 | 20.66 | 20.7 | 22.93 | 23.27 | 23.35 | 23.38 | 21.12 | 20.83 | 20.73
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-5C | 20.15 | 20.13 | 20.13 | 20.19 | 20.29 | 22.58 | 22.98 | 23.09 | 23.1 | 20.81 | 20.43 | 20.26
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-5C | 20.69 | 20.67 | 20.66 | 20.68 | 20.71 | 22.94 | 23.28 | 23.36 | 23.39 | 21.13 | 20.84 | 20.75
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-5C | 20.76 | 20.74 | 20.73 | 20.74 | 20.77 | 22.99 | 23.33 | 23.4 | 23.43 | 21.17 | 20.89 | 20.81
SmallHotel | 90.1-2013 | ASHRAE 169-2006-5C | 20.3 | 20.3 | 20.31 | 20.37 | 20.45 | 20.54 | 20.61 | 20.66 | 20.64 | 20.56 | 20.46 | 20.35
SmallOffice | 90.1-2013 | ASHRAE 169-2006-5C | 20.01 | 19.97 | 19.96 | 20.04 | 20.16 | 22.19 | 22.75 | 22.92 | 22.96 | 20.93 | 20.41 | 20.16
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-5C | 20.61 | 20.59 | 20.58 | 20.6 | 20.65 | 22.89 | 23.23 | 23.32 | 23.34 | 21.08 | 20.77 | 20.67
Warehouse | 90.1-2013 | ASHRAE 169-2006-5C | 12.59 | 12.59 | 12.6 | 12.64 | 12.69 | 14.57 | 16.37 | 16.72 | 14.09 | 12.92 | 12.73 | 12.64
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-6A | 19.63 | 19.54 | 19.62 | 19.9 | 20.28 | 22.6 | 23.09 | 23.18 | 23.08 | 20.74 | 20.21 | 19.86
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-6A | 19.63 | 19.54 | 19.61 | 19.88 | 20.26 | 22.52 | 23.04 | 23.14 | 23.04 | 20.76 | 20.21 | 19.86
Hospital | 90.1-2004 | ASHRAE 169-2006-6A
LargeHotel | 90.1-2004 | ASHRAE 169-2006-6A | 20.67 | 20.63 | 20.62 | 20.66 | 20.72 | 22.97 | 23.32 | 23.4 | 23.42 | 21.16 | 20.87 | 20.75
LargeOffice | 90.1-2004 | ASHRAE 169-2006-6A
MediumOffice | 90.1-2004 | ASHRAE 169-2006-6A | 20.12 | 20.06 | 20.1 | 20.27 | 20.5 | 22.72 | 23.17 | 23.26 | 23.22 | 20.97 | 20.52 | 20.28
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-6A | 19.63 | 19.54 | 19.61 | 19.88 | 20.26 | 22.52 | 23.04 | 23.14 | 23.04 | 20.76 | 20.21 | 19.86
Outpatient | 90.1-2004 | ASHRAE 169-2006-6A | 19.82 | 19.76 | 19.82 | 20.04 | 20.36 | 21.34 | 21.64 | 21.7 | 21.61 | 20.62 | 20.28 | 20
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-6A | 20.29 | 20.24 | 20.27 | 20.4 | 20.59 | 22.86 | 23.26 | 23.34 | 23.31 | 21.01 | 20.63 | 20.42
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-6A | 19.02 | 18.9 | 19.02 | 19.44 | 20 | 22.37 | 22.94 | 23.05 | 22.88 | 20.48 | 19.84 | 19.34
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-6A | 20.33 | 20.27 | 20.3 | 20.43 | 20.61 | 22.87 | 23.27 | 23.35 | 23.32 | 21.03 | 20.65 | 20.45
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-6A | 20.49 | 20.45 | 20.47 | 20.56 | 20.69 | 22.94 | 23.31 | 23.39 | 23.38 | 21.1 | 20.75 | 20.59
SmallHotel | 90.1-2004 | ASHRAE 169-2006-6A | 19.7 | 19.63 | 19.7 | 19.96 | 20.3 | 20.47 | 20.65 | 20.69 | 20.58 | 20.41 | 20.16 | 19.88
SmallOffice | 90.1-2004 | ASHRAE 169-2006-6A | 19.1 | 18.94 | 18.99 | 19.35 | 19.86 | 22.01 | 22.73 | 22.93 | 22.83 | 20.71 | 19.98 | 19.46
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-6A | 20.13 | 20.07 | 20.11 | 20.28 | 20.52 | 22.79 | 23.22 | 23.3 | 23.25 | 20.94 | 20.53 | 20.29
Warehouse | 90.1-2004 | ASHRAE 169-2006-6A | 12.51 | 12.46 | 12.47 | 12.56 | 14.45 | 16.87 | 19.89 | 19.39 | 15.2 | 13.13 | 12.81 | 12.63
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-6A | 20.16 | 20.06 | 20.06 | 20.18 | 20.37 | 22.67 | 23.1 | 23.21 | 23.21 | 20.93 | 20.55 | 20.33
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-6A | 20.1 | 20.01 | 19.99 | 20.12 | 20.33 | 22.57 | 23.04 | 23.17 | 23.17 | 20.94 | 20.53 | 20.29
Hospital | 90.1-2007 | ASHRAE 169-2006-6A
LargeHotel | 90.1-2007 | ASHRAE 169-2006-6A | 20.67 | 20.63 | 20.62 | 20.66 | 20.72 | 22.97 | 23.32 | 23.4 | 23.42 | 21.16 | 20.87 | 20.75
LargeOffice | 90.1-2007 | ASHRAE 169-2006-6A
MediumOffice | 90.1-2007 | ASHRAE 169-2006-6A | 20.38 | 20.31 | 20.3 | 20.39 | 20.53 | 22.75 | 23.17 | 23.27 | 23.28 | 21.07 | 20.69 | 20.51
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-6A | 20.1 | 20.01 | 19.99 | 20.12 | 20.33 | 22.57 | 23.04 | 23.17 | 23.17 | 20.94 | 20.53 | 20.29
Outpatient | 90.1-2007 | ASHRAE 169-2006-6A | 20.17 | 20.09 | 20.1 | 20.22 | 20.41 | 21.36 | 21.62 | 21.7 | 21.68 | 20.75 | 20.5 | 20.31
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-6A | 20.55 | 20.49 | 20.49 | 20.54 | 20.64 | 22.9 | 23.26 | 23.35 | 23.37 | 21.11 | 20.79 | 20.65
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-6A | 19.81 | 19.68 | 19.68 | 19.86 | 20.14 | 22.48 | 22.95 | 23.09 | 23.08 | 20.78 | 20.34 | 20.04
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-6A | 20.57 | 20.52 | 20.51 | 20.56 | 20.66 | 22.91 | 23.27 | 23.36 | 23.38 | 21.12 | 20.8 | 20.67
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-6A | 20.67 | 20.63 | 20.62 | 20.66 | 20.72 | 22.97 | 23.32 | 23.4 | 23.42 | 21.16 | 20.87 | 20.75
SmallHotel | 90.1-2007 | ASHRAE 169-2006-6A | 20.07 | 19.99 | 20 | 20.14 | 20.35 | 20.48 | 20.61 | 20.68 | 20.64 | 20.55 | 20.4 | 20.22
SmallOffice | 90.1-2007 | ASHRAE 169-2006-6A | 19.67 | 19.51 | 19.48 | 19.66 | 19.96 | 22.08 | 22.73 | 22.95 | 22.96 | 20.93 | 20.34 | 19.97
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-6A | 20.45 | 20.39 | 20.38 | 20.45 | 20.57 | 22.84 | 23.22 | 23.32 | 23.33 | 21.07 | 20.73 | 20.57
Warehouse | 90.1-2007 | ASHRAE 169-2006-6A | 12.51 | 12.46 | 12.47 | 12.56 | 14.45 | 16.87 | 19.89 | 19.39 | 15.2 | 13.13 | 12.81 | 12.63
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-6A | 20.16 | 20.06 | 20.06 | 20.18 | 20.37 | 22.67 | 23.1 | 23.21 | 23.21 | 20.93 | 20.55 | 20.33
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-6A | 20.1 | 20.01 | 19.99 | 20.12 | 20.33 | 22.57 | 23.04 | 23.17 | 23.17 | 20.94 | 20.53 | 20.29
Hospital | 90.1-2010 | ASHRAE 169-2006-6A
LargeHotel | 90.1-2010 | ASHRAE 169-2006-6A | 20.67 | 20.63 | 20.62 | 20.66 | 20.72 | 22.97 | 23.32 | 23.4 | 23.42 | 21.16 | 20.87 | 20.75
LargeOffice | 90.1-2010 | ASHRAE 169-2006-6A
MediumOffice | 90.1-2010 | ASHRAE 169-2006-6A | 20.38 | 20.31 | 20.3 | 20.39 | 20.53 | 22.75 | 23.17 | 23.27 | 23.28 | 21.07 | 20.69 | 20.51
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-6A | 20.1 | 20.01 | 19.99 | 20.12 | 20.33 | 22.57 | 23.04 | 23.17 | 23.17 | 20.94 | 20.53 | 20.29
Outpatient | 90.1-2010 | ASHRAE 169-2006-6A | 20.17 | 20.09 | 20.1 | 20.22 | 20.41 | 21.36 | 21.62 | 21.7 | 21.68 | 20.75 | 20.5 | 20.31
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-6A | 20.55 | 20.49 | 20.49 | 20.54 | 20.64 | 22.9 | 23.26 | 23.35 | 23.37 | 21.11 | 20.79 | 20.65
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-6A | 19.81 | 19.68 | 19.68 | 19.86 | 20.14 | 22.48 | 22.95 | 23.09 | 23.08 | 20.78 | 20.34 | 20.04
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-6A | 20.57 | 20.52 | 20.51 | 20.56 | 20.66 | 22.91 | 23.27 | 23.36 | 23.38 | 21.12 | 20.8 | 20.67
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-6A | 20.67 | 20.63 | 20.62 | 20.66 | 20.72 | 22.97 | 23.32 | 23.4 | 23.42 | 21.16 | 20.87 | 20.75
SmallHotel | 90.1-2010 | ASHRAE 169-2006-6A | 20.07 | 19.99 | 20 | 20.14 | 20.35 | 20.48 | 20.61 | 20.68 | 20.64 | 20.55 | 20.4 | 20.22
SmallOffice | 90.1-2010 | ASHRAE 169-2006-6A | 19.67 | 19.51 | 19.48 | 19.66 | 19.96 | 22.08 | 22.73 | 22.95 | 22.96 | 20.93 | 20.34 | 19.97
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-6A | 20.45 | 20.39 | 20.38 | 20.45 | 20.57 | 22.84 | 23.22 | 23.32 | 23.33 | 21.07 | 20.73 | 20.57
Warehouse | 90.1-2010 | ASHRAE 169-2006-6A | 12.51 | 12.46 | 12.47 | 12.56 | 14.45 | 16.87 | 19.89 | 19.39 | 15.2 | 13.13 | 12.81 | 12.63
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-6A | 20.3 | 20.21 | 20.18 | 20.26 | 20.4 | 22.69 | 23.1 | 23.22 | 23.24 | 20.99 | 20.64 | 20.45
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-6A | 20.28 | 20.19 | 20.16 | 20.24 | 20.38 | 22.61 | 23.05 | 23.18 | 23.2 | 21 | 20.63 | 20.43
Hospital | 90.1-2013 | ASHRAE 169-2006-6A
LargeHotel | 90.1-2013 | ASHRAE 169-2006-6A | 20.67 | 20.63 | 20.62 | 20.66 | 20.72 | 22.97 | 23.32 | 23.4 | 23.42 | 21.16 | 20.87 | 20.75
LargeOffice | 90.1-2013 | ASHRAE 169-2006-6A
MediumOffice | 90.1-2013 | ASHRAE 169-2006-6A | 20.45 | 20.38 | 20.36 | 20.43 | 20.54 | 22.76 | 23.17 | 23.28 | 23.3 | 21.09 | 20.74 | 20.57
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-6A | 20.28 | 20.19 | 20.16 | 20.24 | 20.38 | 22.61 | 23.05 | 23.18 | 23.2 | 21 | 20.63 | 20.43
Outpatient | 90.1-2013 | ASHRAE 169-2006-6A | 20.26 | 20.19 | 20.17 | 20.27 | 20.42 | 21.37 | 21.61 | 21.7 | 21.7 | 20.79 | 20.56 | 20.4
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-6A | 20.63 | 20.57 | 20.55 | 20.59 | 20.66 | 22.91 | 23.27 | 23.36 | 23.39 | 21.14 | 20.84 | 20.72
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-6A | 20.02 | 19.89 | 19.86 | 19.97 | 20.18 | 22.51 | 22.96 | 23.11 | 23.13 | 20.86 | 20.47 | 20.22
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-6A | 20.64 | 20.59 | 20.57 | 20.6 | 20.67 | 22.92 | 23.28 | 23.37 | 23.4 | 21.15 | 20.85 | 20.73
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-6A | 20.73 | 20.68 | 20.67 | 20.69 | 20.73 | 22.97 | 23.32 | 23.4 | 23.43 | 21.18 | 20.9 | 20.8
SmallHotel | 90.1-2013 | ASHRAE 169-2006-6A | 20.17 | 20.09 | 20.09 | 20.2 | 20.37 | 20.49 | 20.61 | 20.67 | 20.65 | 20.59 | 20.47 | 20.31
SmallOffice | 90.1-2013 | ASHRAE 169-2006-6A | 19.84 | 19.68 | 19.63 | 19.75 | 20 | 22.1 | 22.73 | 22.96 | 23 | 20.99 | 20.44 | 20.12
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-6A | 20.55 | 20.48 | 20.46 | 20.51 | 20.59 | 22.85 | 23.22 | 23.32 | 23.35 | 21.1 | 20.79 | 20.65
Warehouse | 90.1-2013 | ASHRAE 169-2006-6A | 12.51 | 12.46 | 12.47 | 12.56 | 14.45 | 16.87 | 19.89 | 19.39 | 15.2 | 13.13 | 12.81 | 12.63
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 10.22 | 10.09 | 11.25 | 13.04 | 16.38 | 19.29 | 22.13 | 24.19 | 21.66 | 17.31 | 14.18 | 11.25
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 10.22 | 10.09 | 11.25 | 13.04 | 16.38 | 19.29 | 22.13 | 24.19 | 21.66 | 17.31 | 14.18 | 11.25
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-6B | 19.59 | 19.64 | 19.73 | 19.94 | 20.17 | 22.54 | 23.1 | 23.17 | 23.08 | 20.67 | 20.16 | 19.77
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-6B | 19.58 | 19.63 | 19.71 | 19.93 | 20.15 | 22.45 | 23.05 | 23.13 | 23.04 | 20.69 | 20.16 | 19.77
Hospital | 90.1-2004 | ASHRAE 169-2006-6B
LargeHotel | 90.1-2004 | ASHRAE 169-2006-6B | 20.66 | 20.64 | 20.64 | 20.67 | 20.71 | 22.95 | 23.32 | 23.4 | 23.42 | 21.15 | 20.85 | 20.73
LargeOffice | 90.1-2004 | ASHRAE 169-2006-6B
MediumOffice | 90.1-2004 | ASHRAE 169-2006-6B | 20.1 | 20.12 | 20.16 | 20.29 | 20.43 | 22.68 | 23.18 | 23.25 | 23.21 | 20.93 | 20.49 | 20.23
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-6B | 19.58 | 19.63 | 19.71 | 19.93 | 20.15 | 22.45 | 23.05 | 23.13 | 23.04 | 20.69 | 20.16 | 19.77
Outpatient | 90.1-2004 | ASHRAE 169-2006-6B | 19.79 | 19.83 | 19.9 | 20.08 | 20.27 | 21.29 | 21.64 | 21.69 | 21.6 | 20.56 | 20.23 | 19.93
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-6B | 20.27 | 20.29 | 20.32 | 20.43 | 20.54 | 22.83 | 23.26 | 23.33 | 23.3 | 20.98 | 20.6 | 20.38
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-6B | 18.96 | 19.04 | 19.18 | 19.51 | 19.84 | 22.28 | 22.96 | 23.04 | 22.88 | 20.39 | 19.76 | 19.21
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-6B | 20.31 | 20.32 | 20.35 | 20.45 | 20.56 | 22.84 | 23.27 | 23.34 | 23.32 | 21 | 20.62 | 20.41
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-6B | 20.48 | 20.48 | 20.5 | 20.58 | 20.65 | 22.92 | 23.32 | 23.39 | 23.38 | 21.07 | 20.73 | 20.56
SmallHotel | 90.1-2004 | ASHRAE 169-2006-6B | 19.66 | 19.71 | 19.79 | 20 | 20.2 | 20.41 | 20.66 | 20.68 | 20.57 | 20.35 | 20.11 | 19.8
SmallOffice | 90.1-2004 | ASHRAE 169-2006-6B | 19.02 | 19.05 | 19.11 | 19.42 | 19.74 | 21.91 | 22.73 | 22.9 | 22.82 | 20.61 | 19.89 | 19.33
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-6B | 20.11 | 20.13 | 20.18 | 20.31 | 20.45 | 22.75 | 23.22 | 23.29 | 23.25 | 20.9 | 20.49 | 20.23
Warehouse | 90.1-2004 | ASHRAE 169-2006-6B | 12.48 | 12.48 | 12.5 | 12.57 | 12.65 | 15.81 | 19.34 | 18.33 | 14.81 | 13.04 | 12.75 | 12.57
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-6B | 20.11 | 20.09 | 20.1 | 20.21 | 20.33 | 22.63 | 23.09 | 23.2 | 23.2 | 20.9 | 20.51 | 20.27
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-6B | 20.05 | 20.04 | 20.04 | 20.16 | 20.28 | 22.53 | 23.03 | 23.16 | 23.16 | 20.91 | 20.48 | 20.22
Hospital | 90.1-2007 | ASHRAE 169-2006-6B
LargeHotel | 90.1-2007 | ASHRAE 169-2006-6B | 20.66 | 20.64 | 20.64 | 20.67 | 20.71 | 22.95 | 23.32 | 23.4 | 23.42 | 21.15 | 20.85 | 20.73
LargeOffice | 90.1-2007 | ASHRAE 169-2006-6B
MediumOffice | 90.1-2007 | ASHRAE 169-2006-6B | 20.34 | 20.33 | 20.33 | 20.42 | 20.5 | 22.71 | 23.17 | 23.27 | 23.28 | 21.04 | 20.66 | 20.47
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-6B | 20.05 | 20.04 | 20.04 | 20.16 | 20.28 | 22.53 | 23.03 | 23.16 | 23.16 | 20.91 | 20.48 | 20.22
Outpatient | 90.1-2007 | ASHRAE 169-2006-6B | 20.12 | 20.13 | 20.14 | 20.25 | 20.36 | 21.32 | 21.62 | 21.69 | 21.67 | 20.72 | 20.47 | 20.26
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-6B | 20.53 | 20.51 | 20.51 | 20.56 | 20.62 | 22.87 | 23.26 | 23.35 | 23.37 | 21.09 | 20.77 | 20.62
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-6B | 19.74 | 19.73 | 19.74 | 19.9 | 20.07 | 22.42 | 22.95 | 23.08 | 23.07 | 20.73 | 20.28 | 19.95
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-6B | 20.55 | 20.53 | 20.53 | 20.58 | 20.63 | 22.89 | 23.27 | 23.36 | 23.38 | 21.1 | 20.79 | 20.64
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-6B | 20.66 | 20.64 | 20.64 | 20.67 | 20.71 | 22.95 | 23.32 | 23.4 | 23.42 | 21.15 | 20.85 | 20.73
SmallHotel | 90.1-2007 | ASHRAE 169-2006-6B | 20.02 | 20.03 | 20.05 | 20.18 | 20.3 | 20.43 | 20.61 | 20.67 | 20.63 | 20.51 | 20.36 | 20.15
SmallOffice | 90.1-2007 | ASHRAE 169-2006-6B | 19.6 | 19.54 | 19.54 | 19.71 | 19.91 | 22.02 | 22.72 | 22.93 | 22.95 | 20.87 | 20.27 | 19.88
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-6B | 20.42 | 20.41 | 20.41 | 20.47 | 20.55 | 22.81 | 23.22 | 23.31 | 23.33 | 21.04 | 20.71 | 20.53
Warehouse | 90.1-2007 | ASHRAE 169-2006-6B | 12.48 | 12.48 | 12.5 | 12.57 | 12.65 | 15.81 | 19.34 | 18.33 | 14.81 | 13.04 | 12.75 | 12.57
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-6B | 20.11 | 20.09 | 20.1 | 20.21 | 20.33 | 22.63 | 23.09 | 23.2 | 23.2 | 20.9 | 20.51 | 20.27
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-6B | 20.05 | 20.04 | 20.04 | 20.16 | 20.28 | 22.53 | 23.03 | 23.16 | 23.16 | 20.91 | 20.48 | 20.22
Hospital | 90.1-2010 | ASHRAE 169-2006-6B
LargeHotel | 90.1-2010 | ASHRAE 169-2006-6B | 20.66 | 20.64 | 20.64 | 20.67 | 20.71 | 22.95 | 23.32 | 23.4 | 23.42 | 21.15 | 20.85 | 20.73
LargeOffice | 90.1-2010 | ASHRAE 169-2006-6B
MediumOffice | 90.1-2010 | ASHRAE 169-2006-6B | 20.34 | 20.33 | 20.33 | 20.42 | 20.5 | 22.71 | 23.17 | 23.27 | 23.28 | 21.04 | 20.66 | 20.47
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-6B | 20.05 | 20.04 | 20.04 | 20.16 | 20.28 | 22.53 | 23.03 | 23.16 | 23.16 | 20.91 | 20.48 | 20.22
Outpatient | 90.1-2010 | ASHRAE 169-2006-6B | 20.12 | 20.13 | 20.14 | 20.25 | 20.36 | 21.32 | 21.62 | 21.69 | 21.67 | 20.72 | 20.47 | 20.26
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-6B | 20.53 | 20.51 | 20.51 | 20.56 | 20.62 | 22.87 | 23.26 | 23.35 | 23.37 | 21.09 | 20.77 | 20.62
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-6B | 19.74 | 19.73 | 19.74 | 19.9 | 20.07 | 22.42 | 22.95 | 23.08 | 23.07 | 20.73 | 20.28 | 19.95
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-6B | 20.55 | 20.53 | 20.53 | 20.58 | 20.63 | 22.89 | 23.27 | 23.36 | 23.38 | 21.1 | 20.79 | 20.64
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-6B | 20.66 | 20.64 | 20.64 | 20.67 | 20.71 | 22.95 | 23.32 | 23.4 | 23.42 | 21.15 | 20.85 | 20.73
SmallHotel | 90.1-2010 | ASHRAE 169-2006-6B | 20.02 | 20.03 | 20.05 | 20.18 | 20.3 | 20.43 | 20.61 | 20.67 | 20.63 | 20.51 | 20.36 | 20.15
SmallOffice | 90.1-2010 | ASHRAE 169-2006-6B | 19.6 | 19.54 | 19.54 | 19.71 | 19.91 | 22.02 | 22.72 | 22.93 | 22.95 | 20.87 | 20.27 | 19.88
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-6B | 20.42 | 20.41 | 20.41 | 20.47 | 20.55 | 22.81 | 23.22 | 23.31 | 23.33 | 21.04 | 20.71 | 20.53
Warehouse | 90.1-2010 | ASHRAE 169-2006-6B | 12.48 | 12.48 | 12.5 | 12.57 | 12.65 | 15.81 | 19.34 | 18.33 | 14.81 | 13.04 | 12.75 | 12.57
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-6B | 20.26 | 20.22 | 20.21 | 20.29 | 20.37 | 22.66 | 23.09 | 23.21 | 23.24 | 20.96 | 20.61 | 20.4
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-6B | 20.24 | 20.2 | 20.19 | 20.26 | 20.35 | 22.58 | 23.05 | 23.17 | 23.2 | 20.98 | 20.59 | 20.38
Hospital | 90.1-2013 | ASHRAE 169-2006-6B
LargeHotel | 90.1-2013 | ASHRAE 169-2006-6B | 20.66 | 20.64 | 20.64 | 20.67 | 20.71 | 22.95 | 23.32 | 23.4 | 23.42 | 21.15 | 20.85 | 20.73
LargeOffice | 90.1-2013 | ASHRAE 169-2006-6B
MediumOffice | 90.1-2013 | ASHRAE 169-2006-6B | 20.42 | 20.4 | 20.38 | 20.45 | 20.52 | 22.73 | 23.17 | 23.27 | 23.29 | 21.07 | 20.71 | 20.53
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-6B | 20.24 | 20.2 | 20.19 | 20.26 | 20.35 | 22.58 | 23.05 | 23.17 | 23.2 | 20.98 | 20.59 | 20.38
Outpatient | 90.1-2013 | ASHRAE 169-2006-6B | 20.22 | 20.21 | 20.2 | 20.3 | 20.39 | 21.34 | 21.61 | 21.69 | 21.69 | 20.76 | 20.53 | 20.35
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-6B | 20.6 | 20.58 | 20.57 | 20.6 | 20.64 | 22.89 | 23.26 | 23.35 | 23.39 | 21.12 | 20.82 | 20.69
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-6B | 19.95 | 19.91 | 19.9 | 20.01 | 20.14 | 22.46 | 22.95 | 23.1 | 23.12 | 20.82 | 20.42 | 20.15
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-6B | 20.62 | 20.6 | 20.59 | 20.62 | 20.66 | 22.9 | 23.27 | 23.36 | 23.39 | 21.13 | 20.83 | 20.71
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-6B | 20.71 | 20.69 | 20.68 | 20.7 | 20.72 | 22.96 | 23.32 | 23.4 | 23.43 | 21.18 | 20.89 | 20.78
SmallHotel | 90.1-2013 | ASHRAE 169-2006-6B | 20.12 | 20.12 | 20.12 | 20.23 | 20.33 | 20.45 | 20.6 | 20.66 | 20.65 | 20.56 | 20.43 | 20.25
SmallOffice | 90.1-2013 | ASHRAE 169-2006-6B | 19.77 | 19.69 | 19.67 | 19.8 | 19.96 | 22.05 | 22.71 | 22.93 | 22.99 | 20.94 | 20.39 | 20.03
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-6B | 20.52 | 20.49 | 20.48 | 20.52 | 20.57 | 22.83 | 23.22 | 23.32 | 23.35 | 21.08 | 20.77 | 20.62
Warehouse | 90.1-2013 | ASHRAE 169-2006-6B | 12.48 | 12.48 | 12.5 | 12.57 | 12.65 | 15.81 | 19.34 | 18.33 | 14.81 | 13.04 | 12.75 | 12.57
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 10.24 | 10.13 | 11.21 | 12.96 | 16.3 | 19.16 | 21.87 | 23.95 | 21.47 | 17.19 | 14.1 | 11.21
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 10.24 | 10.13 | 11.21 | 12.96 | 16.3 | 19.16 | 21.87 | 23.95 | 21.47 | 17.19 | 14.1 | 11.21
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-7 | 19.32 | 19.24 | 19.44 | 19.7 | 19.96 | 22.42 | 22.92 | 22.99 | 22.88 | 20.51 | 19.98 | 19.55
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-7 | 19.81 | 19.7 | 19.79 | 19.93 | 20.09 | 22.41 | 22.9 | 23.01 | 23 | 20.75 | 20.31 | 20
Hospital | 90.1-2004 | ASHRAE 169-2006-7
LargeHotel | 90.1-2004 | ASHRAE 169-2006-7 | 20.64 | 20.59 | 20.6 | 20.63 | 20.66 | 22.92 | 23.27 | 23.36 | 23.38 | 21.13 | 20.84 | 20.72
LargeOffice | 90.1-2004 | ASHRAE 169-2006-7
MediumOffice | 90.1-2004 | ASHRAE 169-2006-7 | 19.93 | 19.87 | 19.98 | 20.14 | 20.29 | 22.6 | 23.06 | 23.14 | 23.09 | 20.82 | 20.37 | 20.09
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-7 | 19.81 | 19.7 | 19.79 | 19.93 | 20.09 | 22.41 | 22.9 | 23.01 | 23 | 20.75 | 20.31 | 20
Outpatient | 90.1-2004 | ASHRAE 169-2006-7 | 19.57 | 19.5 | 19.66 | 19.88 | 20.09 | 21.19 | 21.5 | 21.54 | 21.44 | 20.43 | 20.08 | 19.75
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-7 | 20.13 | 20.08 | 20.17 | 20.3 | 20.43 | 22.76 | 23.17 | 23.24 | 23.2 | 20.9 | 20.5 | 20.27
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-7 | 18.57 | 18.47 | 18.76 | 19.16 | 19.54 | 22.11 | 22.71 | 22.78 | 22.59 | 20.16 | 19.49 | 18.9
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-7 | 20.18 | 20.13 | 20.21 | 20.34 | 20.45 | 22.78 | 23.19 | 23.25 | 23.22 | 20.92 | 20.53 | 20.3
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-7 | 20.38 | 20.34 | 20.4 | 20.49 | 20.57 | 22.87 | 23.25 | 23.32 | 23.3 | 21.01 | 20.67 | 20.48
SmallHotel | 90.1-2004 | ASHRAE 169-2006-7 | 19.41 | 19.35 | 19.54 | 19.78 | 20.01 | 20.3 | 20.5 | 20.52 | 20.39 | 20.2 | 19.94 | 19.6
SmallOffice | 90.1-2004 | ASHRAE 169-2006-7 | 18.67 | 18.5 | 18.73 | 19.07 | 19.43 | 21.75 | 22.5 | 22.67 | 22.56 | 20.4 | 19.65 | 19.05
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-7 | 19.94 | 19.88 | 20 | 20.16 | 20.31 | 22.68 | 23.11 | 23.18 | 23.12 | 20.8 | 20.38 | 20.1
Warehouse | 90.1-2004 | ASHRAE 169-2006-7 | 12.35 | 12.31 | 12.37 | 12.47 | 12.56 | 14.73 | 17.7 | 16.37 | 13.17 | 12.78 | 12.62 | 12.44
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-7 | 20.06 | 19.96 | 20 | 20.1 | 20.21 | 22.55 | 22.98 | 23.09 | 23.11 | 20.83 | 20.46 | 20.22
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-7 | 19.89 | 19.78 | 19.85 | 19.98 | 20.12 | 22.42 | 22.91 | 23.02 | 23.02 | 20.79 | 20.37 | 20.08
Hospital | 90.1-2007 | ASHRAE 169-2006-7
LargeHotel | 90.1-2007 | ASHRAE 169-2006-7 | 20.64 | 20.59 | 20.6 | 20.63 | 20.66 | 22.92 | 23.27 | 23.36 | 23.38 | 21.13 | 20.84 | 20.72
LargeOffice | 90.1-2007 | ASHRAE 169-2006-7
MediumOffice | 90.1-2007 | ASHRAE 169-2006-7 | 20.28 | 20.21 | 20.24 | 20.32 | 20.41 | 22.65 | 23.09 | 23.19 | 23.2 | 20.98 | 20.62 | 20.41
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-7 | 19.89 | 19.78 | 19.85 | 19.98 | 20.12 | 22.42 | 22.91 | 23.02 | 23.02 | 20.79 | 20.37 | 20.08
Outpatient | 90.1-2007 | ASHRAE 169-2006-7 | 20.05 | 19.97 | 20.02 | 20.13 | 20.24 | 21.24 | 21.51 | 21.58 | 21.57 | 20.64 | 20.41 | 20.19
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-7 | 20.5 | 20.44 | 20.45 | 20.5 | 20.56 | 22.83 | 23.2 | 23.29 | 23.31 | 21.06 | 20.75 | 20.6
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-7 | 19.68 | 19.54 | 19.6 | 19.74 | 19.91 | 22.31 | 22.79 | 22.93 | 22.93 | 20.64 | 20.22 | 19.9
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-7 | 20.53 | 20.47 | 20.48 | 20.52 | 20.58 | 22.85 | 23.22 | 23.3 | 23.33 | 21.07 | 20.76 | 20.62
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-7 | 20.64 | 20.59 | 20.6 | 20.63 | 20.66 | 22.92 | 23.27 | 23.36 | 23.38 | 21.13 | 20.84 | 20.72
SmallHotel | 90.1-2007 | ASHRAE 169-2006-7 | 19.94 | 19.85 | 19.92 | 20.04 | 20.17 | 20.35 | 20.49 | 20.55 | 20.52 | 20.43 | 20.3 | 20.08
SmallOffice | 90.1-2007 | ASHRAE 169-2006-7 | 19.49 | 19.31 | 19.35 | 19.52 | 19.72 | 21.89 | 22.56 | 22.77 | 22.8 | 20.76 | 20.19 | 19.78
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-7 | 20.39 | 20.32 | 20.34 | 20.4 | 20.47 | 22.76 | 23.15 | 23.24 | 23.26 | 21 | 20.68 | 20.51
Warehouse | 90.1-2007 | ASHRAE 169-2006-7 | 12.35 | 12.31 | 12.37 | 12.47 | 12.56 | 14.73 | 17.7 | 16.37 | 13.17 | 12.78 | 12.62 | 12.44
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-7 | 20.06 | 19.96 | 20 | 20.1 | 20.21 | 22.55 | 22.98 | 23.09 | 23.11 | 20.83 | 20.46 | 20.22
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-7 | 19.89 | 19.78 | 19.85 | 19.98 | 20.12 | 22.42 | 22.91 | 23.02 | 23.02 | 20.79 | 20.37 | 20.08
Hospital | 90.1-2010 | ASHRAE 169-2006-7
LargeHotel | 90.1-2010 | ASHRAE 169-2006-7 | 20.64 | 20.59 | 20.6 | 20.63 | 20.66 | 22.92 | 23.27 | 23.36 | 23.38 | 21.13 | 20.84 | 20.72
LargeOffice | 90.1-2010 | ASHRAE 169-2006-7
MediumOffice | 90.1-2010 | ASHRAE 169-2006-7 | 20.28 | 20.21 | 20.24 | 20.32 | 20.41 | 22.65 | 23.09 | 23.19 | 23.2 | 20.98 | 20.62 | 20.41
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-7 | 19.89 | 19.78 | 19.85 | 19.98 | 20.12 | 22.42 | 22.91 | 23.02 | 23.02 | 20.79 | 20.37 | 20.08
Outpatient | 90.1-2010 | ASHRAE 169-2006-7 | 20.05 | 19.97 | 20.02 | 20.13 | 20.24 | 21.24 | 21.51 | 21.58 | 21.57 | 20.64 | 20.41 | 20.19
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-7 | 20.5 | 20.44 | 20.45 | 20.5 | 20.56 | 22.83 | 23.2 | 23.29 | 23.31 | 21.06 | 20.75 | 20.6
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-7 | 19.68 | 19.54 | 19.6 | 19.74 | 19.91 | 22.31 | 22.79 | 22.93 | 22.93 | 20.64 | 20.22 | 19.9
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-7 | 20.53 | 20.47 | 20.48 | 20.52 | 20.58 | 22.85 | 23.22 | 23.3 | 23.33 | 21.07 | 20.76 | 20.62
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-7 | 20.64 | 20.59 | 20.6 | 20.63 | 20.66 | 22.92 | 23.27 | 23.36 | 23.38 | 21.13 | 20.84 | 20.72
SmallHotel | 90.1-2010 | ASHRAE 169-2006-7 | 19.94 | 19.85 | 19.92 | 20.04 | 20.17 | 20.35 | 20.49 | 20.55 | 20.52 | 20.43 | 20.3 | 20.08
SmallOffice | 90.1-2010 | ASHRAE 169-2006-7 | 19.49 | 19.31 | 19.35 | 19.52 | 19.72 | 21.89 | 22.56 | 22.77 | 22.8 | 20.76 | 20.19 | 19.78
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-7 | 20.39 | 20.32 | 20.34 | 20.4 | 20.47 | 22.76 | 23.15 | 23.24 | 23.26 | 21 | 20.68 | 20.51
Warehouse | 90.1-2010 | ASHRAE 169-2006-7 | 12.35 | 12.31 | 12.37 | 12.47 | 12.56 | 14.73 | 17.7 | 16.37 | 13.17 | 12.78 | 12.62 | 12.44
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-7 | 20.13 | 20.03 | 20.05 | 20.13 | 20.23 | 22.56 | 22.99 | 23.1 | 23.13 | 20.86 | 20.51 | 20.29
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-7 | 20.1 | 20 | 20.03 | 20.11 | 20.21 | 22.48 | 22.94 | 23.06 | 23.08 | 20.88 | 20.49 | 20.26
Hospital | 90.1-2013 | ASHRAE 169-2006-7
LargeHotel | 90.1-2013 | ASHRAE 169-2006-7 | 20.64 | 20.59 | 20.6 | 20.63 | 20.66 | 22.92 | 23.27 | 23.36 | 23.38 | 21.13 | 20.84 | 20.72
LargeOffice | 90.1-2013 | ASHRAE 169-2006-7
MediumOffice | 90.1-2013 | ASHRAE 169-2006-7 | 20.32 | 20.24 | 20.27 | 20.34 | 20.42 | 22.66 | 23.09 | 23.19 | 23.21 | 21 | 20.64 | 20.44
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-7 | 20.1 | 20 | 20.03 | 20.11 | 20.21 | 22.48 | 22.94 | 23.06 | 23.08 | 20.88 | 20.49 | 20.26
Outpatient | 90.1-2013 | ASHRAE 169-2006-7 | 20.1 | 20.01 | 20.06 | 20.15 | 20.26 | 21.25 | 21.51 | 21.59 | 21.58 | 20.66 | 20.44 | 20.23
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-7 | 20.54 | 20.48 | 20.48 | 20.52 | 20.57 | 22.84 | 23.21 | 23.3 | 23.33 | 21.07 | 20.77 | 20.63
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-7 | 19.77 | 19.63 | 19.67 | 19.79 | 19.94 | 22.33 | 22.8 | 22.94 | 22.96 | 20.68 | 20.28 | 19.99
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-7 | 20.56 | 20.5 | 20.51 | 20.54 | 20.59 | 22.85 | 23.22 | 23.31 | 23.34 | 21.08 | 20.78 | 20.65
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-7 | 20.66 | 20.62 | 20.62 | 20.64 | 20.67 | 22.92 | 23.28 | 23.36 | 23.39 | 21.14 | 20.85 | 20.74
SmallHotel | 90.1-2013 | ASHRAE 169-2006-7 | 19.99 | 19.9 | 19.96 | 20.07 | 20.19 | 20.35 | 20.49 | 20.55 | 20.53 | 20.45 | 20.33 | 20.12
SmallOffice | 90.1-2013 | ASHRAE 169-2006-7 | 19.57 | 19.38 | 19.42 | 19.56 | 19.75 | 21.9 | 22.56 | 22.78 | 22.82 | 20.8 | 20.24 | 19.85
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-7 | 20.44 | 20.37 | 20.38 | 20.42 | 20.49 | 22.77 | 23.15 | 23.25 | 23.28 | 21.02 | 20.7 | 20.55
Warehouse | 90.1-2013 | ASHRAE 169-2006-7 | 12.35 | 12.31 | 12.37 | 12.47 | 12.56 | 14.73 | 17.7 | 16.37 | 13.17 | 12.78 | 12.62 | 12.44
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 10.19 | 10.01 | 11.18 | 12.98 | 16.32 | 19.27 | 22.11 | 24.18 | 21.63 | 17.28 | 14.14 | 11.19
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 9.87 | 9.72 | 10.93 | 12.79 | 16.23 | 19.19 | 22.03 | 24.08 | 21.53 | 17.14 | 13.85 | 10.9
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 10.19 | 10.01 | 11.18 | 12.98 | 16.32 | 19.27 | 22.11 | 24.18 | 21.63 | 17.28 | 14.14 | 11.19
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 9.87 | 9.72 | 10.93 | 12.79 | 16.23 | 19.19 | 22.03 | 24.08 | 21.53 | 17.14 | 13.85 | 10.9
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-8 | 19.43 | 19.32 | 19.4 | 19.59 | 19.87 | 22.29 | 22.74 | 22.87 | 22.84 | 20.5 | 19.92 | 19.66
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-8 | 19.33 | 19.22 | 19.3 | 19.5 | 19.79 | 22.17 | 22.67 | 22.81 | 22.78 | 20.49 | 19.87 | 19.58
Hospital | 90.1-2004 | ASHRAE 169-2006-8
LargeHotel | 90.1-2004 | ASHRAE 169-2006-8 | 20.46 | 20.41 | 20.42 | 20.47 | 20.55 | 22.83 | 23.19 | 23.28 | 23.3 | 21.03 | 20.68 | 20.56
LargeOffice | 90.1-2004 | ASHRAE 169-2006-8
MediumOffice | 90.1-2004 | ASHRAE 169-2006-8 | 19.87 | 19.79 | 19.85 | 19.98 | 20.18 | 22.48 | 22.93 | 23.03 | 23.02 | 20.76 | 20.24 | 20.04
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-8 | 19.33 | 19.22 | 19.3 | 19.5 | 19.79 | 22.17 | 22.67 | 22.81 | 22.78 | 20.49 | 19.87 | 19.58
Outpatient | 90.1-2004 | ASHRAE 169-2006-8 | 19.51 | 19.42 | 19.51 | 19.69 | 19.95 | 21.02 | 21.31 | 21.39 | 21.34 | 20.35 | 19.92 | 19.7
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-8 | 20.17 | 20.11 | 20.14 | 20.24 | 20.37 | 22.69 | 23.08 | 23.17 | 23.17 | 20.88 | 20.46 | 20.3
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-8 | 18.77 | 18.62 | 18.75 | 19.02 | 19.42 | 21.94 | 22.46 | 22.61 | 22.56 | 20.16 | 19.45 | 19.08
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-8 | 20.22 | 20.15 | 20.19 | 20.27 | 20.4 | 22.71 | 23.1 | 23.19 | 23.19 | 20.9 | 20.49 | 20.34
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-8 | 20.41 | 20.36 | 20.38 | 20.44 | 20.53 | 22.82 | 23.18 | 23.27 | 23.28 | 21 | 20.64 | 20.51
SmallHotel | 90.1-2004 | ASHRAE 169-2006-8 | 19.34 | 19.25 | 19.35 | 19.56 | 19.86 | 20.11 | 20.27 | 20.34 | 20.27 | 20.1 | 19.76 | 19.54
SmallOffice | 90.1-2004 | ASHRAE 169-2006-8 | 18.59 | 18.4 | 18.47 | 18.75 | 19.2 | 21.51 | 22.24 | 22.47 | 22.45 | 20.31 | 19.46 | 18.99
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-8 | 19.99 | 19.92 | 19.97 | 20.08 | 20.25 | 22.59 | 23 | 23.09 | 23.09 | 20.79 | 20.33 | 20.15
Warehouse | 90.1-2004 | ASHRAE 169-2006-8 | 12.06 | 12.03 | 12.11 | 12.25 | 12.43 | 14.32 | 16.06 | 13.56 | 12.74 | 12.53 | 12.29 | 12.17
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-8 | 19.57 | 19.46 | 19.52 | 19.67 | 19.9 | 22.31 | 22.76 | 22.89 | 22.89 | 20.57 | 20.04 | 19.79
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-8 | 19.39 | 19.28 | 19.35 | 19.53 | 19.81 | 22.18 | 22.68 | 22.82 | 22.81 | 20.53 | 19.92 | 19.64
Hospital | 90.1-2007 | ASHRAE 169-2006-8
LargeHotel | 90.1-2007 | ASHRAE 169-2006-8 | 20.46 | 20.41 | 20.42 | 20.47 | 20.55 | 22.83 | 23.19 | 23.28 | 23.3 | 21.03 | 20.68 | 20.56
LargeOffice | 90.1-2007 | ASHRAE 169-2006-8
MediumOffice | 90.1-2007 | ASHRAE 169-2006-8 | 19.93 | 19.85 | 19.9 | 20.02 | 20.2 | 22.49 | 22.93 | 23.05 | 23.04 | 20.79 | 20.3 | 20.1
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-8 | 19.39 | 19.28 | 19.35 | 19.53 | 19.81 | 22.18 | 22.68 | 22.82 | 22.81 | 20.53 | 19.92 | 19.64
Outpatient | 90.1-2007 | ASHRAE 169-2006-8 | 19.59 | 19.51 | 19.57 | 19.73 | 19.98 | 21.03 | 21.31 | 21.4 | 21.37 | 20.39 | 20 | 19.78
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-8 | 20.25 | 20.18 | 20.2 | 20.28 | 20.39 | 22.7 | 23.09 | 23.18 | 23.2 | 20.92 | 20.52 | 20.37
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-8 | 18.97 | 18.82 | 18.91 | 19.13 | 19.48 | 21.97 | 22.49 | 22.65 | 22.63 | 20.27 | 19.61 | 19.27
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-8 | 20.28 | 20.22 | 20.24 | 20.31 | 20.42 | 22.72 | 23.1 | 23.2 | 23.22 | 20.94 | 20.55 | 20.4
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-8 | 20.46 | 20.41 | 20.42 | 20.47 | 20.55 | 22.83 | 23.19 | 23.28 | 23.3 | 21.03 | 20.68 | 20.56
SmallHotel | 90.1-2007 | ASHRAE 169-2006-8 | 19.43 | 19.34 | 19.42 | 19.61 | 19.88 | 20.11 | 20.28 | 20.35 | 20.3 | 20.15 | 19.84 | 19.63
SmallOffice | 90.1-2007 | ASHRAE 169-2006-8 | 18.74 | 18.54 | 18.59 | 18.83 | 19.25 | 21.53 | 22.25 | 22.5 | 22.5 | 20.4 | 19.58 | 19.13
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-8 | 20.08 | 20.01 | 20.04 | 20.13 | 20.27 | 22.6 | 23.01 | 23.11 | 23.12 | 20.83 | 20.4 | 20.23
Warehouse | 90.1-2007 | ASHRAE 169-2006-8 | 12.06 | 12.03 | 12.11 | 12.25 | 12.43 | 14.32 | 16.06 | 13.56 | 12.74 | 12.53 | 12.29 | 12.17
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-8 | 19.57 | 19.46 | 19.52 | 19.67 | 19.9 | 22.31 | 22.76 | 22.89 | 22.89 | 20.57 | 20.04 | 19.79
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-8 | 19.39 | 19.28 | 19.35 | 19.53 | 19.81 | 22.18 | 22.68 | 22.82 | 22.81 | 20.53 | 19.92 | 19.64
Hospital | 90.1-2010 | ASHRAE 169-2006-8
LargeHotel | 90.1-2010 | ASHRAE 169-2006-8 | 20.46 | 20.41 | 20.42 | 20.47 | 20.55 | 22.83 | 23.19 | 23.28 | 23.3 | 21.03 | 20.68 | 20.56
LargeOffice | 90.1-2010 | ASHRAE 169-2006-8
MediumOffice | 90.1-2010 | ASHRAE 169-2006-8 | 19.93 | 19.85 | 19.9 | 20.02 | 20.2 | 22.49 | 22.93 | 23.05 | 23.04 | 20.79 | 20.3 | 20.1
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-8 | 19.39 | 19.28 | 19.35 | 19.53 | 19.81 | 22.18 | 22.68 | 22.82 | 22.81 | 20.53 | 19.92 | 19.64
Outpatient | 90.1-2010 | ASHRAE 169-2006-8 | 19.59 | 19.51 | 19.57 | 19.73 | 19.98 | 21.03 | 21.31 | 21.4 | 21.37 | 20.39 | 20 | 19.78
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-8 | 20.25 | 20.18 | 20.2 | 20.28 | 20.39 | 22.7 | 23.09 | 23.18 | 23.2 | 20.92 | 20.52 | 20.37
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-8 | 18.97 | 18.82 | 18.91 | 19.13 | 19.48 | 21.97 | 22.49 | 22.65 | 22.63 | 20.27 | 19.61 | 19.27
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-8 | 20.28 | 20.22 | 20.24 | 20.31 | 20.42 | 22.72 | 23.1 | 23.2 | 23.22 | 20.94 | 20.55 | 20.4
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-8 | 20.46 | 20.41 | 20.42 | 20.47 | 20.55 | 22.83 | 23.19 | 23.28 | 23.3 | 21.03 | 20.68 | 20.56
SmallHotel | 90.1-2010 | ASHRAE 169-2006-8 | 19.43 | 19.34 | 19.42 | 19.61 | 19.88 | 20.11 | 20.28 | 20.35 | 20.3 | 20.15 | 19.84 | 19.63
SmallOffice | 90.1-2010 | ASHRAE 169-2006-8 | 18.74 | 18.54 | 18.59 | 18.83 | 19.25 | 21.53 | 22.25 | 22.5 | 22.5 | 20.4 | 19.58 | 19.13
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-8 | 20.08 | 20.01 | 20.04 | 20.13 | 20.27 | 22.6 | 23.01 | 23.11 | 23.12 | 20.83 | 20.4 | 20.23
Warehouse | 90.1-2010 | ASHRAE 169-2006-8 | 12.06 | 12.03 | 12.11 | 12.25 | 12.43 | 14.32 | 16.06 | 13.56 | 12.74 | 12.53 | 12.29 | 12.17
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-8 | 19.66 | 19.55 | 19.59 | 19.71 | 19.93 | 22.32 | 22.77 | 22.91 | 22.92 | 20.62 | 20.11 | 19.87
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-8 | 19.7 | 19.58 | 19.61 | 19.72 | 19.92 | 22.24 | 22.72 | 22.87 | 22.89 | 20.66 | 20.14 | 19.91
Hospital | 90.1-2013 | ASHRAE 169-2006-8
LargeHotel | 90.1-2013 | ASHRAE 169-2006-8 | 20.46 | 20.41 | 20.42 | 20.47 | 20.55 | 22.83 | 23.19 | 23.28 | 23.3 | 21.03 | 20.68 | 20.56
LargeOffice | 90.1-2013 | ASHRAE 169-2006-8
MediumOffice | 90.1-2013 | ASHRAE 169-2006-8 | 20.12 | 20.04 | 20.06 | 20.13 | 20.27 | 22.53 | 22.96 | 23.08 | 23.1 | 20.88 | 20.44 | 20.27
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-8 | 19.7 | 19.58 | 19.61 | 19.72 | 19.92 | 22.24 | 22.72 | 22.87 | 22.89 | 20.66 | 20.14 | 19.91
Outpatient | 90.1-2013 | ASHRAE 169-2006-8 | 19.83 | 19.74 | 19.77 | 19.88 | 20.06 | 21.08 | 21.34 | 21.43 | 21.43 | 20.49 | 20.17 | 19.99
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-8 | 20.29 | 20.23 | 20.24 | 20.3 | 20.41 | 22.71 | 23.09 | 23.19 | 23.21 | 20.94 | 20.56 | 20.41
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-8 | 19.1 | 18.95 | 19.01 | 19.2 | 19.51 | 21.99 | 22.5 | 22.67 | 22.67 | 20.34 | 19.72 | 19.39
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-8 | 20.33 | 20.26 | 20.28 | 20.33 | 20.43 | 22.73 | 23.11 | 23.21 | 23.23 | 20.96 | 20.59 | 20.44
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-8 | 20.49 | 20.44 | 20.44 | 20.48 | 20.56 | 22.83 | 23.19 | 23.28 | 23.31 | 21.05 | 20.71 | 20.59
SmallHotel | 90.1-2013 | ASHRAE 169-2006-8 | 19.7 | 19.61 | 19.65 | 19.78 | 19.98 | 20.16 | 20.3 | 20.38 | 20.36 | 20.27 | 20.05 | 19.87
SmallOffice | 90.1-2013 | ASHRAE 169-2006-8 | 18.84 | 18.64 | 18.67 | 18.89 | 19.27 | 21.55 | 22.26 | 22.51 | 22.54 | 20.45 | 19.66 | 19.22
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-8 | 20.14 | 20.06 | 20.08 | 20.16 | 20.29 | 22.61 | 23.01 | 23.12 | 23.14 | 20.86 | 20.45 | 20.28
Warehouse | 90.1-2013 | ASHRAE 169-2006-8 | 12.29 | 12.25 | 12.28 | 12.35 | 12.46 | 14.3 | 16.04 | 13.55 | 12.77 | 12.63 | 12.48 | 12.38

## Lookups
These lookups are used to help users avoid input mistakes on other tabs. Please do not edit or delete existing entries or rename tables. You may add entries at the bottom of the list, but please avoid near-duplicates.
Intended Surface Type Lookup | Standards Construction Type Lookup | Building Type Lookup | Space Type Lookup | Lighting Standards Lookup | Ventilation Standards Lookup | Material Type Lookup | Construction Category Lookup
Name | Name | Name | Name | Name | Name | Name | Name
AtticFloor | Mass | FullServiceRestaurant | Anesthesia | ASHRAE 90.1-1999 | ASHRAE 62.1-1999 | StandardOpaqueMaterial | Nonresidential
AtticWall | SteelFramed | Hospital | Apartment | ASHRAE 90.1-2001 | ASHRAE 62.1-2004 | AirGap | Residential
AtticRoof | WoodFramed | LargeHotel | Apartment_topfloor_WE | ASHRAE 90.1-2004 | ASHRAE 62.1-2007 | StandardGlazing | Semiheated
DemisingFloor | IEAD | MidriseApartment | Apartment_topfloor_NS | ASHRAE 90.1-2007 | GGHC v2.2 | MasslessOpaqueMaterial
DemisingWall | View | Office | Attic | ASHRAE 189.1-2009 | AIA 2001 | SimpleGlazing
DemisingRoof | Daylight | Outpatient | Auditorium | ASHRAE 90.1-2010 | DOE Ref Pre-1980 | Gas
ExteriorFloor | Swinging | PrimarySchool | Back_Space | ASHRAE 90.1-2013 | DOE Ref 1980-2004
ExteriorWall | NonSwinging | QuickServiceRestaurant | Banquet | DOE Ref Pre-1980 | NECB-CNEB 2011
ExteriorRoof | Heated | Retail | Basement | DOE Ref 1980-2004
ExteriorWindow | Unheated | SecondarySchool | BioHazard | NECB-CNEB 2011
ExteriorDoor | RollUp | SmallHotel | BreakRoom | GGHC v2.2
GlassDoor | Sliding | StripMall | Bulk
GroundContactFloor | Metal | SuperMarket | Cafe
GroundContactWall | Nonmetal framing (all) | Warehouse | Cafeteria
GroundContactRoof | Metal framing (curtainwall/storefront) | SmallOffice | Classroom
InteriorFloor | Metal framing (entrance door) | MediumOffice | CleanWork
InteriorWall | Metal framing (all other) | LargeOffice | ClosedOffice
InteriorCeiling | Metal Building | Automotive facility | Conference
InteriorPartition | Attic and Other | Convention centre | Corridor
InteriorWindow | Glass with Curb | Courthouse | Corridor2
InteriorDoor | Plastic with Curb | Dining - bar/lounge | Corridor_topfloor
OverheadDoor | Without Curb | Dining - cafeteria | Deli/Bakery
Skylight |  | Dining - family | Dining
TubularDaylightDome |  | Dormitory | DressingRoom
TubularDaylightDiffuser |  | Exercise centre | DryStorage
|  | Fire station | Elec/MechRoom
|  | Gymnasium | ElevatorCore
|  | Health-care clinic | ElevatorCore4
|  | Hospital-NECB | Entry
|  | Hotel-NECB | ER_Exam
|  | Library | ER_NurseStn
|  | Manufacturing facility | ER_Trauma
|  | Motel | ER_Triage
|  | Motion picture theatre | Exam
|  | Multi-unit residential | Exercise
|  | Museum | Fine
|  | Office-NECB | GuestLounge
|  | Parking garage | GuestRoom
|  | Penitentiary | GuestRoom123Occ
|  | Performing arts theatre | GuestRoom123Vac
|  | Police station | GuestRoom2
|  | Post office | GuestRoom3
|  | Religious | GuestRoom4
|  | Retail | GuestRoom4Occ
|  | School/university | GuestRoom4Vac
|  | Sports arena | Gym
|  | Town hall | Hall
|  | Transportation | ICU_NurseStn
|  | Warehouse | ICU_Open
|  | Workshop | ICU_PatRm
IT_Room
Janitor
Kitchen
Lab
Laundry
Library
Lobby
LockerRoom
Lounge
Mechanical
MedGas
Meeting
MRI
MRI_Control
NurseStation
NurseStn
Office
OpenOffice
OR
PACU
PatCorridor
PatRoom
PhysicalTherapy
PhysTherapy
Plenum
Point_of_Sale
PreOp
PrintRoom
ProcedureRoom
PublicRestroom
Radiology
Restroom
Retail
Retail2
Sales/Produce
Soil Work
StaffLounge
Stair
Stair4
Storage
Storage4Front
Storage4Rear
Toilet
Vending
WholeBuilding
WholeBuilding - Lg Office
WholeBuilding - Md Office
WholeBuilding - Sm Office
Xray
Dwelling Unit(s)
Atrium - H < 13m
Atrium - H > 13m
Audience - auditorium
Audience - performance arts
Audience - motion picture
Classroom/lecture/training
Conf./meet./multi-purpose
Corr. >= 2.4m wide
Corr. < 2.4m wide
Dining - bar lounge/leisure
Dining - family space
Dining - other
Dress./fitt. - performance arts
Electrical/Mechanical
Food preparation
Lab - classrooms
Lab - research
Lobby - elevator
Lobby - performance arts
Lobby - motion picture
Lobby - other
Locker room
Lounge/recreation
Office - enclosed
Office - open plan
Sales area
Stairway
Storage area
Washroom
Workshop space
Automotive - repair
Bank - banking and offices
Convention centre - audience
Convention centre - exhibit
Courthouse - courtroom
Courthouse - cell
Courthouse - chambers
Penitentiary - audience
Penitentiary - classroom
Penitentiary - dining
Dormitory - living quarters
Fire station - engine room
Fire station - quarters
Gym - fitness
Gym - audience
Gym - play
Hospital corr. >= 2.4m
Hospital corr. < 2.4m
Hospital - emergency
Hospital - exam
Hospital - laundry/washing
Hospital - lounge/recreation
Hospital - medical supply
Hospital - nursery
Hospital - nurses' station
Hospital - operating room
Hospital - patient room
Hospital - pharmacy
Hospital - physical therapy
Hospital - radiology/imaging
Hospital - recovery
Hotel/Motel - dining
Hotel/Motel - rooms
Hotel/Motel - lobby
Hway lodging - dining
Hway lodging - rooms
Library - cataloging
Library - reading
Library - stacks
Mfg - corr. >= 2.4m
Mfg - corr. < 2.4m
Mfg - detailed
Mfg - equipment
Mfg - bay H > 15m
Mfg - 7.5 <= bay H <= 15m
Mfg - bay H < 7.5m
Museum - exhibition
Museum - restoration
Parking garage space
Post office sorting
Religious - audience
Religious - fellowship hall
Religious - pulpit/choir
Retail - dressing/fitting
Retail - mall concourse
Retail - sales
Sports arena - audience
Sports arena - court c4
Sports arena - court c3
Sports arena - court c2
Sports arena - court c1
Sports arena - ring
Strip mall - type 1
Strip mall - type 2
Strip mall - type 3
Transp. baggage
Transp. seating
Transp. concourse
Transp. counter
Warehouse - fine