## Instructions
Instruction Sheet
Worksheet Name | Instructions to 4 Wing | 4 Wing check off after item has been reviewed | 4 Wing Comments / note if information is unavailable
Simulation Assumptions | Please review tab Simulation Assumptions. Provide any comments in column C.
Proposed Energy Conservation Measures | Please review tab Proposed Energy Conservation Measures (ECMs). Provide any comments in column P.
District Heating | Please review tab District Heating tab and provide answers to the questions at the bottom and right.
Demolition and New Construction | Please review tab Demolition and New Construction, verify the lists and provide answers to the questions in yellow.
Costs | Please review tab Costs and provide answers or comments.
Planning | Please review tab Planning and provide answers or comments.
Additional Questions for 4 Wing
Mobile / Pre-Fabricated type buildings | Could 4 Wing please provide us a list of these types of buildings with PRIN number and address? And if possible heating fuel type?

## Infiltration Rates Reference
Air Leakage (Infiltration) Rate Assumptions
Units are = m3/s/m2
Infiltration Building Type | 2005-2014 | 1980-2004 | 1960-1979 | pre-1960
Air Terminal | 0.0002 | 0.00035 | 0.0005 | 0.0007
Communications & Control | 0.0002 | 0.00035 | 0.0005 | 0.0007
Control Tower | 0.0002 | 0.00035 | 0.0005 | 0.0007
Fire Hall | 0.0003 | 0.00045 | 0.00075 | 0.0008
Fitness & Rec. - Arena | 0.0002 | 0.00035 | 0.0005 | 0.0007
Fitness & Rec. - Multi-gym | 0.0002 | 0.00035 | 0.0005 | 0.0007
Fitness & Rec. - Pool | 0.0002 | 0.00035 | 0.0005 | 0.0007
Food Services | 0.0002 | 0.00035 | 0.0005 | 0.0007
Hangars | 0.0003 | 0.00045 | 0.00075 | 0.0008
Infrastructure | 0.0003 | 0.00045 | 0.00075 | 0.0008
Medical Facilities | 0.0002 | 0.00035 | 0.0005 | 0.0007
Misc. Bldgs < 100m2 | 0.0002 | 0.00035 | 0.0005 | 0.0007
Mobile Prefab Buildings | 0.0002 | 0.00035 | 0.0005 | 0.0007
Motel Type Residences | 0.0002 | 0.00035 | 0.0005 | 0.0007
Museum | 0.0002 | 0.00035 | 0.0005 | 0.0007
Offices | 0.0002 | 0.00035 | 0.0005 | 0.0007
Recreational / Club Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Religious Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Retail Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Sleeping barracks | 0.0002 | 0.00035 | 0.0005 | 0.0007
Storage Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Training Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
University Dormitory Type | 0.0002 | 0.00035 | 0.0005 | 0.0007
Warehouses | 0.0003 | 0.00045 | 0.00075 | 0.0008
Workshops | 0.0003 | 0.00045 | 0.00075 | 0.0008
Small Building Types | [5 empty] | Infiltration @ 5 pascals (normal)
Bldg Type | Type | No. Bldgs | Ave. Floor Area (m2) | Total Area (m2) | % Total Floor Area | pre-1960 |  | 1960-1979 |  | 1980-2004 |  | post-2004
[6 empty] | ACH | L/s/m2 | ACH | L/s/m2 | ACH | L/s/m2 | ACH | L/s/m2
Hangars | 1c | 3 | 435 | 1305 | 3.687% | 1.5 | 0.8 | 1 | 0.75 | 0.66 | 0.45 | 0.4 | 0.3
Training Bldgs | 2b | 3 | 292.2 | 876.6 | 2.477% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Warehouses (Sheds) | 3b | 30 | 382.4 | 11472 | 32.41% | 1.5 | 0.8 | 1 | 0.75 | 0.66 | 0.45 | 0.4 | 0.3
Sleeping barracks | 4c | 15 | 133.8 | 2007 | 5.67% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Recreational / Club Bldgs | 5d | 10 | 300.6 | 3006 | 8.492% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Offices | 6b | 11 | 323.8 | 3561.8 | 10.06% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Food Services | 7b | 2 | 290.8 | 581.6 | 1.643% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
(new) Storage Bldgs | 8b | 16 | 310 | 4960 | 14.01% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Workshops | 9b | 6 | 240.1 | 1440.6 | 4.07% | 1.5 | 0.8 | 1 | 0.75 | 0.66 | 0.45 | 0.4 | 0.3
Medical Facilities | 10b | 1 | 278.7 | 278.7 | 0.7874% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Retail Bldgs (+ Retail/Office) | 11b | 1 | 407 | 407 | 1.15% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Communications & Control | 13c | 6 | 260.6 | 1563.6 | 4.417% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Misc. Bldgs < 100m2 | 15 | 162 | 24.3 | 3936.6 | 11.12% | 1.0 (0.70) | 0.7 | 0.6 | 0.5 | 0.44 (0.35) | 0.35 | 0.27 | 0.2
|  |  |  | 35396.5 | 100%
Percentage of total building area represented by Part 9 |  |  |  | 10.5%
|  | 104 |  | 31459.9
Part 3 Building Types | [5 empty] | Infiltration @ 5 pascals (normal)
Bldg Type | Type | No. Bldgs | Ave. Floor Area (m2) | Total Area (m2) | % Total Floor Area | pre-1960 |  | 1960-1979 |  | 1980-2004 |  | post-2004
[6 empty] | ACH (L/sec/m2) |  | ACH (L/sec/m2) |  | ACH (L/sec/m2) |  | ACH (L/sec/m2)
Hangars | 1a | 9 | 9710.5 | 87394.5 | 28.98% | 1.5 (0.80) |  | 1.0 (0.75) |  | 0.66 (0.45) |  | 0.40 (0.30)
Air Terminal | 1b | 1 | 3086 | 3086 | 1.023% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Training Bldgs | 2a | 4 | 4204.6 | 16818.4 | 5.576% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Warehouses (Storage Bldgs) | 3a | 8 | 2202.6 | 17620.8 | 5.842% | 1.5 (0.80) |  | 1.0 (0.75) |  | 0.66 (0.45) |  | 0.40 (0.30)
Motel Type Residences | 4a | 2 | 4497.6 | 8995.2 | 2.982% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
University Dormitory Type | 4b | 5 | 2814.6 | 14073 | 4.666% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Sleeping barracks | 4c | 4 | 710 | 2840 | 0.9416% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Fitness & Rec. - Multi-gym | 5a | 2 | 3119.1 | 6238.2 | 2.068% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Fitness & Rec. - Arena | 5b | 1 | 3414.4 | 3414.4 | 1.132% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Fitness & Rec. - Pool | 5c | 1 | 3042.2 | 3042.2 | 1.009% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Offices | 6a | 14 | 3549.7 | 49695.8 | 16.48% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Food Services | 7a | 3 | 4701.9 | 14105.7 | 4.677% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Infrastructure (former Garage & Process Enclosures) | 8a | 2 | 808.1 | 1616.2 | 0.5359% | 1.5 (0.80) |  | 1.0 (0.75) |  | 0.66 (0.45) |  | 0.40 (0.30)
Workshops | 9a | 20 | 2696.1 | 53922 | 17.88% | 1.5 (0.80) |  | 1.0 (0.75) |  | 0.66 (0.45) |  | 0.40 (0.30)
Medical Facilities | 10a | 1 | 3344.5 | 3344.5 | 1.109% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Retail Bldgs | 11a | 2 | 1576.9 | 3153.8 | 1.046% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Religious Bldgs | 12 | 1 | 1169.2 | 1169.2 | 0.3876% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Control Tower | 13a | 1 | 1294 | 1294 | 0.429% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Fire Hall | 13b | 1 | 1146.54 | 1146.54 | 0.3801% | 1.5 (0.80) |  | 1.0 (0.75) |  | 0.66 (0.45) |  | 0.40 (0.30)
Museum | 14 | 1 | 8643.7 | 8643.7 | 2.866% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
|  | 83 |  | 301614.14 | 100%
Note: Values Taken and Adapted from: (1) U.S. Army Corps of Engineers " Building Air Tightness: Army Requirements and Case Studies (New Construction and Retrofit Projects)"
7th Annual Workshop, Energy Efficient Technologies for Buildings and Communities, Jan 28, 2011 Las Vegas
(2) "Air Barrier Test Results and Trends: Experience from 100+ Buildings" Pie Forensic Consultants, presented at Energy Efficient Technologies for Buildings and Communities, Jan 28, 2011 Las Vegas
(3) "Efficient Technologies to Reduce Building Energy Use and Meet Federal Requirements, Alexender Zhivov, U.S. Army Corps of Engineers
Mobile/Pre-Fabricated archetype | 0.27 ACH (0.20 L/s/m2)
Note on K35: mlubun: ASHRAE 90.1 1999 value
Note on G37: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I37: mlubun: 50% increase in ACH and leakage due to door openings
Note on K37: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M37: mlubun: 50% increase on ACH and leakage due to door openings
Note on G39: mlubun: 50% increase due to hanger door openings
Note on I39: mlubun: 50% increase in ACH and leakage due to door openings
Note on K39: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M39: mlubun: 50% increase on ACH and leakage due to door openings
Note on G45: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I45: mlubun: 50% increase in ACH and leakage due to door openings
Note on K45: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M45: mlubun: 50% increase on ACH and leakage due to door openings
Note on K57: mlubun: ASHRAE 90.1 1999 value
Note on G59: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I59: mlubun: 50% increase in ACH and leakage due to door openings
Note on K59: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M59: mlubun: 50% increase on ACH and leakage due to door openings
Note on G62: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I62: mlubun: 50% increase in ACH and leakage due to door openings
Note on K62: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M62: mlubun: 50% increase on ACH and leakage due to door openings
Note on M69: building renovated in 2005.
Note on G71: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I71: mlubun: 50% increase in ACH and leakage due to door openings
Note on K71: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M71: mlubun: 50% increase on ACH and leakage due to door openings
Note on G72: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I72: mlubun: 50% increase in ACH and leakage due to door openings
Note on K72: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M72: mlubun: 50% increase on ACH and leakage due to door openings
Note on G77: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I77: mlubun: 50% increase in ACH and leakage due to door openings
Note on K77: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M77: mlubun: 50% increase on ACH and leakage due to door openings

## Simulation Assumptions
Input Assumptions for Building Energy Models
Computer simulation models were used to estimate the energy usage in buildings. Simulation models predict the energy consumption and interaction of building systems. 11 buildings have been modelled and will represent the other similar building types - 'archetypes' - throughout the Base. This document lists the inputs or assumptions that were used in the computer models. Wherever possible, the actual equipment, occupancy, schedules and operating values were used in the models. Otherwise, assumptions were based on typical values from the Canadian building code, known as the Model National Energy Code for Buildings (MNECB).
Item | Canmet Energy's Assumptions and Values | 4 Wing Comments?
Weather (historical weather data) | Edmonton average weather data. A data file called Canadian Weather year for Energy Calculation (CWEC)
Occupancy
number of occupants in buildings | Building Code values adjusted for the actual occupancy reported in the audit
occupancy schedules in buildings | actual schedules reported in the audit
Building Construction
insulation levels in walls and ceilings | estimated from the building plans, including renovations to walls and roofs (see attached sheet 'R-values')
air tightness / air leakage | estimated from a U.S. Army Corps of Engineers study (see attached sheet 'Infiltration Rates')
Lighting
type of lamps | metal halides in the bay spaces of recreation centres, storage buildings, workshops, and hangars. Otherwise all T8 fluorescents
lighting density (Watts/m2 of floor area) | Building Code values used to estimate the number of lamps per square metre of floor area
contribution to space heating | In most spaces, lights generate heat that contributes to useful space heating and also contributes to summer cooling loads. This is not the case in bay spaces where the heat from lights does not reach occupants.
schedule | Same as building occupancy schedule reported in the audit
Plug Loads
plug loads (Watts/m2 of floor area) | Building Code values
schedule | Building Code values
Heating Equipment
heating system capacity | auto-sized by the computer model based on heat loss calculation and design temperatures
AHU and RTU heating side efficiency | actual if available, otherwise 80% for direct fired equipment
space temperature setpoint | 20 °C average assumed for all buildings and spaces
boiler capacity | auto-sized by the computer model
boiler efficiency | actual if available, otherwise 80%. 80% estimated for central plant heated buildings
hot water setpoint | 82 °C
boiler with outdoor air reset control | installed in central plant heated buildings; not installed in other buildings
nighttime temperature setback | not currently practiced in any buildings
HVAC night control | assume zone thermal units (if applicable) can cycle on to meet heating setpoint. may be fan coil, terminal unit, baseboard, or RTU
Main Heating Pumps
flow capacity and horsepower | auto-sized by the computer model
pump motor efficiency | adjusted according to age of building
pump speed | constant, single-speed
Cooling Equipment
cooling system capacity | auto-sized by the computer model based on heat loss calculation and design temperatures
space temperature setpoint | 24 °C average for cooled spaces
cooling efficiency | the coefficient of performance (COP) for cooling equipment and air conditioners is corelated to building age: 2.5 for systems pre-1980; 3.0 for 1980-2004; 3.5 post-2004
spaces with cooling | cooling is assumed for spaces with occupants only, for example in offices but not in storage spaces; also based upon actual information from audits
free cooling economizers | assume economizers are installed and operating in all AHUs and RTUs
Ventilation | including AHUs, MUAs, RTUs, exhaust fans, ceiling fans, transfer air fans
fan capacity and horsepower | auto-sized by the computer model. Fan power is estimated separately for supply, return and exhaust fans using typical static pressure of AHUs
fan speed | constant speed
fan motor efficiency | adjusted according to age of building
ventilation fresh air requirement | Building Code outdoor air per person rates, and occupancy levels from audit
ventilation schedule | always on (assumption is the heating and cooling setpoints are met, and fresh air requirement for number of occupants only). Ventilation runs through the night same as daytime
exhaust fans capacity and schedule | actual values reported in audit, otherwise assume 24 hour operation
Domestic Hot Water
peak flow and temperature | based on Building Code values for temperature, litres and draw profiles
water tank capacity | Building Code value
water tank efficiency | actual if available otherwise 80% for gas-fired, 100% for electric with standby losses taken into account separately
schedule | based on predominant Building Code space type
water heater pumps | horsepower autosized by computer model; runs constantly
fuel type | based on audit
Miscellaneous
humidification/dehumidification | no humidification is assumed; dehumidification accounted for by cooling
combining systems | separate HVAC equipment was sometimes combined in order to simplify computer modelling
HVAC system type v.s. age of building? | the type of HVAC equipment was not correlated to the building's age because buildings have undergone so many retrofits and added new heating and ventilation systems
Firehall | use Trenton Firehall and run with Edmonton weather data. The Cold Lake Firehall is the same building design as Trenton's.
B172 CF18 Training | use Trenton Training archetype building and run with Edmonton weather data. No building plans were made available by Cold Lake for this building.

## Proposed ECMs
Proposed Energy Conservation Measures for Buildings
| Type | Energy Conservation Measure Name | Short Description of ECM | Controls Based | Interaction of ECMs | How Modelled? | Costed? | Cost Units | Reference or Source for assumptions | Long Description of ECM / for Modelling | Cold Lake Audit Notes (Matthew's) | Comments | Application Rate | Implementation | Miscellaneous / Other Benefits | 4 Wing Comments?
1 | Ventilation | Occupancy control for exhaust fans | A sensor determines when a space is unoccupied and the control shuts off exhaust fans and make-up air units (MUA). Saves fan energy (electricity) and heating. | yes |  | not modelled for Trenton. could be modelled in OS | yes |  | Followed the MNECB or real schedule for fan operation | same as short description |  | Seems to pay back well on a ½ h.p. fan running 24/7. Phylroy would need to schedule exhaust fans distinctly from air handlers | % of buildings or floor space this ECM applies to
2 | Ventilation | Demand controlled ventilation (DCV) control | Minimizes the delivery of ventilation air by measuring the carbon dioxide concentration in the space, and delivering enough air to meet the building code. Installed in AHUs and RTUs. Saves on fan energy and heating. | yes | overlap with VFD. Increases heating | OS | yes. Did not include the cost of a VFD |  | MNECB 1997 schedules for fan operation, or real schedule | Adjusts the rate of ventilation air delivered to a space by measuring the carbon dioxide concentration in the space. When there are no occupants in the space, ventilation is minimized, saving on fan energy. Two types of demand control ventilation devices assessed: sensors in occupied spaces controlling airflow to the space and sensors in return air duct controlling operation of the air handler. | I observed strong ventilation running in the REC Centre squash courts and activities room while unoccupied. | Risk of comfort problems according to staff. Building specific. Should package DCV with VFD ECM. | % of buildings or floor space this ECM applies to | Control prioritizes space temperature before ventilation. Must not interfere with existing pre-cooling practice. For RTUs an alternate to this ECM could be the Advanced RTU Controller 'Catalyst' that combines fan speed, economizer and DCV controls and saves 25% to 50%. | Where mechanical cooling is undersized, this ECM would keep buildings cooler by reducing the addition of warm outdoor air during summer
3 | Ventilation | Variable frequency drive (VFD) control for air handler fans | A VFD adjusts the fan speed to match the actual need for ventilation air, heating or cooling. Installed in constant speed AHUs and RTUs. This saves on fan energy, heating and cooling. | yes | overlap with DCV. Increases heating | OS | yes |  | Assume existing fans have constant speed, based on MNECB 1997. We will assume a typical fan type curve. | For constant speed AHUs and RTUs, a controller which measures the return air/outdoor air temperatures and adjusts the fan motor to maintain a return air temperature or to adjust the volume of air delivered to maintain return air temperature and/or carbon dioxide in return air stream. A 20% lower fan speed saves 50% of the fan energy. Also reduces the cost to condition outside air. | Some AHU fans have VFDs (REC Centre has at least one AHU). They can be problematic according to Rob Williams | Needed for DCV. Can program VFD to respond to duct static pressure, zone temperature, or CO2 concentration. | % of buildings or floor space this ECM applies to | For RTUs an alternate to this ECM could be the Advanced RTU Controller 'Catalyst' that combines fan speed, economizer and DCV controls and saves 25% to 50%.
4 | Plug Loads | Occupancy sensor control for plug loads | A PIR + ultrasonic sensor turns on a circuit for wall plugs when it is activated by a person entering the room. After the occupant leaves the room and there is no activity sensed, a timer turns the circuit off, saving on electricity. | yes |  | manual | yes |  | MNECB 1997 by space type | same as short description | Many personal heaters and fans are used in offices. This ECM could ensure they are being shut off at night, as well as computers and office equipment. |  | % of buildings or floor space this ECM applies to
5 | Lighting | Replacement of T8 lamp fixtures with T5s | Replace existing T8 and T12 fixtures with dimmable T5 fixtures. This saves approximately 30% on electricity. | no | increases heating, reduces cooling | OS with a manual factor of 30%. Used W/m2 in model and no fixture counts | yes |  | MNECB 1997 by space type | Lighting energy was reduced by 30% over MNECB energy levels per space by assuming existing T8 fluorescent fixtures in offices, barracks, warehouses). |  | Lighting contributes useful space heating in some spaces and conversely adds to cooling loads. In high bay spaces it is assumed not to contribute to space heating. | % of buildings or floor space this ECM applies to
6 | Lighting | Replacement of metal halide lamp fixtures with T5s | Replace existing 400W or 250W Metal Halide lamps with high-intensity, instant start, T5 fixtures. This saves approximately 50%. | no | increases heating, reduces cooling | OS with a manual factor of 30%. Used W/m2 in model and no fixture counts | yes |  | MNECB 1997 by space type | Lighting energy was reduced by 30% over MNECB energy levels per space by assuming existing metal halide fixtures (400W) in hangers and workshops and metal halide fixtures (250W) in gyms and recreational high bay spaces | various wattages of metal halides were observed. | Assume same floor area application as Trenton. Set HIDs to 5% space heat. Note other benefits of fluorescent e.g. lumen depreciation | % of buildings or floor space this ECM applies to |  | Alert Hangars with metal halide lights left on 24/7 could potentially turn off fluorescents if they are instant start. Since metal halides takes time to warm up they are currently left on at all times.
7 | Lighting | Occupancy sensor control for lighting | A PIR + ultrasonic sensor turns on a circuit for lights when it is activated by a person entering the room. After the occupant leaves the room and there is no activity, a timer turns the circuit off, saving on electricity. | yes | increases heating, reduces cooling | not modelled for Trenton | yes, same sensor used for plug loads |  | MNECB 1997 by space type | same as short description | could apply to workshops, mechanical rooms, bathrooms – tend to be infrequently occupied | Include a paragraph on photocells for outdoor lighting | % of buildings or floor space this ECM applies to
8 | Heating | Upgrade of pump and fan motors | Replace standard efficiency pump and fan motors with NEMA rated Premium efficiency motors. Saves in the order of 5% of electricity. | no | increases heating | not modelled for Trenton. could be modelled in OS | yes |  | Start with MNECB 1997 values | same as short description |  | Need to assume efficiency of typical existing motor | % of buildings or floor space this ECM applies to | This could be part of a motor replacement program or a regular maintenance plan. Staff could use Motormaster.com software to inventory and select motors
9 | Heating | Outdoor air temperature reset control for hot water loop | A controller that measures the outdoor air temperature and raises or lowers the hot water loop temperature to better match the building heat loss. It saves energy by minimizing heat loss in the distribution and boiler stack since the boiler cycles less often. | yes | VSD on pumps | not modelled for Trenton. could be modelled in OS. To be determined | yes |  | NECB 2011 sequence for boilers | A hot water reset control measures the outside air temperature; this information is used to estimate the building heating load as the outdoor temperature varies. The supply hot water temperature is modulated up and down range in an inverse linear ratio to outside air temperature. The typical range for conventional boilers is to vary the supply water temperature from 60 .. 82 ⁰C as the outside temperature varies from +18 .. -18 ⁰C. | Outdoor Air Reset of Hot Water Converters: This is supposed to be currently installed in buildings heated by the DES. Was installed by MCW in 1998-2001. | REC centre has it. Assume that buildings newer than 15 year old include it. | % of buildings or floor space this ECM applies to |  | Boiler low-limit setting of 180F seems to prevent the Outdoor air reset from setting as low as it could potentially go.
10 | Heating | Variable speed drive (VSD) control for hydronic/heating pumps | A VSD varies the speed of a hydronic pump as the need for heat in the building changes. For example in warmer weather, the pump speed can be reduced. Saves on heating and pumping energy. | yes | Outdoor air reset | OS | yes |  | Assume existing pumps have constant speed, based on MNECB 1997. | VSD controller for a pump along with a 2-way valve on the hydronic loop which measures the return water temperature and adjusts the pump motor and the 2-way valve position to maintain a design temperature differential. Savings are in heating and pump energy . A 20% lower speed saves 50% of pumping energy. | Pool water pumps – base speed on pool water turbidity. This should ramp down pumping at night |  | % of buildings or floor space this ECM applies to |  | Didn’t energy model this.
11 | Heating | Supply air temperature reset control | In AHUs or RTUs, this control lowers the supply air temperature to more accurately match the space heating load, based on measuring the return air temperature. Saves on heating , cooling and re-heat energy. | yes |  | OS | yes |  | Is a standard control sequence in the NECB 2011 | In AHUs or RTUs, reduces the supply air temperature or reheat temperature based on measuring return air temperature to match the heating load more closely as indoor conditions change. Saves on heating, cooling and reheat energy. |  |  | % of buildings or floor space this ECM applies to
12 | Heating | Retro-commissioning of HVAC systems | Includes the re-calibration of thermostats and re-tuning of all the controls in AHUs and RTUs. This saves on electrical, heating and cooling energy. | no | Not to overlap with the other control ECMs | manual | yes, for two measures |  | Used ASRHAE Energy Efficiency Guides for Existing Commercial Buildings. | Re-calibrating of thermostats in occupied spaces and retuning of all of the controls within the AHUs and RTUs to ensure that the sequence of operations and settings (valve, damper, temperatures, sensors) are within design specifications | Col d Lake has a need to update the missing documentation on building controls | Empirical data is found in the PNNL 2012 Study on Commercial Building Re-tuning | % of buildings or floor space this ECM applies to |  | Zero energy dead band setpoints in heat/cool HVAC equipment so to avoid simultaneous heating and cooling …
13 | Heating | Nighttime temperature setback | Using a programmable thermostat or BAS, the space temperature is lowered by 2°C during unoccupied hours and brought back up 2°C before occupied hours. This reduces the amount of heating. | yes |  | OS | yes |  | 2°C was agreed to be reasonable | Reduction in the heating setpoint by 2°C for unoccupied hours (assumes a zero setback strategy currently exists) | Various technicians, building occupants and CE staff indicated reluctance to set back temperature at night due to previous issues with comfort, recovery time and the risk of freezing the building. There is potential in some spaces (e.g. unit heaters on thermostats). Difficulty recovering temperature in older buildings. | We could assume there is potential in 25% (?) of spaces. Due to the climate and comfort, we did not recommend the occupied hours temperature reduction recommended for Trenton. | % of buildings or floor space this ECM applies to |  | Digital programmable thermostat would be needed for Barracks with perimeter convectors and Braukmann thermostat controls.
14 | DHW Heating | Replacement of electric hot water tanks with gas-fired hot water tanks | Replacement of electric hot water tanks with gas-fired hot water tanks. This saves on energy costs and GHGs. | no |  | OS | yes |  | Assume an E.F. for the electric (EF 0.92, 100% s.s.) and for the gas hot water tank (EF 0.67. 80% s.s.). seasonal efficiency. Use MNECB 1997 daily occupant or space DHW consumption and draw profile. | Replacement of electric hot water tanks with gas-fired hot water tanks. This saves on energy costs and GHGs in Alberta since the GHG factor for natural gas is lower than the factor for electricity. | Many electric DHW tanks were observed in audited buildings |  | % of buildings or floor space this ECM applies to | Must consider the existing capacity of gas pipe and proximity of nearest gas pipe to the electric hot water tank. | because electricity is five times more expensive, consider gas-fired DHW to save operating cost and GHG emissions
15 | DHW Heating | Drainwater heat recovery for Barracks | A copper drain pipe device (a gravity film exchanger) recovers the heat - mainly from shower drainwater - and transfers it to the cold domestic water as it flows into the hot water tank. This saves on DHW heating energy. | yes |  | manual. not modelled for Trenton. There is a DWHR module in EnergyPlus | no |  | Use MNECB 1997 daily occupant or space DHW consumption and draw profile. | same as short description | Potential in the barracks. A main drainwater pipe is close by to the DHW Heater. | Matthew could estimate the cost | % of buildings or floor space this ECM applies to
16 | DES | Replacement of building steam converters with hot water heat exchangers | To accommodate a new DES using low temperature hot water, the existing steam "converters" in buildings would need to be replaced with hot water heat exchangers. | no |  | manual | yes |  | Not applicable | same as short description |  | Is this considered an "ECM"? | % of buildings or floor space this ECM applies to
17 | Cooling | Cold deck reset control | During mechanical cooling, supply air temperature is reset based upon the return air temperature and the outdoor air temperature to ensure the space does not overcool resulting in possible reheat energy. This saves on cooling energy and possibly reheat energy. | yes | impact reduced via compressor upgrade or replacement of cooling | OS | yes |  | Assuming a constant supply air temperature, as per MNECB 1997 | During mechanical cooling, supply air temperature is reset based upon the return air temperature and the outdoor air temperature to ensure the space does not overcool resulting in possible reheat energy. Savings are due to reduced mechanical cooling and some fan energy. Adjust the stages of cooling or the refrigerant valve in response to the return air temperature. Prevents over-cooling of space | Observed only DX cooling during audits |  | % of buildings or floor space this ECM applies to
18 | Cooling | Upgrade of compressors in cooling/air conditioning | Replace the compressors in cooling condensers and air conditioners with the latest energy efficient compressors. This saves on electricity. | no | overlap with replacement of cooling | OS | yes |  | Start with a COP of 2.5 in V3 and V4, and COP 3.0 in V1 and V2 based on typical MNECB 1997 values | Replacement of the AHU and RTU compressor only with a new scroll compressor (COP 4.0) using R-410A refrigerant. Existing compressors are assumed to be COP 2.5 for all pre-2004 buildings and COP 3.0 for all post-2004 buildings. | The average age of condensers is estimated to be 15 years old. | The cost to upgrade < 5 ton compressors was similar to replacing the entire outdoor section of a mini-split air conditioner. See ECM below | % of buildings or floor space this ECM applies to
19 | Cooling | Replacement of cooling section of an AHU or RTU. Or replacement of the whole RTU. | Replace the DX equipment (both the condenser section and evaporator coil) or an entire RTU with a new energy efficient model. Saves on heating, cooling and electricity through better COP, furnace efficiency and more advanced controls. | no | overlap with compressor upgrade | not modelled for Trenton. could be modelled in OS | We costed RTU total replacement, and AHU replacement. But equipment cost is likely to be similar for replacing only the DX section |  | Start with a COP of 2.5 in V3 and V4, and COP 3.0 in V1 and V2 based on typical MNECB 1997 values | Complete replacement of the direct expansion (DX) unit within an AHU or RTU, or replacing a DX/furnace RTU with a high efficiency unit. |  | Applies also to mini-split air conditioners: outdoor section would be replaced with a new higher COP model. Use the cost estimate from the compressor ECM above | % of buildings or floor space this ECM applies to | For RTUs an alternate to this ECM could be the Advanced RTU Controller 'Catalyst' that combines fan speed, economizer and DCV controls and saves 25% to 50%. The COP would not improve but everything else would.
20 | Building Envelope | Air tightening of the building envelope | Sealing or weather-stripping of roofs, walls, windows, doors, and all penetrations through the building envelope. This reduces cold air entering the building (infiltration) and warm air escaping (exfiltration). Saves on heating and cooling. | no | Reduces building heat loss, reducing impact of other heating ECMs | OS | yes |  | US Military study of blower door test results and modified to our vintages | Foaming of envelope penetrations and junctions, weather-stripping of doors to reduce leakage levels to 0.27 air changes per hour at normal pressure from the assumed leakage rates per vintage and building type. Pre-1960s buildings = 1.0 air changes per hour, 1960-1979 buildings = 0.6 air changes per hour, 1980-2004 buildings = 0.44 air changes per hour, post-2004 = 0.27 air changes per hour. If building type contained overhead doors, space containing overhead door assumed increased air leakage of 50%. |  | Is air leakage unknowingly being used for ventilation? Will a tighter building envelope affect air quality and create a need for more ventilation, thus costing more in equipment and fan power? | % of buildings or floor space this ECM applies to | A blower door test is required to determine actual conditions. Could draft proof and test buildings at the same time.
21 | REC Centre | Special/Unique ECMs for the REC Centre | Write up noting the typical measures and associated savings. Specific measures for Ice plant (floating compressor head control), IR camera for ice surface temperature, flood water treatment, pool pump turbidity-controlled VSPs, DCV during winter.ECMs that are unique to the REC Centre. The other ECMs on this sheet apply to the REC Centre. | yes |  | not modelled for Trenton. Will not model special/unique measures | no |  | MNECB, retrofit case studies, figures from Raymond’s previous study in a similar sized REC centre | same as short description | 570 kW demand noted during the audit | Rec Centre is approximately 9% of heated buildings floor area
22 | Centralized BAS Control | Control Centre for Building Automation Systems | Centralized monitoring and control of each building's BAS systems. | yes |  | not modelled | no |  | literature, case studies |  | The technician staff are interested in implementing this system before any building control-type ECMs are attempted. There would be poor acceptance without the ability to monitor the HVAC systems. There are already many comfort issues. There is resistance to alter the current control settings and not enough staff to implement, test and monitor. | Base should update the missing documentation on existing BAS systems. This would be a first step to undertaking a retro-commissioning program. Base recently hired companies to update controls in 3 buildings. MCW updated a lot of buildings controls in 2001. |  | We could cite the O&M benefits to EMS such as predictive maintenance, alarms. | Would a central BAS control save energy?

## District Heating
District Heating
Item | Canmet Energy's Assumptions and Questions | Buildings using Steam directly in their heating systems
Heating Network |  | Bldg No. | Building Name | 4 Wing please list the terminal heating equipment using steam
| · All network modelling will assume integration of a hot water distribution network (~110 °C design supply temperature), constructed over 3 phases: | H1 | Hangar 1
| Phase 1: connect to buildings currently supplied with steam from the CHP, and omitting any buildings slated to be demolished | B177 | F404 Engine Bay/Composite Bldg
| Phase 2/3: connect to buildings currently heated with individual gas-fired systems as seen practical, as well as future buildings to be constructed | H2 | Hangar 2
| · Piping assumed to be new, thin-walled steel district heating pipe (preinsulated, bonded) to be direct buried at approximately 1 metre below grade. | H4 | Hangar 4 | hangar door floor blast heaters , 2 steam coils
| · In an effort to generate conservative estimates for required network piping, analysis will be based upon the estimated base-case (pre-ECM) building heating loads and no diversity or simultaneity of network heating loads will be considered. | H3 | Hangar 3
|  | H6 | Hangar 6
Potential Central Heating Plant options |  | B171 | Supply Warehouse
| · New gas-fired hot water boilers. | B5 | WTN Garage
| · Investigate other alternative supply options including biomass boilers and cogeneration. | B7 | CE Main Bldg
| · Modelled plant to be located at or near the existing CHP building unless directed otherwise. | B63 | GSAR/Battery Shop/Supply
| · Modelled plant operation and fuel consumption analysis will factor estimated building energy reductions achieved through integration of building Energy Conservation Measures. | B66 | Supply Bldg
|  | B192 | GPV Garage
Building Network Interface |  | B8 | Exercise Support Office
| · New hot-water energy transfer stations consisting of one or more brazed-plate or flat plate heat exchangers will replace existing steam convertors in each connected building | B174 | CE Roads and Grounds Bldg
| · It is assumed that the district heating supply will provide both space heating and domestic water heating for each connected building | B81 | Electrical and Sheet Metal Shop
|  | B80 | Roundel Cleaners (NPF)
Questions for 4 Wing. Please answer below. |  | B10 | Standby Power Plant
| · Please confirm the buildings that are still using steam directly in terminal heating equipment. See list at right. Please name the terminal equipment that use steam coils. | B6 | RM Storage
|  | B128 | WOps EOD Centre # 19
· If known, please provide potential time horizon for any planned changes to the existing steam network and CHP
· Also confirm if there are any other specific buildings on the Base that should be excluded from the district heating system modelling?
· Do any of the buildings currently connected to the steam network have thermal meters installed? If so, can data be provided?
· Any additional directional information to consider in the analysis – items Cold Lake personnel would like to see included or not included in the analysis?

## Demolition and New Construction
Demolitions and New Construction
Planned for Demolition - 4 Wing please verify and update
Bld: PRIN Number | Bld: PRIN Name | Bld: PRIN Address | demo/replacement date
22122 | Hangar 1 | H1 - Hangar Lane | to be replaced 2022 w 5000 sq.ft.
22123 | Hangar 2 | H2 - Hangar Lane | to be replaced 2021 w 6000 sq.ft.
22124 | Hangar 3 | H3 - Hangar Lane | to be replaced 2019 w 6000 sq.ft.
22126 | Hangar 6 | H6 - Hangar Lane | to be replaced 2017 w 6000 sq.ft.
22129 | Fire Hall | B4 - Athabasca Road | to be demolished
22146 | Officers Mess | B20-Timberline Drive | to be demolished
22153 | NCO Mess | B30 - Queensway | to be demolished
22156 | All Ranks Mess | B40-Queensway | to be demolished
22157 | Club 41 | B41-Beaverlodge Road | to be demolished
22167 | RC Chapel | B53-Queensway | to be demolished
63089 | Maple Flag Quarters 1 or storage building | B165 - Kingsway | to be demolished
63090 | Maple Flag Quarters 2 or storage building | B166 - Kingsway | to be demolished
Planned New Buildings - 4 Wing please verify and update
construction year | name | location | gross floor area, sq.m | Does it replace an existing building?
2011 | 100 p. accomodation | beside trimess | 5000
2011 | 100 p. accomodation | beside trimess | 5000
2011 | 100 p. accomodation | beside trimess | 5000
2011 | school/daycare | @B82 | 7500
2012 | firehall | beside H7 | 1500
2012 | RTF | beside B84
2013 | trimess | between B20,30,40 | 4000
2013 | Canex | across from B69 | 10000
2014 | airport tower | south of H1 | 500
2014 | chapel |  | 600
2015 | 100 apartmt (750sq.ft ea) |  | 7500
2017 | Hangar 6 | H6 - Hangar Lane | 6000 | replaces Hangar 6
2019 | Hangar 3 | H3 - Hangar Lane | 6000 | replaces Hangar 3
2021 | Hangar 2 | H2 - Hangar Lane | 6000 | replaces Hangar 2
2022 | Hangar 1 | H1 - Hangar Lane | 5000 | replaces Hangar 1
Canmet Energy's Questions
Are there Energy intensity performance targets for new buildings?
Are any buildings anticipated to undergo major changes of use? If so, which ones, what will their use by changed to?

## Costs
Cost Assumtpions
Item | Canmet Energy's Assumptions and Values | 4 Wing Answers / Comments?
Utility Costs
historical rates | historical rates for electricity and natural gas were provided by DND
future rates | Carmal rate forecast for electricity. Gas Alberta forecast for natural gas
Labour Rates (to be used in Payback calculations)
electrician, plumbers, controls technician, insulation contractor, air sealing contractor, and all general labor | $60 per hour
design services | $100 per hour
4 Wing's Budget for Buildings and Infrastructure
Annual budget allocated for Building O&M | ?
Annual budget allocated for building and infrastructure renovations | ?
Annual budget allocated specifically for energy retrofits | ?
Annual budget allocated for new buildings and new infrastructure | ?
Projected annual growth rate of above budgets | ?
New
Projected utility rates for electricity, natural gas and other sources
broken down for each year of the planning horizon
Projected inflation for capital costs for retrofits
broken down for each year of the planning horizon
Projected emissions factors by energy source
May change for electricity due to anticipated supply mix
Planning Horizon
- what are the next two business cycles? (18-19 - 22-23) How many years does mid-long range planning on the base typically look out to?
Additional qualitative questions important for the planning context
- Specific environmental policies, targets or reports of which we should be aware?
- Is there any linkage between planning on the base and that being done in surrounding communities?
- Level of senior level buy-in for energy efficiency/renewable energy technology measures?
- Perception of acceptance of energy efficiency/renewable energy technology measures by Base personell?

## Planning
Planning for Buildings and Infrastructure
Item | Canmet Energy Assumptions and Values | 4 Wing Answers / Comments?
Planning Horizon
What are 4 Wing's five year business cycles? (2018-19, 2022-23?) | ?
How many years does mid-long range planning for 4 Wing typically look out to? | ?
GHG Emissions
Federal Sustainable Development Strategy GHG reporting data back to 2005-06 (GHG emissions baseline year). Does 4 Wing have this data? | ?
Planning and Environmental Policies
Relevant Policies. Are there other policies, not listed here, related to planning, environment or energy? | Canada First Defence Strategy, Defence Renewal Charter, 4 Wing Mission and Vision, Federal Sustainable Development Strategy, Pan-Air Force Environmental Sustainability Plan, Air Force Sustainability Office Five Year Plan, Defence Operational Energy Strategy, Canadian Armed Forces Administrative Order 29-7
How does 4 Wing interact/co-ordinate with the Cold Lake community for its land use or other planning? How are Cold Lake community plans linked with 4 Wing's plans? | ?
Who are the Officers at 4 Wing who are responsible for or handle energy efficiency and GHG emissions? | ?

## Project team - assumptions
Cold Lake modelling assumptions
Weather file | Edmonton CWEC
Use CWEC; perhaps do a comparison to year using for analysis
Occupancy
Loads | MNECB defaults; adjusted for actual occupancy as per audit
Schedule | Actual as per audit or MNECB
Envelope | R values by building type and vintage (see sheet 'Cold Lake R-values') | scripting
Use metal cladding construction
Set R-values for trailer archeype (not based on vintage) (see sheet 'Cold Lake R-values')
no wall retrofit measures (based on trenton, not cost-effective), perhaps only roof ecms
Infiltration | Rate by building type and vintage (see sheet 'Infiltration Assumptions') | scripting
bay doors | increase infiltration rate by 50% when doors are opened (see audit info)
Lighting
Loads | MNECB defaults; some audit information available | Question: ask base contact about when lighting retrofits were done; provide MNECB default and ask if that is in the ball park.
Heat to space | Set based on building type; to be determined | Check if detailed lighting plans available for exemplar buildings; need to check if these were implemented
Schedule | Same as occupancy schedule as per audit or MNECB default by space type
Equipment
Loads | MNECB defaults; do we take into account loads in server rooms? | no; we will not tackle process loads
Schedule | MNECB defaults
HVAC
heating system capacity | auto-sized
cooling system capacity | auto-sized
cooling | for spaces with occupants only (example offices, but not storage spaces); set up systems appropriately (system with no cooling for zones with no cooling)
combine HVAC systems | yes
modify HVAC system by vintage | no
put cooling in exemplar with no cooling if other buildings for this archetype have cooling
economizers | assume in all base case models for buildings with cooling
exhaust fans | explicitly model. This is necessary if we look at exhaust fan ecm - modify exhaust fan schedule to determine impact.
humidification/dehumidification | no for humidification; dehumidification accounted for by cooling
ventilation | MNECB outdoor air per person rates
heating setpoint | Set to 20C
cooling setpoint | Set to 24C
temperature setback | not in base model
boiler with outdoor air reset | not in base model; consider as ECM | assumed to exist in DES heated buildings
boiler capacity | auto-sized
boiler efficiency | actual if available, 80% for DES systems
boiler setpoint | 82C | script
des | Des represented by boiler with 80% efficiency
HVAC system heating efficiency | actual, if available or use 80% default
HVAC system cooling efficiency | vintage COP: 2.5 for systems pre-1980; 3.0 for 1980-2004; 3.5 post-2004 | script; set base model to 2.5
fan schedule | as per audit; if no information assume always on
fan motor efficiency | see | script
fan type | constant
hvac ventilation schedule | always on
hvac night control | assume zone thermal units (if applicable) can cycle on to meet heating setpoint
pump motor efficiency | by vintage; see Mike | script
pump type | constant single-speed
system heating sizing factor | 1.1 | script
system cooling sizing factor | 1.25 | script
zone heating sizing factor | 1 | script
zone cooling sizing factor | 1 | script
plant heating sizing factor | 1.3 | script
SWH
peak flow | based on MNECB default of W/person, actual occupancy and 44C temperature difference
water tank capacity | default size
water tank efficiency | actual if available otherwise 80% for fuel-fired; 100% for electric (standby losses taken into account separately)
schedule | based on default for predominant MNECB space type
water heater pump | constant
fuel type | based on audit
hot water setpoint temperature | 60C | script
Utility costs | use time of use rate for one base case model- office; compare to result with average rate
rates, see Matthew
take into account demand and consumption charges
Simulation outputs
Yearly
load versus consumption | EUI based on energy (versus consumption); analysis will use load values and assume system efficiency
also compile #s based on consumption to compare
EUI | by end-use/fuel-source
Hourly |  | scripting
Cooling Coil Total Cooling Rate
Cooling Coil Electric Power
Heating Coil Air Heating Rate
Heating Coil Heating Rate
Heating Coil Gas Rate
District Heating Hot Water Rate
District Heating Rate
Water Heater Heating Rate
Water Heater Gas Rate
Water Heater Electric rate
Plant Supply Side Heating Demand Rate
Boiler Gas Rate
Facility Total HVAC Electric Demand Power
Facility Total Electric Demand Power
Zone Air Temperature
Demand | once ecm package is finalized, re-run archetypes to get combined demand/energy savings
Exempler model verification | do not reconcile exemplar with metered data at this point; may do this once all archetypes rolled up at base level
electric meter | tolerance? | example: | B688 ammunition maintenance facility
natural gas meter | tolerance? |  | electricity | natural gas
compare to trenton EUI for same building type? |  | metered | 278-368 GJ | 1023-1492 GJ
|  | simulation | 328 GJ | 689 GJ | note this is for setpoint 18C
baseline year | 2013-14 if utility data available for this fiscal year |  |  | 882 GJ | if setpoint is changed to 20C
Firehall archetype | use Trenton archetype and run with Edmonton weather data
B172 CF18 Training archetype | use Trenton archetype and run with Edmonton weather data
ECMs
Individual ECMs | see sheet ''
payback
combinations
Applying ECMs
applying ECM modelling results to buildings corresponding to archetype/vintage based on percentage | different percentages for more aggressive scenarios
New construction | assume no new construction

## Infiltration Rates
Air Leakage (Infiltration) Rate Assumptions
Units are = m3/s/m2
Infiltration Building Type | 2005-2014 | 1980-2004 | 1960-1979 | 1959-pre
Air Terminal | 0.0002 | 0.00035 | 0.0005 | 0.0007
Communications & Control | 0.0002 | 0.00035 | 0.0005 | 0.0007
Control Tower | 0.0002 | 0.00035 | 0.0005 | 0.0007
Fire Hall | 0.0003 | 0.00045 | 0.00075 | 0.0008
Fitness & Rec. - Arena | 0.0002 | 0.00035 | 0.0005 | 0.0007
Fitness & Rec. - Multi-gym | 0.0002 | 0.00035 | 0.0005 | 0.0007
Fitness & Rec. - Pool | 0.0002 | 0.00035 | 0.0005 | 0.0007
Food Services | 0.0002 | 0.00035 | 0.0005 | 0.0007
Hangars | 0.0003 | 0.00045 | 0.00075 | 0.0008
Infrastructure | 0.0003 | 0.00045 | 0.00075 | 0.0008
Medical Facilities | 0.0002 | 0.00035 | 0.0005 | 0.0007
Misc. Bldgs < 100m2 | 0.0002 | 0.00035 | 0.0005 | 0.0007
Mobile Prefab Buildings | 0.0002 | 0.00035 | 0.0005 | 0.0007
Motel Type Residences | 0.0002 | 0.00035 | 0.0005 | 0.0007
Museum | 0.0002 | 0.00035 | 0.0005 | 0.0007
Offices | 0.0002 | 0.00035 | 0.0005 | 0.0007
Recreational / Club Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Religious Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Retail Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Sleeping barracks | 0.0002 | 0.00035 | 0.0005 | 0.0007
Storage Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Training Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
University Dormitory Type | 0.0002 | 0.00035 | 0.0005 | 0.0007
Warehouses | 0.0003 | 0.00045 | 0.00075 | 0.0008
Workshops | 0.0003 | 0.00045 | 0.00075 | 0.0008
Note on K35: mlubun: ASHRAE 90.1 1999 value
Note on G37: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I37: mlubun: 50% increase in ACH and leakage due to door openings
Note on K37: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M37: mlubun: 50% increase on ACH and leakage due to door openings
Note on G39: mlubun: 50% increase due to hanger door openings
Note on I39: mlubun: 50% increase in ACH and leakage due to door openings
Note on K39: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M39: mlubun: 50% increase on ACH and leakage due to door openings
Note on G45: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I45: mlubun: 50% increase in ACH and leakage due to door openings
Note on K45: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M45: mlubun: 50% increase on ACH and leakage due to door openings
Note on K57: mlubun: ASHRAE 90.1 1999 value
Note on G59: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I59: mlubun: 50% increase in ACH and leakage due to door openings
Note on K59: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M59: mlubun: 50% increase on ACH and leakage due to door openings
Note on G62: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I62: mlubun: 50% increase in ACH and leakage due to door openings
Note on K62: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M62: mlubun: 50% increase on ACH and leakage due to door openings
Note on M69: building renovated in 2005.
Note on G71: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I71: mlubun: 50% increase in ACH and leakage due to door openings
Note on K71: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M71: mlubun: 50% increase on ACH and leakage due to door openings
Note on G72: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I72: mlubun: 50% increase in ACH and leakage due to door openings
Note on K72: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M72: mlubun: 50% increase on ACH and leakage due to door openings
Note on G77: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I77: mlubun: 50% increase in ACH and leakage due to door openings
Note on K77: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M77: mlubun: 50% increase on ACH and leakage due to door openings

## Indexes
building_type | building_source | model_file_name
Barracks | B45 | barracks.osm
Fire Hall | Trenton FH B19 | fire_hall.osm
Food Service | B40 | food_service.osm
Hangar | Hangar 4 | hangar.osm
Maintenance Shop | B581 | maintenance_shop.osm
Maintenance Shop-Small | B688 | maintenance_shop_small.osm
Office | B007 | office.osm
Office-Small | B96(Trailer) | office_small.osm
Recreation Center | B720 | recreation_center.osm
Storage Building | B782 | storage_building.osm
Training Building | Trenton Training B34 | training_building.osm
Vehicle Garage | B624 | vehicle_garage.osm
Cold Lake Vintages
1959-pre
1960-1979
1980-2004
2005-2014
BTAP Construction Sets
NA
DND-Concrete
DND-Metal
Boiler Fuel Types
Coal
Diesel
DistrictHeating
Electricity
FuelOil#1
FuelOil#2
Gasoline
NA
NaturalGas
OtherFuel1
OtherFuel2
PropaneGas
SHW Fuel Types
Coal
Diesel
DistrictHeating
Electricity
FuelOil#1
FuelOil#2
Gasoline
NA
NaturalGas
OtherFuel1
OtherFuel2
PropaneGas
Stream

## Equipment_Efficiencies
Reference Info | 1959-pre | 1960-1979 | 1980-2004 | 2005-2014
fan_motor_eff | 0.75 | 0.823 | 0.879 | 0.879
fan_total_eff | 0.75 | 0.75 | 0.75 | 0.8
cop | 2.5 | 2.5 | 3 | 3.5
pump_eff | 0.7 | 0.7 | 0.7 | 0.7
Note on A1: Lopez, Phylroy: Vintage 4 Vintage 3 Vintage 2 Vintage 1 Pre-1960 1960-1979 1980-2004 post-2004 Motor Efficiency 75 (1) 82.3 (2) 87.9 (3) 87.9 (4) Fan Efficiency 75 (5) 75 (5) 75 (5) 80 (5) Pump Efficiency 70 (6) 70 (6) 70 (6) 70 (6) (1) = estimated (2) = average efficiency of “typical” standard efficiency motors as defined in table 12-9 of NEMA MG 1-1993 of nominal full load efficiency for 4 pole enclosed motors of 1 to 25 hp ratings (3) = average efficiency of ASHRAE 90.1 1999 Standard (pg 55) of nominal full load efficiency for 4 pole enclosed motors of 1 to 25 hp ratings (4) = average efficiency of ASHRAE 90.1 2007 Standard (pg 65) of nominal full load efficiency for 4 pole enclosed motors of 1 to 25 hp ratings (5) fan efficiencies depend on the pressure rise and flow and the type of fan. The rated flow will be used for the fan efficiencies for forward curved fans (60-75%), radial fans (69-75%), backward inclined and airfoil fans (75-80%), vane axial (78-85%), tube axial (67-72%), propeller axial (45-50%). Backward inclined fans are the most common in HVAC equipment. (6) pump efficiencies vary by the flow, type of pump and size. For centrifugal pumps, a 2-4 kW motor would have any efficiency of 55-65%, a 5-7.5 kW motor would have an efficiency of 60-70%, a 10-22 kW motor would have an efficiency of 65-75% and a 30-45 kW motor would have an efficiency of 70-80%

## Schedules
schedule_name | schedule_string
heating_always_21C | {"sch": { "name":"always_21C", "type":"TEMPERATURE", "period_rules": [ { "start":"Jan-31", "end":"Dec-31", "day_rules": [ { "days" :"M,T,W,T,F,S,SN", "hour_rules": [ { "value":"21.0", "until":"24:00" } ] } ] } ] } }
cooling_always_24C | {"sch": { "name":"always_24C", "type":"TEMPERATURE", "period_rules": [ { "start":"Jan-31", "end":"Dec-31", "day_rules": [ { "days" :"M,T,W,T,F,S,SN", "hour_rules": [ { "value":"24.0", "until":"24:00" } ] } ] } ] } }
shw_60C | {"sch": { "name":"shw_60C", "type":"TEMPERATURE", "period_rules": [ { "start":"Jan-31", "end":"Dec-31", "day_rules": [ { "days" :"M,T,W,T,F,S,SN", "hour_rules": [ { "value":"60.0", "until":"24:00" } ] } ] } ] } }
heating_always_20C | {"sch": { "name":"always_21C", "type":"TEMPERATURE", "period_rules": [ { "start":"Jan-31", "end":"Dec-31", "day_rules": [ { "days" :"M,T,W,T,F,S,SN", "hour_rules": [ { "value":"20.0", "until":"24:00" } ] } ] } ] } }

## baseline
baseline_index |  | building_type | vintage_name | measure_id | base_model_rel_path | weather_file_rel_path | building_source | building_floor_area | actual_floor_area | library_file | heating_schedule_name | cooling_schedule_name | default_construction_set_name | ext_wall_rsi | ext_floor_rsi | ext_roof_rsi | ground_floor_rsi | ground_wall_rsi | ground_roof_rsi | fixed_window_rsi | operable_window_rsi | door_construction_rsi | glass_door_rsi | overhead_door_rsi | infiltration_building_type | infiltration_flow_per_exterior_area | cop | fan_volume_type | fan_motor_eff | fan_total_eff | pump_motor_eff | pump_speed_type | pump_control_type | erv_enabled | economizer_control_type | economizer_control_action_type | economizer_maximum_limit_dry_bulb_temperature | economizer_maximum_limit_enthalpy | economizer_maximum_limit_dewpoint_temperature | economizer_minimum_limit_dry_bulb_temperature | dcv_enabled | heating_sizing_factor | cooling_sizing_factor | zone_heating_sizing_factor | zone_cooling_sizing_factor | shw_setpoint_sched_name | shw_heating_type | shw_thermal_eff | hw_boiler_fuel_type | hw_boiler_design_water_outlet_temperature | hw_boiler_thermal_eff | lighting_fraction_radiant | lighting_fraction_visible | lighting_return_air_fraction | elec_equipment_fraction_radiant | elec_equipment_fraction_latent | elec_equipment_fraction_lost | cost_per_building
NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0
1 | 4c | Barracks | 1959-pre | baseline | resources/barracks.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B45 | 5495.7246 | 3989 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 3.1701 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Motel Type Residences | 0.0007 | 2.5 | NA | 0.75 | 0.75 | 0.7 | VariableSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.72 | 0.18 | 0 | 0.3 | 0 | 0 | 0
2 | 13b | Fire Hall | 1959-pre | baseline | resources/fire_hall.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | Trenton FH B19 | 911.7335 | 911.7335 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 3.1701 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Fire Hall | 0.0008 | 2.5 | NA | 0.75 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
3 | 7a | Food Service | 1959-pre | baseline | resources/food_service.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B40 | 2693.605 | 2568 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 3.5224 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Food Services | 0.0007 | 2.5 | NA | 0.75 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
4 | 7a | Food Service | 2005-2014 | baseline | resources/food_service.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B40 | 2693.605 | 2568 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 5.2836 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Food Services | 0.0002 | 3.5 | NA | 0.879 | 0.8 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.72 | 0.18 | 0 | 0.4 | 0.3 | 0 | 0
5 | 1a | Hangar | 1959-pre | baseline | resources/hangar.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | Hangar 4 | 6276.5798 | 6423 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 1.4089 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Hangars | 0.0008 | 2.5 | NA | 0.75 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
6 | 1a | Hangar | 1960-1979 | baseline | resources/hangar.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | Hangar 4 | 6276.5798 | 6423 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 2.1134 | 1.7612 | 1.7612 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | Hangars | 0.00075 | 2.5 | NA | 0.823 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
7 | 1a | Hangar | 1980-2004 | baseline | resources/hangar.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | Hangar 4 | 6276.5798 | 6423 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 3.5224 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Hangars | 0.00045 | 3 | NA | 0.879 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
8 | 9a | Maintenance Shop | 1959-pre | baseline | resources/maintenance_shop.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B581 | 2388.545 | 1927 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 0.88059 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Workshops | 0.0008 | 2.5 | NA | 0.75 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
9 | 9a | Maintenance Shop | 1980-2004 | baseline | resources/maintenance_shop.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B581 | 2388.545 | 1927 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 3.1701 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Workshops | 0.00045 | 3 | NA | 0.879 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
10 | 9b | Maintenance Shop-Small | 1959-pre | baseline | resources/maintenance_shop_small.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B688 | 923.718 | 927 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 0.88059 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Workshops | 0.0008 | 2.5 | NA | 0.75 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.37 | 0.18 | 0.44 | 0.3 | 0 | 0 | 0
11 | 9b | Maintenance Shop-Small | 1960-1979 | baseline | resources/maintenance_shop_small.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B688 | 923.718 | 927 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 1.7612 | 1.4089 | 1.4089 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | Workshops | 0.00075 | 2.5 | NA | 0.823 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
12 | 9b | Maintenance Shop-Small | 1980-2004 | baseline | resources/maintenance_shop_small.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B688 | 923.718 | 927 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 3.1701 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Workshops | 0.00045 | 3 | NA | 0.879 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
13 | 6a | Office | 1959-pre | baseline | resources/office.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B007 | 3418.6207 | 3418.6207 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 1.7612 | 2.8179 | 2.8179 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Offices | 0.0007 | 2.5 | NA | 0.75 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.37 | 0.18 | 0.44 | 0.3 | 0 | 0 | 0
14 | 6a | Office | 1960-1979 | baseline | resources/office.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B007 | 3418.6207 | 3418.6207 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 1.7612 | 1.4089 | 1.4089 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | Offices | 0.0005 | 2.5 | NA | 0.823 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.37 | 0.18 | 0.44 | 0.3 | 0 | 0 | 0
15 | 6a | Office | 1980-2004 | baseline | resources/office.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B007 | 3418.6207 | 3418.6207 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 3.5224 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Offices | 0.00035 | 3 | NA | 0.879 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.37 | 0.18 | 0.44 | 0.3 | 0 | 0 | 0
16 | 6b | Office-Small | 1960-1979 | baseline | resources/office_small.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B96(Trailer) | 1211.4622 | 584 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 1.7612 | 1.4089 | 1.4089 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | Offices | 0.0005 | 2.5 | NA | 0.823 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.37 | 0.18 | 0.44 | 0.3 | 0 | 0 | 0
17 | 6b | Office-Small | 1980-2004 | baseline | resources/office_small.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B96(Trailer) | 1211.4622 | 584 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 3.5224 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Offices | 0.00035 | 3 | NA | 0.879 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.37 | 0.18 | 0.44 | 0.3 | 0 | 0 | 0
18 | 6b | Office-Small | 2005-2014 | baseline | resources/office_small.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B96(Trailer) | 1211.4622 | 584 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 5.2836 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Offices | 0.0002 | 3.5 | NA | 0.879 | 0.8 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
19 | 5a | Recreation Center | 1980-2004 | baseline | resources/recreation_center.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B720 | 12612.7339 | 12612.7339 | resources/btap_construction_library.osm | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Fitness & Rec. - Multi-gym | 0.00035 | 3 | NA | 0.879 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
20 | 3b | Storage Building | 1959-pre | baseline | resources/storage_building.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B782 | 965.1569 | 1171 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 0.88059 | 3.5224 | 3.5224 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Storage Bldgs | 0.0007 | 2.5 | NA | 0.75 | 0.75 | 0.7 | VariableSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.37 | 0.18 | 0.44 | 0.3 | 0 | 0 | 0
21 | 3b | Storage Building | 1960-1979 | baseline | resources/storage_building.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B782 | 965.1569 | 1171 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 1.9373 | 1.5851 | 1.5851 | 1.2328 | 1.2328 | 1.2328 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.5851 | Storage Bldgs | 0.0005 | 2.5 | NA | 0.823 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
22 | 3b | Storage Building | 1980-2004 | baseline | resources/storage_building.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B782 | 965.1569 | 1171 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 2.6418 | 3.5224 | 3.5224 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Storage Bldgs | 0.00035 | 3 | NA | 0.879 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
23 | 3b | Storage Building | 2005-2014 | baseline | resources/storage_building.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B782 | 965.1569 | 1171 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 5.2836 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Storage Bldgs | 0.0002 | 3.5 | NA | 0.879 | 0.8 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
24 | 2a | Training Building | 1959-pre | baseline | resources/training_building.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | Trenton Training B34 | 3699.8929 | 3699.8929 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 1.7612 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Training Bldgs | 0.0007 | 2.5 | NA | 0.75 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
25 | 2a | Training Building | 1980-2004 | baseline | resources/training_building.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | Trenton Training B34 | 3699.8929 | 3699.8929 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 3.5224 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Training Bldgs | 0.00035 | 3 | NA | 0.879 | 0.75 | 0.7 | VariableSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.37 | 0.18 | 0.44 | 0.3 | 0 | 0 | 0
26 | 2a | Training Building | 2005-2014 | baseline | resources/training_building.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | Trenton Training B34 | 3699.8929 | 3699.8929 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 5.2836 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Training Bldgs | 0.0002 | 3.5 | NA | 0.879 | 0.8 | 0.7 | VariableSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.37 | 0.18 | 0.44 | 0.3 | 0 | 0 | 0
27 | 8a | Vehicle Garage | 1959-pre | baseline | resources/vehicle_garage.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B624 | 3744.5971 | 2270 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 1.7612 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Hangars | 0.0008 | 2.5 | NA | 0.75 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.72 | 0.18 | 0 | 0.4 | 0.3 | 0 | 0
28 | 8a | Vehicle Garage | 1980-2004 | baseline | resources/vehicle_garage.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B624 | 3744.5971 | 2270 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 2.6418 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Hangars | 0.00045 | 3 | NA | 0.879 | 0.75 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
29 | 1a | Hangar | 2005-2014 | baseline | resources/hangar.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | Hangar 4 | 6276.5798 | 6423 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 5.2836 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Hangars | 0.0003 | 3.5 | NA | 0.879 | 0.8 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
30 | 4c | Barracks | 2005-2014 | baseline | resources/barracks.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | B45 | 5495.7246 | 3989 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 5.2836 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Motel Type Residences | 0.0002 | 3.5 | NA | 0.879 | 0.8 | 0.7 | VariableSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
31 | 13b | Fire Hall | 2005-2014 | baseline | resources/fire_hall.osm | resources/CAN_AB_Edmonton.711230_CWEC.epw | Trenton FH B19 | 911.7335 | 911.7335 | resources/btap_construction_library.osm | heating_always_20C | cooling_always_24C | DND-Concrete | 5.2836 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Fire Hall | 0.0003 | 3.5 | NA | 0.879 | 0.8 | 0.7 | ConstantSpeed | Intermittent | FALSE | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | FALSE | 1.1 | 1.25 | 1 | 1 | shw_60C | NA | NA | NA | 82 | 0.8 | 0.42 | 0.18 | 0 | 0.3 | 0 | 0 | 0
Note on Y1: Lopez, Phylroy: Used for Hanger doors
Note on BD3: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD4: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD5: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD6: Lubun, Mike: from ashrae (varies between 20-60% accoridng to handbook and types of euipment
Note on BD7: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD8: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD9: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD10: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD11: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD12: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD13: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD14: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD15: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD16: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD17: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD18: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD19: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD20: Lubun, Mike: no data just a guess
Note on BD21: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD22: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD23: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD24: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD25: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD26: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD27: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD28: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD29: Lubun, Mike: from ashrae (varies between 30-60% accoridng to handbook and types of euipment
Note on BD30: Lubun, Mike: from ashrae (varies between 10-37% accoridng to handbook and types of euipment
Note on BD31: Lubun, Mike: no data just a guess
Note on BD32: Lubun, Mike: no data just a guess
Note on BD33: Lubun, Mike: no data just a guess

## ecm_cold_deck_reset_control
baseline_index | building_type | vintage_name | measure_id | cold_deck_reset_enabled | cold_deck_reset_max_supply_air_temp | cold_deck_reset_min_supply_air_temp | cost_per_building
NA | Barracks | 1959-pre | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 10864
2 | Fire Hall | 1959-pre | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 3621
3 | Food Service | 1959-pre | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 14485
4 | Food Service | 2005-2014 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 14485
5 | Hangar | 1959-pre | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 7243
6 | Hangar | 1960-1979 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 7243
7 | Hangar | 1980-2004 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 7243
8 | Maintenance Shop | 1959-pre | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 3621
9 | Maintenance Shop | 1980-2004 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 3621
10 | Maintenance Shop-Small | 1959-pre | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 3621
11 | Maintenance Shop-Small | 1960-1979 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 3621
12 | Maintenance Shop-Small | 1980-2004 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 3621
13 | Office | 1959-pre | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 18106
14 | Office | 1960-1979 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 18106
15 | Office | 1980-2004 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 18106
16 | Office-Small | 1960-1979 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 14485
17 | Office-Small | 1980-2004 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 14485
18 | Office-Small | 2005-2014 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 14485
19 | Recreation Center | 1980-2004 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 32591
20 | Storage Building | 1959-pre | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 0
21 | Storage Building | 1960-1979 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 0
22 | Storage Building | 1980-2004 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 0
23 | Storage Building | 2005-2014 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 0
24 | Training Building | 1959-pre | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 14485
25 | Training Building | 1980-2004 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 14485
26 | Training Building | 2005-2014 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 14485
27 | Vehicle Garage | 1959-pre | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 9315
28 | Vehicle Garage | 1980-2004 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 9315
NA | Barracks | 1960-1979 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 10864
NA | Barracks | 1980-2004 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 10864
30 | Barracks | 2005-2014 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 10864
NA | Fire Hall | 1960-1979 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 3621
NA | Fire Hall | 1980-2004 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 3621
31 | Fire Hall | 2005-2014 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 3621
NA | Food Service | 1960-1979 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 14485
NA | Food Service | 1980-2004 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 14485
29 | Hangar | 2005-2014 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 7243
NA | Maintenance Shop | 1960-1979 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 3621
NA | Maintenance Shop | 2005-2014 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 3621
NA | Maintenance Shop-Small | 2005-2014 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 3621
NA | Office | 2005-2014 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 18106
NA | Office-Small | 1959-pre | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 14485
NA | Recreation Center | 1959-pre | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 32591
NA | Recreation Center | 1960-1979 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 32591
NA | Recreation Center | 2005-2014 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 32591
NA | Training Building | 1960-1979 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 14485
NA | Vehicle Garage | 1960-1979 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 9315
NA | Vehicle Garage | 2005-2014 | ecm_cold_deck_reset_control | TRUE | 20 | 13 | 9315

## ecm_cop
baseline_index | building_type | vintage_name | measure_id | cop | cost_per_building
1 | Barracks | 1959-pre | cooling_cop_3_0 | 3.5 | 15263
2 | Fire Hall | 1959-pre | cooling_cop_3_0 | 3.5 | 10120
3 | Food Service | 1959-pre | cooling_cop_3_0 | 3.5 | 20350
4 | Food Service | 2005-2014 | cooling_cop_3_0 | 3.5 | 20350
5 | Hangar | 1959-pre | cooling_cop_3_0 | 3.5 | 16588
6 | Hangar | 1960-1979 | cooling_cop_3_0 | 3.5 | 16588
7 | Hangar | 1980-2004 | cooling_cop_3_0 | 3.5 | 16588
8 | Maintenance Shop | 1959-pre | cooling_cop_3_0 | 3.5 | 5088
9 | Maintenance Shop | 1980-2004 | cooling_cop_3_0 | 3.5 | 5088
10 | Maintenance Shop-Small | 1959-pre | cooling_cop_3_0 | 3.5 | 10350
11 | Maintenance Shop-Small | 1960-1979 | cooling_cop_3_0 | 3.5 | 10350
12 | Maintenance Shop-Small | 1980-2004 | cooling_cop_3_0 | 3.5 | 10350
13 | Office | 1959-pre | cooling_cop_3_0 | 3.5 | 20700
14 | Office | 1960-1979 | cooling_cop_3_0 | 3.5 | 20700
15 | Office | 1980-2004 | cooling_cop_3_0 | 3.5 | 20700
16 | Office-Small | 1960-1979 | cooling_cop_3_0 | 3.5 | 17250
17 | Office-Small | 1980-2004 | cooling_cop_3_0 | 3.5 | 17250
18 | Office-Small | 2005-2014 | cooling_cop_3_0 | 3.5 | 17250
19 | Recreation Center | 1980-2004 | cooling_cop_3_0 | 3.5 | 44675
20 | Storage Building | 1959-pre | NA | NA | NA
21 | Storage Building | 1960-1979 | NA | NA | NA
22 | Storage Building | 1980-2004 | NA | NA | NA
23 | Storage Building | 2005-2014 | NA | NA | NA
24 | Training Building | 1959-pre | cooling_cop_3_0 | 3.5 | 20350
25 | Training Building | 1980-2004 | cooling_cop_3_0 | 3.5 | 20350
26 | Training Building | 2005-2014 | cooling_cop_3_0 | 3.5 | 20350
27 | Vehicle Garage | 1959-pre | NA | NA | NA
28 | Vehicle Garage | 1980-2004 | NA | NA | NA
NA | Barracks | 1960-1979 | cooling_cop_3_0 | 3.5 | 15263
NA | Barracks | 1980-2004 | cooling_cop_3_0 | 3.5 | 15263
30 | Barracks | 2005-2014 | cooling_cop_3_0 | 3.5 | 15263
NA | Fire Hall | 1960-1979 | cooling_cop_3_0 | 3.5 | 10120
NA | Fire Hall | 1980-2004 | cooling_cop_3_0 | 3.5 | 10120
31 | Fire Hall | 2005-2014 | cooling_cop_3_0 | 3.5 | 10120
NA | Food Service | 1960-1979 | cooling_cop_3_0 | 3.5 | 20350
NA | Food Service | 1980-2004 | cooling_cop_3_0 | 3.5 | 20350
29 | Hangar | 2005-2014 | cooling_cop_3_0 | 3.5 | 16588
NA | Maintenance Shop | 1960-1979 | cooling_cop_3_0 | 3.5 | 5088
NA | Maintenance Shop | 2005-2014 | cooling_cop_3_0 | 3.5 | 5088
NA | Maintenance Shop-Small | 2005-2014 | cooling_cop_3_0 | 3.5 | 10350
NA | Office | 2005-2014 | cooling_cop_3_0 | 3.5 | 20700
NA | Office-Small | 1959-pre | cooling_cop_3_0 | 3.5 | 17250
NA | Recreation Center | 1959-pre | cooling_cop_3_0 | 3.5 | 44675
NA | Recreation Center | 1960-1979 | cooling_cop_3_0 | 3.5 | 44675
NA | Recreation Center | 2005-2014 | cooling_cop_3_0 | 3.5 | 44675
NA | Training Building | 1960-1979 | cooling_cop_3_0 | 3.5 | 20350
NA | Vehicle Garage | 1960-1979 | NA | NA | NA
NA | Vehicle Garage | 2005-2014 | NA | NA | NA

## ecm_dcv
baseline_index | building_type | vintage_name | measure_id | dcv_enabled | cost_per_building
1 | Barracks | 1959-pre | dcv_enabled | TRUE | 64275
2 | Fire Hall | 1959-pre | dcv_enabled | TRUE | 8668
3 | Food Service | 1959-pre | dcv_enabled | TRUE | 7713
4 | Food Service | 2005-2014 | dcv_enabled | TRUE | 7713
5 | Hangar | 1959-pre | dcv_enabled | TRUE | 65989
6 | Hangar | 1960-1979 | dcv_enabled | TRUE | 65989
7 | Hangar | 1980-2004 | dcv_enabled | TRUE | 65989
8 | Maintenance Shop | 1959-pre | dcv_enabled | TRUE | 9427
9 | Maintenance Shop | 1980-2004 | dcv_enabled | TRUE | 9427
10 | Maintenance Shop-Small | 1959-pre | dcv_enabled | TRUE | 7713
11 | Maintenance Shop-Small | 1960-1979 | dcv_enabled | TRUE | 7713
12 | Maintenance Shop-Small | 1980-2004 | dcv_enabled | TRUE | 7713
13 | Office | 1959-pre | dcv_enabled | TRUE | 43707
14 | Office | 1960-1979 | dcv_enabled | TRUE | 43707
15 | Office | 1980-2004 | dcv_enabled | TRUE | 43707
16 | Office-Small | 1960-1979 | dcv_enabled | TRUE | 13712
17 | Office-Small | 1980-2004 | dcv_enabled | TRUE | 13712
18 | Office-Small | 2005-2014 | dcv_enabled | TRUE | 13712
19 | Recreation Center | 1980-2004 | dcv_enabled | TRUE | 27424
20 | Storage Building | 1959-pre | dcv_enabled | TRUE | 857
21 | Storage Building | 1960-1979 | dcv_enabled | TRUE | 857
22 | Storage Building | 1980-2004 | dcv_enabled | TRUE | 857
23 | Storage Building | 2005-2014 | dcv_enabled | TRUE | 857
24 | Training Building | 1959-pre | dcv_enabled | TRUE | 35137
25 | Training Building | 1980-2004 | dcv_enabled | TRUE | 35137
26 | Training Building | 2005-2014 | dcv_enabled | TRUE | 35137
27 | Vehicle Garage | 1959-pre | dcv_enabled | TRUE | 8750
28 | Vehicle Garage | 1980-2004 | dcv_enabled | TRUE | 8750
NA | Barracks | 1960-1979 | dcv_enabled | TRUE | 64275
NA | Barracks | 1980-2004 | dcv_enabled | TRUE | 64275
30 | Barracks | 2005-2014 | dcv_enabled | TRUE | 64275
NA | Fire Hall | 1960-1979 | dcv_enabled | TRUE | 8668
NA | Fire Hall | 1980-2004 | dcv_enabled | TRUE | 8668
31 | Fire Hall | 2005-2014 | dcv_enabled | TRUE | 8668
NA | Food Service | 1960-1979 | dcv_enabled | TRUE | 7713
NA | Food Service | 1980-2004 | dcv_enabled | TRUE | 7713
29 | Hangar | 2005-2014 | dcv_enabled | TRUE | 65989
NA | Maintenance Shop | 1960-1979 | dcv_enabled | TRUE | 9427
NA | Maintenance Shop | 2005-2014 | dcv_enabled | TRUE | 9427
NA | Maintenance Shop-Small | 2005-2014 | dcv_enabled | TRUE | 7713
NA | Office | 2005-2014 | dcv_enabled | TRUE | 43707
NA | Office-Small | 1959-pre | dcv_enabled | TRUE | 13712
NA | Recreation Center | 1959-pre | dcv_enabled | TRUE | 27424
NA | Recreation Center | 1960-1979 | dcv_enabled | TRUE | 27424
NA | Recreation Center | 2005-2014 | dcv_enabled | TRUE | 27424
NA | Training Building | 1960-1979 | dcv_enabled | TRUE | 35137
NA | Vehicle Garage | 1960-1979 | dcv_enabled | TRUE | 8750
NA | Vehicle Garage | 2005-2014 | dcv_enabled | TRUE | 8750

## ecm_economizers
baseline_index | building_type | vintage_name | measure_id | economizer_control_type | economizer_control_action_type | economizer_maximum_limit_dry_bulb_temperature | economizer_maximum_limit_enthalpy | economizer_maximum_limit_dewpoint_temperature | economizer_minimum_limit_dry_bulb_temperature | cost_per_building
1 | Barracks | 1959-pre | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 4245
2 | Fire Hall | 1959-pre | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 1104
3 | Food Service | 1959-pre | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 4830
4 | Food Service | 2005-2014 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 4830
5 | Hangar | 1959-pre | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 2830
6 | Hangar | 1960-1979 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 2830
7 | Hangar | 1980-2004 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 2830
8 | Maintenance Shop | 1959-pre | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 1208
9 | Maintenance Shop | 1980-2004 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 1208
10 | Maintenance Shop-Small | 1959-pre | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 1415
11 | Maintenance Shop-Small | 1960-1979 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 1415
12 | Maintenance Shop-Small | 1980-2004 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 1415
13 | Office | 1959-pre | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 7075
14 | Office | 1960-1979 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 7075
15 | Office | 1980-2004 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 7075
16 | Office-Small | 1960-1979 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 5660
17 | Office-Small | 1980-2004 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 5660
18 | Office-Small | 2005-2014 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 5660
19 | Recreation Center | 1980-2004 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 8490
20 | Storage Building | 1959-pre | NA | NA | NA | NA | NA | NA | NA | NA
21 | Storage Building | 1960-1979 | NA | NA | NA | NA | NA | NA | NA | NA
22 | Storage Building | 1980-2004 | NA | NA | NA | NA | NA | NA | NA | NA
23 | Storage Building | 2005-2014 | NA | NA | NA | NA | NA | NA | NA | NA
24 | Training Building | 1959-pre | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 5660
25 | Training Building | 1980-2004 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 5660
26 | Training Building | 2005-2014 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 5660
27 | Vehicle Garage | 1959-pre | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 3623
28 | Vehicle Garage | 1980-2004 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 3623
NA | Barracks | 1960-1979 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 4245
NA | Barracks | 1980-2004 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 4245
30 | Barracks | 2005-2014 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 4245
NA | Fire Hall | 1960-1979 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 1104
NA | Fire Hall | 1980-2004 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 1104
31 | Fire Hall | 2005-2014 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 1104
NA | Food Service | 1960-1979 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 4830
NA | Food Service | 1980-2004 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 4830
29 | Hangar | 2005-2014 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 2830
NA | Maintenance Shop | 1960-1979 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 1208
NA | Maintenance Shop | 2005-2014 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 1208
NA | Maintenance Shop-Small | 2005-2014 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 1415
NA | Office | 2005-2014 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 7075
NA | Office-Small | 1959-pre | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 5660
NA | Recreation Center | 1959-pre | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 8490
NA | Recreation Center | 1960-1979 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 8490
NA | Recreation Center | 2005-2014 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 8490
NA | Training Building | 1960-1979 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 5660
NA | Vehicle Garage | 1960-1979 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 3623
NA | Vehicle Garage | 2005-2014 | economizers_enabled | FixedDryBulb | ModulateFlow | 19 | 64000 | 12 | -40 | 3623

## ecm_envelope
baseline_index | building_type | vintage_name | measure_id | library_file | default_construction_set_name | ext_wall_rsi | ext_floor_rsi | ext_roof_rsi | ground_floor_rsi | ground_wall_rsi | ground_roof_rsi | fixed_window_rsi | operable_window_rsi | door_construction_rsi | glass_door_rsi | overhead_door_rsi | cost_per_building
1 | Barracks | 1959-pre | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.17 | 6.5164 | 9.156 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 232280
1 | Barracks | 1959-pre | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.17 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 512843
1 | Barracks | 1959-pre | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.17 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 378182
2 | Fire Hall | 1959-pre | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 6.5164 | 9.156 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 178944
2 | Fire Hall | 1959-pre | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.17 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 280000
2 | Fire Hall | 1959-pre | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 61245
3 | Food Service | 1959-pre | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.522 | 4.2268 | 6.867 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 458471
3 | Food Service | 1959-pre | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.522 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 419941
3 | Food Service | 1959-pre | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.522 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 277780
4 | Food Service | 2005-2014 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 5.284 | 4.5791 | 7.219 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
4 | Food Service | 2005-2014 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 7.284 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
4 | Food Service | 2005-2014 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 5.284 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 277780
5 | Hangar | 1959-pre | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 1.4089 | 2.1134 | 4.753 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 1150035
5 | Hangar | 1959-pre | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 3.409 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 922651
5 | Hangar | 1959-pre | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 1.4089 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 193168
6 | Hangar | 1960-1979 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 2.1134 | 1.7612 | 4.401 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | 1244509
6 | Hangar | 1960-1979 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 4.113 | 1.7612 | 1.7612 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | 922651
6 | Hangar | 1960-1979 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 2.1134 | 1.7612 | 1.7612 | 1.0567 | 1.0567 | 1.0567 | 0.45 | 0.45 | 0.52836 | 0.28179 | 1.4089 | 193168
7 | Hangar | 1980-2004 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.5224 | 3.1701 | 5.81 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 1150035
7 | Hangar | 1980-2004 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.522 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 922651
7 | Hangar | 1980-2004 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.5224 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 193168
8 | Maintenance Shop | 1959-pre | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 0.88059 | 2.1134 | 5.083 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 265713
8 | Maintenance Shop | 1959-pre | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 2.881 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 515871
8 | Maintenance Shop | 1959-pre | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 0.88059 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 74884
9 | Maintenance Shop | 1980-2004 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 4.2268 | 6.867 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 265713
9 | Maintenance Shop | 1980-2004 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.17 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 515871
9 | Maintenance Shop | 1980-2004 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.76 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 74884
10 | Maintenance Shop-Small | 1959-pre | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 0.88059 | 2.1134 | 5.083 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 108148
10 | Maintenance Shop-Small | 1959-pre | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 2.881 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 264909
10 | Maintenance Shop-Small | 1959-pre | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 0.88059 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 6887
11 | Maintenance Shop-Small | 1960-1979 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 1.4089 | 4.049 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | 158367
11 | Maintenance Shop-Small | 1960-1979 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 3.761 | 1.4089 | 1.4089 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | 264909
11 | Maintenance Shop-Small | 1960-1979 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 1.4089 | 1.4089 | 1.0567 | 1.0567 | 1.0567 | 0.45 | 0.45 | 0.52836 | 0.28179 | 1.4089 | 6887
12 | Maintenance Shop-Small | 1980-2004 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 4.2268 | 6.867 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 137338
12 | Maintenance Shop-Small | 1980-2004 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 4.17 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 264909
12 | Maintenance Shop-Small | 1980-2004 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 6887
13 | Office | 1959-pre | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 2.8179 | 5.458 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 929286
13 | Office | 1959-pre | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 3.761 | 2.8179 | 2.8179 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 397004
13 | Office | 1959-pre | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 2.8179 | 2.8179 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 3124765
14 | Office | 1960-1979 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 1.4089 | 4.049 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | 854741
14 | Office | 1960-1979 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 3.761 | 1.4089 | 1.4089 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | 397004
14 | Office | 1960-1979 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 1.4089 | 1.4089 | 1.0567 | 1.0567 | 1.0567 | 0.45 | 0.45 | 0.52836 | 0.28179 | 1.4089 | 3124765
15 | Office | 1980-2004 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.5224 | 3.1701 | 5.81 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 854741
15 | Office | 1980-2004 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.522 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 397004
15 | Office | 1980-2004 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.5224 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 3124765
16 | Office-Small | 1960-1979 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 1.4089 | 4.049 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | 156449
16 | Office-Small | 1960-1979 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 3.761 | 1.4089 | 1.4089 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | 130284
16 | Office-Small | 1960-1979 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 1.4089 | 1.4089 | 1.0567 | 1.0567 | 1.0567 | 0.45 | 0.45 | 0.52836 | 0.28179 | 1.4089 | 48750
17 | Office-Small | 1980-2004 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.5224 | 3.1701 | 5.81 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 156449
17 | Office-Small | 1980-2004 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.522 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 130284
17 | Office-Small | 1980-2004 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.5224 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 48750
18 | Office-Small | 2005-2014 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 5.2836 | 4.5791 | 7.219 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
18 | Office-Small | 2005-2014 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 7.284 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
18 | Office-Small | 2005-2014 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 5.2836 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 48750
19 | Recreation Center | 1980-2004 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 2.74 | 2.77 | 5.41 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 1484899
19 | Recreation Center | 1980-2004 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 4.74 | 2.77 | 2.77 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 1363343
19 | Recreation Center | 1980-2004 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 2.74 | 2.77 | 2.77 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 243369
20 | Storage Building | 1959-pre | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 0.88059 | 3.5224 | 6.162 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 288135
20 | Storage Building | 1959-pre | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 2.881 | 3.5224 | 3.5224 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 160914
20 | Storage Building | 1959-pre | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 0.88059 | 3.5224 | 3.5224 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 0
21 | Storage Building | 1960-1979 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 1.9373 | 1.5851 | 4.225 | 1.2328 | 1.2328 | 1.2328 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.5851 | 188777
21 | Storage Building | 1960-1979 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 3.937 | 1.5851 | 1.5851 | 1.2328 | 1.2328 | 1.2328 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.5851 | 160914
21 | Storage Building | 1960-1979 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 1.9373 | 1.5851 | 1.5851 | 1.2328 | 1.2328 | 1.2328 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.5851 | 0
22 | Storage Building | 1980-2004 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 2.6418 | 3.5224 | 6.162 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 163711
22 | Storage Building | 1980-2004 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 4.642 | 3.5224 | 3.5224 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 160914
22 | Storage Building | 1980-2004 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 2.6418 | 3.5224 | 3.5224 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 0
23 | Storage Building | 2005-2014 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 5.2836 | 4.5791 | 7.219 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
23 | Storage Building | 2005-2014 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 7.284 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
23 | Storage Building | 2005-2014 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 5.2836 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 0
24 | Training Building | 1959-pre | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 2.1134 | 4.753 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 523108
24 | Training Building | 1959-pre | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 3.761 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 455483
24 | Training Building | 1959-pre | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 165362
25 | Training Building | 1980-2004 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.5224 | 3.1701 | 5.81 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 523108
25 | Training Building | 1980-2004 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.522 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 455483
25 | Training Building | 1980-2004 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.5224 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 165362
26 | Training Building | 2005-2014 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 5.2836 | 4.5791 | 7.219 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
26 | Training Building | 2005-2014 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 7.284 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
26 | Training Building | 2005-2014 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 5.2836 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 165362
27 | Vehicle Garage | 1959-pre | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 2.1134 | 4.753 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 356996
27 | Vehicle Garage | 1959-pre | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 3.761 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 380269
27 | Vehicle Garage | 1959-pre | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 4464
28 | Vehicle Garage | 1980-2004 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 2.6418 | 3.1701 | 5.81 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 356996
28 | Vehicle Garage | 1980-2004 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 4.642 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 380269
28 | Vehicle Garage | 1980-2004 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 2.6418 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 4464
NA | Barracks | 1960-1979 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 6.5164 | 9.156 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 232280
NA | Barracks | 1960-1979 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.17 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 512843
NA | Barracks | 1960-1979 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 378182
NA | Barracks | 1980-2004 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 6.5164 | 9.156 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 232280
NA | Barracks | 1980-2004 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.17 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 512843
NA | Barracks | 1980-2004 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 378182
30 | Barracks | 2005-2014 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 6.5164 | 9.156 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 0
30 | Barracks | 2005-2014 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.17 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 0
30 | Barracks | 2005-2014 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 378182
NA | Fire Hall | 1960-1979 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 6.5164 | 9.156 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 178944
NA | Fire Hall | 1960-1979 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.17 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 280000
NA | Fire Hall | 1960-1979 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 61245
NA | Fire Hall | 1980-2004 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 6.5164 | 9.156 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 178944
NA | Fire Hall | 1980-2004 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.17 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 280000
NA | Fire Hall | 1980-2004 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 61245
31 | Fire Hall | 2005-2014 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 6.5164 | 9.156 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 0
31 | Fire Hall | 2005-2014 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.17 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 0
31 | Fire Hall | 2005-2014 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.1701 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 61245
NA | Food Service | 1960-1979 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.522 | 4.2268 | 6.867 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 458471
NA | Food Service | 1960-1979 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.522 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 419941
NA | Food Service | 1960-1979 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.522 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 277780
NA | Food Service | 1980-2004 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 3.522 | 4.2268 | 6.867 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 458471
NA | Food Service | 1980-2004 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 5.522 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 419941
NA | Food Service | 1980-2004 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 3.522 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 277780
29 | Hangar | 2005-2014 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 5.284 | 4.5791 | 7.219 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
29 | Hangar | 2005-2014 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 7.284 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
29 | Hangar | 2005-2014 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 5.284 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 193168
NA | Maintenance Shop | 1960-1979 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 2.1134 | 1.7612 | 6.867 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 265713
NA | Maintenance Shop | 1960-1979 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 4.113 | 1.7612 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 515871
NA | Maintenance Shop | 1960-1979 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 2.1134 | 1.7612 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 74884
NA | Maintenance Shop | 2005-2014 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 5.284 | 4.5791 | 7.219 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
NA | Maintenance Shop | 2005-2014 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 7.284 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
NA | Maintenance Shop | 2005-2014 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 5.284 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 74884
NA | Maintenance Shop-Small | 2005-2014 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 5.284 | 4.5791 | 7.219 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
NA | Maintenance Shop-Small | 2005-2014 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 7.284 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
NA | Maintenance Shop-Small | 2005-2014 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 5.284 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 6887
NA | Office | 2005-2014 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 5.284 | 4.5791 | 7.219 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
NA | Office | 2005-2014 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 7.284 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
NA | Office | 2005-2014 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 5.284 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 3124765
NA | Office-Small | 1959-pre | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 1.4089 | 4.049 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | 156449
NA | Office-Small | 1959-pre | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 3.761 | 1.4089 | 1.4089 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | 130284
NA | Office-Small | 1959-pre | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 1.4089 | 1.4089 | 1.0567 | 1.0567 | 1.0567 | 0.45 | 0.45 | 0.52836 | 0.28179 | 1.4089 | 48750
NA | Recreation Center | 1959-pre | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 2.74 | 2.77 | 5.41 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 1484899
NA | Recreation Center | 1959-pre | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 4.74 | 2.77 | 2.77 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 1363343
NA | Recreation Center | 1959-pre | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 2.74 | 2.77 | 2.77 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 243369
NA | Recreation Center | 1960-1979 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 2.74 | 2.77 | 5.41 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 1484899
NA | Recreation Center | 1960-1979 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 4.74 | 2.77 | 2.77 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 1363343
NA | Recreation Center | 1960-1979 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 2.74 | 2.77 | 2.77 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 243369
NA | Recreation Center | 2005-2014 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 2.74 | 2.77 | 5.41 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
NA | Recreation Center | 2005-2014 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 4.74 | 2.77 | 2.77 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
NA | Recreation Center | 2005-2014 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 2.74 | 2.77 | 2.77 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 243369
NA | Training Building | 1960-1979 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 2.1134 | 4.753 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 523108
NA | Training Building | 1960-1979 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 3.761 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 455483
NA | Training Building | 1960-1979 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 165362
NA | Vehicle Garage | 1960-1979 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 2.1134 | 4.753 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 356996
NA | Vehicle Garage | 1960-1979 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 3.761 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | 380269
NA | Vehicle Garage | 1960-1979 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 1.7612 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.28179 | 1.7612 | 4464
NA | Vehicle Garage | 2005-2014 | envelope_ecm_roof | resources/btap_construction_library.osm | DND-Concrete | 5.2836 | 4.5791 | 7.219 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
NA | Vehicle Garage | 2005-2014 | envelope_ecm_wall | resources/btap_construction_library.osm | DND-Concrete | 7.284 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | 0
NA | Vehicle Garage | 2005-2014 | envelope_ecm_windows | resources/btap_construction_library.osm | DND-Concrete | 5.2836 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.45 | 0.45 | 0.70447 | 0.31701 | 1.7612 | 4464
Note on Q1: Lopez, Phylroy: Used for Hanger doors

## ecm_erv
baseline_index | building_type | vintage_name | measure_id | erv_enabled | erv_autosizeNominalSupplyAirFlowRate | erv_NominalSupplyAirFlowRate | erv_HeatExchangerType | erv_SensibleEffectivenessat100CoolingAirFlow | erv_SensibleEffectivenessat75CoolingAirFlow | erv_LatentEffectiveness100Cooling | erv_LatentEffectiveness75Cooling | erv_SensibleEffectiveness100Heating | erv_SensibleEffectiveness75Heating | erv_LatentEffectiveness100Heating | erv_LatentEffectiveness75Heating | erv_SupplyAirOutletTemperatureControl | erv_setFrostControlType | erv_ThresholdTemperature | erv_InitialDefrostTimeFraction | erv_nominal_electric_power | erv_economizer_lockout | cost_per_building
1 | Barracks | 1959-pre | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 271466
2 | Fire Hall | 1959-pre | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 72910
3 | Food Service | 1959-pre | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 296001
4 | Food Service | 2005-2014 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 296001
5 | Hangar | 1959-pre | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 187064
6 | Hangar | 1960-1979 | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 187064
7 | Hangar | 1980-2004 | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 187064
8 | Maintenance Shop | 1959-pre | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 138209
9 | Maintenance Shop | 1980-2004 | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 138209
10 | Maintenance Shop-Small | 1959-pre | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 48855
11 | Maintenance Shop-Small | 1960-1979 | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 48855
12 | Maintenance Shop-Small | 1980-2004 | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 48855
13 | Office | 1959-pre | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 313530
14 | Office | 1960-1979 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 313530
15 | Office | 1980-2004 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 313530
16 | Office-Small | 1960-1979 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 167025
17 | Office-Small | 1980-2004 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 167025
18 | Office-Small | 2005-2014 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 167025
19 | Recreation Center | 1980-2004 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 796294
20 | Storage Building | 1959-pre | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 0
21 | Storage Building | 1960-1979 | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 0
22 | Storage Building | 1980-2004 | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 0
23 | Storage Building | 2005-2014 | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 0
24 | Training Building | 1959-pre | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 254281
25 | Training Building | 1980-2004 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 254281
26 | Training Building | 2005-2014 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 254281
27 | Vehicle Garage | 1959-pre | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 163879
28 | Vehicle Garage | 1980-2004 | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 163879
NA | Barracks | 1960-1979 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 271466
NA | Barracks | 1980-2004 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 271466
30 | Barracks | 2005-2014 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 271466
NA | Fire Hall | 1960-1979 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 72910
NA | Fire Hall | 1980-2004 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 72910
31 | Fire Hall | 2005-2014 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 72910
NA | Food Service | 1960-1979 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 296001
NA | Food Service | 1980-2004 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 296001
29 | Hangar | 2005-2014 | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 187064
NA | Maintenance Shop | 1960-1979 | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 138209
NA | Maintenance Shop | 2005-2014 | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 138209
NA | Maintenance Shop-Small | 2005-2014 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 48855
NA | Office | 2005-2014 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 313530
NA | Office-Small | 1959-pre | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 167025
NA | Recreation Center | 1959-pre | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 796294
NA | Recreation Center | 1960-1979 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 796294
NA | Recreation Center | 2005-2014 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 796294
NA | Training Building | 1960-1979 | hrv_enabled | TRUE | YES | NA | Plate | 0.76 | 0.81 | 0.68 | 0.73 | 0.76 | 0.81 | 0.68 | 0.73 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 254281
NA | Vehicle Garage | 1960-1979 | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 163879
NA | Vehicle Garage | 2005-2014 | hrv_enabled | TRUE | YES | NA | Plate | 0.54 | 0.59 | 0.3 | 0.37 | 0.58 | 0.62 | 0.41 | 0.45 | No | ExhaustAirRecirculation | 1.7 | 0 | 500 | Yes | 163879

## ecm_exhaust_fans
baseline_index | building_type | vintage_name | measure_id | exhaust_fans_occ_control_enabled | cost_per_building
1 | Barracks | 1959-pre | NA | NA | 4523
2 | Fire Hall | 1959-pre | NA | NA | 2261
3 | Food Service | 1959-pre | exhaust_fans_occ_control | TRUE | 6784
4 | Food Service | 2005-2014 | exhaust_fans_occ_control | TRUE | 6784
5 | Hangar | 1959-pre | exhaust_fans_occ_control | TRUE | 3769
6 | Hangar | 1960-1979 | exhaust_fans_occ_control | TRUE | 3769
7 | Hangar | 1980-2004 | exhaust_fans_occ_control | TRUE | 3769
8 | Maintenance Shop | 1959-pre | exhaust_fans_occ_control | TRUE | 2261
9 | Maintenance Shop | 1980-2004 | exhaust_fans_occ_control | TRUE | 2261
10 | Maintenance Shop-Small | 1959-pre | exhaust_fans_occ_control | TRUE | 754
11 | Maintenance Shop-Small | 1960-1979 | exhaust_fans_occ_control | TRUE | 754
12 | Maintenance Shop-Small | 1980-2004 | exhaust_fans_occ_control | TRUE | 754
13 | Office | 1959-pre | exhaust_fans_occ_control | TRUE | 5276
14 | Office | 1960-1979 | exhaust_fans_occ_control | TRUE | 5276
15 | Office | 1980-2004 | exhaust_fans_occ_control | TRUE | 5276
16 | Office-Small | 1960-1979 | exhaust_fans_occ_control | TRUE | 1508
17 | Office-Small | 1980-2004 | exhaust_fans_occ_control | TRUE | 1508
18 | Office-Small | 2005-2014 | exhaust_fans_occ_control | TRUE | 1508
19 | Recreation Center | 1980-2004 | NA | NA | 6030
20 | Storage Building | 1959-pre | exhaust_fans_occ_control | TRUE | 754
21 | Storage Building | 1960-1979 | exhaust_fans_occ_control | TRUE | 754
22 | Storage Building | 1980-2004 | exhaust_fans_occ_control | TRUE | 754
23 | Storage Building | 2005-2014 | exhaust_fans_occ_control | TRUE | 754
24 | Training Building | 1959-pre | exhaust_fans_occ_control | TRUE | 1508
25 | Training Building | 1980-2004 | exhaust_fans_occ_control | TRUE | 1508
26 | Training Building | 2005-2014 | exhaust_fans_occ_control | TRUE | 1508
27 | Vehicle Garage | 1959-pre | exhaust_fans_occ_control | TRUE | 754
28 | Vehicle Garage | 1980-2004 | exhaust_fans_occ_control | TRUE | 754
NA | Barracks | 1960-1979 | NA | NA | 4523
NA | Barracks | 1980-2004 | NA | NA | 4523
30 | Barracks | 2005-2014 | NA | NA | 4523
NA | Fire Hall | 1960-1979 | NA | NA | 2261
NA | Fire Hall | 1980-2004 | NA | NA | 2261
31 | Fire Hall | 2005-2014 | NA | NA | 2261
NA | Food Service | 1960-1979 | exhaust_fans_occ_control | TRUE | 6784
NA | Food Service | 1980-2004 | exhaust_fans_occ_control | TRUE | 6784
29 | Hangar | 2005-2014 | exhaust_fans_occ_control | TRUE | 3769
NA | Maintenance Shop | 1960-1979 | exhaust_fans_occ_control | TRUE | 2261
NA | Maintenance Shop | 2005-2014 | exhaust_fans_occ_control | TRUE | 2261
NA | Maintenance Shop-Small | 2005-2014 | exhaust_fans_occ_control | TRUE | 754
NA | Office | 2005-2014 | exhaust_fans_occ_control | TRUE | 5276
NA | Office-Small | 1959-pre | exhaust_fans_occ_control | TRUE | 1508
NA | Recreation Center | 1959-pre | NA | NA | 6030
NA | Recreation Center | 1960-1979 | NA | NA | 6030
NA | Recreation Center | 2005-2014 | NA | NA | 6030
NA | Training Building | 1960-1979 | exhaust_fans_occ_control | TRUE | 1508
NA | Vehicle Garage | 1960-1979 | exhaust_fans_occ_control | TRUE | 754
NA | Vehicle Garage | 2005-2014 | exhaust_fans_occ_control | TRUE | 754

## ecm_fans_pumps
baseline_index | building_type | vintage_name | measure_id | fan_volume_type | fan_motor_eff | pump_speed_type | pump_control_type | pump_motor_eff | cost_per_building
1 | Barracks | 1959-pre | fans_to_variable | VariableVolume | NA | NA | NA | NA | 3120
2 | Fire Hall | 1959-pre | fans_to_variable | VariableVolume | NA | NA | NA | NA | 1088
3 | Food Service | 1959-pre | fans_to_variable | VariableVolume | NA | NA | NA | NA | 4160
4 | Food Service | 2005-2014 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 4160
5 | Hangar | 1959-pre | fans_to_variable | VariableVolume | NA | NA | NA | NA | 2255
6 | Hangar | 1960-1979 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 2255
7 | Hangar | 1980-2004 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 2255
8 | Maintenance Shop | 1959-pre | fans_to_variable | VariableVolume | NA | NA | NA | NA | 1215
9 | Maintenance Shop | 1980-2004 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 1215
10 | Maintenance Shop-Small | 1959-pre | fans_to_variable | VariableVolume | NA | NA | NA | NA | 2707
11 | Maintenance Shop-Small | 1960-1979 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 2707
12 | Maintenance Shop-Small | 1980-2004 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 2707
13 | Office | 1959-pre | fans_to_variable | VariableVolume | NA | NA | NA | NA | 5200
14 | Office | 1960-1979 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 5200
15 | Office | 1980-2004 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 5200
16 | Office-Small | 1960-1979 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 4160
17 | Office-Small | 1980-2004 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 4160
18 | Office-Small | 2005-2014 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 4160
19 | Recreation Center | 1980-2004 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 11913
24 | Training Building | 1959-pre | fans_to_variable | NA | NA | NA | NA | NA | 7564
25 | Training Building | 1980-2004 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 7564
26 | Training Building | 2005-2014 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 7564
27 | Vehicle Garage | 1959-pre | fans_to_variable | VariableVolume | NA | NA | NA | NA | 3120
28 | Vehicle Garage | 1980-2004 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 3120
NA | Barracks | 1960-1979 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 3120
NA | Barracks | 1980-2004 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 3120
30 | Barracks | 2005-2014 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 3120
NA | Fire Hall | 1960-1979 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 1088
NA | Fire Hall | 1980-2004 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 1088
31 | Fire Hall | 2005-2014 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 1088
NA | Food Service | 1960-1979 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 4160
NA | Food Service | 1980-2004 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 4160
29 | Hangar | 2005-2014 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 2255
NA | Maintenance Shop | 1960-1979 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 1215
NA | Maintenance Shop | 2005-2014 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 1215
NA | Maintenance Shop-Small | 2005-2014 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 2707
NA | Office | 2005-2014 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 5200
NA | Office-Small | 1959-pre | fans_to_variable | VariableVolume | NA | NA | NA | NA | 4160
NA | Recreation Center | 1959-pre | fans_to_variable | VariableVolume | NA | NA | NA | NA | 11913
NA | Recreation Center | 1960-1979 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 11913
NA | Recreation Center | 2005-2014 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 11913
NA | Training Building | 1960-1979 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 7564
NA | Vehicle Garage | 1960-1979 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 3120
NA | Vehicle Garage | 2005-2014 | fans_to_variable | VariableVolume | NA | NA | NA | NA | 3120
1 | Barracks | 1959-pre | NA | NA | NA | NA | NA | NA | NA
2 | Fire Hall | 1959-pre | NA | NA | NA | NA | NA | NA | NA
3 | Food Service | 1959-pre | NA | NA | NA | NA | NA | NA | NA
4 | Food Service | 2005-2014 | NA | NA | NA | NA | NA | NA | NA
8 | Maintenance Shop | 1959-pre | NA | NA | NA | NA | NA | NA | NA
9 | Maintenance Shop | 1980-2004 | NA | NA | NA | NA | NA | NA | NA
10 | Maintenance Shop-Small | 1959-pre | NA | NA | NA | NA | NA | NA | NA
11 | Maintenance Shop-Small | 1960-1979 | NA | NA | NA | NA | NA | NA | NA
12 | Maintenance Shop-Small | 1980-2004 | NA | NA | NA | NA | NA | NA | NA
16 | Office-Small | 1960-1979 | NA | NA | NA | NA | NA | NA | NA
17 | Office-Small | 1980-2004 | NA | NA | NA | NA | NA | NA | NA
18 | Office-Small | 2005-2014 | NA | NA | NA | NA | NA | NA | NA
20 | Storage Building | 1959-pre | NA | NA | NA | NA | NA | NA | NA
20 | Storage Building | 1959-pre | NA | NA | NA | NA | NA | NA | NA
20 | Storage Building | 1959-pre | NA | NA | NA | NA | NA | NA | NA
21 | Storage Building | 1960-1979 | NA | NA | NA | NA | NA | NA | NA
21 | Storage Building | 1960-1979 | NA | NA | NA | NA | NA | NA | NA
21 | Storage Building | 1960-1979 | NA | NA | NA | NA | NA | NA | NA
22 | Storage Building | 1980-2004 | NA | NA | NA | NA | NA | NA | NA
22 | Storage Building | 1980-2004 | NA | NA | NA | NA | NA | NA | NA
22 | Storage Building | 1980-2004 | NA | NA | NA | NA | NA | NA | NA
23 | Storage Building | 2005-2014 | NA | NA | NA | NA | NA | NA | NA
23 | Storage Building | 2005-2014 | NA | NA | NA | NA | NA | NA | NA
23 | Storage Building | 2005-2014 | NA | NA | NA | NA | NA | NA | NA
27 | Vehicle Garage | 1959-pre | NA | NA | NA | NA | NA | NA | NA
28 | Vehicle Garage | 1980-2004 | NA | NA | NA | NA | NA | NA | NA
NA | Barracks | 1960-1979 | NA | NA | NA | NA | NA | NA | NA
NA | Barracks | 1980-2004 | NA | NA | NA | NA | NA | NA | NA
30 | Barracks | 2005-2014 | NA | NA | NA | NA | NA | NA | NA
NA | Fire Hall | 1960-1979 | NA | NA | NA | NA | NA | NA | NA
NA | Fire Hall | 1980-2004 | NA | NA | NA | NA | NA | NA | NA
31 | Fire Hall | 2005-2014 | NA | NA | NA | NA | NA | NA | NA
NA | Food Service | 1960-1979 | NA | NA | NA | NA | NA | NA | NA
NA | Food Service | 1980-2004 | NA | NA | NA | NA | NA | NA | NA
29 | Hangar | 2005-2014 | NA | NA | NA | NA | NA | NA | NA
NA | Maintenance Shop | 1960-1979 | NA | NA | NA | NA | NA | NA | NA
NA | Maintenance Shop | 2005-2014 | NA | NA | NA | NA | NA | NA | NA
NA | Office-Small | 1959-pre | NA | NA | NA | NA | NA | NA | NA
NA | Recreation Center | 2005-2014 | NA | NA | NA | NA | NA | NA | NA
NA | Vehicle Garage | 1960-1979 | NA | NA | NA | NA | NA | NA | NA
NA | Vehicle Garage | 2005-2014 | NA | NA | NA | NA | NA | NA | NA
1 | Barracks | 1959-pre | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 10200
2 | Fire Hall | 1959-pre | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 6120
3 | Food Service | 1959-pre | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 10636
4 | Food Service | 2005-2014 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 10636
5 | Hangar | 1959-pre | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 6855
6 | Hangar | 1960-1979 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 6855
7 | Hangar | 1980-2004 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 6855
8 | Maintenance Shop | 1959-pre | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 5266
9 | Maintenance Shop | 1980-2004 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 5266
10 | Maintenance Shop-Small | 1959-pre | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 4516
11 | Maintenance Shop-Small | 1960-1979 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 4516
12 | Maintenance Shop-Small | 1980-2004 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 4516
13 | Office | 1959-pre | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 8276
14 | Office | 1960-1979 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 8276
15 | Office | 1980-2004 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 8276
16 | Office-Small | 1960-1979 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 1745
17 | Office-Small | 1980-2004 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 1745
18 | Office-Small | 2005-2014 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 1745
19 | Recreation Center | 1980-2004 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 35398
24 | Training Building | 1959-pre | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 20033
25 | Training Building | 1980-2004 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 20033
26 | Training Building | 2005-2014 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 20033
27 | Vehicle Garage | 1959-pre | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 3349
28 | Vehicle Garage | 1980-2004 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 3349
NA | Barracks | 1960-1979 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 10200
NA | Barracks | 1980-2004 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 10200
30 | Barracks | 2005-2014 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 10200
NA | Fire Hall | 1960-1979 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 6120
NA | Fire Hall | 1980-2004 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 6120
31 | Fire Hall | 2005-2014 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 6120
NA | Food Service | 1960-1979 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 10636
NA | Food Service | 1980-2004 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 10636
29 | Hangar | 2005-2014 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 6855
NA | Maintenance Shop | 1960-1979 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 5266
NA | Maintenance Shop | 2005-2014 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 5266
NA | Maintenance Shop-Small | 2005-2014 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 4516
NA | Office | 2005-2014 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 8276
NA | Office-Small | 1959-pre | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 1745
NA | Recreation Center | 1959-pre | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 35398
NA | Recreation Center | 1960-1979 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 35398
NA | Recreation Center | 2005-2014 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 35398
NA | Training Building | 1960-1979 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 20033
NA | Vehicle Garage | 1960-1979 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 3349
NA | Vehicle Garage | 2005-2014 | pump_fan_eff_ | NA | 0.895 | NA | NA | 0.895 | 3349
5 | Hangar | 1959-pre | pumps_to_variable | NA | NA | VariableSpeed | Intermittent | NA | 3528
6 | Hangar | 1960-1979 | pumps_to_variable | NA | NA | VariableSpeed | Intermittent | NA | 3528
7 | Hangar | 1980-2004 | pumps_to_variable | NA | NA | VariableSpeed | Intermittent | NA | 3528
13 | Office | 1959-pre | pumps_to_variable | NA | NA | VariableSpeed | Intermittent | NA | 3528
14 | Office | 1960-1979 | pumps_to_variable | NA | NA | VariableSpeed | Intermittent | NA | 3528
15 | Office | 1980-2004 | pumps_to_variable | NA | NA | VariableSpeed | Intermittent | NA | 3528
19 | Recreation Center | 1980-2004 | pumps_to_variable | NA | NA | VariableSpeed | Intermittent | NA | 14112
24 | Training Building | 1959-pre | pumps_to_variable | NA | NA | VariableSpeed | Intermittent | NA | 8311
25 | Training Building | 1980-2004 | pumps_to_variable | NA | NA | VariableSpeed | Intermittent | NA | 8311
26 | Training Building | 2005-2014 | pumps_to_variable | NA | NA | VariableSpeed | Intermittent | NA | 8311
NA | Maintenance Shop-Small | 2005-2014 | pumps_to_variable | NA | NA | VariableSpeed | Intermittent | NA | 0
NA | Office | 2005-2014 | pumps_to_variable | NA | NA | VariableSpeed | Intermittent | NA | 3528
NA | Recreation Center | 1959-pre | pumps_to_variable | NA | NA | VariableSpeed | Intermittent | NA | 14112
NA | Recreation Center | 1960-1979 | pumps_to_variable | NA | NA | VariableSpeed | Intermittent | NA | 14112
NA | Training Building | 1960-1979 | pumps_to_variable | NA | NA | VariableSpeed | Intermittent | NA | 8311

## ecm_hw_boiler
baseline_index | building_type | vintage_name | measure_id | hw_boiler_nominal_thermal_efficiency | hw_boiler_flow_mode | hw_boiler_curve | hw_boiler_efficiency_curve_temperature_evaluation_variable | hw_boiler_reset_enabled | hw_boiler_reset_highsupplytemp | hw_boiler_reset_outsidehighsupplytemp | hw_boiler_reset_lowsupplytemp | hw_boiler_reset_outsidelowsupplytemp | cost_per_building
1 | Barracks | 1959-pre | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
2 | Fire Hall | 1959-pre | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 33911
3 | Food Service | 1959-pre | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
4 | Food Service | 2005-2014 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 33911
5 | Hangar | 1959-pre | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 175036
6 | Hangar | 1960-1979 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 175036
7 | Hangar | 1980-2004 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
8 | Maintenance Shop | 1959-pre | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
9 | Maintenance Shop | 1980-2004 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 33911
10 | Maintenance Shop-Small | 1959-pre | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
11 | Maintenance Shop-Small | 1960-1979 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
12 | Maintenance Shop-Small | 1980-2004 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 33911
13 | Office | 1959-pre | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 175036
14 | Office | 1960-1979 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
15 | Office | 1980-2004 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 33911
19 | Recreation Center | 1980-2004 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
24 | Training Building | 1959-pre | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
25 | Training Building | 1980-2004 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
26 | Training Building | 2005-2014 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 33911
27 | Vehicle Garage | 1959-pre | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
28 | Vehicle Garage | 1980-2004 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 33911
NA | Barracks | 1960-1979 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
NA | Barracks | 1980-2004 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 33911
30 | Barracks | 2005-2014 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 33911
NA | Fire Hall | 1960-1979 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 33911
NA | Fire Hall | 1980-2004 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 33911
31 | Fire Hall | 2005-2014 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 12022
NA | Food Service | 1960-1979 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
NA | Food Service | 1980-2004 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 33911
29 | Hangar | 2005-2014 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 33911
NA | Maintenance Shop | 1960-1979 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
NA | Maintenance Shop | 2005-2014 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 12022
NA | Maintenance Shop-Small | 2005-2014 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 33911
NA | Office | 2005-2014 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 33911
NA | Recreation Center | 1959-pre | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 175036
NA | Recreation Center | 1960-1979 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 175036
NA | Recreation Center | 2005-2014 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
NA | Training Building | 1960-1979 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
NA | Vehicle Garage | 1960-1979 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 67292
NA | Vehicle Garage | 2005-2014 | boiler_eff_upgrade | 0.9 | NA | condensing | LeavingBoiler | FALSE | NA | NA | NA | NA | 12022
1 | Barracks | 1959-pre | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
2 | Fire Hall | 1959-pre | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
3 | Food Service | 1959-pre | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
4 | Food Service | 2005-2014 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
5 | Hangar | 1959-pre | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
6 | Hangar | 1960-1979 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
7 | Hangar | 1980-2004 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
8 | Maintenance Shop | 1959-pre | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
9 | Maintenance Shop | 1980-2004 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
10 | Maintenance Shop-Small | 1959-pre | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
11 | Maintenance Shop-Small | 1960-1979 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
12 | Maintenance Shop-Small | 1980-2004 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
13 | Office | 1959-pre | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
14 | Office | 1960-1979 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
15 | Office | 1980-2004 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
16 | Office-Small | 1960-1979 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
17 | Office-Small | 1980-2004 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
18 | Office-Small | 2005-2014 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
19 | Recreation Center | 1980-2004 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
24 | Training Building | 1959-pre | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
25 | Training Building | 1980-2004 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
26 | Training Building | 2005-2014 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
27 | Vehicle Garage | 1959-pre | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
28 | Vehicle Garage | 1980-2004 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Barracks | 1960-1979 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Barracks | 1980-2004 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
30 | Barracks | 2005-2014 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Fire Hall | 1960-1979 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Fire Hall | 1980-2004 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
31 | Fire Hall | 2005-2014 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Food Service | 1960-1979 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Food Service | 1980-2004 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
29 | Hangar | 2005-2014 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Maintenance Shop | 1960-1979 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Maintenance Shop | 2005-2014 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Maintenance Shop-Small | 2005-2014 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Office | 2005-2014 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Office-Small | 1959-pre | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Recreation Center | 1959-pre | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Recreation Center | 1960-1979 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Recreation Center | 2005-2014 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Training Building | 1960-1979 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Vehicle Garage | 1960-1979 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
NA | Vehicle Garage | 2005-2014 | boiler_reset | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | 957
16 | Office-Small | 1960-1979 | NA | NA | NA | condensing | NA | FALSE | NA | NA | NA | NA | 0
17 | Office-Small | 1980-2004 | NA | NA | NA | condensing | NA | FALSE | NA | NA | NA | NA | 0
18 | Office-Small | 2005-2014 | NA | NA | NA | condensing | NA | FALSE | NA | NA | NA | NA | 0
20 | Storage Building | 1959-pre | NA | NA | NA | atmospheric | NA | NA | NA | NA | NA | NA | NA
20 | Storage Building | 1959-pre | NA | NA | NA | condensing | NA | FALSE | NA | NA | NA | NA | 0
21 | Storage Building | 1960-1979 | NA | NA | NA | atmospheric | NA | NA | NA | NA | NA | NA | NA
21 | Storage Building | 1960-1979 | NA | NA | NA | condensing | NA | FALSE | NA | NA | NA | NA | 0
22 | Storage Building | 1980-2004 | NA | NA | NA | atmospheric | NA | NA | NA | NA | NA | NA | NA
22 | Storage Building | 1980-2004 | NA | NA | NA | condensing | NA | FALSE | NA | NA | NA | NA | 0
23 | Storage Building | 2005-2014 | NA | NA | NA | atmospheric | NA | NA | NA | NA | NA | NA | NA
23 | Storage Building | 2005-2014 | NA | NA | NA | condensing | NA | FALSE | NA | NA | NA | NA | 0
NA | Office-Small | 1959-pre | NA | NA | NA | condensing | NA | FALSE | NA | NA | NA | NA | 0

## ecm_infiltration
baseline_index | building_type | vintage_name | measure_id | infiltration_flow_per_exterior_area | cost_per_building
1 | Barracks | 1959-pre | infil_reduce | 0.0002 | 122012
2 | Fire Hall | 1959-pre | infil_reduce | 0.0003 | 67418
3 | Food Service | 1959-pre | infil_reduce | 0.0002 | 83796
4 | Food Service | 2005-2014 | NA | 0.0002 | 0
5 | Hangar | 1959-pre | infil_reduce | 0.0003 | 96777
6 | Hangar | 1960-1979 | infil_reduce | 0.0003 | 96777
7 | Hangar | 1980-2004 | infil_reduce | 0.0003 | 88824
8 | Maintenance Shop | 1959-pre | infil_reduce | 0.0003 | 74019
9 | Maintenance Shop | 1980-2004 | infil_reduce | 0.0003 | 67140
10 | Maintenance Shop-Small | 1959-pre | infil_reduce | 0.0003 | 47106
11 | Maintenance Shop-Small | 1960-1979 | infil_reduce | 0.0003 | 47106
12 | Maintenance Shop-Small | 1980-2004 | infil_reduce | 0.0003 | 43200
13 | Office | 1959-pre | infil_reduce | 0.0002 | 54491
14 | Office | 1960-1979 | infil_reduce | 0.0002 | 54491
15 | Office | 1980-2004 | infil_reduce | 0.0002 | 49901
16 | Office-Small | 1960-1979 | infil_reduce | 0.0002 | 36956
17 | Office-Small | 1980-2004 | infil_reduce | 0.0002 | 33552
18 | Office-Small | 2005-2014 | NA | 0.0002 | 0
19 | Recreation Center | 1980-2004 | infil_reduce | 0.0002 | 112850
20 | Storage Building | 1959-pre | infil_reduce | 0.0003 | 37359
21 | Storage Building | 1960-1979 | infil_reduce | 0.0003 | 37359
22 | Storage Building | 1980-2004 | infil_reduce | 0.0003 | 33525
23 | Storage Building | 2005-2014 | NA | 0.0003 | 0
24 | Training Building | 1959-pre | infil_reduce | 0.0002 | 116444
25 | Training Building | 1980-2004 | infil_reduce | 0.0002 | 103803
26 | Training Building | 2005-2014 | NA | 0.0002 | 0
27 | Vehicle Garage | 1959-pre | infil_reduce | 0.0003 | 67248
28 | Vehicle Garage | 1980-2004 | infil_reduce | 0.0003 | 62140
NA | Barracks | 1960-1979 | infil_reduce | 0.0002 | 122012
NA | Barracks | 1980-2004 | infil_reduce | 0.0002 | 110890
30 | Barracks | 2005-2014 | NA | 0.0002 | 0
NA | Fire Hall | 1960-1979 | infil_reduce | 0.0003 | 67418
NA | Fire Hall | 1980-2004 | infil_reduce | 0.0003 | 62831
31 | Fire Hall | 2005-2014 | infil_reduce | 0.0003 | 0
NA | Food Service | 1960-1979 | infil_reduce | 0.0002 | 83796
NA | Food Service | 1980-2004 | infil_reduce | 0.0002 | 76635
29 | Hangar | 2005-2014 | NA | 0.0003 | 0
NA | Maintenance Shop | 1960-1979 | infil_reduce | 0.0003 | 74019
NA | Maintenance Shop | 2005-2014 | NA | 0.0003 | 0
NA | Maintenance Shop-Small | 2005-2014 | NA | 0.0003 | 0
NA | Office | 2005-2014 | NA | 0.0002 | 0
NA | Office-Small | 1959-pre | infil_reduce | 0.0002 | 36956
NA | Recreation Center | 1959-pre | infil_reduce | 0.0002 | 123257
NA | Recreation Center | 1960-1979 | infil_reduce | 0.0002 | 123257
NA | Recreation Center | 2005-2014 | NA | 0.0002 | 0
NA | Training Building | 1960-1979 | infil_reduce | 0.0002 | 116444
NA | Vehicle Garage | 1960-1979 | infil_reduce | 0.0003 | 67248
NA | Vehicle Garage | 2005-2014 | NA | 0.0003 | 0

## ecm_lighting_reduction
baseline_index | building_type | vintage_name | measure_id | lighting_scaling_factor | lighting_fraction_radiant | lighting_fraction_visible | lighting_return_air_fraction | cost_per_building
1 | Barracks | 1959-pre | lights_reduce_70p | 0.7 | NA | NA | NA | 92265
2 | Fire Hall | 1959-pre | lights_reduce_70p | 0.7 | NA | NA | NA | 15765
3 | Food Service | 1959-pre | lights_reduce_70p | 0.7 | NA | NA | NA | 111667
4 | Food Service | 2005-2014 | lights_reduce_70p | 0.7 | NA | NA | NA | 111667
5 | Hangar | 1959-pre | lights_reduce_70p | 0.7 | NA | NA | NA | 133713
6 | Hangar | 1960-1979 | lights_reduce_70p | 0.7 | NA | NA | NA | 133713
7 | Hangar | 1980-2004 | lights_reduce_70p | 0.7 | NA | NA | NA | 133713
8 | Maintenance Shop | 1959-pre | lights_reduce_70p | 0.7 | NA | NA | NA | 45581
9 | Maintenance Shop | 1980-2004 | lights_reduce_70p | 0.7 | NA | NA | NA | 45581
10 | Maintenance Shop-Small | 1959-pre | lights_reduce_70p | 0.7 | NA | NA | NA | 24169
11 | Maintenance Shop-Small | 1960-1979 | lights_reduce_70p | 0.7 | NA | NA | NA | 24169
12 | Maintenance Shop-Small | 1980-2004 | lights_reduce_70p | 0.7 | NA | NA | NA | 24169
13 | Office | 1959-pre | lights_reduce_70p | 0.7 | NA | NA | NA | 83176
14 | Office | 1960-1979 | lights_reduce_70p | 0.7 | NA | NA | NA | 83176
15 | Office | 1980-2004 | lights_reduce_70p | 0.7 | NA | NA | NA | 83176
16 | Office-Small | 1960-1979 | lights_reduce_70p | 0.7 | NA | NA | NA | 20189
17 | Office-Small | 1980-2004 | lights_reduce_70p | 0.7 | NA | NA | NA | 20189
18 | Office-Small | 2005-2014 | lights_reduce_70p | 0.7 | NA | NA | NA | 20189
19 | Recreation Center | 1980-2004 | lights_reduce_70p | 0.7 | NA | NA | NA | 232340
20 | Storage Building | 1959-pre | lights_reduce_70p | 0.7 | NA | NA | NA | 24436
21 | Storage Building | 1960-1979 | lights_reduce_70p | 0.7 | NA | NA | NA | 24436
22 | Storage Building | 1980-2004 | lights_reduce_70p | 0.7 | NA | NA | NA | 24436
23 | Storage Building | 2005-2014 | lights_reduce_70p | 0.7 | NA | NA | NA | 24436
24 | Training Building | 1959-pre | lights_reduce_70p | 0.7 | NA | NA | NA | 160307
25 | Training Building | 1980-2004 | lights_reduce_70p | 0.7 | NA | NA | NA | 160307
26 | Training Building | 2005-2014 | lights_reduce_70p | 0.7 | NA | NA | NA | 160307
27 | Vehicle Garage | 1959-pre | lights_reduce_70p | 0.7 | NA | NA | NA | 26160
28 | Vehicle Garage | 1980-2004 | lights_reduce_70p | 0.7 | NA | NA | NA | 26160
NA | Barracks | 1960-1979 | lights_reduce_70p | 0.7 | NA | NA | NA | 92265
NA | Barracks | 1980-2004 | lights_reduce_70p | 0.7 | NA | NA | NA | 92265
30 | Barracks | 2005-2014 | lights_reduce_70p | 0.7 | NA | NA | NA | 92265
NA | Fire Hall | 1960-1979 | lights_reduce_70p | 0.7 | NA | NA | NA | 15765
NA | Fire Hall | 1980-2004 | lights_reduce_70p | 0.7 | NA | NA | NA | 15765
31 | Fire Hall | 2005-2014 | lights_reduce_70p | 0.7 | NA | NA | NA | 15765
NA | Food Service | 1960-1979 | lights_reduce_70p | 0.7 | NA | NA | NA | 111667
NA | Food Service | 1980-2004 | lights_reduce_70p | 0.7 | NA | NA | NA | 111667
29 | Hangar | 2005-2014 | lights_reduce_70p | 0.7 | NA | NA | NA | 133713
NA | Maintenance Shop | 1960-1979 | lights_reduce_70p | 0.7 | NA | NA | NA | 45581
NA | Maintenance Shop | 2005-2014 | lights_reduce_70p | 0.7 | NA | NA | NA | 45581
NA | Maintenance Shop-Small | 2005-2014 | lights_reduce_70p | 0.7 | NA | NA | NA | 24169
NA | Office | 2005-2014 | lights_reduce_70p | 0.7 | NA | NA | NA | 83176
NA | Office-Small | 1959-pre | lights_reduce_70p | 0.7 | NA | NA | NA | 20189
NA | Recreation Center | 1959-pre | lights_reduce_70p | 0.7 | NA | NA | NA | 232340
NA | Recreation Center | 1960-1979 | lights_reduce_70p | 0.7 | NA | NA | NA | 232340
NA | Recreation Center | 2005-2014 | lights_reduce_70p | 0.7 | NA | NA | NA | 232340
NA | Training Building | 1960-1979 | lights_reduce_70p | 0.7 | NA | NA | NA | 160307
NA | Vehicle Garage | 1960-1979 | lights_reduce_70p | 0.7 | NA | NA | NA | 26160
NA | Vehicle Garage | 2005-2014 | lights_reduce_70p | 0.7 | NA | NA | NA | 26160

## ecm_plug
baseline_index | building_type | vintage_name | measure_id | elec_equipment_load_scaling_factor | elec_equipment_fraction_radiant | elec_equipment_fraction_latent | elec_equipment_fraction_lost | cost_per_building
1 | Barracks | 1959-pre | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 21281
2 | Fire Hall | 1959-pre | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2750
3 | Food Service | 1959-pre | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2554
4 | Food Service | 2005-2014 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2554
5 | Hangar | 1959-pre | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 21849
6 | Hangar | 1960-1979 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 21849
7 | Hangar | 1980-2004 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 21849
8 | Maintenance Shop | 1959-pre | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 3121
9 | Maintenance Shop | 1980-2004 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 3121
10 | Maintenance Shop-Small | 1959-pre | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2554
11 | Maintenance Shop-Small | 1960-1979 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2554
12 | Maintenance Shop-Small | 1980-2004 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2554
13 | Office | 1959-pre | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 14471
14 | Office | 1960-1979 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 14471
15 | Office | 1980-2004 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 14471
16 | Office-Small | 1960-1979 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 4540
17 | Office-Small | 1980-2004 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 4540
18 | Office-Small | 2005-2014 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 4540
19 | Recreation Center | 1980-2004 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 9080
20 | Storage Building | 1959-pre | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 284
21 | Storage Building | 1960-1979 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 284
22 | Storage Building | 1980-2004 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 284
23 | Storage Building | 2005-2014 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 284
24 | Training Building | 1959-pre | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 11634
25 | Training Building | 1980-2004 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 11634
26 | Training Building | 2005-2014 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 11634
27 | Vehicle Garage | 1959-pre | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2838
28 | Vehicle Garage | 1980-2004 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2838
NA | Barracks | 1960-1979 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 21281
NA | Barracks | 1980-2004 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 21281
30 | Barracks | 2005-2014 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 21281
NA | Fire Hall | 1960-1979 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2750
NA | Fire Hall | 1980-2004 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2750
31 | Fire Hall | 2005-2014 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2750
NA | Food Service | 1960-1979 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2554
NA | Food Service | 1980-2004 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2554
29 | Hangar | 2005-2014 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 21849
NA | Maintenance Shop | 1960-1979 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 3121
NA | Maintenance Shop | 2005-2014 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 3121
NA | Maintenance Shop-Small | 2005-2014 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2554
NA | Office | 2005-2014 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 14471
NA | Office-Small | 1959-pre | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 4540
NA | Recreation Center | 1959-pre | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 9080
NA | Recreation Center | 1960-1979 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 9080
NA | Recreation Center | 2005-2014 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 9080
NA | Training Building | 1960-1979 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 11634
NA | Vehicle Garage | 1960-1979 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2838
NA | Vehicle Garage | 2005-2014 | plug_loads_90_percent | 0.9 | 0.3 | NA | NA | 2838

## ecm_occ_temp_setback
baseline_index | building_type | vintage_name | measure_id | occ_stbck_enabled | occ_stbck_tolerance | occ_stbck_heat_setback | occ_stbck_heat_setpoint | occ_stbck_cool_setback | occ_stbck_cool_setpoint | cost_per_building
1 | Barracks | 1959-pre | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 36806
2 | Fire Hall | 1959-pre | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 5066
3 | Food Service | 1959-pre | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 4417
4 | Food Service | 2005-2014 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 4417
5 | Hangar | 1959-pre | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 37788
6 | Hangar | 1960-1979 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 37788
7 | Hangar | 1980-2004 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 37788
8 | Maintenance Shop | 1959-pre | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 5398
9 | Maintenance Shop | 1980-2004 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 5398
10 | Maintenance Shop-Small | 1959-pre | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 4417
11 | Maintenance Shop-Small | 1960-1979 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 4417
12 | Maintenance Shop-Small | 1980-2004 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 4417
13 | Office | 1959-pre | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 25028
14 | Office | 1960-1979 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 25028
15 | Office | 1980-2004 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 25028
16 | Office-Small | 1960-1979 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 7852
17 | Office-Small | 1980-2004 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 7852
18 | Office-Small | 2005-2014 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 7852
19 | Recreation Center | 1980-2004 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 15704
20 | Storage Building | 1959-pre | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 491
21 | Storage Building | 1960-1979 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 491
22 | Storage Building | 1980-2004 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 491
23 | Storage Building | 2005-2014 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 491
24 | Training Building | 1959-pre | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 20121
25 | Training Building | 1980-2004 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 20121
26 | Training Building | 2005-2014 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 20121
27 | Vehicle Garage | 1959-pre | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 4908
28 | Vehicle Garage | 1980-2004 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 4908
NA | Barracks | 1960-1979 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 36806
NA | Barracks | 1980-2004 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 36806
30 | Barracks | 2005-2014 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 36806
NA | Fire Hall | 1960-1979 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 5066
NA | Fire Hall | 1980-2004 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 5066
31 | Fire Hall | 2005-2014 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 5066
NA | Food Service | 1960-1979 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 4417
NA | Food Service | 1980-2004 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 4417
29 | Hangar | 2005-2014 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 37788
NA | Maintenance Shop | 1960-1979 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 5398
NA | Maintenance Shop | 2005-2014 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 5398
NA | Maintenance Shop-Small | 2005-2014 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 4417
NA | Office | 2005-2014 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 25028
NA | Office-Small | 1959-pre | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 7852
NA | Recreation Center | 1959-pre | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 15704
NA | Recreation Center | 1960-1979 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 15704
NA | Recreation Center | 2005-2014 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 15704
NA | Training Building | 1960-1979 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 20121
NA | Vehicle Garage | 1960-1979 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 4908
NA | Vehicle Garage | 2005-2014 | occupancy_setback | TRUE | 0.05 | 17 | 22 | 99 | 24 | 4908

## ecm_sat_reset
baseline_index | building_type | vintage_name | measure_id | sat_reset_enabled | sat_reset_outdoor_high_temperature | sat_reset_outdoor_low_temperature | sat_reset_setpoint_at_outdoor_high_temperature | sat_reset_setpoint_at_outdoor_low_temperature | cost_per_building
1 | Barracks | 1959-pre | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 10864
2 | Fire Hall | 1959-pre | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 2760
3 | Food Service | 1959-pre | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 14485
4 | Food Service | 2005-2014 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 14485
5 | Hangar | 1959-pre | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 7243
6 | Hangar | 1960-1979 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 7243
7 | Hangar | 1980-2004 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 7243
8 | Maintenance Shop | 1959-pre | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 3621
9 | Maintenance Shop | 1980-2004 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 3621
10 | Maintenance Shop-Small | 1959-pre | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 3621
11 | Maintenance Shop-Small | 1960-1979 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 3621
12 | Maintenance Shop-Small | 1980-2004 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 3621
13 | Office | 1959-pre | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 18106
14 | Office | 1960-1979 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 18106
15 | Office | 1980-2004 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 18106
16 | Office-Small | 1960-1979 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 14485
17 | Office-Small | 1980-2004 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 14485
18 | Office-Small | 2005-2014 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 14485
19 | Recreation Center | 1980-2004 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 32591
20 | Storage Building | 1959-pre | NA | NA | NA | NA | NA | NA | NA
21 | Storage Building | 1960-1979 | NA | NA | NA | NA | NA | NA | NA
22 | Storage Building | 1980-2004 | NA | NA | NA | NA | NA | NA | NA
23 | Storage Building | 2005-2014 | NA | NA | NA | NA | NA | NA | NA
24 | Training Building | 1959-pre | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 14485
25 | Training Building | 1980-2004 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 14485
26 | Training Building | 2005-2014 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 14485
27 | Vehicle Garage | 1959-pre | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 9315
28 | Vehicle Garage | 1980-2004 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 9315
NA | Barracks | 1960-1979 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 10864
NA | Barracks | 1980-2004 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 10864
30 | Barracks | 2005-2014 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 10864
NA | Fire Hall | 1960-1979 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 2760
NA | Fire Hall | 1980-2004 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 2760
31 | Fire Hall | 2005-2014 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 2760
NA | Food Service | 1960-1979 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 14485
NA | Food Service | 1980-2004 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 14485
29 | Hangar | 2005-2014 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 7243
NA | Maintenance Shop | 1960-1979 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 3621
NA | Maintenance Shop | 2005-2014 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 3621
NA | Maintenance Shop-Small | 2005-2014 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 3621
NA | Office | 2005-2014 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 18106
NA | Office-Small | 1959-pre | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 14485
NA | Recreation Center | 1959-pre | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 32591
NA | Recreation Center | 1960-1979 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 32591
NA | Recreation Center | 2005-2014 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 32591
NA | Training Building | 1960-1979 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 14485
NA | Vehicle Garage | 1960-1979 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 9315
NA | Vehicle Garage | 2005-2014 | air_temp_reset_enabled | TRUE | 24 | 10 | 12.8 | 24 | 9315

## ecm_elec_reduce
baseline_index | building_type | vintage_name | measure_id | lighting_scaling_factor | lighting_fraction_radiant | lighting_fraction_visible | lighting_return_air_fraction | elec_equipment_load_scaling_factor | elec_equipment_fraction_radiant | elec_equipment_fraction_latent | elec_equipment_fraction_lost | exhaust_fans_occ_control_enabled | dcv_enabled | fan_motor_eff | pump_motor_eff | cost_per_building | cost_per_building_dcv | cost_per_building_exhaustfans | cost_per_building_plugreduce | cost_per_building_lightreduce | cost_per_building_fansandpumps
1 | Barracks | 1959-pre | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.895 | 0.895 | 192544 | 64275 | 4523 | 21281 | 92265 | 10200
2 | Fire Hall | 1959-pre | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.895 | 0.895 | 35564 | 8668 | 2261 | 2750 | 15765 | 6120
3 | Food Service | 1959-pre | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 139354 | 7713 | 6784 | 2554 | 111667 | 10636
4 | Food Service | 2005-2014 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 139354 | 7713 | 6784 | 2554 | 111667 | 10636
5 | Hangar | 1959-pre | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 232175 | 65989 | 3769 | 21849 | 133713 | 6855
6 | Hangar | 1960-1979 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 232175 | 65989 | 3769 | 21849 | 133713 | 6855
7 | Hangar | 1980-2004 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 232175 | 65989 | 3769 | 21849 | 133713 | 6855
8 | Maintenance Shop | 1959-pre | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 65656 | 9427 | 2261 | 3121 | 45581 | 5266
9 | Maintenance Shop | 1980-2004 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 65656 | 9427 | 2261 | 3121 | 45581 | 5266
10 | Maintenance Shop-Small | 1959-pre | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 39706 | 7713 | 754 | 2554 | 24169 | 4516
11 | Maintenance Shop-Small | 1960-1979 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 39706 | 7713 | 754 | 2554 | 24169 | 4516
12 | Maintenance Shop-Small | 1980-2004 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 39706 | 7713 | 754 | 2554 | 24169 | 4516
13 | Office | 1959-pre | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 154906 | 43707 | 5276 | 14471 | 83176 | 8276
14 | Office | 1960-1979 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 154906 | 43707 | 5276 | 14471 | 83176 | 8276
15 | Office | 1980-2004 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 154906 | 43707 | 5276 | 14471 | 83176 | 8276
16 | Office-Small | 1960-1979 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 41694 | 13712 | 1508 | 4540 | 20189 | 1745
17 | Office-Small | 1980-2004 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 41694 | 13712 | 1508 | 4540 | 20189 | 1745
18 | Office-Small | 2005-2014 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 41694 | 13712 | 1508 | 4540 | 20189 | 1745
19 | Recreation Center | 1980-2004 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.895 | 0.895 | 310272 | 27424 | 6030 | 9080 | 232340 | 35398
20 | Storage Building | 1959-pre | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 46364 | 857 | 754 | 284 | 24436 | 0
21 | Storage Building | 1960-1979 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 46364 | 857 | 754 | 284 | 24436 | 0
22 | Storage Building | 1980-2004 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 46364 | 857 | 754 | 284 | 24436 | 0
23 | Storage Building | 2005-2014 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 29680 | 857 | 754 | 284 | 24436 | 0
24 | Training Building | 1959-pre | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 211935 | 35137 | 1508 | 11634 | 160307 | 20033
25 | Training Building | 1980-2004 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 218786 | 35137 | 1508 | 11634 | 160307 | 20033
26 | Training Building | 2005-2014 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 218786 | 35137 | 1508 | 11634 | 160307 | 20033
27 | Vehicle Garage | 1959-pre | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 48702 | 8750 | 754 | 2838 | 26160 | 3349
28 | Vehicle Garage | 1980-2004 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 44622 | 8750 | 754 | 2838 | 26160 | 3349
NA | Barracks | 1960-1979 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.895 | 0.895 | 188464 | 64275 | 4523 | 21281 | 92265 | 10200
NA | Barracks | 1980-2004 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.895 | 0.895 | 188464 | 64275 | 4523 | 21281 | 92265 | 10200
30 | Barracks | 2005-2014 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.895 | 0.895 | 192980 | 64275 | 4523 | 21281 | 92265 | 10200
NA | Fire Hall | 1960-1979 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.895 | 0.895 | 40080 | 8668 | 2261 | 2750 | 15765 | 6120
NA | Fire Hall | 1980-2004 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.895 | 0.895 | 36299 | 8668 | 2261 | 2750 | 15765 | 6120
31 | Fire Hall | 2005-2014 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.895 | 0.895 | 34710 | 8668 | 2261 | 2750 | 15765 | 6120
NA | Food Service | 1960-1979 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 133984 | 7713 | 6784 | 2554 | 111667 | 10636
NA | Food Service | 1980-2004 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 133234 | 7713 | 6784 | 2554 | 111667 | 10636
29 | Hangar | 2005-2014 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 233596 | 65989 | 3769 | 21849 | 133713 | 6855
NA | Maintenance Shop | 1960-1979 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 62135 | 9427 | 2261 | 3121 | 45581 | 5266
NA | Maintenance Shop | 2005-2014 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 95788 | 9427 | 2261 | 3121 | 45581 | 5266
NA | Maintenance Shop-Small | 2005-2014 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 70588 | 7713 | 754 | 2554 | 24169 | 4516
NA | Office | 2005-2014 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 182028 | 43707 | 5276 | 14471 | 83176 | 8276
NA | Office-Small | 1959-pre | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 59982 | 13712 | 1508 | 4540 | 20189 | 1745
NA | Recreation Center | 1959-pre | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.895 | 0.895 | 278223 | 27424 | 6030 | 9080 | 232340 | 35398
NA | Recreation Center | 1960-1979 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.895 | 0.895 | 278223 | 27424 | 6030 | 9080 | 232340 | 35398
NA | Recreation Center | 2005-2014 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.895 | 0.895 | 274874 | 27424 | 6030 | 9080 | 232340 | 35398
NA | Training Building | 1960-1979 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 208586 | 35137 | 1508 | 11634 | 160307 | 20033
NA | Vehicle Garage | 1960-1979 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 38502 | 8750 | 754 | 2838 | 26160 | 3349
NA | Vehicle Garage | 2005-2014 | elec_reduce | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.895 | 0.895 | 38502 | 8750 | 754 | 2838 | 26160 | 3349

## ecm_infil_andsetback
baseline_index | building_type | vintage_name | measure_id | infiltration_flow_per_exterior_area | occ_stbck_enabled | occ_stbck_tolerance | occ_stbck_heat_setback | occ_stbck_heat_setpoint | occ_stbck_cool_setback | occ_stbck_cool_setpoint | pump_speed_type | pump_control_type | pump_motor_eff | cost_per_building | infil_cost_per_building
1 | Barracks | 1959-pre | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 195624 | 158818
2 | Fire Hall | 1959-pre | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 72484 | 67418
3 | Food Service | 1959-pre | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 88213 | 83796
4 | Food Service | 2005-2014 | NA | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 4417 | 0
5 | Hangar | 1959-pre | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 134565 | 96777
6 | Hangar | 1960-1979 | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 134565 | 96777
7 | Hangar | 1980-2004 | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 126612 | 88824
8 | Maintenance Shop | 1959-pre | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 79417 | 74019
9 | Maintenance Shop | 1980-2004 | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 72538 | 67140
10 | Maintenance Shop-Small | 1959-pre | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 51523 | 47106
11 | Maintenance Shop-Small | 1960-1979 | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 51523 | 47106
12 | Maintenance Shop-Small | 1980-2004 | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 47617 | 43200
13 | Office | 1959-pre | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 79519 | 54491
14 | Office | 1960-1979 | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 79519 | 54491
15 | Office | 1980-2004 | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 74929 | 49901
16 | Office-Small | 1960-1979 | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 44808 | 36956
17 | Office-Small | 1980-2004 | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 41404 | 33552
18 | Office-Small | 2005-2014 | NA | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 7852 | 0
19 | Recreation Center | 1980-2004 | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 128554 | 112850
20 | Storage Building | 1959-pre | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 37850 | 37359
21 | Storage Building | 1960-1979 | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 37850 | 37359
22 | Storage Building | 1980-2004 | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 34016 | 33525
23 | Storage Building | 2005-2014 | NA | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 491 | 0
24 | Training Building | 1959-pre | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 136565 | 116444
25 | Training Building | 1980-2004 | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 123924 | 103803
26 | Training Building | 2005-2014 | NA | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 20121 | 0
27 | Vehicle Garage | 1959-pre | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | VariableSpeed | Intermittent | 0.895 | 72156 | 67248
28 | Vehicle Garage | 1980-2004 | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | VariableSpeed | Intermittent | 0.895 | 67048 | 62140
NA | Barracks | 1960-1979 | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 158818 | 122012
NA | Barracks | 1980-2004 | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 147696 | 110890
30 | Barracks | 2005-2014 | NA | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 36806 | 0
NA | Fire Hall | 1960-1979 | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 72484 | 67418
NA | Fire Hall | 1980-2004 | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 67897 | 62831
31 | Fire Hall | 2005-2014 | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 5066 | 0
NA | Food Service | 1960-1979 | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 88213 | 83796
NA | Food Service | 1980-2004 | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 81052 | 76635
29 | Hangar | 2005-2014 | NA | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 37788 | 0
NA | Maintenance Shop | 1960-1979 | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 79417 | 74019
NA | Maintenance Shop | 2005-2014 | NA | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 5398 | 0
NA | Maintenance Shop-Small | 2005-2014 | NA | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 4417 | 0
NA | Office | 2005-2014 | NA | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 25028 | 0
NA | Office-Small | 1959-pre | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 44808 | 36956
NA | Recreation Center | 1959-pre | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 138961 | 123257
NA | Recreation Center | 1960-1979 | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 138961 | 123257
NA | Recreation Center | 2005-2014 | NA | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 15704 | 0
NA | Training Building | 1960-1979 | infil_reduce_plus_setback | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 136565 | 116444
NA | Vehicle Garage | 1960-1979 | infil_reduce_plus_setback | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 72156 | 67248
NA | Vehicle Garage | 2005-2014 | NA | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | NA | 4908 | 0

## ecm_load_reduce
baseline_index | building_type | vintage_name | measure_id | infiltration_flow_per_exterior_area | occ_stbck_enabled | occ_stbck_tolerance | occ_stbck_heat_setback | occ_stbck_heat_setpoint | occ_stbck_cool_setback | occ_stbck_cool_setpoint | hw_boiler_nominal_thermal_efficiency | hw_boiler_flow_mode | hw_boiler_curve | hw_boiler_efficiency_curve_temperature_evaluation_variable | hw_boiler_reset_enabled | hw_boiler_reset_highsupplytemp | hw_boiler_reset_outsidehighsupplytemp | hw_boiler_reset_lowsupplytemp | hw_boiler_reset_outsidelowsupplytemp | pump_speed_type | pump_control_type | pump_motor_eff | cost_per_building | infil_cost_per_building | cost_per_building_reset
1 | Barracks | 1959-pre | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 196581 | 158818 | 957
2 | Fire Hall | 1959-pre | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 73441 | 67418 | 957
3 | Food Service | 1959-pre | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 89170 | 83796 | 957
4 | Food Service | 2005-2014 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 5374 | 0 | 957
5 | Hangar | 1959-pre | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 135522 | 96777 | 957
6 | Hangar | 1960-1979 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 135522 | 96777 | 957
7 | Hangar | 1980-2004 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 127569 | 88824 | 957
8 | Maintenance Shop | 1959-pre | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 80374 | 74019 | 957
9 | Maintenance Shop | 1980-2004 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 73495 | 67140 | 957
10 | Maintenance Shop-Small | 1959-pre | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 52480 | 47106 | 957
11 | Maintenance Shop-Small | 1960-1979 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 52480 | 47106 | 957
12 | Maintenance Shop-Small | 1980-2004 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 48574 | 43200 | 957
13 | Office | 1959-pre | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 80476 | 54491 | 957
14 | Office | 1960-1979 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 80476 | 54491 | 957
15 | Office | 1980-2004 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 75886 | 49901 | 957
16 | Office-Small | 1960-1979 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 45765 | 36956 | 957
17 | Office-Small | 1980-2004 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 42361 | 33552 | 957
18 | Office-Small | 2005-2014 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 8809 | 0 | 957
19 | Recreation Center | 1980-2004 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 129511 | 112850 | 957
20 | Storage Building | 1959-pre | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | atmospheric | NA | NA | NA | NA | NA | NA | NA | NA | NA | 37850 | 37359 | 0
21 | Storage Building | 1960-1979 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | atmospheric | NA | NA | NA | NA | NA | NA | NA | NA | NA | 37850 | 37359 | 0
22 | Storage Building | 1980-2004 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | atmospheric | NA | NA | NA | NA | NA | NA | NA | NA | NA | 34016 | 33525 | 0
23 | Storage Building | 2005-2014 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | atmospheric | NA | NA | NA | NA | NA | NA | NA | NA | NA | 491 | 0 | 0
24 | Training Building | 1959-pre | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | atmospheric | NA | NA | NA | NA | NA | NA | NA | NA | NA | 136565 | 116444 | 0
25 | Training Building | 1980-2004 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | atmospheric | NA | NA | NA | NA | NA | NA | NA | NA | NA | 123924 | 103803 | 0
26 | Training Building | 2005-2014 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | NA | atmospheric | NA | NA | NA | NA | NA | NA | NA | NA | NA | 20121 | 0 | 0
27 | Vehicle Garage | 1959-pre | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | VariableSpeed | Intermittent | 0.895 | 73113 | 67248 | 957
28 | Vehicle Garage | 1980-2004 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | VariableSpeed | Intermittent | 0.895 | 68005 | 62140 | 957
NA | Barracks | 1960-1979 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 159775 | 122012 | 957
NA | Barracks | 1980-2004 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 148653 | 110890 | 957
30 | Barracks | 2005-2014 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 37763 | 0 | 957
NA | Fire Hall | 1960-1979 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 73441 | 67418 | 957
NA | Fire Hall | 1980-2004 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 68854 | 62831 | 957
31 | Fire Hall | 2005-2014 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 6023 | 0 | 957
NA | Food Service | 1960-1979 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 89170 | 83796 | 957
NA | Food Service | 1980-2004 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 82009 | 76635 | 957
29 | Hangar | 2005-2014 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 38745 | 0 | 957
NA | Maintenance Shop | 1960-1979 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 80374 | 74019 | 957
NA | Maintenance Shop | 2005-2014 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 6355 | 0 | 957
NA | Maintenance Shop-Small | 2005-2014 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 5374 | 0 | 957
NA | Office | 2005-2014 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 25985 | 0 | 957
NA | Office-Small | 1959-pre | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 45765 | 36956 | 957
NA | Recreation Center | 1959-pre | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 139918 | 123257 | 957
NA | Recreation Center | 1960-1979 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 139918 | 123257 | 957
NA | Recreation Center | 2005-2014 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 16661 | 0 | 957
NA | Training Building | 1960-1979 | load_reduce | 0.0002 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 137522 | 116444 | 957
NA | Vehicle Garage | 1960-1979 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 73113 | 67248 | 957
NA | Vehicle Garage | 2005-2014 | load_reduce | 0.0003 | TRUE | 0.05 | 17 | 22 | 99 | 24 | NA | LeavingSetpointModulated | atmospheric | NA | TRUE | 82 | -25 | 40 | 20 | NA | NA | NA | 5865 | 0 | 957

## ecm_payback
baseline_index | building_type | vintage_name | measure_id | lighting_scaling_factor | lighting_fraction_radiant | lighting_fraction_visible | lighting_return_air_fraction | elec_equipment_load_scaling_factor | elec_equipment_fraction_radiant | elec_equipment_fraction_latent | elec_equipment_fraction_lost | exhaust_fans_occ_control_enabled | dcv_enabled | fan_motor_eff | pump_motor_eff | boiler_reset | hw_boiler_flow_mode | hw_boiler_curve | hw_boiler_reset_enabled | hw_boiler_reset_highsupplytemp | hw_boiler_reset_outsidehighsupplytemp | hw_boiler_reset_lowsupplytemp | hw_boiler_reset_outsidelowsupplytemp | occ_stbck_enabled | occ_stbck_tolerance | occ_stbck_heat_setback | occ_stbck_heat_setpoint | occ_stbck_cool_setback | occ_stbck_cool_setpoint | infiltration_flow_per_exterior_area | cold_deck_reset_enabled | cold_deck_reset_max_supply_air_temp | cold_deck_reset_min_supply_air_temp | pump_speed_type | pump_control_type | pump_motor_eff | cost_per_building | cost_per_building_dcv | cost_per_building_exhaustfans | cost_per_building_plugreduce | cost_per_building_lightreduce | cost_per_building_fansandpumps | cost_per_boiler_reset | cost_per_occ_temp_setback | infil_cost_per_building | cost_per_cold_deck_reset | cost_per_building_recommissioning
1 | Barracks | 1959-pre | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 397597 | 64275 | 4523 | 21281 | 92265 | 10200 | 957 | 36806 | 122012 | 10864 | 34414
2 | Fire Hall | 1959-pre | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 124528 | 8668 | 2261 | 2750 | 15765 | 6120 | 957 | 5066 | 67418 | 3621 | 11902
3 | Food Service | 1959-pre | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 259055 | 7713 | 6784 | 2554 | 111667 | 10636 | 957 | 4417 | 83796 | 14485 | 16046
4 | Food Service | 2005-2014 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 175259 | 7713 | 6784 | 2554 | 111667 | 10636 | 957 | 4417 | 0 | 14485 | 16046
5 | Hangar | 1959-pre | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 408060 | 65989 | 3769 | 21849 | 133713 | 6855 | 957 | 37788 | 96777 | 7243 | 33120
6 | Hangar | 1960-1979 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 408060 | 65989 | 3769 | 21849 | 133713 | 6855 | 957 | 37788 | 96777 | 7243 | 33120
7 | Hangar | 1980-2004 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 400107 | 65989 | 3769 | 21849 | 133713 | 6855 | 957 | 37788 | 88824 | 7243 | 33120
8 | Maintenance Shop | 1959-pre | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 160260 | 9427 | 2261 | 3121 | 45581 | 5266 | 957 | 5398 | 74019 | 3621 | 10609
9 | Maintenance Shop | 1980-2004 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 153381 | 9427 | 2261 | 3121 | 45581 | 5266 | 957 | 5398 | 67140 | 3621 | 10609
10 | Maintenance Shop-Small | 1959-pre | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 102017 | 7713 | 754 | 2554 | 24169 | 4516 | 957 | 4417 | 47106 | 3621 | 6210
11 | Maintenance Shop-Small | 1960-1979 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 102017 | 7713 | 754 | 2554 | 24169 | 4516 | 957 | 4417 | 47106 | 3621 | 6210
12 | Maintenance Shop-Small | 1980-2004 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 98111 | 7713 | 754 | 2554 | 24169 | 4516 | 957 | 4417 | 43200 | 3621 | 6210
13 | Office | 1959-pre | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 282727 | 43707 | 5276 | 14471 | 83176 | 8276 | 957 | 25028 | 54491 | 18106 | 29239
14 | Office | 1960-1979 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 282727 | 43707 | 5276 | 14471 | 83176 | 8276 | 957 | 25028 | 54491 | 18106 | 29239
15 | Office | 1980-2004 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | VariableSpeed | Intermittent | 0.895 | 278137 | 43707 | 5276 | 14471 | 83176 | 8276 | 957 | 25028 | 49901 | 18106 | 29239
16 | Office-Small | 1960-1979 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 114105 | 13712 | 1508 | 4540 | 20189 | 1745 | 957 | 7852 | 36956 | 14485 | 12161
17 | Office-Small | 1980-2004 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 110701 | 13712 | 1508 | 4540 | 20189 | 1745 | 957 | 7852 | 33552 | 14485 | 12161
18 | Office-Small | 2005-2014 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 77149 | 13712 | 1508 | 4540 | 20189 | 1745 | 957 | 7852 | 0 | 14485 | 12161
19 | Recreation Center | 1980-2004 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 501354 | 27424 | 6030 | 9080 | 232340 | 35398 | 957 | 15704 | 112850 | 32591 | 28980
20 | Storage Building | 1959-pre | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 65397 | 857 | 754 | 284 | 24436 | 0 | 957 | 491 | 37359 | 0 | 259
21 | Storage Building | 1960-1979 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 65397 | 857 | 754 | 284 | 24436 | 0 | 957 | 491 | 37359 | 0 | 259
22 | Storage Building | 1980-2004 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 61563 | 857 | 754 | 284 | 24436 | 0 | 957 | 491 | 33525 | 0 | 259
23 | Storage Building | 2005-2014 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 28038 | 857 | 754 | 284 | 24436 | 0 | 957 | 491 | 0 | 0 | 259
24 | Training Building | 1959-pre | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 400032 | 35137 | 1508 | 11634 | 160307 | 20033 | 957 | 20121 | 116444 | 14485 | 19406
25 | Training Building | 1980-2004 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 387391 | 35137 | 1508 | 11634 | 160307 | 20033 | 957 | 20121 | 103803 | 14485 | 19406
26 | Training Building | 2005-2014 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 283588 | 35137 | 1508 | 11634 | 160307 | 20033 | 957 | 20121 | 0 | 14485 | 19406
27 | Vehicle Garage | 1959-pre | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 134111 | 8750 | 754 | 2838 | 26160 | 3349 | 957 | 4908 | 67248 | 9315 | 9832
28 | Vehicle Garage | 1980-2004 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 129003 | 8750 | 754 | 2838 | 26160 | 3349 | 957 | 4908 | 62140 | 9315 | 9832
NA | Barracks | 1960-1979 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 0 | 64275 | 4523 | 21281 | 92265 | 10200 | 957 | 36806 | 122012 | 10864 | 34414
NA | Barracks | 1980-2004 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 0 | 64275 | 4523 | 21281 | 92265 | 10200 | 957 | 36806 | 110890 | 10864 | 34414
30 | Barracks | 2005-2014 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 275585 | 64275 | 4523 | 21281 | 92265 | 10200 | 957 | 36806 | 0 | 10864 | 34414
NA | Fire Hall | 1960-1979 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 0 | 8668 | 2261 | 2750 | 15765 | 6120 | 957 | 5066 | 67418 | 3621 | 11902
NA | Fire Hall | 1980-2004 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 0 | 8668 | 2261 | 2750 | 15765 | 6120 | 957 | 5066 | 62831 | 3621 | 11902
31 | Fire Hall | 2005-2014 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 57110 | 8668 | 2261 | 2750 | 15765 | 6120 | 957 | 5066 | 0 | 3621 | 11902
NA | Food Service | 1960-1979 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 0 | 7713 | 6784 | 2554 | 111667 | 10636 | 957 | 4417 | 83796 | 14485 | 16046
NA | Food Service | 1980-2004 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 0 | 7713 | 6784 | 2554 | 111667 | 10636 | 957 | 4417 | 76635 | 14485 | 16046
29 | Hangar | 2005-2014 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 311283 | 65989 | 3769 | 21849 | 133713 | 6855 | 957 | 37788 | 0 | 7243 | 33120
NA | Maintenance Shop | 1960-1979 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 0 | 9427 | 2261 | 3121 | 45581 | 5266 | 957 | 5398 | 74019 | 3621 | 10609
NA | Maintenance Shop | 2005-2014 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 0 | 9427 | 2261 | 3121 | 45581 | 5266 | 957 | 5398 | 0 | 3621 | 10609
NA | Maintenance Shop-Small | 2005-2014 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 0 | 7713 | 754 | 2554 | 24169 | 4516 | 957 | 4417 | 0 | 3621 | 6210
NA | Office | 2005-2014 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 0 | 43707 | 5276 | 14471 | 83176 | 8276 | 957 | 25028 | 0 | 18106 | 29239
NA | Office-Small | 1959-pre | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 0 | 13712 | 1508 | 4540 | 20189 | 1745 | 957 | 7852 | 36956 | 14485 | 12161
NA | Recreation Center | 1959-pre | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 0 | 27424 | 6030 | 9080 | 232340 | 35398 | 957 | 15704 | 123257 | 32591 | 28980
NA | Recreation Center | 1960-1979 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 0 | 27424 | 6030 | 9080 | 232340 | 35398 | 957 | 15704 | 123257 | 32591 | 28980
NA | Recreation Center | 2005-2014 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | NA | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 0 | 27424 | 6030 | 9080 | 232340 | 35398 | 957 | 15704 | 0 | 32591 | 28980
NA | Training Building | 1960-1979 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0002 | TRUE | 20 | 13 | NA | NA | NA | 0 | 35137 | 1508 | 11634 | 160307 | 20033 | 957 | 20121 | 116444 | 14485 | 19406
NA | Vehicle Garage | 1960-1979 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 0 | 8750 | 754 | 2838 | 26160 | 3349 | 957 | 4908 | 67248 | 9315 | 9832
NA | Vehicle Garage | 2005-2014 | payback_less_than_20 | 0.7 | NA | NA | NA | 0.9 | 0.3 | NA | NA | TRUE | TRUE | 0.92 | 0.92 | TRUE | LeavingSetpointModulated | atmospheric | TRUE | 82 | -25 | 40 | 20 | TRUE | 0.05 | 17 | 22 | 99 | 24 | 0.0003 | TRUE | 20 | 13 | NA | NA | NA | 0 | 8750 | 754 | 2838 | 26160 | 3349 | 957 | 4908 | 0 | 9315 | 9832

## constants
cost_index | Building Heating Efficiency | Building DES Heating Efficiency | DES Boiler Efficiency | Electricity Fuel Cost Ratio | Natural Gas GHG factor | Electricity GHG factor | Score Energy Reduction Weighting Factor | Score GHG Reduction Weighting Factor | Score Cost Reduction Weighting Factor | Score Probability of Success Weighting Factor | Future growth of base area | Future improvements in V1 EUI | Elec 2014 Cost ($/kWh) | Gas 2014 Cost ($/kWh) | Inflation (%) | Elec Annual Escalation (real %) | Gas Annual Escalation (real %)
1 | 0.6 | 0.8 | 0.55 | 5 | 179 | 870 | 0.35 | 0.35 | 0.15 | 0.15 | 1 | 1 | 0.113 | 0.0162 | 0.02 | 0.04 | 0.02
Note on N1: Lubun, Mike: from sample bill and emails
Note on O1: Lubun, Mike: based on 4.5/GJ

## sim_annual_output
sim_annual_output_index | baseline_id | building_name | vintage_name | measure_id | Simulation Total Capitol Costs $ | Total Floor Area M2 | Conditioned Floor Area M2 | Electricity-Heating KWh | Natural Gas-Heating KWh | Electricity-Cooling KWh | Electricity-Water Systems KWh | Natural Gas-Water Systems KWh | Electricity-Interior Lighting KWh | Electricity-Interior Equipment KWh | District Heating-Interior Equipment KWh | Electricity-Fans KWh | Electricity-Pumps KWh | Electricity-Heat Recovery KWh
1 | 1 | Barracks | 1959-pre | air_temp_reset_enabled | 10547.57 | 5495.7246 | 3894.8 | 0 | 692733.8875 | 19336.1266 | 0 | 168544.5793 | 78836.1742 | 21772.2396 | 0 | 44933.3693 | 33155.5821 | 0
2 | 1 | Barracks | 1959-pre | baseline | 0 | 5495.7246 | 3894.8 | 0 | 660878.3065 | 6675.0053 | 0 | 168547.3571 | 78836.1742 | 21772.2396 | 0 | 43827.8128 | 29830.5794 | 0
3 | 1 | Barracks | 1959-pre | boiler_eff_upgrade | 65332.04 | 5495.7246 | 3894.8 | 0 | 650750.5206 | 8158.3399 | 0 | 168547.3571 | 78836.1742 | 21772.2396 | 0 | 44933.3693 | 30508.3577 | 0
4 | 1 | Barracks | 1959-pre | boiler_reset | 929.13 | 5495.7246 | 3894.8 | 0 | 432303.1236 | 8158.3399 | 0 | 168547.3571 | 78836.1742 | 21772.2396 | 0 | 44933.3693 | 775.0006 | 0
5 | 1 | Barracks | 1959-pre | cooling_cop_3_0 | 14818.45 | 5495.7246 | 3894.8 | 0 | 650750.5206 | 5827.7824 | 0 | 168547.3571 | 78836.1742 | 21772.2396 | 0 | 44933.3693 | 30508.3577 | 0
6 | 1 | Barracks | 1959-pre | dcv_enabled | 62402.91 | 5495.7246 | 3894.8 | 0 | 628542.1695 | 9147.2295 | 0 | 168547.3571 | 78836.1742 | 21772.2396 | 0 | 44933.3693 | 30230.5797 | 0
7 | 1 | Barracks | 1959-pre | ecm_cold_deck_reset_control | 10547.57 | 5495.7246 | 3894.8 | 0 | 649131.0749 | 16533.3466 | 0 | 168541.8015 | 78836.1742 | 21772.2396 | 0 | 44933.3693 | 31044.4693 | 0
8 | 1 | Barracks | 1959-pre | economizers_enabled | 4121.36 | 5495.7246 | 3894.8 | 0 | 650686.6317 | 6297.2273 | 0 | 168547.3571 | 78836.1742 | 21772.2396 | 0 | 44933.3693 | 30430.5799 | 0
9 | 1 | Barracks | 1959-pre | elec_reduce | 186935.92 | 5495.7246 | 3894.8 | 0 | 658981.0827 | 6866.6722 | 0 | 168547.3571 | 55183.3775 | 21772.2396 | 0 | 43994.4796 | 23702.7967 | 0
10 | 1 | Barracks | 1959-pre | envelope_ecm_roof | 225514.56 | 5495.7246 | 3894.8 | 0 | 647361.629 | 8127.7843 | 0 | 168547.3571 | 78836.1742 | 21772.2396 | 0 | 44802.8136 | 30361.1354 | 0
11 | 1 | Barracks | 1959-pre | envelope_ecm_wall | 497905.83 | 5495.7246 | 3894.8 | 0 | 617806.0498 | 8238.8955 | 0 | 168547.3571 | 78836.1742 | 21772.2396 | 0 | 44083.3686 | 29366.6902 | 0
12 | 1 | Barracks | 1959-pre | envelope_ecm_windows | 367166.99 | 5495.7246 | 3894.8 | 0 | 588850.4711 | 8930.5627 | 0 | 168547.3571 | 78836.1742 | 21772.2396 | 0 | 43397.2569 | 28463.9117 | 0
13 | 1 | Barracks | 1959-pre | fans_to_variable | 3029.13 | 5495.7246 | 3894.8 | 0 | 651189.4098 | 8127.7843 | 0 | 168547.3571 | 78836.1742 | 21772.2396 | 0 | 44580.5912 | 30513.9133 | 0
14 | 1 | Barracks | 1959-pre | hrv_enabled | 263559.22 | 5495.7246 | 3894.8 | 0 | 601394.9256 | 9186.1185 | 0 | 168547.3571 | 78836.1742 | 21772.2396 | 0 | 44933.3693 | 30208.3575 | 13138.8994
15 | 1 | Barracks | 1959-pre | infil_reduce | 118458.25 | 5495.7246 | 3894.8 | 0 | 309661.3588 | 13633.3442 | 0 | 168544.5793 | 78836.1742 | 21772.2396 | 0 | 40450.0324 | 19622.2379 | 0
16 | 1 | Barracks | 1959-pre | infil_reduce_plus_setback | 189926.21 | 5495.7246 | 3894.8 | 0 | 346969.722 | 12811.1214 | 0 | 168544.5793 | 78836.1742 | 21772.2396 | 0 | 25730.5761 | 12483.3433 | 0
17 | 1 | Barracks | 1959-pre | lights_reduce_70p | 89577.67 | 5495.7246 | 3894.8 | 0 | 680856.1002 | 6200.005 | 0 | 168547.3571 | 55183.3775 | 21772.2396 | 0 | 43975.0352 | 30575.0245 | 0
18 | 1 | Barracks | 1959-pre | load_reduce | 190855.34 | 5495.7246 | 3894.8 | 0 | 246394.6416 | 12811.1214 | 0 | 168544.5793 | 78836.1742 | 21772.2396 | 0 | 25730.5761 | 691.6672 | 0
19 | 1 | Barracks | 1959-pre | occupancy_setback | 35733.98 | 5495.7246 | 3894.8 | 0 | 697303.3356 | 8808.3404 | 0 | 168547.3571 | 78836.1742 | 21772.2396 | 0 | 37466.6966 | 26033.3542 | 0
20 | 1 | Barracks | 1959-pre | payback_less_than_20 | 386016.5 | 5495.7246 | 3894.8 | 0 | 257975.2064 | 16988.9025 | 0 | 168541.8015 | 55183.3775 | 21772.2396 | 0 | 25858.354 | 611.1116 | 0
21 | 1 | Barracks | 1959-pre | plug_loads_90_percent | 20661.17 | 5495.7246 | 3894.8 | 0 | 651650.5213 | 8033.3398 | 0 | 168547.3571 | 78836.1742 | 21772.2396 | 0 | 44938.9248 | 30536.1355 | 0
22 | 1 | Barracks | 1959-pre | pump_fan_eff_ | 9902.91 | 5495.7246 | 3894.8 | 0 | 650750.5206 | 8158.3399 | 0 | 168547.3571 | 78836.1742 | 21772.2396 | 0 | 44933.3693 | 23861.1302 | 0
23 | 2 | Fire Hall | 1959-pre | air_temp_reset_enabled | 2679.61 | 911.7335 | 911.734 | 0 | 474355.935 | 6308.3384 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 36722.2516 | 12633.3434 | 0
24 | 2 | Fire Hall | 1959-pre | baseline | 0 | 911.7335 | 911.734 | 0 | 489444.836 | 1347.2233 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 36811.1406 | 14077.789 | 0
25 | 2 | Fire Hall | 1959-pre | boiler_eff_upgrade | 32923.3 | 911.7335 | 911.734 | 0 | 483664.2758 | 1400.0011 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 36697.2516 | 14016.6779 | 0
26 | 2 | Fire Hall | 1959-pre | boiler_reset | 929.13 | 911.7335 | 911.734 | 0 | 354739.1727 | 1400.0011 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 36697.2516 | 14016.6779 | 0
27 | 2 | Fire Hall | 1959-pre | cooling_cop_3_0 | 9825.24 | 911.7335 | 911.734 | 0 | 483664.2758 | 1000.0008 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 36697.2516 | 14016.6779 | 0
28 | 2 | Fire Hall | 1959-pre | dcv_enabled | 8415.53 | 911.7335 | 911.734 | 0 | 483664.2758 | 1400.0011 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 36697.2516 | 14016.6779 | 0
29 | 2 | Fire Hall | 1959-pre | ecm_cold_deck_reset_control | 3515.53 | 911.7335 | 911.734 | 0 | 430644.789 | 4144.4478 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 36722.2516 | 12355.5654 | 0
30 | 2 | Fire Hall | 1959-pre | economizers_enabled | 1071.84 | 911.7335 | 911.734 | 0 | 484342.0541 | 1338.89 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 36697.2516 | 13405.5663 | 0
31 | 2 | Fire Hall | 1959-pre | elec_reduce | 34528.16 | 911.7335 | 911.734 | 0 | 513030.966 | 941.6674 | 21566.6839 | 0 | 58833.3804 | 24133.3526 | 0 | 37077.8074 | 11177.7867 | 0
32 | 2 | Fire Hall | 1959-pre | envelope_ecm_roof | 173732.04 | 911.7335 | 911.734 | 0 | 476569.8257 | 1361.1122 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 36416.6958 | 13844.4555 | 0
33 | 2 | Fire Hall | 1959-pre | envelope_ecm_wall | 271844.66 | 911.7335 | 911.734 | 0 | 471578.155 | 1402.7789 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 36191.6956 | 13663.8998 | 0
34 | 2 | Fire Hall | 1959-pre | envelope_ecm_windows | 59461.17 | 911.7335 | 911.734 | 0 | 474286.4905 | 1427.7789 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 36322.2513 | 13713.8999 | 0
35 | 2 | Fire Hall | 1959-pre | fans_to_variable | 1056.31 | 911.7335 | 911.734 | 0 | 483794.8315 | 1394.4456 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 36586.1404 | 14019.4557 | 0
36 | 2 | Fire Hall | 1959-pre | hrv_enabled | 70786.41 | 911.7335 | 911.734 | 0 | 420011.4471 | 2388.8908 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 36683.3627 | 13366.6774 | 4380.5591
37 | 2 | Fire Hall | 1959-pre | infil_reduce | 65454.37 | 911.7335 | 911.734 | 0 | 219483.5089 | 2461.1131 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 26547.2435 | 7250.0058 | 0
38 | 2 | Fire Hall | 1959-pre | infil_reduce_plus_setback | 70372.82 | 911.7335 | 911.734 | 0 | 260089.097 | 2569.4465 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 28100.0225 | 7780.5618 | 0
39 | 2 | Fire Hall | 1959-pre | lights_reduce_70p | 15305.83 | 911.7335 | 911.734 | 0 | 512717.0768 | 930.5563 | 21566.6839 | 0 | 58833.3804 | 24133.3526 | 0 | 37058.363 | 14291.6781 | 0
40 | 2 | Fire Hall | 1959-pre | load_reduce | 71301.94 | 911.7335 | 911.734 | 0 | 188861.2622 | 2569.4465 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 28100.0225 | 7780.5618 | 0
41 | 2 | Fire Hall | 1959-pre | occupancy_setback | 4918.45 | 911.7335 | 911.734 | 0 | 563394.8952 | 1725.0014 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 40458.3657 | 15338.9012 | 0
42 | 2 | Fire Hall | 1959-pre | payback_less_than_20 | 120900.97 | 911.7335 | 911.734 | 0 | 168547.3571 | 2911.1134 | 21566.6839 | 0 | 58833.3804 | 24133.3526 | 0 | 28569.4673 | 5525.0044 | 0
43 | 2 | Fire Hall | 1959-pre | plug_loads_90_percent | 2669.9 | 911.7335 | 911.734 | 0 | 483978.165 | 1413.89 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 36713.9183 | 14016.6779 | 0
44 | 2 | Fire Hall | 1959-pre | pump_fan_eff_ | 5941.75 | 911.7335 | 911.734 | 0 | 483664.2758 | 1400.0011 | 21566.6839 | 0 | 84050.0672 | 24133.3526 | 0 | 36697.2516 | 10963.8977 | 0
45 | 3 | Food Service | 1959-pre | air_temp_reset_enabled | 14063.11 | 2693.605 | 2210.07 | 0 | 1760948.631 | 27791.6889 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 95752.8544 | 39475.0316 | 0
46 | 3 | Food Service | 1959-pre | baseline | 0 | 2693.605 | 2210.07 | 0 | 1677520.7865 | 8136.1176 | 146561.2284 | 0 | 217955.7299 | 33694.4714 | 0 | 95433.4097 | 38436.1419 | 0
47 | 3 | Food Service | 1959-pre | boiler_eff_upgrade | 65332.04 | 2693.605 | 2210.07 | 0 | 1653040.2113 | 11319.4535 | 146558.4506 | 0 | 217955.7299 | 33694.4714 | 0 | 95819.5211 | 39030.5868 | 0
48 | 3 | Food Service | 1959-pre | boiler_reset | 929.13 | 2693.605 | 2210.07 | 0 | 1327234.3951 | 11319.4535 | 146558.4506 | 0 | 217955.7299 | 33694.4714 | 0 | 95819.5211 | 2083.335 | 0
49 | 3 | Food Service | 1959-pre | cooling_cop_3_0 | 19757.28 | 2693.605 | 2210.07 | 0 | 1653040.2113 | 8086.1176 | 146558.4506 | 0 | 217955.7299 | 33694.4714 | 0 | 95819.5211 | 39030.5868 | 0
50 | 3 | Food Service | 1959-pre | dcv_enabled | 7488.35 | 2693.605 | 2210.07 | 0 | 1154262.0345 | 16955.5691 | 146558.4506 | 0 | 217955.7299 | 33694.4714 | 0 | 95827.8544 | 38194.475 | 0
51 | 3 | Food Service | 1959-pre | ecm_cold_deck_reset_control | 14063.11 | 2693.605 | 2210.07 | 0 | 1597920.7228 | 15061.1232 | 146552.895 | 0 | 217955.7299 | 33694.4714 | 0 | 96058.4102 | 38655.5865 | 0
52 | 3 | Food Service | 1959-pre | economizers_enabled | 4689.32 | 2693.605 | 2210.07 | 0 | 1653045.7669 | 10280.5638 | 146558.4506 | 0 | 217955.7299 | 33694.4714 | 0 | 95819.5211 | 38983.3645 | 0
53 | 3 | Food Service | 1959-pre | elec_reduce | 135295.15 | 2693.605 | 2210.07 | 0 | 1231556.5408 | 10919.4532 | 146561.2284 | 0 | 152569.5665 | 33694.4714 | 0 | 63572.2731 | 30116.6908 | 0
54 | 3 | Food Service | 1959-pre | envelope_ecm_roof | 445117.48 | 2693.605 | 2210.07 | 0 | 1593265.1635 | 11077.7866 | 146558.4506 | 0 | 217955.7299 | 33694.4714 | 0 | 93672.2972 | 37369.4743 | 0
55 | 3 | Food Service | 1959-pre | envelope_ecm_wall | 407709.71 | 2693.605 | 2210.07 | 0 | 1628451.3028 | 11361.1202 | 146558.4506 | 0 | 217955.7299 | 33694.4714 | 0 | 94847.2981 | 38213.9195 | 0
56 | 3 | Food Service | 1959-pre | envelope_ecm_windows | 269689.32 | 2693.605 | 2210.07 | 0 | 1593704.0527 | 11416.6758 | 146558.4506 | 0 | 217955.7299 | 33694.4714 | 0 | 93869.5195 | 37558.3634 | 0
57 | 3 | Food Service | 1959-pre | exhaust_fans_occ_control | 6586.41 | 2693.605 | 2210.07 | 0 | 1653034.6558 | 11319.4535 | 146558.4506 | 0 | 217955.7299 | 33694.4714 | 0 | 63300.0506 | 39025.0312 | 0
58 | 3 | Food Service | 1959-pre | fans_to_variable | 4038.83 | 2693.605 | 2210.07 | 0 | 1653715.2119 | 11294.4535 | 146558.4506 | 0 | 217955.7299 | 33694.4714 | 0 | 95300.0762 | 39030.5868 | 0
59 | 3 | Food Service | 1959-pre | hrv_enabled | 287379.61 | 2693.605 | 2210.07 | 0 | 1037595.2745 | 17136.1248 | 146558.4506 | 0 | 217955.7299 | 33694.4714 | 0 | 95813.9655 | 37580.5856 | 17519.4585
60 | 3 | Food Service | 1959-pre | infil_reduce | 81355.34 | 2693.605 | 2210.07 | 0 | 923961.8503 | 14519.4561 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 78836.1742 | 22944.4628 | 0
61 | 3 | Food Service | 1959-pre | infil_reduce_plus_setback | 85643.69 | 2693.605 | 2210.07 | 0 | 841017.3395 | 6800.0054 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 79361.1746 | 22438.9068 | 0
62 | 3 | Food Service | 1959-pre | lights_reduce_70p | 108414.56 | 2693.605 | 2210.07 | 0 | 1734084.7206 | 7588.895 | 146561.2284 | 0 | 152569.5665 | 33694.4714 | 0 | 96050.0768 | 39438.9204 | 0
63 | 3 | Food Service | 1959-pre | load_reduce | 86572.82 | 2693.605 | 2210.07 | 0 | 661692.196 | 6800.0054 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 79361.1746 | 1213.8899 | 0
64 | 3 | Food Service | 1959-pre | occupancy_setback | 4288.35 | 2693.605 | 2210.07 | 0 | 1547387.349 | 4888.8928 | 146558.4506 | 0 | 217955.7299 | 33694.4714 | 0 | 104436.1947 | 41438.922 | 0
65 | 3 | Food Service | 1959-pre | payback_less_than_20 | 251509.71 | 2693.605 | 2210.07 | 0 | 406655.8809 | 20263.9051 | 146552.895 | 0 | 152569.5665 | 33694.4714 | 0 | 41863.9224 | 491.6671 | 0
66 | 3 | Food Service | 1959-pre | plug_loads_90_percent | 2479.61 | 2693.605 | 2210.07 | 0 | 1654851.3239 | 11122.2311 | 146558.4506 | 0 | 217955.7299 | 33694.4714 | 0 | 95847.2989 | 38933.3645 | 0
67 | 3 | Food Service | 1959-pre | pump_fan_eff_ | 10326.21 | 2693.605 | 2210.07 | 0 | 1653040.2113 | 11319.4535 | 146558.4506 | 0 | 217955.7299 | 33694.4714 | 0 | 95819.5211 | 30525.0244 | 0
68 | 4 | Food Service | 2005-2014 | air_temp_reset_enabled | 14063.11 | 2693.605 | 2210.07 | 0 | 1108434.2201 | 14727.7896 | 146552.895 | 0 | 217955.7299 | 33694.4714 | 0 | 76180.6165 | 24583.353 | 0
69 | 4 | Food Service | 2005-2014 | baseline | 0 | 2693.605 | 2210.07 | 0 | 884311.8186 | 5825.0047 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 69336.1666 | 18133.3478 | 0
70 | 4 | Food Service | 2005-2014 | boiler_eff_upgrade | 32923.3 | 2693.605 | 2210.07 | 0 | 892445.1584 | 10363.8972 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 76313.9499 | 22208.3511 | 0
71 | 4 | Food Service | 2005-2014 | boiler_reset | 929.13 | 2693.605 | 2210.07 | 0 | 698803.3368 | 10363.8972 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 76313.9499 | 1308.3344 | 0
72 | 4 | Food Service | 2005-2014 | cooling_cop_3_0 | 19757.28 | 2693.605 | 2210.07 | 0 | 892445.1584 | 10363.8972 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 76313.9499 | 22208.3511 | 0
73 | 4 | Food Service | 2005-2014 | dcv_enabled | 7488.35 | 2693.605 | 2210.07 | 0 | 419939.2248 | 18902.7929 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 76319.5055 | 19575.0157 | 0
74 | 4 | Food Service | 2005-2014 | ecm_cold_deck_reset_control | 14063.11 | 2693.605 | 2210.07 | 0 | 877709.0355 | 11036.1199 | 146552.895 | 0 | 217955.7299 | 33694.4714 | 0 | 76338.95 | 22352.7957 | 0
75 | 4 | Food Service | 2005-2014 | economizers_enabled | 4689.32 | 2693.605 | 2210.07 | 0 | 892461.8251 | 8755.5626 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 76313.9499 | 22177.7955 | 0
76 | 4 | Food Service | 2005-2014 | elec_reduce | 135295.15 | 2693.605 | 2210.07 | 0 | 448155.9141 | 12361.121 | 146555.6728 | 0 | 152569.5665 | 33694.4714 | 0 | 38030.586 | 14102.7891 | 0
77 | 4 | Food Service | 2005-2014 | envelope_ecm_roof | 0 | 2693.605 | 2210.07 | 0 | 853025.6824 | 10358.3416 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 75466.727 | 21216.6836 | 0
78 | 4 | Food Service | 2005-2014 | envelope_ecm_wall | 0 | 2693.605 | 2210.07 | 0 | 884161.8184 | 10391.675 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 76294.5055 | 22011.1287 | 0
79 | 4 | Food Service | 2005-2014 | envelope_ecm_windows | 269689.32 | 2693.605 | 2210.07 | 0 | 864628.4695 | 10666.6752 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 76352.8389 | 21811.1286 | 0
80 | 4 | Food Service | 2005-2014 | exhaust_fans_occ_control | 6586.41 | 2693.605 | 2210.07 | 0 | 892442.3806 | 10363.8972 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 43794.4795 | 22208.3511 | 0
81 | 4 | Food Service | 2005-2014 | fans_to_variable | 4038.83 | 2693.605 | 2210.07 | 0 | 892845.1587 | 10350.0083 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 75986.1719 | 22211.1289 | 0
82 | 4 | Food Service | 2005-2014 | hrv_enabled | 287379.61 | 2693.605 | 2210.07 | 0 | 298155.7941 | 20247.2384 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 76300.061 | 19222.2376 | 17516.6807
83 | 4 | Food Service | 2005-2014 | lights_reduce_70p | 108414.56 | 2693.605 | 2210.07 | 0 | 916467.3998 | 6541.6719 | 146555.6728 | 0 | 152569.5665 | 33694.4714 | 0 | 70522.2786 | 19819.4603 | 0
84 | 4 | Food Service | 2005-2014 | load_reduce | 5217.48 | 2693.605 | 2210.07 | 0 | 625750.5006 | 4897.2261 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 76380.6167 | 1175.0009 | 0
85 | 4 | Food Service | 2005-2014 | occupancy_setback | 4288.35 | 2693.605 | 2210.07 | 0 | 799420.084 | 4897.2261 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 76380.6167 | 21825.0175 | 0
86 | 4 | Food Service | 2005-2014 | payback_less_than_20 | 170154.37 | 2693.605 | 2210.07 | 0 | 372208.6311 | 14491.6783 | 146552.895 | 0 | 152569.5665 | 33694.4714 | 0 | 39080.5868 | 475.0004 | 0
87 | 4 | Food Service | 2005-2014 | plug_loads_90_percent | 2479.61 | 2693.605 | 2210.07 | 0 | 892034.047 | 10141.6748 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 76294.5055 | 22191.6844 | 0
88 | 4 | Food Service | 2005-2014 | pump_fan_eff_ | 10326.21 | 2693.605 | 2210.07 | 0 | 892445.1584 | 10363.8972 | 146555.6728 | 0 | 217955.7299 | 33694.4714 | 0 | 76313.9499 | 17369.4583 | 0
89 | 5 | Hangar | 1959-pre | air_temp_reset_enabled | 7032.04 | 6276.5798 | 6146.53 | 0 | 2810866.1376 | 29638.9126 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 65186.1633 | 63533.3842 | 0
90 | 5 | Hangar | 1959-pre | baseline | 0 | 6276.5798 | 6146.53 | 0 | 2787785.5636 | 2172.224 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 64925.0519 | 55930.6003 | 0
91 | 5 | Hangar | 1959-pre | boiler_eff_upgrade | 169937.86 | 6276.5798 | 6146.53 | 0 | 2765213.3233 | 2700.0022 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 65186.1633 | 55916.7114 | 0
92 | 5 | Hangar | 1959-pre | boiler_reset | 929.13 | 6276.5798 | 6146.53 | 0 | 2280968.4914 | 2700.0022 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 65186.1633 | 2386.113 | 0
93 | 5 | Hangar | 1959-pre | cooling_cop_3_0 | 16104.85 | 6276.5798 | 6146.53 | 0 | 2765213.3233 | 1927.7793 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 65186.1633 | 55916.7114 | 0
94 | 5 | Hangar | 1959-pre | dcv_enabled | 64066.99 | 6276.5798 | 6146.53 | 0 | 2374085.2326 | 3327.7804 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 65186.1633 | 54458.3769 | 0
95 | 5 | Hangar | 1959-pre | ecm_cold_deck_reset_control | 7032.04 | 6276.5798 | 6146.53 | 0 | 2719763.2869 | 14191.678 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 65186.1633 | 55797.2669 | 0
96 | 5 | Hangar | 1959-pre | economizers_enabled | 2747.57 | 6276.5798 | 6146.53 | 0 | 2765263.3233 | 2619.4465 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 65186.1633 | 55902.8225 | 0
97 | 5 | Hangar | 1959-pre | elec_reduce | 225412.62 | 6276.5798 | 6146.53 | 0 | 2478210.3159 | 2147.2239 | 0 | 35836.1398 | 245597.4187 | 39044.4757 | 0 | 60030.6036 | 43475.0348 | 0
98 | 5 | Hangar | 1959-pre | envelope_ecm_roof | 1116538.83 | 6276.5798 | 6146.53 | 0 | 2569113.1664 | 2425.0019 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 61880.6051 | 52466.7086 | 0
99 | 5 | Hangar | 1959-pre | envelope_ecm_wall | 895777.67 | 6276.5798 | 6146.53 | 0 | 2654668.7904 | 2541.6687 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 60925.0487 | 51569.4857 | 0
100 | 5 | Hangar | 1959-pre | envelope_ecm_windows | 187541.75 | 6276.5798 | 6146.53 | 0 | 2734493.8543 | 2644.4466 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 63944.4956 | 54552.8214 | 0
101 | 5 | Hangar | 1959-pre | exhaust_fans_occ_control | 3659.22 | 6276.5798 | 6146.53 | 0 | 2765202.2122 | 2708.3355 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 59875.0479 | 55916.7114 | 0
102 | 5 | Hangar | 1959-pre | fans_to_variable | 2189.32 | 6276.5798 | 6146.53 | 0 | 2766113.324 | 2686.1133 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 64597.2739 | 55919.4892 | 0
103 | 5 | Hangar | 1959-pre | hrv_enabled | 181615.53 | 6276.5798 | 6146.53 | 0 | 2441946.398 | 3805.5586 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 65186.1633 | 54419.488 | 8761.1181
104 | 5 | Hangar | 1959-pre | infil_reduce | 93958.25 | 6276.5798 | 6146.53 | 0 | 1596437.3883 | 2900.0023 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 44075.0353 | 33336.1378 | 0
105 | 5 | Hangar | 1959-pre | infil_reduce_plus_setback | 130645.63 | 6276.5798 | 6146.53 | 0 | 1380506.66 | 1786.1125 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 37830.5858 | 26397.2433 | 0
106 | 5 | Hangar | 1959-pre | lights_reduce_70p | 129818.45 | 6276.5798 | 6146.53 | 0 | 2868477.2948 | 1761.1125 | 0 | 35836.1398 | 245597.4187 | 39044.4757 | 0 | 65311.1634 | 56852.8233 | 0
107 | 5 | Hangar | 1959-pre | load_reduce | 131574.76 | 6276.5798 | 6146.53 | 0 | 1121112.008 | 1786.1125 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 37830.5858 | 1783.3348 | 0
108 | 5 | Hangar | 1959-pre | occupancy_setback | 36687.38 | 6276.5798 | 6146.53 | 0 | 2445082.5116 | 1466.6678 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 55150.0441 | 45500.0364 | 0
109 | 5 | Hangar | 1959-pre | payback_less_than_20 | 396174.76 | 6276.5798 | 6146.53 | 0 | 947200.7578 | 11636.1204 | 0 | 35836.1398 | 245597.4187 | 39044.4757 | 0 | 32669.4706 | 680.5561 | 0
110 | 5 | Hangar | 1959-pre | plug_loads_90_percent | 21212.62 | 6276.5798 | 6146.53 | 0 | 2766066.1017 | 2638.891 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 65219.4966 | 55952.8225 | 0
111 | 5 | Hangar | 1959-pre | pumps_to_variable | 3425.24 | 6276.5798 | 6146.53 | 0 | 2765213.3233 | 2700.0022 | 0 | 35936.1399 | 350853.0585 | 39044.4757 | 0 | 65186.1633 | 55816.7113 | 0
112 | 5 | Hangar | 1959-pre | pump_fan_eff_ | 6655.34 | 6276.5798 | 6146.53 | 0 | 2765213.3233 | 2700.0022 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 65186.1633 | 43733.3683 | 0
113 | 6 | Hangar | 1960-1979 | air_temp_reset_enabled | 7032.04 | 6276.5798 | 6146.53 | 0 | 2717154.9515 | 27986.1335 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 61836.1606 | 59686.1589 | 0
114 | 6 | Hangar | 1960-1979 | baseline | 0 | 6276.5798 | 6146.53 | 0 | 2706629.9431 | 1758.3347 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 61605.6048 | 52755.5978 | 0
115 | 6 | Hangar | 1960-1979 | boiler_eff_upgrade | 169937.86 | 6276.5798 | 6146.53 | 0 | 2676379.9189 | 2269.4463 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 61836.1606 | 52694.4866 | 0
116 | 6 | Hangar | 1960-1979 | boiler_reset | 929.13 | 6276.5798 | 6146.53 | 0 | 2213046.2149 | 2269.4463 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 61836.1606 | 2319.4463 | 0
117 | 6 | Hangar | 1960-1979 | cooling_cop_3_0 | 16104.85 | 6276.5798 | 6146.53 | 0 | 2676379.9189 | 1619.4457 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 61836.1606 | 52694.4866 | 0
118 | 6 | Hangar | 1960-1979 | dcv_enabled | 64066.99 | 6276.5798 | 6146.53 | 0 | 2286535.1626 | 2750.0022 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 61836.1606 | 51308.3744 | 0
119 | 6 | Hangar | 1960-1979 | ecm_cold_deck_reset_control | 7032.04 | 6276.5798 | 6146.53 | 0 | 2628588.214 | 13294.4551 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 61836.1606 | 52555.5976 | 0
120 | 6 | Hangar | 1960-1979 | economizers_enabled | 2747.57 | 6276.5798 | 6146.53 | 0 | 2676427.1411 | 2197.224 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 61836.1606 | 52666.7088 | 0
121 | 6 | Hangar | 1960-1979 | elec_reduce | 225412.62 | 6276.5798 | 6146.53 | 0 | 2388668.5776 | 1694.4458 | 0 | 35836.1398 | 245597.4187 | 39044.4757 | 0 | 56683.3787 | 40972.255 | 0
122 | 6 | Hangar | 1960-1979 | envelope_ecm_roof | 1208261.17 | 6276.5798 | 6146.53 | 0 | 2433260.2799 | 1944.446 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 57644.4906 | 48350.0387 | 0
123 | 6 | Hangar | 1960-1979 | envelope_ecm_wall | 895777.67 | 6276.5798 | 6146.53 | 0 | 2613604.8687 | 2211.1129 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 59338.9364 | 50180.5957 | 0
124 | 6 | Hangar | 1960-1979 | envelope_ecm_windows | 187541.75 | 6276.5798 | 6146.53 | 0 | 2645999.339 | 2208.3351 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 60600.0485 | 51363.93 | 0
125 | 6 | Hangar | 1960-1979 | exhaust_fans_occ_control | 3659.22 | 6276.5798 | 6146.53 | 0 | 2676368.8078 | 2275.0018 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 56525.0452 | 52694.4866 | 0
126 | 6 | Hangar | 1960-1979 | fans_to_variable | 2189.32 | 6276.5798 | 6146.53 | 0 | 2677221.5862 | 2258.3351 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 61280.6046 | 52705.5977 | 0
127 | 6 | Hangar | 1960-1979 | hrv_enabled | 181615.53 | 6276.5798 | 6146.53 | 0 | 2354624.1059 | 3255.5582 | 0 | 35838.9176 | 350853.0585 | 39044.4757 | 0 | 61836.1606 | 51322.2633 | 8761.1181
128 | 6 | Hangar | 1960-1979 | infil_reduce | 93958.25 | 6276.5798 | 6146.53 | 0 | 1622087.4088 | 2302.7796 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 42772.2564 | 32419.4704 | 0
129 | 6 | Hangar | 1960-1979 | infil_reduce_plus_setback | 130645.63 | 6276.5798 | 6146.53 | 0 | 1387317.7765 | 1444.4456 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 36613.9182 | 25458.3537 | 0
130 | 6 | Hangar | 1960-1979 | lights_reduce_70p | 129818.45 | 6276.5798 | 6146.53 | 0 | 2777718.8888 | 1411.1122 | 0 | 35836.1398 | 245597.4187 | 39044.4757 | 0 | 61961.1607 | 53619.4873 | 0
131 | 6 | Hangar | 1960-1979 | load_reduce | 131574.76 | 6276.5798 | 6146.53 | 0 | 1136350.9091 | 1444.4456 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 36613.9182 | 1769.4459 | 0
132 | 6 | Hangar | 1960-1979 | occupancy_setback | 36687.38 | 6276.5798 | 6146.53 | 0 | 2348490.7677 | 1255.5566 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 52244.4862 | 42577.8118 | 0
133 | 6 | Hangar | 1960-1979 | payback_less_than_20 | 396174.76 | 6276.5798 | 6146.53 | 0 | 959553.5454 | 10588.8974 | 0 | 35836.1398 | 245597.4187 | 39044.4757 | 0 | 31452.8029 | 666.6672 | 0
134 | 6 | Hangar | 1960-1979 | plug_loads_90_percent | 21212.62 | 6276.5798 | 6146.53 | 0 | 2677485.4753 | 2213.8907 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 61869.4939 | 52741.7089 | 0
135 | 6 | Hangar | 1960-1979 | pumps_to_variable | 3425.24 | 6276.5798 | 6146.53 | 0 | 2676379.9189 | 2269.4463 | 0 | 35936.1399 | 350853.0585 | 39044.4757 | 0 | 61836.1606 | 52594.4865 | 0
136 | 6 | Hangar | 1960-1979 | pump_fan_eff_ | 6655.34 | 6276.5798 | 6146.53 | 0 | 2676379.9189 | 2269.4463 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 61836.1606 | 41213.9219 | 0
137 | 7 | Hangar | 1980-2004 | air_temp_reset_enabled | 7032.04 | 6276.5798 | 6146.53 | 0 | 1734993.0547 | 16738.9023 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 43650.0349 | 37572.2523 | 0
138 | 7 | Hangar | 1980-2004 | baseline | 0 | 6276.5798 | 6146.53 | 0 | 1713948.5934 | 1405.5567 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 43352.8125 | 33055.582 | 0
139 | 7 | Hangar | 1980-2004 | boiler_eff_upgrade | 65332.04 | 6276.5798 | 6146.53 | 0 | 1702043.0283 | 1972.2238 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 43650.0349 | 33230.5821 | 0
140 | 7 | Hangar | 1980-2004 | boiler_reset | 929.13 | 6276.5798 | 6146.53 | 0 | 1384106.6628 | 1972.2238 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 43650.0349 | 1813.8903 | 0
141 | 7 | Hangar | 1980-2004 | cooling_cop_3_0 | 16104.85 | 6276.5798 | 6146.53 | 0 | 1702043.0283 | 1691.668 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 43650.0349 | 33230.5821 | 0
142 | 7 | Hangar | 1980-2004 | dcv_enabled | 64066.99 | 6276.5798 | 6146.53 | 0 | 1321026.0568 | 2944.4468 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 43650.0349 | 31052.8026 | 0
143 | 7 | Hangar | 1980-2004 | ecm_cold_deck_reset_control | 7032.04 | 6276.5798 | 6146.53 | 0 | 1656767.9921 | 8494.4512 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 43650.0349 | 33558.3602 | 0
144 | 7 | Hangar | 1980-2004 | economizers_enabled | 2747.57 | 6276.5798 | 6146.53 | 0 | 1702093.0283 | 1877.7793 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 43650.0349 | 33216.6932 | 0
145 | 7 | Hangar | 1980-2004 | elec_reduce | 225412.62 | 6276.5798 | 6146.53 | 0 | 1414073.3535 | 1561.1124 | 0 | 35836.1398 | 245597.4187 | 39044.4757 | 0 | 38508.3641 | 25180.5757 | 0
146 | 7 | Hangar | 1980-2004 | envelope_ecm_roof | 1116538.83 | 6276.5798 | 6146.53 | 0 | 1591792.9401 | 1830.557 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 41725.0334 | 31283.3584 | 0
147 | 7 | Hangar | 1980-2004 | envelope_ecm_wall | 895777.67 | 6276.5798 | 6146.53 | 0 | 1670093.0027 | 1930.5571 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 42405.5895 | 31977.8034 | 0
148 | 7 | Hangar | 1980-2004 | envelope_ecm_windows | 187541.75 | 6276.5798 | 6146.53 | 0 | 1680634.6778 | 1975.0016 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 42736.1453 | 32250.0258 | 0
149 | 7 | Hangar | 1980-2004 | exhaust_fans_occ_control | 3659.22 | 6276.5798 | 6146.53 | 0 | 1702031.9172 | 1977.7794 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 38338.9196 | 33230.5821 | 0
150 | 7 | Hangar | 1980-2004 | fans_to_variable | 2189.32 | 6276.5798 | 6146.53 | 0 | 1702565.2509 | 1966.6682 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 43280.5902 | 33241.6933 | 0
151 | 7 | Hangar | 1980-2004 | hrv_enabled | 181615.53 | 6276.5798 | 6146.53 | 0 | 1386895.554 | 3450.0028 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 43650.0349 | 31836.1366 | 8761.1181
152 | 7 | Hangar | 1980-2004 | infil_reduce | 86236.89 | 6276.5798 | 6146.53 | 0 | 1358681.6425 | 2244.4462 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 37961.1415 | 26952.7993 | 0
153 | 7 | Hangar | 1980-2004 | infil_reduce_plus_setback | 122924.27 | 6276.5798 | 6146.53 | 0 | 1156120.3693 | 1366.6678 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 32275.0258 | 20922.239 | 0
154 | 7 | Hangar | 1980-2004 | lights_reduce_70p | 129818.45 | 6276.5798 | 6146.53 | 0 | 1795754.2144 | 1011.1119 | 0 | 35836.1398 | 245597.4187 | 39044.4757 | 0 | 43788.9239 | 34183.3607 | 0
155 | 7 | Hangar | 1980-2004 | load_reduce | 123853.4 | 6276.5798 | 6146.53 | 0 | 944861.867 | 1366.6678 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 32275.0258 | 1608.3346 | 0
156 | 7 | Hangar | 1980-2004 | occupancy_setback | 36687.38 | 6276.5798 | 6146.53 | 0 | 1473328.9564 | 1180.5565 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 37488.9189 | 26358.3544 | 0
157 | 7 | Hangar | 1980-2004 | payback_less_than_20 | 388453.4 | 6276.5798 | 6146.53 | 0 | 768983.9485 | 8411.1178 | 0 | 35836.1398 | 245597.4187 | 39044.4757 | 0 | 27125.0217 | 583.3338 | 0
158 | 7 | Hangar | 1980-2004 | plug_loads_90_percent | 21212.62 | 6276.5798 | 6146.53 | 0 | 1702254.1396 | 1922.2238 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 43680.5905 | 33269.4711 | 0
159 | 7 | Hangar | 1980-2004 | pumps_to_variable | 3425.24 | 6276.5798 | 6146.53 | 0 | 1702043.0283 | 1972.2238 | 0 | 35936.1399 | 350853.0585 | 39044.4757 | 0 | 43650.0349 | 33130.5821 | 0
160 | 7 | Hangar | 1980-2004 | pump_fan_eff_ | 6655.34 | 6276.5798 | 6146.53 | 0 | 1702043.0283 | 1972.2238 | 0 | 35836.1398 | 350853.0585 | 39044.4757 | 0 | 43650.0349 | 25991.6875 | 0
161 | 10 | Maintenance Shop-Small | 1959-pre | air_temp_reset_enabled | 3515.53 | 923.718 | 898.218 | 0 | 711289.4579 | 7380.5615 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 26041.6875 | 38194.475 | 0
162 | 10 | Maintenance Shop-Small | 1959-pre | baseline | 0 | 923.718 | 898.218 | 0 | 696908.8909 | 808.334 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 24988.9089 | 37502.8078 | 0
163 | 10 | Maintenance Shop-Small | 1959-pre | boiler_eff_upgrade | 65332.04 | 923.718 | 898.218 | 0 | 692678.3319 | 1119.4453 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 24972.2422 | 37508.3633 | 0
164 | 10 | Maintenance Shop-Small | 1959-pre | boiler_reset | 929.13 | 923.718 | 898.218 | 0 | 430800.3446 | 1119.4453 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 24972.2422 | 37508.3633 | 0
165 | 10 | Maintenance Shop-Small | 1959-pre | cooling_cop_3_0 | 10048.54 | 923.718 | 898.218 | 0 | 692678.3319 | 800.0006 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 24972.2422 | 37508.3633 | 0
166 | 10 | Maintenance Shop-Small | 1959-pre | dcv_enabled | 7488.35 | 923.718 | 898.218 | 0 | 692678.3319 | 1119.4453 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 24972.2422 | 37508.3633 | 0
167 | 10 | Maintenance Shop-Small | 1959-pre | ecm_cold_deck_reset_control | 3515.53 | 923.718 | 898.218 | 0 | 690564.4413 | 4161.1144 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 26644.4658 | 37105.5852 | 0
168 | 10 | Maintenance Shop-Small | 1959-pre | economizers_enabled | 1373.79 | 923.718 | 898.218 | 0 | 692797.7765 | 1044.4453 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 24975.02 | 37427.8077 | 0
169 | 10 | Maintenance Shop-Small | 1959-pre | elec_reduce | 38549.51 | 923.718 | 898.218 | 0 | 713903.3489 | 644.445 | 0 | 4455.5591 | 35530.584 | 6080.5604 | 0 | 25250.0202 | 29661.1348 | 0
170 | 10 | Maintenance Shop-Small | 1959-pre | envelope_ecm_roof | 104998.06 | 923.718 | 898.218 | 0 | 647231.0733 | 983.3341 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 23491.6855 | 35100.0281 | 0
171 | 10 | Maintenance Shop-Small | 1959-pre | envelope_ecm_wall | 257193.2 | 923.718 | 898.218 | 0 | 604222.7056 | 1097.2231 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 22030.5732 | 33169.471 | 0
172 | 10 | Maintenance Shop-Small | 1959-pre | envelope_ecm_windows | 6686.41 | 923.718 | 898.218 | 0 | 691508.8865 | 1119.4453 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 24958.3533 | 37455.5855 | 0
173 | 10 | Maintenance Shop-Small | 1959-pre | exhaust_fans_occ_control | 732.04 | 923.718 | 898.218 | 0 | 692678.3319 | 1119.4453 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 24972.2422 | 37508.3633 | 0
174 | 10 | Maintenance Shop-Small | 1959-pre | fans_to_variable | 2628.16 | 923.718 | 898.218 | 0 | 692794.9987 | 1113.8898 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 24886.131 | 37513.9189 | 0
175 | 10 | Maintenance Shop-Small | 1959-pre | hrv_enabled | 47432.04 | 923.718 | 898.218 | 0 | 680308.8776 | 1213.8899 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 24930.5755 | 37430.5855 | 2211.1129
176 | 10 | Maintenance Shop-Small | 1959-pre | infil_reduce | 45733.98 | 923.718 | 898.218 | 0 | 384350.3075 | 1422.2234 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 14883.3452 | 21750.0174 | 0
177 | 10 | Maintenance Shop-Small | 1959-pre | infil_reduce_plus_setback | 50022.33 | 923.718 | 898.218 | 0 | 335789.1575 | 1391.6678 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 15597.2347 | 21833.3508 | 0
178 | 10 | Maintenance Shop-Small | 1959-pre | lights_reduce_70p | 23465.05 | 923.718 | 898.218 | 0 | 713706.1265 | 663.8894 | 0 | 4455.5591 | 35530.584 | 6080.5604 | 0 | 25244.4646 | 37916.697 | 0
179 | 10 | Maintenance Shop-Small | 1959-pre | load_reduce | 50951.46 | 923.718 | 898.218 | 0 | 207264.0547 | 1391.6678 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 15597.2347 | 21833.3508 | 0
180 | 10 | Maintenance Shop-Small | 1959-pre | occupancy_setback | 4288.35 | 923.718 | 898.218 | 0 | 610378.2661 | 1027.7786 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 26858.3548 | 38405.5863 | 0
181 | 10 | Maintenance Shop-Small | 1959-pre | payback_less_than_20 | 99045.63 | 923.718 | 898.218 | 0 | 231891.8522 | 4936.1151 | 0 | 4455.5591 | 35530.584 | 6080.5604 | 0 | 17416.6806 | 16980.5691 | 0
182 | 10 | Maintenance Shop-Small | 1959-pre | plug_loads_90_percent | 2479.61 | 923.718 | 898.218 | 0 | 692836.6654 | 1088.8898 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 24975.02 | 37519.4745 | 0
183 | 10 | Maintenance Shop-Small | 1959-pre | pump_fan_eff_ | 4384.47 | 923.718 | 898.218 | 0 | 692678.3319 | 1119.4453 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 24972.2422 | 29336.1346 | 0
184 | 11 | Maintenance Shop-Small | 1960-1979 | air_temp_reset_enabled | 3515.53 | 923.718 | 898.218 | 0 | 656414.414 | 6730.5609 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 24138.9082 | 35769.4731 | 0
185 | 11 | Maintenance Shop-Small | 1960-1979 | baseline | 0 | 923.718 | 898.218 | 0 | 648072.7407 | 666.6672 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 23205.5741 | 35025.028 | 0
186 | 11 | Maintenance Shop-Small | 1960-1979 | boiler_eff_upgrade | 65332.04 | 923.718 | 898.218 | 0 | 642142.1804 | 1125.0009 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 23244.463 | 35088.917 | 0
187 | 11 | Maintenance Shop-Small | 1960-1979 | boiler_reset | 929.13 | 923.718 | 898.218 | 0 | 398955.8747 | 1125.0009 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 23244.463 | 35088.917 | 0
188 | 11 | Maintenance Shop-Small | 1960-1979 | cooling_cop_3_0 | 10048.54 | 923.718 | 898.218 | 0 | 642142.1804 | 802.7784 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 23244.463 | 35088.917 | 0
189 | 11 | Maintenance Shop-Small | 1960-1979 | dcv_enabled | 7488.35 | 923.718 | 898.218 | 0 | 642142.1804 | 1125.0009 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 23244.463 | 35088.917 | 0
190 | 11 | Maintenance Shop-Small | 1960-1979 | ecm_cold_deck_reset_control | 3515.53 | 923.718 | 898.218 | 0 | 639467.1782 | 4016.6699 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 24783.3532 | 34627.8055 | 0
191 | 11 | Maintenance Shop-Small | 1960-1979 | economizers_enabled | 1373.79 | 923.718 | 898.218 | 0 | 642306.0694 | 1047.2231 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 23247.2408 | 34975.028 | 0
192 | 11 | Maintenance Shop-Small | 1960-1979 | elec_reduce | 38549.51 | 923.718 | 898.218 | 0 | 663047.7527 | 633.3338 | 0 | 4455.5591 | 35530.584 | 6080.5604 | 0 | 23513.9077 | 27783.3556 | 0
193 | 11 | Maintenance Shop-Small | 1960-1979 | envelope_ecm_roof | 153754.37 | 923.718 | 898.218 | 0 | 570233.7895 | 919.4452 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 20911.1278 | 31311.1362 | 0
194 | 11 | Maintenance Shop-Small | 1960-1979 | envelope_ecm_wall | 257193.2 | 923.718 | 898.218 | 0 | 604925.4839 | 1155.5565 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 21966.6842 | 33152.8043 | 0
195 | 11 | Maintenance Shop-Small | 1960-1979 | envelope_ecm_windows | 6686.41 | 923.718 | 898.218 | 0 | 640992.1795 | 1125.0009 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 23230.5741 | 35030.5836 | 0
196 | 11 | Maintenance Shop-Small | 1960-1979 | exhaust_fans_occ_control | 732.04 | 923.718 | 898.218 | 0 | 642142.1804 | 1125.0009 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 23244.463 | 35088.917 | 0
197 | 11 | Maintenance Shop-Small | 1960-1979 | fans_to_variable | 2628.16 | 923.718 | 898.218 | 0 | 642253.2916 | 1119.4453 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 23163.9074 | 35091.6947 | 0
198 | 11 | Maintenance Shop-Small | 1960-1979 | hrv_enabled | 47432.04 | 923.718 | 898.218 | 0 | 629728.2816 | 1227.7788 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 23205.5741 | 35030.5836 | 2211.1129
199 | 11 | Maintenance Shop-Small | 1960-1979 | infil_reduce | 45733.98 | 923.718 | 898.218 | 0 | 364544.7361 | 1383.3344 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 14202.7891 | 20844.4611 | 0
200 | 11 | Maintenance Shop-Small | 1960-1979 | infil_reduce_plus_setback | 50022.33 | 923.718 | 898.218 | 0 | 314186.3625 | 1358.3344 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 14855.5674 | 20705.5721 | 0
201 | 11 | Maintenance Shop-Small | 1960-1979 | lights_reduce_70p | 23465.05 | 923.718 | 898.218 | 0 | 662794.9747 | 652.7783 | 0 | 4455.5591 | 35530.584 | 6080.5604 | 0 | 23508.3521 | 35522.2506 | 0
202 | 11 | Maintenance Shop-Small | 1960-1979 | load_reduce | 50951.46 | 923.718 | 898.218 | 0 | 193552.9326 | 1358.3344 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 14855.5674 | 20705.5721 | 0
203 | 11 | Maintenance Shop-Small | 1960-1979 | occupancy_setback | 4288.35 | 923.718 | 898.218 | 0 | 560889.3376 | 1036.1119 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 24961.1311 | 35763.9175 | 0
204 | 11 | Maintenance Shop-Small | 1960-1979 | payback_less_than_20 | 99045.63 | 923.718 | 898.218 | 0 | 216727.9512 | 4683.3371 | 0 | 4455.5591 | 35530.584 | 6080.5604 | 0 | 16636.1244 | 16175.0129 | 0
205 | 11 | Maintenance Shop-Small | 1960-1979 | plug_loads_90_percent | 2479.61 | 923.718 | 898.218 | 0 | 642344.9583 | 1094.4453 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 23247.2408 | 35102.8059 | 0
206 | 11 | Maintenance Shop-Small | 1960-1979 | pump_fan_eff_ | 4384.47 | 923.718 | 898.218 | 0 | 642142.1804 | 1125.0009 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 23244.463 | 27441.6886 | 0
207 | 12 | Maintenance Shop-Small | 1980-2004 | air_temp_reset_enabled | 3515.53 | 923.718 | 898.218 | 0 | 349491.9463 | 3458.3361 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 13750.011 | 19902.7937 | 0
208 | 12 | Maintenance Shop-Small | 1980-2004 | baseline | 0 | 923.718 | 898.218 | 0 | 345153.0539 | 516.6671 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 13394.4552 | 19627.7935 | 0
209 | 12 | Maintenance Shop-Small | 1980-2004 | boiler_eff_upgrade | 32923.3 | 923.718 | 898.218 | 0 | 342828.052 | 988.8897 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 13522.233 | 19730.5713 | 0
210 | 12 | Maintenance Shop-Small | 1980-2004 | boiler_reset | 929.13 | 923.718 | 898.218 | 0 | 212439.0588 | 988.8897 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 13522.233 | 19730.5713 | 0
211 | 12 | Maintenance Shop-Small | 1980-2004 | cooling_cop_3_0 | 10048.54 | 923.718 | 898.218 | 0 | 342828.052 | 847.2229 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 13522.233 | 19730.5713 | 0
212 | 12 | Maintenance Shop-Small | 1980-2004 | dcv_enabled | 7488.35 | 923.718 | 898.218 | 0 | 342828.052 | 988.8897 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 13522.233 | 19730.5713 | 0
213 | 12 | Maintenance Shop-Small | 1980-2004 | ecm_cold_deck_reset_control | 3515.53 | 923.718 | 898.218 | 0 | 342161.3848 | 2547.2243 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 14113.9002 | 19316.6821 | 0
214 | 12 | Maintenance Shop-Small | 1980-2004 | economizers_enabled | 1373.79 | 923.718 | 898.218 | 0 | 343189.1634 | 858.334 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 13525.0108 | 19427.7933 | 0
215 | 12 | Maintenance Shop-Small | 1980-2004 | elec_reduce | 38549.51 | 923.718 | 898.218 | 0 | 362533.6234 | 427.7781 | 0 | 4455.5591 | 35530.584 | 6080.5604 | 0 | 13819.4555 | 15911.1238 | 0
216 | 12 | Maintenance Shop-Small | 1980-2004 | envelope_ecm_roof | 133337.86 | 923.718 | 898.218 | 0 | 326411.3722 | 947.223 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 12977.7882 | 18861.1262 | 0
217 | 12 | Maintenance Shop-Small | 1980-2004 | envelope_ecm_wall | 257193.2 | 923.718 | 898.218 | 0 | 332416.9326 | 1011.1119 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 13161.1216 | 19152.7931 | 0
218 | 12 | Maintenance Shop-Small | 1980-2004 | envelope_ecm_windows | 6686.41 | 923.718 | 898.218 | 0 | 341933.6069 | 994.4452 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 13511.1219 | 19686.1269 | 0
219 | 12 | Maintenance Shop-Small | 1980-2004 | exhaust_fans_occ_control | 732.04 | 923.718 | 898.218 | 0 | 342828.052 | 988.8897 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 13522.233 | 19730.5713 | 0
220 | 12 | Maintenance Shop-Small | 1980-2004 | fans_to_variable | 2628.16 | 923.718 | 898.218 | 0 | 342886.3854 | 986.1119 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 13477.7886 | 19733.3491 | 0
221 | 12 | Maintenance Shop-Small | 1980-2004 | hrv_enabled | 47432.04 | 923.718 | 898.218 | 0 | 330350.2643 | 1141.6676 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 13466.6774 | 19630.5713 | 2211.1129
222 | 12 | Maintenance Shop-Small | 1980-2004 | infil_reduce | 41941.75 | 923.718 | 898.218 | 0 | 251039.0897 | 1194.4454 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 10488.8973 | 14927.7897 | 0
223 | 12 | Maintenance Shop-Small | 1980-2004 | infil_reduce_plus_setback | 46230.1 | 923.718 | 898.218 | 0 | 215889.0616 | 1105.5564 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 10672.2308 | 14575.0117 | 0
224 | 12 | Maintenance Shop-Small | 1980-2004 | lights_reduce_70p | 23465.05 | 923.718 | 898.218 | 0 | 362472.5122 | 447.2226 | 0 | 4455.5591 | 35530.584 | 6080.5604 | 0 | 13816.6777 | 20333.3496 | 0
225 | 12 | Maintenance Shop-Small | 1980-2004 | load_reduce | 47159.22 | 923.718 | 898.218 | 0 | 133813.9959 | 1105.5564 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 10672.2308 | 14575.0117 | 0
226 | 12 | Maintenance Shop-Small | 1980-2004 | occupancy_setback | 4288.35 | 923.718 | 898.218 | 0 | 296797.4597 | 880.5563 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 13991.6779 | 19530.5712 | 0
227 | 12 | Maintenance Shop-Small | 1980-2004 | payback_less_than_20 | 95253.4 | 923.718 | 898.218 | 0 | 150097.3423 | 2630.5577 | 0 | 4455.5591 | 35530.584 | 6080.5604 | 0 | 11977.7874 | 11372.2313 | 0
228 | 12 | Maintenance Shop-Small | 1980-2004 | plug_loads_90_percent | 2479.61 | 923.718 | 898.218 | 0 | 342864.1632 | 961.1119 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 13522.233 | 19738.9047 | 0
229 | 12 | Maintenance Shop-Small | 1980-2004 | pump_fan_eff_ | 4384.47 | 923.718 | 898.218 | 0 | 342828.052 | 988.8897 | 0 | 4455.5591 | 50755.5962 | 6080.5604 | 0 | 13522.233 | 15430.5679 | 0
230 | 8 | Maintenance Shop | 1959-pre | air_temp_reset_enabled | 3515.53 | 2388.545 | 2388.54 | 0 | 1645137.4272 | 2216.6684 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 100897.3029 | 85863.9576 | 0
231 | 8 | Maintenance Shop | 1959-pre | baseline | 0 | 2388.545 | 2388.54 | 0 | 1652142.9884 | 1130.5565 | 6427.7829 | 0 | 84158.4007 | 12063.8985 | 0 | 92950.0744 | 85244.5126 | 0
232 | 8 | Maintenance Shop | 1959-pre | boiler_eff_upgrade | 65332.04 | 2388.545 | 2388.54 | 0 | 1647884.6516 | 1258.3343 | 6427.7829 | 0 | 84158.4007 | 12063.8985 | 0 | 93130.6301 | 85863.9576 | 0
233 | 8 | Maintenance Shop | 1959-pre | boiler_reset | 929.13 | 2388.545 | 2388.54 | 0 | 1039209.1647 | 1258.3343 | 6427.7829 | 0 | 84158.4007 | 12063.8985 | 0 | 93130.6301 | 85863.9576 | 0
234 | 8 | Maintenance Shop | 1959-pre | cooling_cop_3_0 | 4939.81 | 2388.545 | 2388.54 | 0 | 1647884.6516 | 897.2229 | 6427.7829 | 0 | 84158.4007 | 12063.8985 | 0 | 93130.6301 | 85863.9576 | 0
235 | 8 | Maintenance Shop | 1959-pre | dcv_enabled | 9152.43 | 2388.545 | 2388.54 | 0 | 1264956.5675 | 1369.4455 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 92566.7407 | 85861.1798 | 0
236 | 8 | Maintenance Shop | 1959-pre | ecm_cold_deck_reset_control | 3515.53 | 2388.545 | 2388.54 | 0 | 1649037.4303 | 1927.7793 | 6427.7829 | 0 | 84158.4007 | 12063.8985 | 0 | 93075.0745 | 85863.9576 | 0
237 | 8 | Maintenance Shop | 1959-pre | economizers_enabled | 1172.82 | 2388.545 | 2388.54 | 0 | 1648170.763 | 950.0008 | 6427.7829 | 0 | 84158.4007 | 12063.8985 | 0 | 93136.1856 | 85863.9576 | 0
238 | 8 | Maintenance Shop | 1959-pre | elec_reduce | 63743.69 | 2388.545 | 2388.54 | 0 | 1296337.1482 | 1163.8898 | 6425.0051 | 0 | 58911.1582 | 12063.8985 | 0 | 88838.96 | 66941.7202 | 0
239 | 8 | Maintenance Shop | 1959-pre | envelope_ecm_roof | 257973.79 | 2388.545 | 2388.54 | 0 | 1558223.4688 | 1247.2232 | 6427.7829 | 0 | 84158.4007 | 12063.8985 | 0 | 87552.8478 | 80547.2867 | 0
240 | 8 | Maintenance Shop | 1959-pre | envelope_ecm_wall | 500845.63 | 2388.545 | 2388.54 | 0 | 1463592.8375 | 1269.4455 | 6427.7829 | 0 | 84158.4007 | 12063.8985 | 0 | 82591.7327 | 75311.1714 | 0
241 | 8 | Maintenance Shop | 1959-pre | envelope_ecm_windows | 72702.91 | 2388.545 | 2388.54 | 0 | 1636040.1977 | 1333.3344 | 6427.7829 | 0 | 84158.4007 | 12063.8985 | 0 | 92925.0743 | 85511.1795 | 0
242 | 8 | Maintenance Shop | 1959-pre | exhaust_fans_occ_control | 2195.15 | 2388.545 | 2388.54 | 0 | 1645945.7612 | 1258.3343 | 6427.7829 | 0 | 84158.4007 | 12063.8985 | 0 | 90569.5169 | 85863.9576 | 0
243 | 8 | Maintenance Shop | 1959-pre | fans_to_variable | 1179.61 | 2388.545 | 2388.54 | 0 | 1649081.8748 | 1255.5566 | 6427.7829 | 0 | 84158.4007 | 12063.8985 | 0 | 92408.4073 | 85863.9576 | 0
244 | 8 | Maintenance Shop | 1959-pre | hrv_enabled | 134183.5 | 2388.545 | 2388.54 | 0 | 1424548.3619 | 1525.0012 | 6427.7829 | 0 | 84158.4007 | 12063.8985 | 0 | 92538.9629 | 85863.9576 | 26280.5766
245 | 8 | Maintenance Shop | 1959-pre | infil_reduce | 71863.11 | 2388.545 | 2388.54 | 0 | 1058589.7358 | 1433.3345 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 60202.8259 | 54836.155 | 0
246 | 8 | Maintenance Shop | 1959-pre | infil_reduce_plus_setback | 77103.88 | 2388.545 | 2388.54 | 0 | 925031.2956 | 825.0007 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 67069.4981 | 61172.2712 | 0
247 | 8 | Maintenance Shop | 1959-pre | lights_reduce_70p | 44253.4 | 2388.545 | 2388.54 | 0 | 1682054.1234 | 1080.5564 | 6427.7829 | 0 | 58911.1582 | 12063.8985 | 0 | 92486.1851 | 85588.9574 | 0
248 | 8 | Maintenance Shop | 1959-pre | load_reduce | 78033.01 | 2388.545 | 2388.54 | 0 | 578792.1297 | 825.0007 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 67069.4981 | 61172.2712 | 0
249 | 8 | Maintenance Shop | 1959-pre | occupancy_setback | 5240.78 | 2388.545 | 2388.54 | 0 | 1443342.8213 | 711.1117 | 6427.7829 | 0 | 84158.4007 | 12063.8985 | 0 | 105458.4177 | 96063.9657 | 0
250 | 8 | Maintenance Shop | 1959-pre | payback_less_than_20 | 155592.23 | 2388.545 | 2388.54 | 0 | 403250.3226 | 2113.8906 | 6425.0051 | 0 | 58911.1582 | 12063.8985 | 0 | 62105.6052 | 46369.4815 | 0
251 | 8 | Maintenance Shop | 1959-pre | plug_loads_90_percent | 3030.1 | 2388.545 | 2388.54 | 0 | 1649054.097 | 1238.8899 | 6427.7829 | 0 | 84158.4007 | 12063.8985 | 0 | 93044.5189 | 85872.2909 | 0
252 | 8 | Maintenance Shop | 1959-pre | pump_fan_eff_ | 5112.62 | 2388.545 | 2388.54 | 0 | 1647884.6516 | 1258.3343 | 6427.7829 | 0 | 84158.4007 | 12063.8985 | 0 | 93130.6301 | 67155.6093 | 0
253 | 9 | Maintenance Shop | 1980-2004 | air_temp_reset_enabled | 3515.53 | 2388.545 | 2388.54 | 0 | 987578.5678 | 1866.6682 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 55083.3774 | 48283.372 | 0
254 | 9 | Maintenance Shop | 1980-2004 | baseline | 0 | 2388.545 | 2388.54 | 0 | 959995.2124 | 1044.4453 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 52863.9312 | 47638.927 | 0
255 | 9 | Maintenance Shop | 1980-2004 | boiler_eff_upgrade | 32923.3 | 2388.545 | 2388.54 | 0 | 959128.5451 | 1166.6676 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 53527.8206 | 48283.372 | 0
256 | 9 | Maintenance Shop | 1980-2004 | boiler_reset | 929.13 | 2388.545 | 2388.54 | 0 | 611811.6006 | 1166.6676 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 53527.8206 | 48283.372 | 0
257 | 9 | Maintenance Shop | 1980-2004 | cooling_cop_3_0 | 4939.81 | 2388.545 | 2388.54 | 0 | 959128.5451 | 1000.0008 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 53527.8206 | 48283.372 | 0
258 | 9 | Maintenance Shop | 1980-2004 | dcv_enabled | 9152.43 | 2388.545 | 2388.54 | 0 | 643592.1815 | 1313.8899 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 52605.5976 | 48280.5942 | 0
259 | 9 | Maintenance Shop | 1980-2004 | ecm_cold_deck_reset_control | 3515.53 | 2388.545 | 2388.54 | 0 | 960486.8795 | 1705.5569 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 53541.7095 | 48283.372 | 0
260 | 9 | Maintenance Shop | 1980-2004 | economizers_enabled | 1172.82 | 2388.545 | 2388.54 | 0 | 959761.8789 | 830.5562 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 53538.9317 | 48283.372 | 0
261 | 9 | Maintenance Shop | 1980-2004 | elec_reduce | 63743.69 | 2388.545 | 2388.54 | 0 | 672792.2049 | 1091.6675 | 6425.0051 | 0 | 58911.1582 | 12063.8985 | 0 | 48847.2613 | 37555.5856 | 0
262 | 9 | Maintenance Shop | 1980-2004 | envelope_ecm_roof | 257973.79 | 2388.545 | 2388.54 | 0 | 926325.7411 | 1161.112 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 51419.4856 | 46355.5926 | 0
263 | 9 | Maintenance Shop | 1980-2004 | envelope_ecm_wall | 500845.63 | 2388.545 | 2388.54 | 0 | 923781.2946 | 1175.0009 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 51302.8188 | 46225.037 | 0
264 | 9 | Maintenance Shop | 1980-2004 | envelope_ecm_windows | 72702.91 | 2388.545 | 2388.54 | 0 | 950622.9827 | 1263.8899 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 53344.4871 | 48044.4829 | 0
265 | 9 | Maintenance Shop | 1980-2004 | exhaust_fans_occ_control | 2195.15 | 2388.545 | 2388.54 | 0 | 958550.7668 | 1166.6676 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 50211.1513 | 48283.372 | 0
266 | 9 | Maintenance Shop | 1980-2004 | fans_to_variable | 1179.61 | 2388.545 | 2388.54 | 0 | 959770.2123 | 1163.8898 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 53133.3758 | 48283.372 | 0
267 | 9 | Maintenance Shop | 1980-2004 | hrv_enabled | 134183.5 | 2388.545 | 2388.54 | 0 | 725739.4695 | 1572.2235 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 52694.4866 | 48280.5942 | 26280.5766
268 | 9 | Maintenance Shop | 1980-2004 | infil_reduce | 65184.47 | 2388.545 | 2388.54 | 0 | 783842.2937 | 1225.001 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 43211.1457 | 39013.9201 | 0
269 | 9 | Maintenance Shop | 1980-2004 | infil_reduce_plus_setback | 70425.24 | 2388.545 | 2388.54 | 0 | 678053.3202 | 719.445 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 47625.0381 | 43400.0347 | 0
270 | 9 | Maintenance Shop | 1980-2004 | lights_reduce_70p | 44253.4 | 2388.545 | 2388.54 | 0 | 991064.6817 | 980.5563 | 6425.0051 | 0 | 58911.1582 | 12063.8985 | 0 | 53283.376 | 48013.9273 | 0
271 | 9 | Maintenance Shop | 1980-2004 | load_reduce | 71354.37 | 2388.545 | 2388.54 | 0 | 427205.8973 | 719.445 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 47625.0381 | 43400.0347 | 0
272 | 9 | Maintenance Shop | 1980-2004 | occupancy_setback | 5240.78 | 2388.545 | 2388.54 | 0 | 832775.6662 | 666.6672 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 59216.714 | 53822.2653 | 0
273 | 9 | Maintenance Shop | 1980-2004 | payback_less_than_20 | 148913.59 | 2388.545 | 2388.54 | 0 | 274433.5529 | 1775.0014 | 6425.0051 | 0 | 58911.1582 | 12063.8985 | 0 | 42736.1453 | 32825.0263 | 0
274 | 9 | Maintenance Shop | 1980-2004 | plug_loads_90_percent | 3030.1 | 2388.545 | 2388.54 | 0 | 959697.99 | 1150.0009 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 53533.3762 | 48288.9275 | 0
275 | 9 | Maintenance Shop | 1980-2004 | pump_fan_eff_ | 5112.62 | 2388.545 | 2388.54 | 0 | 959128.5451 | 1166.6676 | 6425.0051 | 0 | 84158.4007 | 12063.8985 | 0 | 53527.8206 | 37763.9191 | 0
276 | 16 | Office-Small | 1960-1979 | air_temp_reset_enabled | 14063.11 | 1211.4622 | 590.75 | 11569.4537 | 134486.2187 | 9411.1186 | 7194.4502 | 0 | 32363.9148 | 7750.0062 | 0 | 22872.2405 | 16.6667 | 0
277 | 16 | Office-Small | 1960-1979 | baseline | 0 | 1211.4622 | 590.75 | 725.0006 | 161922.3518 | 2636.1132 | 7163.8946 | 0 | 32363.9148 | 7750.0062 | 0 | 22894.4628 | 16.6667 | 0
278 | 16 | Office-Small | 1960-1979 | boiler_reset | 929.13 | 1211.4622 | 590.75 | 1655.5569 | 157327.9036 | 3541.6695 | 7163.8946 | 0 | 32363.9148 | 7750.0062 | 0 | 22827.796 | 16.6667 | 0
279 | 16 | Office-Small | 1960-1979 | cooling_cop_3_0 | 16747.57 | 1211.4622 | 590.75 | 1655.5569 | 157327.9036 | 2530.5576 | 7163.8946 | 0 | 32363.9148 | 7750.0062 | 0 | 22827.796 | 16.6667 | 0
280 | 16 | Office-Small | 1960-1979 | dcv_enabled | 13312.62 | 1211.4622 | 590.75 | 1655.5569 | 157327.9036 | 3541.6695 | 7163.8946 | 0 | 32363.9148 | 7750.0062 | 0 | 22827.796 | 16.6667 | 0
281 | 16 | Office-Small | 1960-1979 | ecm_cold_deck_reset_control | 14063.11 | 1211.4622 | 590.75 | 20102.7939 | 88311.1818 | 6705.5609 | 7225.0058 | 0 | 32363.9148 | 7750.0062 | 0 | 23030.574 | 16.6667 | 0
282 | 16 | Office-Small | 1960-1979 | economizers_enabled | 5495.15 | 1211.4622 | 590.75 | 1655.5569 | 157327.9036 | 3541.6695 | 7163.8946 | 0 | 32363.9148 | 7750.0062 | 0 | 22827.796 | 16.6667 | 0
283 | 16 | Office-Small | 1960-1979 | elec_reduce | 40479.61 | 1211.4622 | 590.75 | 1258.3343 | 165264.0211 | 2525.002 | 7166.6724 | 0 | 22655.5737 | 7750.0062 | 0 | 20369.4607 | 11.1111 | 0
284 | 16 | Office-Small | 1960-1979 | envelope_ecm_roof | 151892.23 | 1211.4622 | 590.75 | 1727.7792 | 127475.102 | 3100.0025 | 7125.0057 | 0 | 32363.9148 | 7750.0062 | 0 | 19777.7936 | 16.6667 | 0
285 | 16 | Office-Small | 1960-1979 | envelope_ecm_wall | 126489.32 | 1211.4622 | 590.75 | 1613.8902 | 145941.7834 | 3591.6695 | 7113.8946 | 0 | 32363.9148 | 7750.0062 | 0 | 21569.4617 | 16.6667 | 0
286 | 16 | Office-Small | 1960-1979 | envelope_ecm_windows | 47330.1 | 1211.4622 | 590.75 | 1652.7791 | 152733.4555 | 3572.2251 | 7161.1168 | 0 | 32363.9148 | 7750.0062 | 0 | 22475.018 | 16.6667 | 0
287 | 16 | Office-Small | 1960-1979 | exhaust_fans_occ_control | 1464.08 | 1211.4622 | 590.75 | 1655.5569 | 157327.9036 | 3563.8917 | 7163.8946 | 0 | 32363.9148 | 7750.0062 | 0 | 20288.9051 | 16.6667 | 0
288 | 16 | Office-Small | 1960-1979 | fans_to_variable | 4038.83 | 1211.4622 | 590.75 | 1658.3347 | 157502.9038 | 3530.5584 | 7163.8946 | 0 | 32363.9148 | 7750.0062 | 0 | 22638.907 | 16.6667 | 0
289 | 16 | Office-Small | 1960-1979 | hrv_enabled | 162160.19 | 1211.4622 | 590.75 | 1655.5569 | 157327.9036 | 3541.6695 | 7163.8946 | 0 | 32363.9148 | 7750.0062 | 0 | 22827.796 | 16.6667 | 0
290 | 16 | Office-Small | 1960-1979 | infil_reduce | 35879.61 | 1211.4622 | 590.75 | 1555.5568 | 94361.1866 | 4313.8923 | 6986.1167 | 0 | 32363.9148 | 7750.0062 | 0 | 16641.68 | 16.6667 | 0
291 | 16 | Office-Small | 1960-1979 | infil_reduce_plus_setback | 43502.91 | 1211.4622 | 590.75 | 1394.4456 | 79605.6192 | 3419.4472 | 7005.5612 | 0 | 32363.9148 | 7750.0062 | 0 | 18808.3484 | 16.6667 | 0
292 | 16 | Office-Small | 1960-1979 | lights_reduce_70p | 19600.97 | 1211.4622 | 590.75 | 1288.8899 | 164989.0209 | 2583.3354 | 7166.6724 | 0 | 22655.5737 | 7750.0062 | 0 | 22880.5739 | 16.6667 | 0
293 | 16 | Office-Small | 1960-1979 | load_reduce | 44432.04 | 1211.4622 | 590.75 | 1394.4456 | 79605.6192 | 3419.4472 | 7005.5612 | 0 | 32363.9148 | 7750.0062 | 0 | 18808.3484 | 16.6667 | 0
294 | 16 | Office-Small | 1960-1979 | occupancy_setback | 7623.3 | 1211.4622 | 590.75 | 1450.0012 | 135277.886 | 2763.8911 | 7183.3391 | 0 | 32363.9148 | 7750.0062 | 0 | 25925.0207 | 16.6667 | 0
295 | 16 | Office-Small | 1960-1979 | payback_less_than_20 | 110781.55 | 1211.4622 | 590.75 | 9944.4524 | 57530.6016 | 6300.005 | 7058.339 | 0 | 22655.5737 | 7750.0062 | 0 | 16436.1243 | 11.1111 | 0
296 | 16 | Office-Small | 1960-1979 | plug_loads_90_percent | 4407.77 | 1211.4622 | 590.75 | 1630.5569 | 157544.5705 | 3447.225 | 7161.1168 | 0 | 32363.9148 | 7750.0062 | 0 | 22852.7961 | 16.6667 | 0
297 | 16 | Office-Small | 1960-1979 | pump_fan_eff_ | 1694.17 | 1211.4622 | 590.75 | 1655.5569 | 157327.9036 | 3541.6695 | 7163.8946 | 0 | 32363.9148 | 7750.0062 | 0 | 22827.796 | 11.1111 | 0
298 | 17 | Office-Small | 1980-2004 | air_temp_reset_enabled | 14063.11 | 1211.4622 | 590.75 | 7066.6723 | 76333.3944 | 6077.7826 | 7008.3389 | 0 | 32363.9148 | 7750.0062 | 0 | 15800.0126 | 16.6667 | 0
299 | 17 | Office-Small | 1980-2004 | baseline | 0 | 1211.4622 | 590.75 | 800.0006 | 90105.6276 | 2255.5574 | 6980.5611 | 0 | 32363.9148 | 7750.0062 | 0 | 15811.1238 | 16.6667 | 0
300 | 17 | Office-Small | 1980-2004 | boiler_reset | 929.13 | 1211.4622 | 590.75 | 1575.0013 | 87047.2919 | 3202.7803 | 6983.3389 | 0 | 32363.9148 | 7750.0062 | 0 | 15797.2349 | 16.6667 | 0
301 | 17 | Office-Small | 1980-2004 | cooling_cop_3_0 | 16747.57 | 1211.4622 | 590.75 | 1575.0013 | 87047.2919 | 2744.4466 | 6983.3389 | 0 | 32363.9148 | 7750.0062 | 0 | 15797.2349 | 16.6667 | 0
302 | 17 | Office-Small | 1980-2004 | dcv_enabled | 13312.62 | 1211.4622 | 590.75 | 1575.0013 | 87047.2919 | 3202.7803 | 6983.3389 | 0 | 32363.9148 | 7750.0062 | 0 | 15797.2349 | 16.6667 | 0
303 | 17 | Office-Small | 1980-2004 | ecm_cold_deck_reset_control | 14063.11 | 1211.4622 | 590.75 | 13108.3438 | 46516.7039 | 5127.7819 | 7050.0056 | 0 | 32363.9148 | 7750.0062 | 0 | 15938.9016 | 16.6667 | 0
304 | 17 | Office-Small | 1980-2004 | economizers_enabled | 5495.15 | 1211.4622 | 590.75 | 1575.0013 | 87047.2919 | 3202.7803 | 6983.3389 | 0 | 32363.9148 | 7750.0062 | 0 | 15797.2349 | 16.6667 | 0
305 | 17 | Office-Small | 1980-2004 | elec_reduce | 40479.61 | 1211.4622 | 590.75 | 1275.001 | 93830.6306 | 2113.8906 | 6988.8945 | 0 | 22655.5737 | 7750.0062 | 0 | 13316.6773 | 11.1111 | 0
306 | 17 | Office-Small | 1980-2004 | envelope_ecm_roof | 151892.23 | 1211.4622 | 590.75 | 1586.1124 | 76958.3949 | 3150.0025 | 6963.8945 | 0 | 32363.9148 | 7750.0062 | 0 | 14725.0118 | 16.6667 | 0
307 | 17 | Office-Small | 1980-2004 | envelope_ecm_wall | 126489.32 | 1211.4622 | 590.75 | 1544.4457 | 82838.9552 | 3275.0026 | 6958.3389 | 0 | 32363.9148 | 7750.0062 | 0 | 15311.1234 | 16.6667 | 0
308 | 17 | Office-Small | 1980-2004 | envelope_ecm_windows | 47330.1 | 1211.4622 | 590.75 | 1569.4457 | 83672.2892 | 3275.0026 | 6980.5611 | 0 | 32363.9148 | 7750.0062 | 0 | 15530.568 | 16.6667 | 0
309 | 17 | Office-Small | 1980-2004 | exhaust_fans_occ_control | 1464.08 | 1211.4622 | 590.75 | 1575.0013 | 87047.2919 | 3219.447 | 6983.3389 | 0 | 32363.9148 | 7750.0062 | 0 | 13261.1217 | 16.6667 | 0
310 | 17 | Office-Small | 1980-2004 | fans_to_variable | 4038.83 | 1211.4622 | 590.75 | 1577.779 | 87147.2919 | 3194.447 | 6983.3389 | 0 | 32363.9148 | 7750.0062 | 0 | 15677.7903 | 16.6667 | 0
311 | 17 | Office-Small | 1980-2004 | hrv_enabled | 162160.19 | 1211.4622 | 590.75 | 1575.0013 | 87047.2919 | 3202.7803 | 6983.3389 | 0 | 32363.9148 | 7750.0062 | 0 | 15797.2349 | 16.6667 | 0
312 | 17 | Office-Small | 1980-2004 | infil_reduce | 32574.76 | 1211.4622 | 590.75 | 1797.2237 | 56169.4894 | 3763.8919 | 6875.0055 | 0 | 32363.9148 | 7750.0062 | 0 | 12897.2325 | 16.6667 | 0
313 | 17 | Office-Small | 1980-2004 | infil_reduce_plus_setback | 40198.06 | 1211.4622 | 590.75 | 1441.6678 | 46208.3703 | 3188.8914 | 6894.45 | 0 | 32363.9148 | 7750.0062 | 0 | 14252.7892 | 16.6667 | 0
314 | 17 | Office-Small | 1980-2004 | lights_reduce_70p | 19600.97 | 1211.4622 | 590.75 | 1294.4455 | 93736.1861 | 2180.5573 | 6988.8945 | 0 | 22655.5737 | 7750.0062 | 0 | 15841.6793 | 16.6667 | 0
315 | 17 | Office-Small | 1980-2004 | load_reduce | 41127.18 | 1211.4622 | 590.75 | 1441.6678 | 46208.3703 | 3188.8914 | 6894.45 | 0 | 32363.9148 | 7750.0062 | 0 | 14252.7892 | 16.6667 | 0
316 | 17 | Office-Small | 1980-2004 | occupancy_setback | 7623.3 | 1211.4622 | 590.75 | 1452.7789 | 72805.6138 | 2702.7799 | 7005.5612 | 0 | 32363.9148 | 7750.0062 | 0 | 17802.792 | 16.6667 | 0
317 | 17 | Office-Small | 1980-2004 | payback_less_than_20 | 107476.7 | 1211.4622 | 590.75 | 7227.7836 | 34383.3608 | 4716.6704 | 6944.45 | 0 | 22655.5737 | 7750.0062 | 0 | 11833.3428 | 11.1111 | 0
318 | 17 | Office-Small | 1980-2004 | plug_loads_90_percent | 4407.77 | 1211.4622 | 590.75 | 1563.8901 | 87058.403 | 3105.558 | 6980.5611 | 0 | 32363.9148 | 7750.0062 | 0 | 15813.9015 | 16.6667 | 0
319 | 17 | Office-Small | 1980-2004 | pump_fan_eff_ | 1694.17 | 1211.4622 | 590.75 | 1575.0013 | 87047.2919 | 3202.7803 | 6983.3389 | 0 | 32363.9148 | 7750.0062 | 0 | 15797.2349 | 11.1111 | 0
320 | 18 | Office-Small | 2005-2014 | air_temp_reset_enabled | 14063.11 | 1211.4622 | 590.75 | 4097.2255 | 42719.4786 | 4488.8925 | 6836.1166 | 0 | 32363.9148 | 7750.0062 | 0 | 11533.3426 | 16.6667 | 0
321 | 18 | Office-Small | 2005-2014 | baseline | 0 | 1211.4622 | 590.75 | 1727.7792 | 46588.9262 | 2558.3354 | 6816.6721 | 0 | 32363.9148 | 7750.0062 | 0 | 11175.0089 | 16.6667 | 0
322 | 18 | Office-Small | 2005-2014 | boiler_reset | 929.13 | 1211.4622 | 590.75 | 1983.3349 | 46127.8147 | 3341.6693 | 6827.7832 | 0 | 32363.9148 | 7750.0062 | 0 | 11572.2315 | 16.6667 | 0
323 | 18 | Office-Small | 2005-2014 | cooling_cop_3_0 | 16747.57 | 1211.4622 | 590.75 | 1983.3349 | 46127.8147 | 3341.6693 | 6827.7832 | 0 | 32363.9148 | 7750.0062 | 0 | 11572.2315 | 16.6667 | 0
324 | 18 | Office-Small | 2005-2014 | dcv_enabled | 13312.62 | 1211.4622 | 590.75 | 1983.3349 | 46127.8147 | 3341.6693 | 6827.7832 | 0 | 32363.9148 | 7750.0062 | 0 | 11572.2315 | 16.6667 | 0
325 | 18 | Office-Small | 2005-2014 | ecm_cold_deck_reset_control | 14063.11 | 1211.4622 | 590.75 | 8491.6735 | 23458.3521 | 4658.3371 | 6883.3388 | 0 | 32363.9148 | 7750.0062 | 0 | 11644.4538 | 16.6667 | 0
326 | 18 | Office-Small | 2005-2014 | economizers_enabled | 5495.15 | 1211.4622 | 590.75 | 1983.3349 | 46127.8147 | 3341.6693 | 6827.7832 | 0 | 32363.9148 | 7750.0062 | 0 | 11572.2315 | 16.6667 | 0
327 | 18 | Office-Small | 2005-2014 | elec_reduce | 40479.61 | 1211.4622 | 590.75 | 1466.6678 | 52083.375 | 2141.6684 | 6833.3388 | 0 | 22655.5737 | 7750.0062 | 0 | 8566.6735 | 11.1111 | 0
328 | 18 | Office-Small | 2005-2014 | envelope_ecm_roof | 0 | 1211.4622 | 590.75 | 1944.446 | 40680.5881 | 3402.7805 | 6813.8943 | 0 | 32363.9148 | 7750.0062 | 0 | 11144.4534 | 16.6667 | 0
329 | 18 | Office-Small | 2005-2014 | envelope_ecm_wall | 0 | 1211.4622 | 590.75 | 1958.3349 | 43958.3685 | 3394.4472 | 6811.1166 | 0 | 32363.9148 | 7750.0062 | 0 | 11411.1202 | 16.6667 | 0
330 | 18 | Office-Small | 2005-2014 | envelope_ecm_windows | 47330.1 | 1211.4622 | 590.75 | 2055.5572 | 42805.5898 | 3463.8917 | 6827.7832 | 0 | 32363.9148 | 7750.0062 | 0 | 11391.6758 | 16.6667 | 0
331 | 18 | Office-Small | 2005-2014 | exhaust_fans_occ_control | 1464.08 | 1211.4622 | 590.75 | 1983.3349 | 46127.8147 | 3361.1138 | 6827.7832 | 0 | 32363.9148 | 7750.0062 | 0 | 9033.3406 | 16.6667 | 0
332 | 18 | Office-Small | 2005-2014 | fans_to_variable | 4038.83 | 1211.4622 | 590.75 | 1983.3349 | 46183.3703 | 3336.1138 | 6827.7832 | 0 | 32363.9148 | 7750.0062 | 0 | 11494.4536 | 16.6667 | 0
333 | 18 | Office-Small | 2005-2014 | hrv_enabled | 162160.19 | 1211.4622 | 590.75 | 1983.3349 | 46127.8147 | 3341.6693 | 6827.7832 | 0 | 32363.9148 | 7750.0062 | 0 | 11572.2315 | 16.6667 | 0
334 | 18 | Office-Small | 2005-2014 | lights_reduce_70p | 19600.97 | 1211.4622 | 590.75 | 1466.6678 | 52080.5972 | 2202.7795 | 6836.1166 | 0 | 22655.5737 | 7750.0062 | 0 | 11100.0089 | 16.6667 | 0
335 | 18 | Office-Small | 2005-2014 | load_reduce | 8552.43 | 1211.4622 | 590.75 | 1711.1125 | 37061.1408 | 2788.8911 | 6850.0055 | 0 | 32363.9148 | 7750.0062 | 0 | 12336.121 | 16.6667 | 0
336 | 18 | Office-Small | 2005-2014 | occupancy_setback | 7623.3 | 1211.4622 | 590.75 | 1711.1125 | 37061.1408 | 2788.8911 | 6850.0055 | 0 | 32363.9148 | 7750.0062 | 0 | 12336.121 | 16.6667 | 0
337 | 18 | Office-Small | 2005-2014 | payback_less_than_20 | 74901.94 | 1211.4622 | 590.75 | 6430.5607 | 28108.3558 | 3847.2253 | 6900.0055 | 0 | 22655.5737 | 7750.0062 | 0 | 9886.119 | 11.1111 | 0
338 | 18 | Office-Small | 2005-2014 | plug_loads_90_percent | 4407.77 | 1211.4622 | 590.75 | 1975.0016 | 46061.148 | 3247.2248 | 6827.7832 | 0 | 32363.9148 | 7750.0062 | 0 | 11572.2315 | 16.6667 | 0
339 | 18 | Office-Small | 2005-2014 | pump_fan_eff_ | 1694.17 | 1211.4622 | 590.75 | 1983.3349 | 46127.8147 | 3341.6693 | 6827.7832 | 0 | 32363.9148 | 7750.0062 | 0 | 11572.2315 | 11.1111 | 0
340 | 13 | Office | 1959-pre | air_temp_reset_enabled | 17578.64 | 3418.6207 | 2700.72 | 0 | 1225195.4246 | 12036.1207 | 0 | 155164.013 | 129052.881 | 39061.1424 | 0 | 105880.6403 | 43530.5904 | 0
341 | 13 | Office | 1959-pre | baseline | 0 | 3418.6207 | 2700.72 | 0 | 1507162.3168 | 71483.3905 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 105730.6401 | 43333.368 | 0
342 | 13 | Office | 1959-pre | boiler_eff_upgrade | 169937.86 | 3418.6207 | 2700.72 | 0 | 1481959.5189 | 73013.9473 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 105525.0844 | 43566.7015 | 0
343 | 13 | Office | 1959-pre | boiler_reset | 929.13 | 3418.6207 | 2700.72 | 0 | 1046181.3925 | 73013.9473 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 105525.0844 | 36236.1401 | 0
344 | 13 | Office | 1959-pre | cooling_cop_3_0 | 20097.09 | 3418.6207 | 2700.72 | 0 | 1481959.5189 | 52152.8195 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 105525.0844 | 43566.7015 | 0
345 | 13 | Office | 1959-pre | dcv_enabled | 42433.98 | 3418.6207 | 2700.72 | 0 | 1273845.4635 | 73277.8364 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 105525.0844 | 43433.3681 | 0
346 | 13 | Office | 1959-pre | ecm_cold_deck_reset_control | 17578.64 | 3418.6207 | 2700.72 | 0 | 1169703.7135 | 8358.34 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 105630.6401 | 43116.7012 | 0
347 | 13 | Office | 1959-pre | economizers_enabled | 6868.93 | 3418.6207 | 2700.72 | 0 | 1482034.519 | 72500.058 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 105525.0844 | 43569.4793 | 0
348 | 13 | Office | 1959-pre | elec_reduce | 150394.17 | 3418.6207 | 2700.72 | 0 | 1324317.7261 | 72586.1692 | 0 | 155177.9019 | 90338.9612 | 39061.1424 | 0 | 50975.0408 | 34141.694 | 0
349 | 13 | Office | 1959-pre | envelope_ecm_roof | 902219.42 | 3418.6207 | 2700.72 | 0 | 1386951.1096 | 66977.8314 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 103500.0828 | 41119.4773 | 0
350 | 13 | Office | 1959-pre | envelope_ecm_wall | 385440.78 | 3418.6207 | 2700.72 | 0 | 1411978.9074 | 69161.1664 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 103788.9719 | 41541.6999 | 0
351 | 13 | Office | 1959-pre | envelope_ecm_windows | 3033752.43 | 3418.6207 | 2700.72 | 0 | 1474509.5129 | 73030.614 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 105202.8619 | 43225.0346 | 0
352 | 13 | Office | 1959-pre | exhaust_fans_occ_control | 5122.33 | 3418.6207 | 2700.72 | 0 | 1481959.5189 | 73013.9473 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 50430.5959 | 43566.7015 | 0
353 | 13 | Office | 1959-pre | fans_to_variable | 5048.54 | 3418.6207 | 2700.72 | 0 | 1482226.1858 | 73008.3917 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 105322.3065 | 43566.7015 | 0
354 | 13 | Office | 1959-pre | hrv_enabled | 304398.06 | 3418.6207 | 2700.72 | 0 | 1260487.1195 | 74125.0593 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 105527.8622 | 43455.5903 | 21897.2397
355 | 13 | Office | 1959-pre | infil_reduce | 52903.88 | 3418.6207 | 2700.72 | 0 | 895634.0498 | 60936.1599 | 0 | 155169.5686 | 129052.881 | 39061.1424 | 0 | 92938.9632 | 28783.3564 | 0
356 | 13 | Office | 1959-pre | infil_reduce_plus_setback | 77202.91 | 3418.6207 | 2700.72 | 0 | 808403.4245 | 59861.159 | 0 | 155166.7908 | 129052.881 | 39061.1424 | 0 | 92813.9631 | 29466.6902 | 0
357 | 13 | Office | 1959-pre | lights_reduce_70p | 80753.4 | 3418.6207 | 2700.72 | 0 | 1529537.3347 | 72325.0579 | 0 | 155177.9019 | 90338.9612 | 39061.1424 | 0 | 106041.7515 | 43741.7017 | 0
358 | 13 | Office | 1959-pre | load_reduce | 78132.04 | 3418.6207 | 2700.72 | 0 | 547300.4378 | 59861.159 | 0 | 155166.7908 | 129052.881 | 39061.1424 | 0 | 92816.7409 | 26150.0209 | 0
359 | 13 | Office | 1959-pre | occupancy_setback | 24299.03 | 3418.6207 | 2700.72 | 0 | 1417220.5782 | 84300.0674 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 108688.9758 | 47022.2598 | 0
360 | 13 | Office | 1959-pre | payback_less_than_20 | 274492.23 | 3418.6207 | 2700.72 | 0 | 250600.2005 | 8594.4513 | 0 | 155166.7908 | 90338.9612 | 39061.1424 | 0 | 37069.4741 | 18944.4596 | 0
361 | 13 | Office | 1959-pre | plug_loads_90_percent | 14049.51 | 3418.6207 | 2700.72 | 0 | 1484148.4095 | 73025.0584 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 105558.4178 | 43588.9238 | 0
362 | 13 | Office | 1959-pre | pumps_to_variable | 3425.24 | 3418.6207 | 2700.72 | 0 | 1514081.7668 | 73013.9473 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 105525.0844 | 10152.7859 | 0
363 | 13 | Office | 1959-pre | pump_fan_eff_ | 8034.95 | 3418.6207 | 2700.72 | 0 | 1481959.5189 | 73013.9473 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 105525.0844 | 34075.0273 | 0
364 | 14 | Office | 1960-1979 | air_temp_reset_enabled | 17578.64 | 3418.6207 | 2700.72 | 0 | 1141417.5798 | 11600.0093 | 0 | 155164.013 | 129052.881 | 39061.1424 | 0 | 103238.9715 | 40469.4768 | 0
365 | 14 | Office | 1960-1979 | baseline | 0 | 3418.6207 | 2700.72 | 0 | 1406556.6808 | 67386.165 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 103005.638 | 40477.8102 | 0
366 | 14 | Office | 1960-1979 | boiler_eff_upgrade | 65332.04 | 3418.6207 | 2700.72 | 0 | 1377242.7685 | 68816.7217 | 0 | 155175.1241 | 129052.881 | 39061.1424 | 0 | 102797.3045 | 40633.3658 | 0
367 | 14 | Office | 1960-1979 | boiler_reset | 929.13 | 3418.6207 | 2700.72 | 0 | 974659.1131 | 68816.7217 | 0 | 155175.1241 | 129052.881 | 39061.1424 | 0 | 102797.3045 | 33950.0272 | 0
368 | 14 | Office | 1960-1979 | cooling_cop_3_0 | 20097.09 | 3418.6207 | 2700.72 | 0 | 1377242.7685 | 49155.5949 | 0 | 155175.1241 | 129052.881 | 39061.1424 | 0 | 102797.3045 | 40633.3658 | 0
369 | 14 | Office | 1960-1979 | dcv_enabled | 42433.98 | 3418.6207 | 2700.72 | 0 | 1170995.3812 | 69133.3886 | 0 | 155175.1241 | 129052.881 | 39061.1424 | 0 | 102797.3045 | 40469.4768 | 0
370 | 14 | Office | 1960-1979 | ecm_cold_deck_reset_control | 17578.64 | 3418.6207 | 2700.72 | 0 | 1086914.7584 | 8383.34 | 0 | 155177.9019 | 129052.881 | 39061.1424 | 0 | 102922.3046 | 40136.1432 | 0
371 | 14 | Office | 1960-1979 | economizers_enabled | 6868.93 | 3418.6207 | 2700.72 | 0 | 1377301.1018 | 68344.4991 | 0 | 155175.1241 | 129052.881 | 39061.1424 | 0 | 102794.5267 | 40636.1436 | 0
372 | 14 | Office | 1960-1979 | elec_reduce | 150394.17 | 3418.6207 | 2700.72 | 0 | 1219470.42 | 68458.3881 | 0 | 155175.1241 | 90338.9612 | 39061.1424 | 0 | 48166.7052 | 31791.6921 | 0
373 | 14 | Office | 1960-1979 | envelope_ecm_roof | 829845.63 | 3418.6207 | 2700.72 | 0 | 1163548.1531 | 57422.2682 | 0 | 155175.1241 | 129052.881 | 39061.1424 | 0 | 98122.3007 | 34972.2502 | 0
374 | 14 | Office | 1960-1979 | envelope_ecm_wall | 385440.78 | 3418.6207 | 2700.72 | 0 | 1311631.6049 | 65127.8299 | 0 | 155175.1241 | 129052.881 | 39061.1424 | 0 | 101430.6367 | 38919.4756 | 0
375 | 14 | Office | 1960-1979 | envelope_ecm_windows | 3033752.43 | 3418.6207 | 2700.72 | 0 | 1370514.9853 | 68816.7217 | 0 | 155175.1241 | 129052.881 | 39061.1424 | 0 | 102575.0821 | 40375.0323 | 0
376 | 14 | Office | 1960-1979 | exhaust_fans_occ_control | 5122.33 | 3418.6207 | 2700.72 | 0 | 1377242.7685 | 68816.7217 | 0 | 155175.1241 | 129052.881 | 39061.1424 | 0 | 47700.0382 | 40633.3658 | 0
377 | 14 | Office | 1960-1979 | fans_to_variable | 5048.54 | 3418.6207 | 2700.72 | 0 | 1377484.4353 | 68808.3884 | 0 | 155175.1241 | 129052.881 | 39061.1424 | 0 | 102611.1932 | 40636.1436 | 0
378 | 14 | Office | 1960-1979 | hrv_enabled | 304398.06 | 3418.6207 | 2700.72 | 0 | 1157412.037 | 69991.7227 | 0 | 155175.1241 | 129052.881 | 39061.1424 | 0 | 102800.0822 | 40505.588 | 21897.2397
379 | 14 | Office | 1960-1979 | infil_reduce | 52903.88 | 3418.6207 | 2700.72 | 0 | 1033545.2713 | 63011.1615 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 94822.2981 | 31525.0252 | 0
380 | 14 | Office | 1960-1979 | infil_reduce_plus_setback | 77202.91 | 3418.6207 | 2700.72 | 0 | 928581.2984 | 61938.9384 | 0 | 155166.7908 | 129052.881 | 39061.1424 | 0 | 95469.5208 | 32866.693 | 0
381 | 14 | Office | 1960-1979 | lights_reduce_70p | 80753.4 | 3418.6207 | 2700.72 | 0 | 1421790.0263 | 68100.0545 | 0 | 155175.1241 | 90338.9612 | 39061.1424 | 0 | 103216.7492 | 40755.5882 | 0
382 | 14 | Office | 1960-1979 | load_reduce | 78132.04 | 3418.6207 | 2700.72 | 0 | 634800.5078 | 61938.9384 | 0 | 155166.7908 | 129052.881 | 39061.1424 | 0 | 95469.5208 | 28636.134 | 0
383 | 14 | Office | 1960-1979 | occupancy_setback | 24299.03 | 3418.6207 | 2700.72 | 0 | 1310609.3818 | 79741.7305 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 105680.6401 | 44075.0353 | 0
384 | 14 | Office | 1960-1979 | payback_less_than_20 | 274492.23 | 3418.6207 | 2700.72 | 0 | 326008.5941 | 8205.5621 | 0 | 155166.7908 | 90338.9612 | 39061.1424 | 0 | 40163.921 | 21255.5726 | 0
385 | 14 | Office | 1960-1979 | plug_loads_90_percent | 14049.51 | 3418.6207 | 2700.72 | 0 | 1379889.9928 | 68894.4996 | 0 | 155175.1241 | 129052.881 | 39061.1424 | 0 | 102805.6378 | 40641.6992 | 0
386 | 14 | Office | 1960-1979 | pumps_to_variable | 3425.24 | 3418.6207 | 2700.72 | 0 | 1407017.7923 | 68816.7217 | 0 | 155175.1241 | 129052.881 | 39061.1424 | 0 | 102797.3045 | 9355.563 | 0
387 | 14 | Office | 1960-1979 | pump_fan_eff_ | 8034.95 | 3418.6207 | 2700.72 | 0 | 1377242.7685 | 68816.7217 | 0 | 155175.1241 | 129052.881 | 39061.1424 | 0 | 102797.3045 | 31780.581 | 0
388 | 15 | Office | 1980-2004 | air_temp_reset_enabled | 17578.64 | 3418.6207 | 2700.72 | 0 | 805631.2001 | 8727.7848 | 0 | 155164.013 | 129052.881 | 39061.1424 | 0 | 94841.7425 | 30100.0241 | 0
389 | 15 | Office | 1980-2004 | baseline | 0 | 3418.6207 | 2700.72 | 0 | 920739.6255 | 33463.9157 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 92583.4074 | 28594.4673 | 0
390 | 15 | Office | 1980-2004 | boiler_eff_upgrade | 32923.3 | 3418.6207 | 2700.72 | 0 | 987348.0121 | 50694.485 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 94033.4086 | 30347.2465 | 0
391 | 15 | Office | 1980-2004 | boiler_reset | 929.13 | 3418.6207 | 2700.72 | 0 | 692889.4432 | 50694.485 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 94033.4086 | 26513.9101 | 0
392 | 15 | Office | 1980-2004 | cooling_cop_3_0 | 20097.09 | 3418.6207 | 2700.72 | 0 | 987348.0121 | 43452.8125 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 94033.4086 | 30347.2465 | 0
393 | 15 | Office | 1980-2004 | dcv_enabled | 42433.98 | 3418.6207 | 2700.72 | 0 | 776575.6213 | 51197.2632 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 94033.4086 | 30152.8019 | 0
394 | 15 | Office | 1980-2004 | ecm_cold_deck_reset_control | 17578.64 | 3418.6207 | 2700.72 | 0 | 745714.4855 | 7233.3391 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 94250.0754 | 30052.8018 | 0
395 | 15 | Office | 1980-2004 | economizers_enabled | 6868.93 | 3418.6207 | 2700.72 | 0 | 987450.79 | 50077.8178 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 94033.4086 | 30350.0243 | 0
396 | 15 | Office | 1980-2004 | elec_reduce | 150394.17 | 3418.6207 | 2700.72 | 0 | 744011.7063 | 38155.5861 | 0 | 155172.3464 | 90338.9612 | 39061.1424 | 0 | 38358.364 | 22788.9071 | 0
397 | 15 | Office | 1980-2004 | envelope_ecm_roof | 829845.63 | 3418.6207 | 2700.72 | 0 | 924275.7394 | 49058.3726 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 93172.2968 | 29000.0232 | 0
398 | 15 | Office | 1980-2004 | envelope_ecm_wall | 385440.78 | 3418.6207 | 2700.72 | 0 | 970536.8875 | 50816.7073 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 93838.964 | 29988.9129 | 0
399 | 15 | Office | 1980-2004 | envelope_ecm_windows | 3033752.43 | 3418.6207 | 2700.72 | 0 | 983067.4531 | 50747.2628 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 94047.2975 | 30308.3576 | 0
400 | 15 | Office | 1980-2004 | exhaust_fans_occ_control | 5122.33 | 3418.6207 | 2700.72 | 0 | 987350.7899 | 50694.485 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 38938.92 | 30347.2465 | 0
401 | 15 | Office | 1980-2004 | fans_to_variable | 5048.54 | 3418.6207 | 2700.72 | 0 | 987531.3456 | 50688.9294 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 93891.7418 | 30347.2465 | 0
402 | 15 | Office | 1980-2004 | hrv_enabled | 304398.06 | 3418.6207 | 2700.72 | 0 | 762297.8321 | 52400.0419 | 0 | 155169.5686 | 129052.881 | 39061.1424 | 0 | 94038.9641 | 30216.6908 | 21897.2397
403 | 15 | Office | 1980-2004 | infil_reduce | 48447.57 | 3418.6207 | 2700.72 | 0 | 829664.5526 | 50519.4849 | 0 | 155169.5686 | 129052.881 | 39061.1424 | 0 | 92672.2964 | 27616.6888 | 0
404 | 15 | Office | 1980-2004 | infil_reduce_plus_setback | 72746.6 | 3418.6207 | 2700.72 | 0 | 749703.3775 | 49619.4841 | 0 | 155166.7908 | 129052.881 | 39061.1424 | 0 | 91972.2958 | 28050.0224 | 0
405 | 15 | Office | 1980-2004 | lights_reduce_70p | 80753.4 | 3418.6207 | 2700.72 | 0 | 957767.4329 | 38116.6972 | 0 | 155172.3464 | 90338.9612 | 39061.1424 | 0 | 93441.7414 | 29300.0234 | 0
406 | 15 | Office | 1980-2004 | load_reduce | 73675.73 | 3418.6207 | 2700.72 | 0 | 503189.2914 | 49619.4841 | 0 | 155166.7908 | 129052.881 | 39061.1424 | 0 | 91972.2958 | 25330.5758 | 0
407 | 15 | Office | 1980-2004 | occupancy_setback | 24299.03 | 3418.6207 | 2700.72 | 0 | 891439.602 | 49952.8177 | 0 | 155166.7908 | 129052.881 | 39061.1424 | 0 | 94700.0758 | 31580.5808 | 0
408 | 15 | Office | 1980-2004 | payback_less_than_20 | 270035.92 | 3418.6207 | 2700.72 | 0 | 229005.7388 | 7258.3391 | 0 | 155166.7908 | 90338.9612 | 39061.1424 | 0 | 35525.0284 | 519.4449 | 0
409 | 15 | Office | 1980-2004 | plug_loads_90_percent | 14049.51 | 3418.6207 | 2700.72 | 0 | 986331.3446 | 50319.4847 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 94008.4085 | 30330.5798 | 0
410 | 15 | Office | 1980-2004 | pumps_to_variable | 3425.24 | 3418.6207 | 2700.72 | 0 | 1011625.8093 | 50694.485 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 94033.4086 | 5911.1158 | 0
411 | 15 | Office | 1980-2004 | pump_fan_eff_ | 8034.95 | 3418.6207 | 2700.72 | 0 | 987348.0121 | 50694.485 | 0 | 155172.3464 | 129052.881 | 39061.1424 | 0 | 94033.4086 | 23736.1301 | 0
412 | 19 | Recreation Center | 1980-2004 | air_temp_reset_enabled | 31641.75 | 12612.7339 | 12410 | 109691.7544 | 5247709.7537 | 19669.4602 | 0 | 295047.4583 | 671719.9818 | 83347.2889 | 64130.6069 | 210072.3903 | 52877.8201 | 0
413 | 19 | Recreation Center | 1980-2004 | baseline | 0 | 12612.7339 | 12410 | 154936.2351 | 4443675.7772 | 16975.0136 | 0 | 295069.6805 | 671719.9818 | 83347.2889 | 64130.6069 | 210072.3903 | 52544.4865 | 0
414 | 19 | Recreation Center | 1980-2004 | boiler_eff_upgrade | 65332.04 | 12612.7339 | 12410 | 153633.4562 | 4368939.6063 | 18483.3481 | 0 | 295064.1249 | 671719.9818 | 83347.2889 | 64130.6069 | 210072.3903 | 52850.0423 | 0
415 | 19 | Recreation Center | 1980-2004 | boiler_reset | 929.13 | 12612.7339 | 12410 | 153633.4562 | 4035708.7841 | 18483.3481 | 0 | 295064.1249 | 671719.9818 | 83347.2889 | 64130.6069 | 210072.3903 | 52850.0423 | 0
416 | 19 | Recreation Center | 1980-2004 | cooling_cop_3_0 | 43373.79 | 12612.7339 | 12410 | 153633.4562 | 4368939.6063 | 15844.4571 | 0 | 295064.1249 | 671719.9818 | 83347.2889 | 64130.6069 | 210072.3903 | 52850.0423 | 0
417 | 19 | Recreation Center | 1980-2004 | dcv_enabled | 26625.24 | 12612.7339 | 12410 | 149139.0082 | 3179596.9881 | 30908.3581 | 0 | 295058.5694 | 671719.9818 | 83347.2889 | 64130.6069 | 210072.3903 | 52808.3756 | 0
418 | 19 | Recreation Center | 1980-2004 | ecm_cold_deck_reset_control | 31641.75 | 12612.7339 | 12410 | 156055.6804 | 4348345.1453 | 17602.7919 | 0 | 295061.3472 | 671719.9818 | 83347.2889 | 64130.6069 | 210072.3903 | 52841.7089 | 0
419 | 19 | Recreation Center | 1980-2004 | economizers_enabled | 8242.72 | 12612.7339 | 12410 | 153675.1229 | 4370175.7184 | 18100.0145 | 0 | 295064.1249 | 671719.9818 | 83347.2889 | 64130.6069 | 210072.3903 | 52622.2643 | 0
420 | 19 | Recreation Center | 1980-2004 | elec_reduce | 301234.95 | 12612.7339 | 12410 | 162572.3523 | 3322663.7692 | 27358.3552 | 0 | 295072.4583 | 470203.1539 | 83347.2889 | 64130.6069 | 209575.1677 | 41230.5885 | 0
421 | 19 | Recreation Center | 1980-2004 | envelope_ecm_roof | 1441649.51 | 12612.7339 | 12410 | 147291.7845 | 4451431.3389 | 19547.2379 | 0 | 295033.5694 | 671719.9818 | 83347.2889 | 64130.6069 | 185216.8148 | 54630.5993 | 0
422 | 19 | Recreation Center | 1980-2004 | envelope_ecm_wall | 1323633.98 | 12612.7339 | 12410 | 166777.9112 | 4590584.228 | 21016.6835 | 0 | 295036.3471 | 671719.9818 | 83347.2889 | 64130.6069 | 201855.717 | 58950.0472 | 0
423 | 19 | Recreation Center | 1980-2004 | envelope_ecm_windows | 236280.58 | 12612.7339 | 12410 | 176511.2523 | 4613025.9126 | 20983.3501 | 0 | 295036.3471 | 671719.9818 | 83347.2889 | 64130.6069 | 205539.0533 | 59344.4919 | 0
424 | 19 | Recreation Center | 1980-2004 | fans_to_variable | 11566.02 | 12612.7339 | 12410 | 153639.0118 | 4370661.8299 | 18466.6814 | 0 | 295064.1249 | 671719.9818 | 83347.2889 | 64130.6069 | 207936.2775 | 52850.0423 | 0
425 | 19 | Recreation Center | 1980-2004 | hrv_enabled | 773100.97 | 12612.7339 | 12410 | 143758.4483 | 2800463.3515 | 40091.6987 | 0 | 295058.5694 | 671719.9818 | 83347.2889 | 64130.6069 | 210072.3903 | 52858.3756 | 39272.2536
426 | 19 | Recreation Center | 1980-2004 | infil_reduce | 109563.11 | 12612.7339 | 12410 | 105277.862 | 3969383.7311 | 17611.1252 | 0 | 295050.236 | 671719.9818 | 83347.2889 | 64130.6069 | 179639.0326 | 41813.9223 | 0
427 | 19 | Recreation Center | 1980-2004 | infil_reduce_plus_setback | 124809.71 | 12612.7339 | 12410 | 122677.8759 | 4946831.7352 | 45063.9249 | 0 | 294983.5693 | 671719.9818 | 83347.2889 | 64130.6069 | 136811.2206 | 43616.7016 | 0
428 | 19 | Recreation Center | 1980-2004 | lights_reduce_70p | 225572.82 | 12612.7339 | 12410 | 165714.0215 | 4504378.6035 | 16522.2354 | 0 | 295075.2361 | 470203.1539 | 83347.2889 | 64130.6069 | 209694.6122 | 52761.1533 | 0
429 | 19 | Recreation Center | 1980-2004 | load_reduce | 125738.83 | 12612.7339 | 12410 | 122677.8759 | 4570325.8785 | 45063.9249 | 0 | 294983.5693 | 671719.9818 | 83347.2889 | 64130.6069 | 136811.2206 | 43616.7016 | 0
430 | 19 | Recreation Center | 1980-2004 | occupancy_setback | 15246.6 | 12612.7339 | 12410 | 201939.0504 | 5413940.4423 | 44983.3693 | 0 | 294994.6804 | 671719.9818 | 83347.2889 | 64130.6069 | 157805.6818 | 52233.3751 | 0
431 | 19 | Recreation Center | 1980-2004 | payback_less_than_20 | 486751.46 | 12612.7339 | 12410 | 136344.5535 | 3456652.7653 | 62725.0502 | 0 | 294989.1249 | 470203.1539 | 83347.2889 | 64130.6069 | 136963.9985 | 33338.9156 | 0
432 | 19 | Recreation Center | 1980-2004 | plug_loads_90_percent | 8815.53 | 12612.7339 | 12410 | 153600.1229 | 4373150.7207 | 18336.1258 | 0 | 295064.1249 | 671719.9818 | 83347.2889 | 64130.6069 | 209952.9457 | 52825.0423 | 0
433 | 19 | Recreation Center | 1980-2004 | pumps_to_variable | 13700.97 | 12612.7339 | 12410 | 153633.4562 | 4409461.8609 | 18383.348 | 0 | 295633.5698 | 671719.9818 | 83347.2889 | 64130.6069 | 210072.3903 | 5891.6714 | 0
434 | 19 | Recreation Center | 1980-2004 | pump_fan_eff_ | 34366.99 | 12612.7339 | 12410 | 153633.4562 | 4368939.6063 | 18483.3481 | 0 | 295064.1249 | 671719.9818 | 83347.2889 | 64130.6069 | 210072.3903 | 41336.1442 | 0
435 | 20 | Storage Building | 1959-pre | baseline | 0 | 965.1569 | 965.157 | 0 | 316208.5863 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 13102.7883 | 0 | 0
436 | 20 | Storage Building | 1959-pre | dcv_enabled | 832.04 | 965.1569 | 965.157 | 0 | 313475.2508 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 12925.0103 | 0 | 0
437 | 20 | Storage Building | 1959-pre | ecm_cold_deck_reset_control | 0 | 965.1569 | 965.157 | 0 | 313475.2508 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 12925.0103 | 0 | 0
438 | 20 | Storage Building | 1959-pre | elec_reduce | 45013.59 | 965.1569 | 965.157 | 0 | 322053.0354 | 0 | 0 | 0 | 19416.6822 | 2569.4465 | 0 | 13233.3439 | 0 | 0
439 | 20 | Storage Building | 1959-pre | envelope_ecm_roof | 279742.72 | 965.1569 | 965.157 | 0 | 292369.6783 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 12055.5652 | 0 | 0
440 | 20 | Storage Building | 1959-pre | envelope_ecm_wall | 156227.18 | 965.1569 | 965.157 | 0 | 303889.132 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 12511.1211 | 0 | 0
441 | 20 | Storage Building | 1959-pre | envelope_ecm_windows | 0 | 965.1569 | 965.157 | 0 | 313475.2508 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 12925.0103 | 0 | 0
442 | 20 | Storage Building | 1959-pre | exhaust_fans_occ_control | 732.04 | 965.1569 | 965.157 | 0 | 313475.2508 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 12925.0103 | 0 | 0
443 | 20 | Storage Building | 1959-pre | hrv_enabled | 0 | 965.1569 | 965.157 | 0 | 313475.2508 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 12925.0103 | 0 | 0
444 | 20 | Storage Building | 1959-pre | infil_reduce | 36270.87 | 965.1569 | 965.157 | 0 | 163047.3527 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 6875.0055 | 0 | 0
445 | 20 | Storage Building | 1959-pre | infil_reduce_plus_setback | 36747.57 | 965.1569 | 965.157 | 0 | 141416.7798 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 7072.2279 | 0 | 0
446 | 20 | Storage Building | 1959-pre | lights_reduce_70p | 23724.27 | 965.1569 | 965.157 | 0 | 321925.2575 | 0 | 0 | 0 | 19416.6822 | 2569.4465 | 0 | 13219.455 | 0 | 0
447 | 20 | Storage Building | 1959-pre | load_reduce | 36747.57 | 965.1569 | 965.157 | 0 | 141416.7798 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 7072.2279 | 0 | 0
448 | 20 | Storage Building | 1959-pre | occupancy_setback | 476.7 | 965.1569 | 965.157 | 0 | 276058.5542 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 13847.2333 | 0 | 0
449 | 20 | Storage Building | 1959-pre | payback_less_than_20 | 63492.23 | 965.1569 | 965.157 | 0 | 150136.2312 | 0 | 0 | 0 | 19416.6822 | 2569.4465 | 0 | 7297.2281 | 0 | 0
450 | 20 | Storage Building | 1959-pre | plug_loads_90_percent | 275.73 | 965.1569 | 965.157 | 0 | 313586.362 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 12936.1215 | 0 | 0
451 | 21 | Storage Building | 1960-1979 | baseline | 0 | 965.1569 | 965.157 | 0 | 288566.8975 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 11944.454 | 0 | 0
452 | 21 | Storage Building | 1960-1979 | dcv_enabled | 832.04 | 965.1569 | 965.157 | 0 | 284619.6721 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 11752.7872 | 0 | 0
453 | 21 | Storage Building | 1960-1979 | ecm_cold_deck_reset_control | 0 | 965.1569 | 965.157 | 0 | 284619.6721 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 11752.7872 | 0 | 0
454 | 21 | Storage Building | 1960-1979 | elec_reduce | 45013.59 | 965.1569 | 965.157 | 0 | 293000.2344 | 0 | 0 | 0 | 19416.6822 | 2569.4465 | 0 | 12041.6763 | 0 | 0
455 | 21 | Storage Building | 1960-1979 | envelope_ecm_roof | 183278.64 | 965.1569 | 965.157 | 0 | 223666.8456 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 9297.2297 | 0 | 0
456 | 21 | Storage Building | 1960-1979 | envelope_ecm_wall | 156227.18 | 965.1569 | 965.157 | 0 | 281264.1139 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 11605.5648 | 0 | 0
457 | 21 | Storage Building | 1960-1979 | envelope_ecm_windows | 0 | 965.1569 | 965.157 | 0 | 284619.6721 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 11752.7872 | 0 | 0
458 | 21 | Storage Building | 1960-1979 | exhaust_fans_occ_control | 732.04 | 965.1569 | 965.157 | 0 | 284619.6721 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 11752.7872 | 0 | 0
459 | 21 | Storage Building | 1960-1979 | hrv_enabled | 0 | 965.1569 | 965.157 | 0 | 284619.6721 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 11752.7872 | 0 | 0
460 | 21 | Storage Building | 1960-1979 | infil_reduce | 36270.87 | 965.1569 | 965.157 | 0 | 209655.7233 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 8705.5625 | 0 | 0
461 | 21 | Storage Building | 1960-1979 | infil_reduce_plus_setback | 36747.57 | 965.1569 | 965.157 | 0 | 181977.9234 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 9127.7851 | 0 | 0
462 | 21 | Storage Building | 1960-1979 | lights_reduce_70p | 23724.27 | 965.1569 | 965.157 | 0 | 292825.2343 | 0 | 0 | 0 | 19416.6822 | 2569.4465 | 0 | 12030.5652 | 0 | 0
463 | 21 | Storage Building | 1960-1979 | load_reduce | 36747.57 | 965.1569 | 965.157 | 0 | 181977.9234 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 9127.7851 | 0 | 0
464 | 21 | Storage Building | 1960-1979 | occupancy_setback | 476.7 | 965.1569 | 965.157 | 0 | 249030.7548 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 12561.1212 | 0 | 0
465 | 21 | Storage Building | 1960-1979 | payback_less_than_20 | 63492.23 | 965.1569 | 965.157 | 0 | 190725.1526 | 0 | 0 | 0 | 19416.6822 | 2569.4465 | 0 | 9380.5631 | 0 | 0
466 | 21 | Storage Building | 1960-1979 | plug_loads_90_percent | 275.73 | 965.1569 | 965.157 | 0 | 284775.2278 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 11766.6761 | 0 | 0
467 | 22 | Storage Building | 1980-2004 | baseline | 0 | 965.1569 | 965.157 | 0 | 174964.0289 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 7383.3392 | 0 | 0
468 | 22 | Storage Building | 1980-2004 | dcv_enabled | 832.04 | 965.1569 | 965.157 | 0 | 172552.9158 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 7238.8947 | 0 | 0
469 | 22 | Storage Building | 1980-2004 | ecm_cold_deck_reset_control | 0 | 965.1569 | 965.157 | 0 | 172552.9158 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 7238.8947 | 0 | 0
470 | 22 | Storage Building | 1980-2004 | elec_reduce | 45013.59 | 965.1569 | 965.157 | 0 | 180622.3667 | 0 | 0 | 0 | 19416.6822 | 2569.4465 | 0 | 7541.6727 | 0 | 0
471 | 22 | Storage Building | 1980-2004 | envelope_ecm_roof | 158942.72 | 965.1569 | 965.157 | 0 | 151222.3432 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 6394.4496 | 0 | 0
472 | 22 | Storage Building | 1980-2004 | envelope_ecm_wall | 156227.18 | 965.1569 | 965.157 | 0 | 170236.2473 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 7136.1168 | 0 | 0
473 | 22 | Storage Building | 1980-2004 | envelope_ecm_windows | 0 | 965.1569 | 965.157 | 0 | 172552.9158 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 7238.8947 | 0 | 0
474 | 22 | Storage Building | 1980-2004 | exhaust_fans_occ_control | 732.04 | 965.1569 | 965.157 | 0 | 172552.9158 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 7238.8947 | 0 | 0
475 | 22 | Storage Building | 1980-2004 | hrv_enabled | 0 | 965.1569 | 965.157 | 0 | 172552.9158 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 7238.8947 | 0 | 0
476 | 22 | Storage Building | 1980-2004 | infil_reduce | 32548.54 | 965.1569 | 965.157 | 0 | 153855.6786 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 6494.4496 | 0 | 0
477 | 22 | Storage Building | 1980-2004 | infil_reduce_plus_setback | 33025.24 | 965.1569 | 965.157 | 0 | 133052.8842 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 6663.8942 | 0 | 0
478 | 22 | Storage Building | 1980-2004 | lights_reduce_70p | 23724.27 | 965.1569 | 965.157 | 0 | 180519.5889 | 0 | 0 | 0 | 19416.6822 | 2569.4465 | 0 | 7530.5616 | 0 | 0
479 | 22 | Storage Building | 1980-2004 | load_reduce | 33025.24 | 965.1569 | 965.157 | 0 | 133052.8842 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 6663.8942 | 0 | 0
480 | 22 | Storage Building | 1980-2004 | occupancy_setback | 476.7 | 965.1569 | 965.157 | 0 | 149675.1197 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 7486.1171 | 0 | 0
481 | 22 | Storage Building | 1980-2004 | payback_less_than_20 | 59769.9 | 965.1569 | 965.157 | 0 | 141752.8912 | 0 | 0 | 0 | 19416.6822 | 2569.4465 | 0 | 6888.8944 | 0 | 0
482 | 22 | Storage Building | 1980-2004 | plug_loads_90_percent | 275.73 | 965.1569 | 965.157 | 0 | 172641.8048 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 7247.228 | 0 | 0
483 | 23 | Storage Building | 2005-2014 | baseline | 0 | 965.1569 | 965.157 | 0 | 104988.9729 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 4255.559 | 0 | 0
484 | 23 | Storage Building | 2005-2014 | dcv_enabled | 832.04 | 965.1569 | 965.157 | 0 | 103050.0824 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 4136.1144 | 0 | 0
485 | 23 | Storage Building | 2005-2014 | ecm_cold_deck_reset_control | 0 | 965.1569 | 965.157 | 0 | 103050.0824 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 4136.1144 | 0 | 0
486 | 23 | Storage Building | 2005-2014 | elec_reduce | 28815.53 | 965.1569 | 965.157 | 0 | 110652.8663 | 0 | 0 | 0 | 19416.6822 | 2569.4465 | 0 | 4425.0035 | 0 | 0
487 | 23 | Storage Building | 2005-2014 | envelope_ecm_roof | 0 | 965.1569 | 965.157 | 0 | 88722.2932 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 3591.6695 | 0 | 0
488 | 23 | Storage Building | 2005-2014 | envelope_ecm_wall | 0 | 965.1569 | 965.157 | 0 | 102244.5262 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 4102.7811 | 0 | 0
489 | 23 | Storage Building | 2005-2014 | envelope_ecm_windows | 0 | 965.1569 | 965.157 | 0 | 103050.0824 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 4136.1144 | 0 | 0
490 | 23 | Storage Building | 2005-2014 | exhaust_fans_occ_control | 732.04 | 965.1569 | 965.157 | 0 | 103050.0824 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 4136.1144 | 0 | 0
491 | 23 | Storage Building | 2005-2014 | hrv_enabled | 0 | 965.1569 | 965.157 | 0 | 103050.0824 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 4136.1144 | 0 | 0
492 | 23 | Storage Building | 2005-2014 | lights_reduce_70p | 23724.27 | 965.1569 | 965.157 | 0 | 110566.7551 | 0 | 0 | 0 | 19416.6822 | 2569.4465 | 0 | 4416.6702 | 0 | 0
493 | 23 | Storage Building | 2005-2014 | load_reduce | 476.7 | 965.1569 | 965.157 | 0 | 120650.0965 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 5680.5601 | 0 | 0
494 | 23 | Storage Building | 2005-2014 | occupancy_setback | 476.7 | 965.1569 | 965.157 | 0 | 87672.2924 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 4177.7811 | 0 | 0
495 | 23 | Storage Building | 2005-2014 | payback_less_than_20 | 27221.36 | 965.1569 | 965.157 | 0 | 129366.7702 | 0 | 0 | 0 | 19416.6822 | 2569.4465 | 0 | 5891.6714 | 0 | 0
496 | 23 | Storage Building | 2005-2014 | plug_loads_90_percent | 275.73 | 965.1569 | 965.157 | 0 | 103119.5269 | 0 | 0 | 0 | 27736.1333 | 2569.4465 | 0 | 4144.4478 | 0 | 0
497 | 24 | Training Building | 1959-pre | air_temp_reset_enabled | 14063.11 | 3699.8929 | 3631.96 | 0 | 2002384.9352 | 52405.5975 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 101180.6365 | 2002.7794 | 0
498 | 24 | Training Building | 1959-pre | baseline | 0 | 3699.8929 | 3631.96 | 0 | 1910162.6392 | 7097.2279 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 100080.6356 | 2794.4467 | 0
499 | 24 | Training Building | 1959-pre | boiler_eff_upgrade | 65332.04 | 3699.8929 | 3631.96 | 0 | 1898023.7406 | 11288.8979 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 101180.6365 | 2755.5578 | 0
500 | 24 | Training Building | 1959-pre | boiler_reset | 929.13 | 3699.8929 | 3631.96 | 0 | 1190559.2858 | 11288.8979 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 101180.6365 | 2755.5578 | 0
501 | 24 | Training Building | 1959-pre | cooling_cop_3_0 | 19757.28 | 3699.8929 | 3631.96 | 0 | 1898023.7406 | 8063.8953 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 101180.6365 | 2755.5578 | 0
502 | 24 | Training Building | 1959-pre | dcv_enabled | 34113.59 | 3699.8929 | 3631.96 | 0 | 1618615.1838 | 11661.1204 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 100741.7473 | 2250.0018 | 0
503 | 24 | Training Building | 1959-pre | ecm_cold_deck_reset_control | 14063.11 | 3699.8929 | 3631.96 | 0 | 1818623.6771 | 27658.3555 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 101180.6365 | 1544.4457 | 0
504 | 24 | Training Building | 1959-pre | economizers_enabled | 5495.15 | 3699.8929 | 3631.96 | 0 | 1897109.851 | 9452.7853 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 101180.6365 | 2755.5578 | 0
505 | 24 | Training Building | 1959-pre | elec_reduce | 205762.14 | 3699.8929 | 3631.96 | 0 | 1673545.7833 | 7069.4501 | 28530.5784 | 0 | 98308.412 | 34280.583 | 0 | 100616.7472 | 1827.7792 | 0
506 | 24 | Training Building | 1959-pre | envelope_ecm_roof | 507871.84 | 3699.8929 | 3631.96 | 0 | 1726340.27 | 10811.1198 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 90966.7394 | 2775.0022 | 0
507 | 24 | Training Building | 1959-pre | envelope_ecm_wall | 442216.5 | 3699.8929 | 3631.96 | 0 | 1818815.3439 | 11741.6761 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 96625.0773 | 2763.8911 | 0
508 | 24 | Training Building | 1959-pre | envelope_ecm_windows | 160545.63 | 3699.8929 | 3631.96 | 0 | 1867957.0499 | 11397.2313 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 99788.9687 | 2744.4466 | 0
509 | 24 | Training Building | 1959-pre | exhaust_fans_occ_control | 1464.08 | 3699.8929 | 3631.96 | 0 | 1898059.8518 | 11263.8979 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 101105.6364 | 2752.78 | 0
510 | 24 | Training Building | 1959-pre | fans_to_variable | 7343.69 | 3699.8929 | 3631.96 | 0 | 1898023.7406 | 11288.8979 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 101180.6365 | 2755.5578 | 0
511 | 24 | Training Building | 1959-pre | hrv_enabled | 246874.76 | 3699.8929 | 3631.96 | 0 | 1619801.2958 | 12916.677 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 101150.0809 | 2263.8907 | 4380.5591
512 | 24 | Training Building | 1959-pre | infil_reduce | 113052.43 | 3699.8929 | 3631.96 | 0 | 1049411.9506 | 18558.3482 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 61269.4935 | 2419.4464 | 0
513 | 24 | Training Building | 1959-pre | infil_reduce_plus_setback | 132587.38 | 3699.8929 | 3631.96 | 0 | 892417.3806 | 15977.7906 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 77480.6175 | 1363.89 | 0
514 | 24 | Training Building | 1959-pre | lights_reduce_70p | 155637.86 | 3699.8929 | 3631.96 | 0 | 1952793.2289 | 7161.1168 | 28530.5784 | 0 | 98308.412 | 34280.583 | 0 | 100822.3029 | 2844.4467 | 0
515 | 24 | Training Building | 1959-pre | load_reduce | 132587.38 | 3699.8929 | 3631.96 | 0 | 551450.4412 | 15977.7906 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 77480.6175 | 1363.89 | 0
516 | 24 | Training Building | 1959-pre | occupancy_setback | 19534.95 | 3699.8929 | 3631.96 | 0 | 1702437.4731 | 8977.785 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 101661.1924 | 2227.7796 | 0
517 | 24 | Training Building | 1959-pre | payback_less_than_20 | 388380.58 | 3699.8929 | 3631.96 | 0 | 413069.7749 | 30505.58 | 28530.5784 | 0 | 98308.412 | 34280.583 | 0 | 81766.7321 | 502.7782 | 0
518 | 24 | Training Building | 1959-pre | plug_loads_90_percent | 11295.15 | 3699.8929 | 3631.96 | 0 | 1899004.297 | 10791.6753 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 101050.0808 | 2758.3355 | 0
519 | 24 | Training Building | 1959-pre | pumps_to_variable | 8068.93 | 3699.8929 | 3631.96 | 0 | 1898023.7406 | 11288.8979 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 101180.6365 | 2755.5578 | 0
520 | 24 | Training Building | 1959-pre | pump_fan_eff_ | 19449.51 | 3699.8929 | 3631.96 | 0 | 1898023.7406 | 11288.8979 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 101180.6365 | 2155.5573 | 0
521 | 25 | Training Building | 1980-2004 | air_temp_reset_enabled | 14063.11 | 3699.8929 | 3631.96 | 0 | 1186912.0606 | 34069.4717 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 61255.6046 | 1686.1125 | 0
522 | 25 | Training Building | 1980-2004 | baseline | 0 | 3699.8929 | 3631.96 | 0 | 1116109.2262 | 6866.6722 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 56355.6006 | 2755.5578 | 0
523 | 25 | Training Building | 1980-2004 | boiler_eff_upgrade | 65332.04 | 3699.8929 | 3631.96 | 0 | 1112939.7792 | 13669.4554 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 61255.6046 | 2597.2243 | 0
524 | 25 | Training Building | 1980-2004 | boiler_reset | 929.13 | 3699.8929 | 3631.96 | 0 | 714270.0159 | 13669.4554 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 61255.6046 | 2597.2243 | 0
525 | 25 | Training Building | 1980-2004 | cooling_cop_3_0 | 19757.28 | 3699.8929 | 3631.96 | 0 | 1112939.7792 | 11716.676 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 61255.6046 | 2597.2243 | 0
526 | 25 | Training Building | 1980-2004 | dcv_enabled | 34113.59 | 3699.8929 | 3631.96 | 0 | 834997.8902 | 14477.7894 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 60813.9375 | 1497.2234 | 0
527 | 25 | Training Building | 1980-2004 | ecm_cold_deck_reset_control | 14063.11 | 3699.8929 | 3631.96 | 0 | 1058523.069 | 21836.1286 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 61255.6046 | 980.5563 | 0
528 | 25 | Training Building | 1980-2004 | economizers_enabled | 5495.15 | 3699.8929 | 3631.96 | 0 | 1111625.8893 | 9547.2299 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 61255.6046 | 2594.4465 | 0
529 | 25 | Training Building | 1980-2004 | elec_reduce | 212413.59 | 3699.8929 | 3631.96 | 0 | 881797.9277 | 8094.4509 | 28530.5784 | 0 | 98308.412 | 34280.583 | 0 | 57797.2685 | 1747.2236 | 0
530 | 25 | Training Building | 1980-2004 | envelope_ecm_roof | 507871.84 | 3699.8929 | 3631.96 | 0 | 1020056.3716 | 14091.6779 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 56805.601 | 2547.2243 | 0
531 | 25 | Training Building | 1980-2004 | envelope_ecm_wall | 442216.5 | 3699.8929 | 3631.96 | 0 | 1084511.9787 | 14088.9002 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 60050.048 | 2583.3354 | 0
532 | 25 | Training Building | 1980-2004 | envelope_ecm_windows | 160545.63 | 3699.8929 | 3631.96 | 0 | 1091878.6513 | 13991.6779 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 60741.7153 | 2563.8909 | 0
533 | 25 | Training Building | 1980-2004 | exhaust_fans_occ_control | 1464.08 | 3699.8929 | 3631.96 | 0 | 1112281.4454 | 13644.4554 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 61180.6045 | 2594.4465 | 0
534 | 25 | Training Building | 1980-2004 | fans_to_variable | 7343.69 | 3699.8929 | 3631.96 | 0 | 1121967.5642 | 13597.2331 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 56086.156 | 1755.557 | 0
535 | 25 | Training Building | 1980-2004 | hrv_enabled | 246874.76 | 3699.8929 | 3631.96 | 0 | 842484.0073 | 16455.5687 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 61225.049 | 1583.3346 | 4377.7813
536 | 25 | Training Building | 1980-2004 | infil_reduce | 100779.61 | 3699.8929 | 3631.96 | 0 | 864270.1359 | 16202.7907 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 55686.1557 | 1927.7793 | 0
537 | 25 | Training Building | 1980-2004 | infil_reduce_plus_setback | 120314.56 | 3699.8929 | 3631.96 | 0 | 730039.4729 | 15122.2343 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 66425.0531 | 1230.5565 | 0
538 | 25 | Training Building | 1980-2004 | lights_reduce_70p | 155637.86 | 3699.8929 | 3631.96 | 0 | 1154195.3678 | 7936.1175 | 28530.5784 | 0 | 98308.412 | 34280.583 | 0 | 58302.8244 | 2788.8911 | 0
539 | 25 | Training Building | 1980-2004 | load_reduce | 120314.56 | 3699.8929 | 3631.96 | 0 | 453853.1409 | 15122.2343 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 66425.0531 | 1230.5565 | 0
540 | 25 | Training Building | 1980-2004 | occupancy_setback | 19534.95 | 3699.8929 | 3631.96 | 0 | 953189.6514 | 11627.7871 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 78627.8407 | 1455.5567 | 0
541 | 25 | Training Building | 1980-2004 | payback_less_than_20 | 376107.77 | 3699.8929 | 3631.96 | 0 | 312333.5832 | 23497.241 | 28530.5784 | 0 | 98308.412 | 34280.583 | 0 | 67752.832 | 430.5559 | 0
542 | 25 | Training Building | 1980-2004 | plug_loads_90_percent | 11295.15 | 3699.8929 | 3631.96 | 0 | 1111381.4447 | 12922.2326 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 60536.1595 | 2613.891 | 0
543 | 25 | Training Building | 1980-2004 | pumps_to_variable | 8068.93 | 3699.8929 | 3631.96 | 0 | 1112939.7792 | 13669.4554 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 61255.6046 | 2597.2243 | 0
544 | 25 | Training Building | 1980-2004 | pump_fan_eff_ | 19449.51 | 3699.8929 | 3631.96 | 0 | 1112939.7792 | 13669.4554 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 61255.6046 | 2030.5572 | 0
545 | 26 | Training Building | 2005-2014 | air_temp_reset_enabled | 14063.11 | 3699.8929 | 3631.96 | 0 | 870828.4744 | 27472.2442 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 50002.8178 | 1369.4455 | 0
546 | 26 | Training Building | 2005-2014 | baseline | 0 | 3699.8929 | 3631.96 | 0 | 771503.395 | 6536.1163 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 35119.4725 | 2636.1132 | 0
547 | 26 | Training Building | 2005-2014 | boiler_eff_upgrade | 32923.3 | 3699.8929 | 3631.96 | 0 | 778117.2892 | 14130.5669 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 50002.8178 | 1694.4458 | 0
548 | 26 | Training Building | 2005-2014 | boiler_reset | 929.13 | 3699.8929 | 3631.96 | 0 | 490464.2813 | 14130.5669 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 50002.8178 | 1694.4458 | 0
549 | 26 | Training Building | 2005-2014 | cooling_cop_3_0 | 19757.28 | 3699.8929 | 3631.96 | 0 | 778117.2892 | 14130.5669 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 50002.8178 | 1694.4458 | 0
550 | 26 | Training Building | 2005-2014 | dcv_enabled | 34113.59 | 3699.8929 | 3631.96 | 0 | 490375.3923 | 15372.2345 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 49588.9286 | 833.334 | 0
551 | 26 | Training Building | 2005-2014 | ecm_cold_deck_reset_control | 14063.11 | 3699.8929 | 3631.96 | 0 | 742536.7051 | 19525.0156 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 50002.8178 | 702.7783 | 0
552 | 26 | Training Building | 2005-2014 | economizers_enabled | 5495.15 | 3699.8929 | 3631.96 | 0 | 776592.2879 | 8830.5626 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 50002.8178 | 1694.4458 | 0
553 | 26 | Training Building | 2005-2014 | elec_reduce | 212413.59 | 3699.8929 | 3631.96 | 0 | 547275.4378 | 9297.2297 | 28530.5784 | 0 | 98308.412 | 34280.583 | 0 | 40388.9212 | 1491.6679 | 0
554 | 26 | Training Building | 2005-2014 | envelope_ecm_roof | 0 | 3699.8929 | 3631.96 | 0 | 724606.1352 | 14311.1226 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 48191.7052 | 1566.6679 | 0
555 | 26 | Training Building | 2005-2014 | envelope_ecm_wall | 0 | 3699.8929 | 3631.96 | 0 | 762064.4985 | 14230.5669 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 49819.4843 | 1641.668 | 0
556 | 26 | Training Building | 2005-2014 | envelope_ecm_windows | 160545.63 | 3699.8929 | 3631.96 | 0 | 755695.049 | 14383.3448 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 49955.5955 | 1613.8902 | 0
557 | 26 | Training Building | 2005-2014 | exhaust_fans_occ_control | 1464.08 | 3699.8929 | 3631.96 | 0 | 777781.1778 | 14175.0113 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 49927.8177 | 1694.4458 | 0
558 | 26 | Training Building | 2005-2014 | fans_to_variable | 7343.69 | 3699.8929 | 3631.96 | 0 | 781103.4027 | 14050.0112 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 47100.0377 | 1086.112 | 0
559 | 26 | Training Building | 2005-2014 | hrv_enabled | 246874.76 | 3699.8929 | 3631.96 | 0 | 507433.7393 | 18169.459 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 49975.04 | 891.6674 | 4375.0035
560 | 26 | Training Building | 2005-2014 | lights_reduce_70p | 155637.86 | 3699.8929 | 3631.96 | 0 | 814858.9852 | 8702.7847 | 28530.5784 | 0 | 98308.412 | 34280.583 | 0 | 41391.6998 | 2405.5575 | 0
561 | 26 | Training Building | 2005-2014 | load_reduce | 19534.95 | 3699.8929 | 3631.96 | 0 | 399986.4311 | 13005.566 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 57994.4908 | 1091.6675 | 0
562 | 26 | Training Building | 2005-2014 | occupancy_setback | 19534.95 | 3699.8929 | 3631.96 | 0 | 640775.5126 | 13005.566 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 57994.4908 | 1091.6675 | 0
563 | 26 | Training Building | 2005-2014 | payback_less_than_20 | 275328.16 | 3699.8929 | 3631.96 | 0 | 265680.7681 | 18766.6817 | 28530.5784 | 0 | 98308.412 | 34280.583 | 0 | 56141.7116 | 400.0003 | 0
564 | 26 | Training Building | 2005-2014 | plug_loads_90_percent | 11295.15 | 3699.8929 | 3631.96 | 0 | 777039.5105 | 13508.3441 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 48880.5947 | 1741.6681 | 0
565 | 26 | Training Building | 2005-2014 | pumps_to_variable | 8068.93 | 3699.8929 | 3631.96 | 0 | 778117.2892 | 14130.5669 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 50002.8178 | 1694.4458 | 0
566 | 26 | Training Building | 2005-2014 | pump_fan_eff_ | 19449.51 | 3699.8929 | 3631.96 | 0 | 778117.2892 | 14130.5669 | 28530.5784 | 0 | 140441.779 | 34280.583 | 0 | 50002.8178 | 1325.0011 | 0
567 | 27 | Vehicle Garage | 1959-pre | air_temp_reset_enabled | 9043.69 | 3744.5971 | 1890.42 | 0 | 728836.6942 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 51663.9302 | 46977.8154 | 0
568 | 27 | Vehicle Garage | 1959-pre | baseline | 0 | 3744.5971 | 1890.42 | 0 | 748947.8214 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 44172.2576 | 46744.4818 | 0
569 | 27 | Vehicle Garage | 1959-pre | boiler_eff_upgrade | 65332.04 | 3744.5971 | 1890.42 | 0 | 728022.8046 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 44130.5909 | 46947.2598 | 0
570 | 27 | Vehicle Garage | 1959-pre | boiler_reset | 929.13 | 3744.5971 | 1890.42 | 0 | 450008.6933 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 44130.5909 | 46947.2598 | 0
571 | 27 | Vehicle Garage | 1959-pre | dcv_enabled | 8495.15 | 3744.5971 | 1890.42 | 0 | 630967.1714 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 44027.813 | 46947.2598 | 0
572 | 27 | Vehicle Garage | 1959-pre | ecm_cold_deck_reset_control | 9043.69 | 3744.5971 | 1890.42 | 0 | 728022.8046 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 44130.5909 | 46947.2598 | 0
573 | 27 | Vehicle Garage | 1959-pre | economizers_enabled | 3517.48 | 3744.5971 | 1890.42 | 0 | 729228.3612 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 44136.1464 | 46077.8146 | 0
574 | 27 | Vehicle Garage | 1959-pre | elec_reduce | 47283.5 | 3744.5971 | 1890.42 | 0 | 659914.4168 | 0 | 4625.0037 | 0 | 44730.5913 | 13780.5666 | 0 | 43908.3685 | 36822.2517 | 0
575 | 27 | Vehicle Garage | 1959-pre | envelope_ecm_roof | 346598.06 | 3744.5971 | 1890.42 | 0 | 713583.9042 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 43025.0344 | 45836.1478 | 0
576 | 27 | Vehicle Garage | 1959-pre | envelope_ecm_wall | 369193.2 | 3744.5971 | 1890.42 | 0 | 686269.9935 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 41461.1443 | 43886.1462 | 0
577 | 27 | Vehicle Garage | 1959-pre | envelope_ecm_windows | 4333.98 | 3744.5971 | 1890.42 | 0 | 727289.4707 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 44091.7019 | 46905.5931 | 0
578 | 27 | Vehicle Garage | 1959-pre | exhaust_fans_occ_control | 732.04 | 3744.5971 | 1890.42 | 0 | 728022.8046 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 43722.2572 | 46947.2598 | 0
579 | 27 | Vehicle Garage | 1959-pre | fans_to_variable | 3029.13 | 3744.5971 | 1890.42 | 0 | 728725.583 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 43719.4794 | 46947.2598 | 0
580 | 27 | Vehicle Garage | 1959-pre | hrv_enabled | 159105.83 | 3744.5971 | 1890.42 | 0 | 647961.6295 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 43980.5907 | 46955.5931 | 13138.8994
581 | 27 | Vehicle Garage | 1959-pre | infil_reduce | 65289.32 | 3744.5971 | 1890.42 | 0 | 458855.9226 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 27636.1332 | 30197.2464 | 0
582 | 27 | Vehicle Garage | 1959-pre | infil_reduce_plus_setback | 70054.37 | 3744.5971 | 1890.42 | 0 | 418747.5572 | 0 | 4627.7815 | 0 | 63900.0511 | 13780.5666 | 0 | 32633.3594 | 433.3337 | 0
583 | 27 | Vehicle Garage | 1959-pre | lights_reduce_70p | 25398.06 | 3744.5971 | 1890.42 | 0 | 756778.3832 | 0 | 4625.0037 | 0 | 44730.5913 | 13780.5666 | 0 | 44291.7021 | 47063.9265 | 0
584 | 27 | Vehicle Garage | 1959-pre | load_reduce | 70983.5 | 3744.5971 | 1890.42 | 0 | 263219.655 | 0 | 4627.7815 | 0 | 63900.0511 | 13780.5666 | 0 | 32633.3594 | 433.3337 | 0
585 | 27 | Vehicle Garage | 1959-pre | occupancy_setback | 4765.05 | 3744.5971 | 1890.42 | 0 | 617069.9381 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 51405.5967 | 53236.1537 | 0
586 | 27 | Vehicle Garage | 1959-pre | payback_less_than_20 | 130204.85 | 3744.5971 | 1890.42 | 0 | 202194.6062 | 0 | 4625.0037 | 0 | 44730.5913 | 13780.5666 | 0 | 32177.8035 | 26263.9099 | 0
587 | 27 | Vehicle Garage | 1959-pre | plug_loads_90_percent | 2755.34 | 3744.5971 | 1890.42 | 0 | 728645.0274 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 44211.1465 | 46963.9265 | 0
588 | 27 | Vehicle Garage | 1959-pre | pump_fan_eff_ | 3251.46 | 3744.5971 | 1890.42 | 0 | 728022.8046 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 44130.5909 | 36716.696 | 0
589 | 28 | Vehicle Garage | 1980-2004 | air_temp_reset_enabled | 9043.69 | 3744.5971 | 1890.42 | 0 | 512736.5213 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 34919.4724 | 32700.0262 | 0
590 | 28 | Vehicle Garage | 1980-2004 | baseline | 0 | 3744.5971 | 1890.42 | 0 | 512247.632 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 30052.8018 | 32441.6926 | 0
591 | 28 | Vehicle Garage | 1980-2004 | boiler_eff_upgrade | 32923.3 | 3744.5971 | 1890.42 | 0 | 504333.7368 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 30130.5797 | 32655.5817 | 0
592 | 28 | Vehicle Garage | 1980-2004 | boiler_reset | 929.13 | 3744.5971 | 1890.42 | 0 | 313297.4729 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 30130.5797 | 32655.5817 | 0
593 | 28 | Vehicle Garage | 1980-2004 | dcv_enabled | 8495.15 | 3744.5971 | 1890.42 | 0 | 409253.1052 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 29891.6906 | 32655.5817 | 0
594 | 28 | Vehicle Garage | 1980-2004 | ecm_cold_deck_reset_control | 9043.69 | 3744.5971 | 1890.42 | 0 | 504333.7368 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 30130.5797 | 32655.5817 | 0
595 | 28 | Vehicle Garage | 1980-2004 | economizers_enabled | 3517.48 | 3744.5971 | 1890.42 | 0 | 505705.9601 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 30133.3574 | 31688.9142 | 0
596 | 28 | Vehicle Garage | 1980-2004 | elec_reduce | 43322.33 | 3744.5971 | 1890.42 | 0 | 436653.1271 | 0 | 4625.0037 | 0 | 44730.5913 | 13780.5666 | 0 | 29788.9127 | 25666.6872 | 0
597 | 28 | Vehicle Garage | 1980-2004 | envelope_ecm_roof | 346598.06 | 3744.5971 | 1890.42 | 0 | 490936.5039 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 29191.69 | 31669.4698 | 0
598 | 28 | Vehicle Garage | 1980-2004 | envelope_ecm_wall | 369193.2 | 3744.5971 | 1890.42 | 0 | 479783.7172 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 28508.3561 | 30827.8024 | 0
599 | 28 | Vehicle Garage | 1980-2004 | envelope_ecm_windows | 4333.98 | 3744.5971 | 1890.42 | 0 | 503764.2919 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 30105.5796 | 32625.0261 | 0
600 | 28 | Vehicle Garage | 1980-2004 | exhaust_fans_occ_control | 732.04 | 3744.5971 | 1890.42 | 0 | 504333.7368 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 29722.246 | 32655.5817 | 0
601 | 28 | Vehicle Garage | 1980-2004 | fans_to_variable | 3029.13 | 3744.5971 | 1890.42 | 0 | 504800.4038 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 29847.2461 | 32655.5817 | 0
602 | 28 | Vehicle Garage | 1980-2004 | hrv_enabled | 159105.83 | 3744.5971 | 1890.42 | 0 | 425486.4515 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 29922.2462 | 32700.0262 | 13138.8994
603 | 28 | Vehicle Garage | 1980-2004 | infil_reduce | 60330.1 | 3744.5971 | 1890.42 | 0 | 417328.1116 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 24838.9088 | 27200.0218 | 0
604 | 28 | Vehicle Garage | 1980-2004 | infil_reduce_plus_setback | 65095.15 | 3744.5971 | 1890.42 | 0 | 378111.4136 | 0 | 4627.7815 | 0 | 63900.0511 | 13780.5666 | 0 | 29444.468 | 397.2225 | 0
605 | 28 | Vehicle Garage | 1980-2004 | lights_reduce_70p | 25398.06 | 3744.5971 | 1890.42 | 0 | 531978.2034 | 0 | 4625.0037 | 0 | 44730.5913 | 13780.5666 | 0 | 30341.6909 | 32800.0262 | 0
606 | 28 | Vehicle Garage | 1980-2004 | load_reduce | 66024.27 | 3744.5971 | 1890.42 | 0 | 238408.5241 | 0 | 4627.7815 | 0 | 63900.0511 | 13780.5666 | 0 | 29444.468 | 397.2225 | 0
607 | 28 | Vehicle Garage | 1980-2004 | occupancy_setback | 4765.05 | 3744.5971 | 1890.42 | 0 | 422378.1157 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 35436.1395 | 37194.4742 | 0
608 | 28 | Vehicle Garage | 1980-2004 | payback_less_than_20 | 125245.63 | 3744.5971 | 1890.42 | 0 | 180005.6996 | 0 | 4625.0037 | 0 | 44730.5913 | 13780.5666 | 0 | 28955.5787 | 23708.3523 | 0
609 | 28 | Vehicle Garage | 1980-2004 | plug_loads_90_percent | 2755.34 | 3744.5971 | 1890.42 | 0 | 505042.0707 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 30125.0241 | 32677.8039 | 0
610 | 28 | Vehicle Garage | 1980-2004 | pump_fan_eff_ | 3251.46 | 3744.5971 | 1890.42 | 0 | 504333.7368 | 0 | 4625.0037 | 0 | 63900.0511 | 13780.5666 | 0 | 30130.5797 | 25538.9093 | 0

## retro-x
baseline_id | building_name | vintage_name | measure_id | actual_floor_area | Total Floor Area M2 | baseline-Electricity-Heating KWh/m2 | baseline-Natural Gas-Heating KWh/m2 | baseline-Electricity-Cooling KWh/m2 | baseline-Electricity-Water Systems KWh/m2 | baseline-Natural Gas-Water Systems KWh/m2 | baseline-Electricity-Interior Lighting KWh/m2 | baseline-Electricity-Interior Equipment KWh/m2 | baseline-District Heating-Interior Equipment KWh/m2 | baseline-Electricity-Fans KWh/m2 | baseline-Electricity-Pumps KWh/m2 | baseline-Electricity-Heat Recovery KWh/m2 | Baseline Total Energy kWh/m2 | Gas Energy Savings KWh/m2 | Elec Energy Savings KWh/m2 | Total Energy Savings % | Baseline Total Cost $/m2 | Gas Cost Savings $/m2 | Elec Cost Savings $/m2 | Total Cost Savings % | Total Savings $ | Capital Cost | Payback Period | GHG Baseline g/m2 | GHG Savings g/m2 | GHG Savings % | %base Area | Electricity-Heating KWh/m2 | Natural Gas-Heating KWh/m2 | Electricity-Cooling KWh/m2 | Electricity-Water Systems KWh/m2 | Natural Gas-Water Systems KWh/m2 | Electricity-Interior Lighting KWh/m2 | Electricity-Interior Equipment KWh/m2 | District Heating-Interior Equipment KWh/m2 | Electricity-Fans KWh/m2 | Electricity-Pumps KWh/m2 | Electricity-Heat Recovery KWh/m2 | % base area | Area for Base (m2) | Saving $
1 | Barracks | 1959-pre | retro-x | 3989 | 5495.7246 | 0 | 34.0716 | 2.2438 | 0 | 22.2598 | 7.2882 | 2.8755 | 0 | 3.4152 | 0.080711 | 0 | 72.2348 | 4.0886 | 0.68876 | 6.6136 | 1.8861 | 0.066235 | 0.07783 | 7.6383 | 574.6759 | 34414 | 59.8842 | 40399.3636 | 1331.0796 | 3.2948 | 0.08671
2 | Fire Hall | 1959-pre | retro-x | 911.7335 | 911.7335 | 0 | 184.8647 | 3.1929 | 23.6546 | 0 | 64.5291 | 26.4697 | 0 | 31.3353 | 6.0599 | 0 | 340.1063 | 22.1838 | 4.8706 | 7.9547 | 13.2453 | 0.35938 | 0.55038 | 6.8685 | 829.4518 | 11902 | 14.3492 | 269748.4079 | 8208.2978 | 3.0429 | 0.0055698
3 | Food Service | 1959-pre | retro-x | 2568 | 2693.605 | 0 | 143.931 | 7.1722 | 51.8706 | 0 | 54.0002 | 11.9258 | 0 | 14.8172 | 0.17402 | 0 | 283.8909 | 17.2717 | 2.6596 | 7.0208 | 12.0451 | 0.2798 | 0.30054 | 4.818 | 1490.3074 | 16046 | 10.7669 | 272626.0852 | 5405.4981 | 1.9828 | 0.043262
4 | Food Service | 2005-2014 | retro-x | 2568 | 2693.605 | 0 | 131.7388 | 5.1292 | 51.8706 | 0 | 54.0002 | 11.9258 | 0 | 13.8321 | 0.16812 | 0 | 268.6647 | 15.8087 | 2.2955 | 6.7386 | 11.5048 | 0.2561 | 0.25939 | 4.4807 | 1323.7901 | 16046 | 12.1213 | 207371.2662 | 4826.8563 | 2.3276 | 0
5 | Hangar | 1959-pre | retro-x | 6423 | 6276.5798 | 0 | 154.4308 | 1.8971 | 0 | 5.8427 | 40.042 | 6.3658 | 0 | 5.3264 | 0.11096 | 0 | 214.0157 | 18.5317 | 0.88014 | 9.0703 | 4.1446 | 0.30021 | 0.099456 | 9.6432 | 2567.0757 | 33120 | 12.9018 | 155159.9863 | 4082.8949 | 2.6314 | 0.26866
6 | Hangar | 1960-1979 | retro-x | 6423 | 6276.5798 | 0 | 156.4448 | 1.7264 | 0 | 5.8427 | 40.042 | 6.3658 | 0 | 5.128 | 0.10869 | 0 | 215.6583 | 18.7734 | 0.83558 | 9.0926 | 4.1352 | 0.30413 | 0.09442 | 9.6379 | 2559.8784 | 33120 | 12.9381 | 151811.634 | 4087.3847 | 2.6924 | 0.026924
7 | Hangar | 1980-2004 | retro-x | 6423 | 6276.5798 | 0 | 125.3745 | 1.3713 | 0 | 5.8427 | 40.042 | 6.3658 | 0 | 4.4224 | 0.095106 | 0 | 183.5138 | 15.0449 | 0.70667 | 8.5833 | 3.5105 | 0.24373 | 0.079853 | 9.2175 | 2078.3624 | 33120 | 15.9356 | 117407.8014 | 3307.8432 | 2.8174 | 0.031409
10 | Maintenance Shop-Small | 1959-pre | retro-x | 927 | 923.718 | 0 | 251.9338 | 5.3627 | 0 | 4.8406 | 38.6014 | 6.6061 | 0 | 18.922 | 18.4482 | 0 | 344.7148 | 30.2321 | 5.1279 | 10.2578 | 9.735 | 0.48976 | 0.57946 | 10.9832 | 991.1642 | 10609 | 10.7036 | 249946.6073 | 9872.8499 | 3.95 | 0.0067581
11 | Maintenance Shop-Small | 1960-1979 | retro-x | 927 | 923.718 | 0 | 235.4593 | 5.0881 | 0 | 4.8406 | 38.6014 | 6.6061 | 0 | 18.074 | 17.573 | 0 | 326.2425 | 28.2551 | 4.8882 | 10.1591 | 9.2424 | 0.45773 | 0.55237 | 10.929 | 936.3629 | 10609 | 11.33 | 236287.9356 | 9310.4053 | 3.9403 | 0.0031284
12 | Maintenance Shop-Small | 1980-2004 | retro-x | 927 | 923.718 | 0 | 163.07 | 2.8579 | 0 | 4.8406 | 38.6014 | 6.6061 | 0 | 13.013 | 12.3551 | 0 | 241.3441 | 19.5684 | 3.3871 | 9.5115 | 6.6562 | 0.31701 | 0.38274 | 10.5128 | 648.671 | 6210 | 9.5734 | 153410.4339 | 6449.5399 | 4.2041 | 0.021039
8 | Maintenance Shop | 1959-pre | retro-x | 1927 | 2388.545 | 0 | 136.2039 | 0.714 | 2.1701 | 0 | 19.8981 | 4.0748 | 0 | 20.9771 | 15.662 | 0 | 199.7001 | 16.3445 | 4.4824 | 10.4291 | 7.1331 | 0.26478 | 0.50651 | 10.8128 | 1486.273 | 6210 | 4.1782 | 182748.5368 | 6825.3243 | 3.7348 | 0.017211
9 | Maintenance Shop | 1980-2004 | retro-x | 1927 | 2388.545 | 0 | 92.6941 | 0.59953 | 2.1701 | 0 | 19.8981 | 4.0748 | 0 | 14.4348 | 11.0872 | 0 | 144.9586 | 11.1233 | 3.1346 | 9.8358 | 5.159 | 0.1802 | 0.35421 | 10.3586 | 1029.7973 | 6210 | 6.0303 | 118045.0277 | 4718.1502 | 3.9969 | 0.047471
16 | Office-Small | 1960-1979 | retro-x | 584 | 1211.4622 | 3.9571 | 22.8924 | 2.5069 | 2.8086 | 0 | 9.0151 | 3.0839 | 0 | 6.5402 | 0.0044213 | 0 | 50.8086 | 2.7471 | 1.561 | 8.4791 | 2.5067 | 0.044503 | 0.1764 | 8.8124 | 129.0053 | 29239 | 226.6496 | 36744.4638 | 1849.8272 | 5.0343 | 0.0049605
17 | Office-Small | 1980-2004 | retro-x | 584 | 1211.4622 | 2.8761 | 13.6817 | 1.8768 | 2.7633 | 0 | 9.0151 | 3.0839 | 0 | 4.7087 | 0.0044213 | 0 | 38.01 | 1.6418 | 1.1359 | 7.3079 | 1.952 | 0.026597 | 0.12836 | 7.9382 | 90.4947 | 29239 | 323.102 | 28981.7758 | 1282.1368 | 4.4239 | 0.018822
18 | Office-Small | 2005-2014 | retro-x | 584 | 1211.4622 | 2.5588 | 11.1848 | 1.5309 | 2.7456 | 0 | 9.0151 | 3.0839 | 0 | 3.9339 | 0.0044213 | 0 | 34.0573 | 1.3422 | 0.96336 | 6.7696 | 1.7471 | 0.021743 | 0.10886 | 7.4754 | 76.2721 | 29239 | 383.3514 | 24325.3143 | 1078.3722 | 4.4331 | 0.0021648
13 | Office | 1959-pre | retro-x | 3418.6207 | 3418.6207 | 0 | 73.3045 | 2.514 | 0 | 45.3887 | 26.4256 | 11.426 | 0 | 10.8434 | 5.5416 | 0 | 175.4437 | 8.7965 | 2.2679 | 6.3065 | 5.3495 | 0.1425 | 0.25627 | 7.4543 | 1363.2565 | 12161 | 8.9206 | 185950.5308 | 3547.6318 | 1.9078 | 0.071353
14 | Office | 1960-1979 | retro-x | 3418.6207 | 3418.6207 | 0 | 95.3626 | 2.4003 | 0 | 45.3887 | 26.4256 | 11.426 | 0 | 11.7486 | 6.2176 | 0 | 198.9693 | 11.4435 | 2.444 | 6.9797 | 5.8727 | 0.18538 | 0.27617 | 7.8593 | 1577.8765 | 12161 | 7.7072 | 178219.9036 | 4174.6428 | 2.3424 | 0.015037
15 | Office | 1980-2004 | retro-x | 3418.6207 | 3418.6207 | 0 | 66.9878 | 2.1232 | 0 | 45.3887 | 26.4256 | 11.426 | 0 | 10.3916 | 0.15195 | 0 | 162.8948 | 8.0385 | 1.52 | 5.8679 | 4.543 | 0.13022 | 0.17176 | 6.6473 | 1032.3733 | 12161 | 11.7797 | 138472.7469 | 2761.3057 | 1.9941 | 0.076404
19 | Recreation Center | 1980-2004 | retro-x | 12612.7339 | 12612.7339 | 10.8101 | 274.0605 | 4.9732 | 0 | 23.3882 | 37.28 | 6.6082 | 5.0846 | 10.8592 | 2.6433 | 0 | 375.7072 | 32.8873 | 3.5143 | 9.6888 | 9.4492 | 0.53277 | 0.39711 | 9.8409 | 11728.4243 | 28980 | 2.4709 | 143044.5256 | 8944.2458 | 6.2528 | 0.068406
20 | Storage Building | 1959-pre | retro-x | 1171 | 965.1569 | 0 | 188.7324 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 9.1732 | 0 | 0 | 225.5438 | 22.6479 | 1.1008 | 10.5295 | 4.459 | 0.3669 | 0.12439 | 11.0178 | 575.2935 | 259 | 0.45021 | 118625.8777 | 5011.6508 | 4.2248 | 0.0014259
21 | Storage Building | 1960-1979 | retro-x | 1171 | 965.1569 | 0 | 239.7557 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 11.7921 | 0 | 0 | 279.186 | 28.7707 | 1.415 | 10.8121 | 5.5815 | 0.46609 | 0.1599 | 11.2153 | 733.0291 | 259 | 0.35333 | 111139.2277 | 6381.0453 | 5.7415 | 0.0035951
22 | Storage Building | 1980-2004 | retro-x | 1171 | 965.1569 | 0 | 178.194 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 8.6599 | 0 | 0 | 214.492 | 21.3833 | 1.0392 | 10.4537 | 4.2303 | 0.34641 | 0.11743 | 10.9646 | 543.1528 | 259 | 0.47685 | 80588.4389 | 4731.695 | 5.8714 | 0.043746
23 | Storage Building | 2005-2014 | retro-x | 1171 | 965.1569 | 0 | 162.6237 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 7.4063 | 0 | 0 | 197.6682 | 19.5148 | 0.88875 | 10.3221 | 3.8364 | 0.31614 | 0.10043 | 10.8583 | 487.8028 | 259 | 0.53095 | 61422.1947 | 4266.3713 | 6.946 | 0.0021648
24 | Training Building | 1959-pre | retro-x | 3699.8929 | 3699.8929 | 0 | 111.6437 | 8.245 | 7.7112 | 0 | 26.5706 | 9.2653 | 0 | 22.0998 | 0.13589 | 0 | 185.6714 | 13.3972 | 3.6577 | 9.1855 | 7.1713 | 0.21704 | 0.41332 | 8.79 | 2332.2379 | 19406 | 8.3208 | 166065.6394 | 5580.2854 | 3.3603 | 0.029521
25 | Training Building | 1980-2004 | retro-x | 3699.8929 | 3699.8929 | 0 | 84.4169 | 6.3508 | 7.7112 | 0 | 26.5706 | 9.2653 | 0 | 18.3121 | 0.11637 | 0 | 152.7433 | 10.13 | 2.9735 | 8.5788 | 6.086 | 0.16411 | 0.33601 | 8.2175 | 1850.3658 | 19406 | 10.4877 | 117304.5636 | 4400.2309 | 3.7511 | 0.020875
26 | Training Building | 2005-2014 | retro-x | 3699.8929 | 3699.8929 | 0 | 71.8077 | 5.0722 | 7.7112 | 0 | 26.5706 | 9.2653 | 0 | 15.1739 | 0.10811 | 0 | 135.709 | 8.6169 | 2.4425 | 8.1494 | 5.3817 | 0.13959 | 0.276 | 7.7225 | 1537.6652 | 19406 | 12.6204 | 95533.2914 | 3667.4086 | 3.8389 | 0.008076
27 | Vehicle Garage | 1959-pre | retro-x | 2270 | 3744.5971 | 0 | 32.733 | 0 | 0.74873 | 0 | 7.2414 | 2.2309 | 0 | 5.2092 | 4.2518 | 0 | 52.415 | 3.928 | 1.1353 | 9.66 | 1.9361 | 0.063633 | 0.12829 | 9.9131 | 435.6686 | 9832 | 22.5676 | 46100.1604 | 1690.8358 | 3.6677 | 0.02256
28 | Vehicle Garage | 1980-2004 | retro-x | 2270 | 3744.5971 | 0 | 29.1408 | 0 | 0.74873 | 0 | 7.2414 | 2.2309 | 0 | 4.6876 | 3.8381 | 0 | 47.8875 | 3.4969 | 1.0231 | 9.4387 | 1.7722 | 0.05665 | 0.11561 | 9.7201 | 391.0256 | 9832 | 25.1441 | 35237.987 | 1516.0258 | 4.3022 | 0.051036
Base Summaries | sum of capital costs $ | 1694143.6657
| Sum of savings $ | 41399.7538
| Payback | 40.9216
Note on AC1: Lubun, Mike: includes gas space heating

## solar dhw ecm
baseline_id | building_name | vintage_name | measure_id | actual_floor_area | Total Floor Area M2 | Electricity-Heating KWh/m2 | Natural Gas-Heating KWh/m2 | Electricity-Cooling KWh/m2 | Electricity-Water Systems KWh/m2 | Natural Gas-Water Systems KWh/m2 | Electricity-Interior Lighting KWh/m2 | Electricity-Interior Equipment KWh/m2 | District Heating-Interior Equipment KWh/m2 | Electricity-Fans KWh/m2 | Electricity-Pumps KWh/m2 | Electricity-Heat Recovery KWh/m2 | baseline-Electricity-Heating KWh/m2 | baseline-Natural Gas-Heating KWh/m2 | baseline-Electricity-Cooling KWh/m2 | baseline-Electricity-Water Systems KWh/m2 | baseline-Natural Gas-Water Systems KWh/m2 | baseline-Electricity-Interior Lighting KWh/m2 | baseline-Electricity-Interior Equipment KWh/m2 | baseline-District Heating-Interior Equipment KWh/m2 | baseline-Electricity-Fans KWh/m2 | baseline-Electricity-Pumps KWh/m2 | baseline-Electricity-Heat Recovery KWh/m2 | Baseline Total Energy kWh/m2 | Gas Energy Savings KWh/m2 | Elec Energy Savings KWh/m2 | Total Energy Savings % | Baseline Total Cost $/m2 | Gas Cost Savings $/m2 | Elec Cost Savings $/m2 | Total Cost Savings % | Vintage Score | Capital Cost | Payback Period | GHG Baseline g/m2 | GHG Savings g/m2 | GHG Savings % | %base Area | Electricity-Heating KWh/m2 | Natural Gas-Heating KWh/m2 | Electricity-Cooling KWh/m2 | Electricity-Water Systems KWh/m2 | Natural Gas-Water Systems KWh/m2 | Electricity-Interior Lighting KWh/m2 | Electricity-Interior Equipment KWh/m2 | District Heating-Interior Equipment KWh/m2 | Electricity-Fans KWh/m2 | Electricity-Pumps KWh/m2 | Electricity-Heat Recovery KWh/m2 | % base area | Area for Base (m2) | Saving $
1 | Barracks | 1959-pre | solar_dhw | 3989 | 5495.7246 | 0 | 87.2842 | 0.88159 | 0 | 12.6806 | 10.4121 | 2.8755 | 0 | 5.7885 | 4.2198 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 9.58 | -0.28 | 6.9693 | 4.475 | 0.1552 | -0.03164 | 2.761 | 0 | 126230 | 256.1148 | 40399.3636 | 1471.22 | 3.6417 | 0.08671 | 0 | 7.5684 | 0.076442 | 0 | 1.0995 | 0.90283 | 0.24934 | 0 | 0.50192 | 0.3659 | 0 | 0.086502 | 20018.9049 | 2473.4558
2 | Fire Hall | 1959-pre | solar_dhw | 911.7335 | 911.7335 | 0 | 536.8288 | 1.4777 | 20.2546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.5507 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 0 | 3.29 | 0.44675 | 31.252 | 0 | 0.37177 | 1.1896 | 0 | 11619 | 34.2789 | 269748.4079 | 2862.3 | 1.0611 | 0.0055698 | 0 | 2.99 | 0.0082302 | 0.11281 | 0 | 0.51346 | 0.14743 | 0 | 0.22488 | 0.086614 | 0 | 0.0055564 | 1285.9106 | 478.063
3 | Food Service | 1959-pre | solar_dhw | 2568 | 2693.605 | 0 | 593.7383 | 2.8797 | 35.6336 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 14.074 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 0 | 15.77 | 2.0091 | 31.2245 | 0 | 1.782 | 5.7071 | 0 | 138243 | 30.2091 | 272626.0852 | 13719.9 | 5.0325 | 0.043262 | 0 | 25.6863 | 0.12458 | 1.5416 | 0 | 3.3374 | 0.51593 | 0 | 1.4613 | 0.60887 | 0 | 0.043262 | 10012 | 17841.4841
4 | Food Service | 2005-2014 | solar_dhw | 2568 | 2693.605 | 0 | 312.9916 | 2.0617 | 35.6316 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.8881 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | 0 | 15.77 | 3.2385 | 24.728 | 0 | 1.782 | 7.2064 | 0 | 138243 | 30.2091 | 207371.2662 | 13719.9 | 6.6161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Hangar | 1959-pre | solar_dhw | 6423 | 6276.5798 | 0 | 454.5181 | 0.35416 | 0 | 3.0227 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1989 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 2.82 | -0.08 | 0.50369 | 16.9077 | 0.045684 | -0.00904 | 0.21673 | 0 | 58447 | 248.3256 | 155159.9863 | 435.18 | 0.28047 | 0.26866 | 0 | 122.1124 | 0.095149 | 0 | 0.81209 | 15.3683 | 1.7103 | 0 | 2.8439 | 2.4714 | 0 | 0.24428 | 56533.1799 | 2071.6018
6 | Hangar | 1960-1979 | solar_dhw | 6423 | 6276.5798 | 0 | 441.2865 | 0.28668 | 0 | 3.0227 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6812 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 2.82 | -0.08 | 0.51734 | 16.5661 | 0.045684 | -0.00904 | 0.2212 | 0 | 58447 | 248.3256 | 151811.634 | 435.18 | 0.28666 | 0.026924 | 0 | 11.8813 | 0.0077186 | 0 | 0.081384 | 1.5401 | 0.17139 | 0 | 0.27043 | 0.23374 | 0 | 0.02686 | 6216.066 | 227.7815
7 | Hangar | 1980-2004 | solar_dhw | 6423 | 6276.5798 | 0 | 279.4407 | 0.22916 | 0 | 3.0227 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.4694 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 2.82 | -0.08 | 0.75787 | 13.2384 | 0.045684 | -0.00904 | 0.2768 | 0 | 58447 | 248.3256 | 117407.8014 | 435.18 | 0.37066 | 0.031409 | 0 | 8.7771 | 0.0071978 | 0 | 0.094941 | 1.7967 | 0.19995 | 0 | 0.22201 | 0.17179 | 0 | 0.028239 | 6535.299 | 239.4795
10 | Maintenance Shop-Small | 1959-pre | solar_dhw | 927 | 923.718 | 0 | 757.1414 | 0.8782 | 0 | 1.8206 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.8541 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 3.02 | -0.11 | 0.32605 | 27.0928 | 0.048924 | -0.01243 | 0.1347 | 0 | 11619 | 343.4532 | 249946.6073 | 444.88 | 0.17799 | 0.0067581 | 0 | 5.1168 | 0.0059349 | 0 | 0.012304 | 0.37266 | 0.044644 | 0 | 0.18347 | 0.27609 | 0 | 0.0067581 | 1564 | 57.0766
11 | Maintenance Shop-Small | 1960-1979 | solar_dhw | 927 | 923.718 | 0 | 704.0844 | 0.72429 | 0 | 1.8206 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.1622 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 3.02 | -0.11 | 0.34864 | 25.6928 | 0.048924 | -0.01243 | 0.14204 | 0 | 11619 | 343.4532 | 236287.9356 | 444.88 | 0.18828 | 0.0031284 | 0 | 2.2027 | 0.0022659 | 0 | 0.0056957 | 0.17251 | 0.020667 | 0 | 0.078871 | 0.11939 | 0 | 0.0031284 | 724 | 26.4217
12 | Maintenance Shop-Small | 1980-2004 | solar_dhw | 927 | 923.718 | 0 | 374.984 | 0.56132 | 0 | 1.8206 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.4342 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 3.02 | -0.11 | 0.60877 | 17.2482 | 0.048924 | -0.01243 | 0.21158 | 0 | 11619 | 343.4532 | 153410.4339 | 444.88 | 0.28999 | 0.021039 | 0 | 7.8893 | 0.01181 | 0 | 0.038305 | 1.1601 | 0.13899 | 0 | 0.30616 | 0.45095 | 0 | 0.021039 | 4869 | 177.6893
8 | Maintenance Shop | 1959-pre | solar_dhw | 1927 | 2388.545 | 0 | 558.0364 | 0.38186 | 0.49108 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.8926 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 0 | 1.58 | 0.24186 | 19.8025 | 0 | 0.17854 | 0.9016 | 0 | 24608 | 71.5252 | 182748.5368 | 1374.6 | 0.75218 | 0.017211 | 0 | 9.6041 | 0.0065721 | 0.0084518 | 0 | 0.48922 | 0.070129 | 0 | 0.54033 | 0.49726 | 0 | 0.017211 | 3983 | 711.1248
9 | Maintenance Shop | 1980-2004 | solar_dhw | 1927 | 2388.545 | 0 | 324.2529 | 0.35278 | 0.49014 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.1908 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 0 | 1.58 | 0.40181 | 13.0465 | 0 | 0.17854 | 1.3685 | 0 | 24608 | 71.5252 | 118045.0277 | 1374.6 | 1.1645 | 0.047471 | 0 | 15.3925 | 0.016747 | 0.023267 | 0 | 1.3494 | 0.19343 | 0 | 0.84762 | 0.76859 | 0 | 0.047471 | 10986 | 1961.4404
16 | Office-Small | 1960-1979 | solar_dhw | 584 | 1211.4622 | 0.28849 | 64.4317 | 1.049 | 0.85064 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.17663 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 0 | 1.83 | 1.9531 | 4.3509 | 0 | 0.20679 | 4.7528 | 0 | 11619 | 96.2114 | 36744.4638 | 1592.1 | 4.3329 | 0.0049605 | 0.0014311 | 0.31962 | 0.0052034 | 0.0042196 | 0 | 0.063883 | 0.015298 | 0 | 0.045191 | 0.00087619 | 0 | 0.0049605 | 1148 | 237.3949
17 | Office-Small | 1980-2004 | solar_dhw | 584 | 1211.4622 | 0.31833 | 35.8546 | 0.89753 | 0.77769 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.17663 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 0 | 1.83 | 2.9465 | 3.5475 | 0 | 0.20679 | 5.8291 | 0 | 11619 | 96.2114 | 28981.7758 | 1592.1 | 5.4935 | 0.018822 | 0.0059918 | 0.67487 | 0.016894 | 0.014638 | 0 | 0.2424 | 0.058046 | 0 | 0.11842 | 0.0033246 | 0 | 0.018822 | 4356 | 900.7772
18 | Office-Small | 2005-2014 | solar_dhw | 584 | 1211.4622 | 0.68751 | 18.5386 | 1.018 | 0.71247 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.17663 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 0 | 1.83 | 4.2193 | 3.1065 | 0 | 0.20679 | 6.6567 | 0 | 11619 | 96.2114 | 24325.3143 | 1592.1 | 6.545 | 0.0021648 | 0.0014883 | 0.040133 | 0.0022038 | 0.0015424 | 0 | 0.027879 | 0.006676 | 0 | 0.0096264 | 0.00038238 | 0 | 0.0021648 | 501 | 103.6018
13 | Office | 1959-pre | solar_dhw | 3418.6207 | 3418.6207 | 0 | 440.8685 | 20.91 | 0 | 42.232 | 37.75 | 11.426 | 0 | 30.9279 | 12.7657 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 3.16 | -0.09 | 0.51171 | 20.7243 | 0.051192 | -0.01017 | 0.19794 | 0 | 36060 | 257.1331 | 185950.5308 | 487.34 | 0.26208 | 0.071353 | 0 | 31.4573 | 1.492 | 0 | 3.0134 | 2.6936 | 0.81528 | 0 | 2.2068 | 0.91087 | 0 | 0.071353 | 16513 | 677.3963
14 | Office | 1960-1979 | solar_dhw | 3418.6207 | 3418.6207 | 0 | 411.4398 | 19.7115 | 0 | 42.232 | 37.75 | 11.426 | 0 | 30.1308 | 11.9304 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 3.16 | -0.09 | 0.54079 | 19.9277 | 0.051192 | -0.01017 | 0.20585 | 0 | 36060 | 257.1331 | 178219.9036 | 487.34 | 0.27345 | 0.015037 | 0 | 6.1869 | 0.2964 | 0 | 0.63505 | 0.56765 | 0.17181 | 0 | 0.45308 | 0.1794 | 0 | 0.015037 | 3480 | 142.7566
15 | Office | 1980-2004 | solar_dhw | 3418.6207 | 3418.6207 | 0 | 269.3307 | 9.7887 | 0 | 42.2303 | 37.75 | 11.426 | 0 | 27.0821 | 8.4543 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | 3.16 | -0.09 | 0.75037 | 15.7669 | 0.051192 | -0.01017 | 0.26018 | 0 | 36060 | 257.1331 | 138472.7469 | 487.34 | 0.35194 | 0.076404 | 0 | 20.578 | 0.7479 | 0 | 3.2266 | 2.8843 | 0.87299 | 0 | 2.0692 | 0.64595 | 0 | 0.076404 | 17682 | 725.351
19 | Recreation Center | 1980-2004 | solar_dhw | 12612.7339 | 12612.7339 | 12.2841 | 352.3166 | 1.3459 | 0 | 16.0246 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.386 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 7.37 | -0.22 | 1.5049 | 16.8267 | 0.11939 | -0.02486 | 0.56181 | 0 | 306550 | 257.1012 | 143044.5256 | 1127.83 | 0.78845 | 0.068406 | 0.84031 | 24.1006 | 0.092065 | 0 | 1.0962 | 3.6431 | 0.45204 | 0.34782 | 1.1393 | 0.30003 | 0 | 0.068406 | 15831 | 1496.5678
20 | Storage Building | 1959-pre | solar_dhw | 1171 | 965.1569 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | 0 | 0 | 0 | 12.6056 | 0 | 0 | 0 | 0 | 0 | 0 | 118625.8777 | 0 | 0 | 0.0014259 | 0 | 0.56681 | 0 | 0 | 0 | 0.049717 | 0.0046058 | 0 | 0.023487 | 0 | 0 | 0.0014259 | 330 | 0
21 | Storage Building | 1960-1979 | solar_dhw | 1171 | 965.1569 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | 0 | 0 | 0 | 11.8781 | 0 | 0 | 0 | 0 | 0 | 0 | 111139.2277 | 0 | 0 | 0.0035951 | 0 | 1.3041 | 0 | 0 | 0 | 0.12535 | 0.011612 | 0 | 0.05398 | 0 | 0 | 0.0035951 | 832 | 0
22 | Storage Building | 1980-2004 | solar_dhw | 1171 | 965.1569 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | 0 | 0 | 0 | 8.9168 | 0 | 0 | 0 | 0 | 0 | 0 | 80588.4389 | 0 | 0 | 0.043746 | 0 | 9.6216 | 0 | 0 | 0 | 1.5253 | 0.1413 | 0 | 0.40602 | 0 | 0 | 0.043746 | 10124 | 0
23 | Storage Building | 2005-2014 | solar_dhw | 1171 | 965.1569 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 175.4249 | 0 | 0 | 0 | 7.0474 | 0 | 0 | 0 | 0 | 0 | 0 | 61422.1947 | 0 | 0 | 0.0021648 | 0 | 0.28571 | 0 | 0 | 0 | 0.07548 | 0.0069924 | 0 | 0.011581 | 0 | 0 | 0.0021648 | 501 | 0
24 | Training Building | 1959-pre | solar_dhw | 3699.8929 | 3699.8929 | 0 | 516.2751 | 1.9182 | 4.7912 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.83528 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 0 | 2.84 | 0.4726 | 17.93 | 0 | 0.32092 | 1.7898 | 0 | 36060 | 30.3696 | 166065.6394 | 2470.8 | 1.4878 | 0.029521 | 0 | 15.2411 | 0.056628 | 0.14144 | 0 | 1.1206 | 0.27352 | 0 | 0.79854 | 0.024658 | 0 | 0.029521 | 6832 | 2192.5254
25 | Training Building | 1980-2004 | solar_dhw | 3699.8929 | 3699.8929 | 0 | 301.6599 | 1.8559 | 4.7912 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.82477 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 0 | 2.84 | 0.75849 | 13.1096 | 0 | 0.32092 | 2.448 | 0 | 36060 | 30.3696 | 117304.5636 | 2470.8 | 2.1063 | 0.020875 | 0 | 6.2971 | 0.038742 | 0.10002 | 0 | 0.79237 | 0.19341 | 0 | 0.31796 | 0.017217 | 0 | 0.020875 | 4831 | 1550.3645
26 | Training Building | 2005-2014 | solar_dhw | 3699.8929 | 3699.8929 | 0 | 208.5205 | 1.7666 | 4.7912 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.79248 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | 0 | 2.84 | 1.0311 | 10.9384 | 0 | 0.32092 | 2.9339 | 0 | 36060 | 30.3696 | 95533.2914 | 2470.8 | 2.5863 | 0.008076 | 0 | 1.684 | 0.014267 | 0.038694 | 0 | 0.30655 | 0.074826 | 0 | 0.076657 | 0.0064001 | 0 | 0.008076 | 1869 | 599.7995
27 | Vehicle Garage | 1959-pre | solar_dhw | 2270 | 3744.5971 | 0 | 121.2459 | 0 | 0.098734 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.6574 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 0 | 0.56 | 0.37511 | 5.133 | 0 | 0.06328 | 1.2328 | 0 | 20566 | 143.1718 | 46100.1604 | 487.2 | 1.0568 | 0.02256 | 0 | 2.7353 | 0 | 0.0022274 | 0 | 0.23338 | 0.050329 | 0 | 0.16133 | 0.17275 | 0 | 0.02256 | 5221 | 330.3849
28 | Vehicle Garage | 1980-2004 | solar_dhw | 2270 | 3744.5971 | 0 | 82.9269 | 0 | 0.098734 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.3419 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 0 | 0.56 | 0.52647 | 3.9923 | 0 | 0.06328 | 1.5851 | 0 | 20566 | 143.1718 | 35237.987 | 487.2 | 1.3826 | 0.051036 | 0 | 4.2322 | 0 | 0.005039 | 0 | 0.52795 | 0.11386 | 0 | 0.2483 | 0.27263 | 0 | 0.051036 | 11811 | 747.4001
Base Summaries | sum of capital costs $ | 3638984.6328 | [30 empty] | 0.71199 | 4.0691
| Sum of savings $ | 35969.9386
| Payback | 101.1674
Note on AN1: Lubun, Mike: includes gas space heating

## model_eui_end_uses
baseline_id | building_name | vintage_name | measure_id | actual_floor_area | Total Floor Area M2 | Electricity-Heating KWh/m2 | Natural Gas-Heating KWh/m2 | Electricity-Cooling KWh/m2 | Electricity-Water Systems KWh/m2 | Natural Gas-Water Systems KWh/m2 | Electricity-Interior Lighting KWh/m2 | Electricity-Interior Equipment KWh/m2 | District Heating-Interior Equipment KWh/m2 | Electricity-Fans KWh/m2 | Electricity-Pumps KWh/m2 | Electricity-Heat Recovery KWh/m2 | baseline-Electricity-Heating KWh/m2 | baseline-Natural Gas-Heating KWh/m2 | baseline-Electricity-Cooling KWh/m2 | baseline-Electricity-Water Systems KWh/m2 | baseline-Natural Gas-Water Systems KWh/m2 | baseline-Electricity-Interior Lighting KWh/m2 | baseline-Electricity-Interior Equipment KWh/m2 | baseline-District Heating-Interior Equipment KWh/m2 | baseline-Electricity-Fans KWh/m2 | baseline-Electricity-Pumps KWh/m2 | baseline-Electricity-Heat Recovery KWh/m2 | Baseline Total Energy kWh/m2 | Gas Energy Savings KWh/m2 | Elec Energy Savings KWh/m2 | Total Energy Savings % | Baseline Total Cost $/m2 | Gas Cost Savings $/m2 | Elec Cost Savings $/m2 | Total Cost Savings % | Vintage Score | Vintage Rank | Payback Period | GHG Baseline g/m2 | GHG Savings g/m2 | GHG Savings %
1 | Barracks | 1959-pre | air_temp_reset_enabled | 3989 | 5495.7246 | 0 | 91.4915 | 2.5538 | 0 | 22.2602 | 10.4121 | 2.8755 | 0 | 5.9345 | 4.379 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | -4.2069 | -2.2573 | -4.8442 | 4.475 | -0.068152 | -0.25508 | -7.223 | -0.32323 | 1 | 100 | 40399.3636 | -2716.9288 | -6.7252
1 | Barracks | 1959-pre | baseline | 3989 | 5495.7246 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 0 | 0 | 0 | 4.475 | 0 | 0 | 0 | 0 | 8 | NA | 40399.3636 | 0 | 0
1 | Barracks | 1959-pre | boiler_eff_upgrade | 3989 | 5495.7246 | 0 | 85.9466 | 1.0775 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.9345 | 4.0293 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 1.3376 | -0.43144 | 0.67907 | 4.475 | 0.021669 | -0.048753 | -0.60521 | -0.027083 | 5 | 100 | 40399.3636 | -135.9201 | -0.33644
1 | Barracks | 1959-pre | boiler_reset | 3989 | 5495.7246 | 0 | 57.0956 | 1.0775 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.9345 | 0.10236 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 30.1886 | 3.4955 | 25.2425 | 4.475 | 0.48906 | 0.395 | 19.7551 | 0.88405 | 19 | 0.26347 | 40399.3636 | 8444.8779 | 20.9035
1 | Barracks | 1959-pre | cooling_cop_3_0 | 3989 | 5495.7246 | 0 | 85.9466 | 0.76969 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.9345 | 4.0293 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 1.3376 | -0.12364 | 0.90974 | 4.475 | 0.021669 | -0.013971 | 0.17203 | 0.0076985 | 10 | 482.5412 | 40399.3636 | 131.8691 | 0.32641
1 | Barracks | 1959-pre | dcv_enabled | 3989 | 5495.7246 | 0 | 83.0135 | 1.2081 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.9345 | 3.9926 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 4.2707 | -0.52536 | 2.8067 | 4.475 | 0.069186 | -0.059365 | 0.21945 | 0.0098204 | 11 | 1592.9776 | 40399.3636 | 307.3998 | 0.7609
1 | Barracks | 1959-pre | ecm_cold_deck_reset_control | 3989 | 5495.7246 | 0 | 85.7327 | 2.1836 | 0 | 22.2598 | 10.4121 | 2.8755 | 0 | 5.9345 | 4.1001 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 1.5522 | -1.6084 | -0.042064 | 4.475 | 0.025146 | -0.18174 | -3.4994 | -0.1566 | 2 | 100 | 40399.3636 | -1121.4223 | -2.7758
1 | Barracks | 1959-pre | economizers_enabled | 3989 | 5495.7246 | 0 | 85.9381 | 0.83169 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.9345 | 4.0191 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 1.346 | -0.17536 | 0.87729 | 4.475 | 0.021806 | -0.019816 | 0.044465 | 0.0019898 | 9 | 519.2313 | 40399.3636 | 88.3756 | 0.21876
1 | Barracks | 1959-pre | elec_reduce | 3989 | 5495.7246 | 0 | 87.0336 | 0.9069 | 0 | 22.2606 | 7.2882 | 2.8755 | 0 | 5.8105 | 3.1305 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 0.25057 | 3.8859 | 3.0998 | 4.475 | 0.0040593 | 0.4391 | 9.903 | 0.44316 | 17 | 105.746 | 40399.3636 | 3425.5723 | 8.4793
1 | Barracks | 1959-pre | envelope_ecm_roof | 3989 | 5495.7246 | 0 | 85.499 | 1.0735 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.9172 | 4.0099 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 1.7852 | -0.39072 | 1.045 | 4.475 | 0.02892 | -0.044151 | -0.34035 | -0.015231 | 7 | 100 | 40399.3636 | -20.3745 | -0.050433
1 | Barracks | 1959-pre | envelope_ecm_wall | 3989 | 5495.7246 | 0 | 81.5955 | 1.0881 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.8222 | 3.8785 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 5.6887 | -0.17903 | 4.1289 | 4.475 | 0.092157 | -0.020231 | 1.6073 | 0.071926 | 13 | 1735.3908 | 40399.3636 | 862.516 | 2.135
1 | Barracks | 1959-pre | envelope_ecm_windows | 3989 | 5495.7246 | 0 | 77.7713 | 1.1795 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7316 | 3.7593 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 9.5129 | -0.060534 | 7.0835 | 4.475 | 0.15411 | -0.0068403 | 3.2909 | 0.14727 | 15 | 625.0108 | 40399.3636 | 1650.151 | 4.0846
1 | Barracks | 1959-pre | fans_to_variable | 3989 | 5495.7246 | 0 | 86.0046 | 1.0735 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.8879 | 4.0301 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 1.2796 | -0.38154 | 0.67302 | 4.475 | 0.02073 | -0.043115 | -0.5002 | -0.022384 | 6 | 100 | 40399.3636 | -102.8879 | -0.25468
1 | Barracks | 1959-pre | hrv_enabled | 3989 | 5495.7246 | 0 | 79.428 | 1.2132 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.9345 | 3.9897 | 1.7353 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 7.8561 | -2.2629 | 4.1915 | 4.475 | 0.12727 | -0.2557 | -2.87 | -0.12843 | 3 | 100 | 40399.3636 | -562.4312 | -1.3922
1 | Barracks | 1959-pre | infil_reduce | 3989 | 5495.7246 | 0 | 40.8979 | 1.8006 | 0 | 22.2602 | 10.4121 | 2.8755 | 0 | 5.3424 | 2.5916 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 46.3867 | 0.87535 | 35.4176 | 4.475 | 0.75146 | 0.098915 | 19.0027 | 0.85038 | 18 | 34.9212 | 40399.3636 | 9064.7661 | 22.4379
1 | Barracks | 1959-pre | infil_reduce_plus_setback | 3989 | 5495.7246 | 0 | 45.8253 | 1.692 | 0 | 22.2602 | 10.4121 | 2.8755 | 0 | 3.3983 | 1.6487 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 41.4592 | 3.8708 | 33.9698 | 4.475 | 0.67164 | 0.43741 | 24.7829 | 1.109 | 20 | 42.9311 | 40399.3636 | 10788.8344 | 26.7055
1 | Barracks | 1959-pre | lights_reduce_70p | 3989 | 5495.7246 | 0 | 89.9227 | 0.81885 | 0 | 22.2606 | 7.2882 | 2.8755 | 0 | 5.8079 | 4.0381 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | -2.6385 | 3.0689 | 0.32249 | 4.475 | -0.042744 | 0.34678 | 6.7941 | 0.30404 | 16 | 73.8598 | 40399.3636 | 2197.6169 | 5.4397
1 | Barracks | 1959-pre | load_reduce | 3989 | 5495.7246 | 0 | 32.5421 | 1.692 | 0 | 22.2602 | 10.4121 | 2.8755 | 0 | 3.3983 | 0.091351 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 54.7425 | 5.4282 | 45.0912 | 4.475 | 0.88683 | 0.61339 | 33.524 | 1.5002 | 21 | 31.8924 | 40399.3636 | 14521.4422 | 35.9447
1 | Barracks | 1959-pre | occupancy_setback | 3989 | 5495.7246 | 0 | 92.095 | 1.1633 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 4.9483 | 3.4383 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | -4.8108 | 1.0599 | -2.8109 | 4.475 | -0.077934 | 0.11977 | 0.9348 | 0.041833 | 12 | 214.1411 | 40399.3636 | 60.9749 | 0.15093
1 | Barracks | 1959-pre | payback_less_than_20 | 3989 | 5495.7246 | 0 | 34.0716 | 2.2438 | 0 | 22.2598 | 7.2882 | 2.8755 | 0 | 3.4152 | 0.080711 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 53.2134 | 7.9941 | 45.8681 | 4.475 | 0.86206 | 0.90333 | 39.4496 | 1.7654 | 22 | 54.8153 | 40399.3636 | 16480.0529 | 40.7929
1 | Barracks | 1959-pre | plug_loads_90_percent | 3989 | 5495.7246 | 0 | 86.0655 | 1.061 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.9352 | 4.033 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 1.2187 | -0.41933 | 0.59907 | 4.475 | 0.019744 | -0.047385 | -0.61767 | -0.027641 | 4 | 100 | 40399.3636 | -146.6643 | -0.36304
1 | Barracks | 1959-pre | pump_fan_eff_ | 3989 | 5495.7246 | 0 | 85.9466 | 1.0775 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.9345 | 3.1514 | 0 | 0 | 87.2842 | 0.88159 | 0 | 22.2606 | 10.4121 | 2.8755 | 0 | 5.7885 | 3.9398 | 0 | 133.4423 | 1.3376 | 0.44648 | 1.337 | 4.475 | 0.021669 | 0.050452 | 1.6116 | 0.072122 | 14 | 34.4218 | 40399.3636 | 627.8698 | 1.5542
2 | Fire Hall | 1959-pre | air_temp_reset_enabled | 911.7335 | 911.7335 | 0 | 520.2791 | 6.9191 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.2774 | 13.8564 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 16.5497 | -3.7596 | 1.7368 | 31.252 | 0.2681 | -0.42484 | -0.50152 | -0.15673 | 2 | 100 | 269748.4079 | -308.4846 | -0.11436
2 | Fire Hall | 1959-pre | baseline | 911.7335 | 911.7335 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 0 | 0 | 0 | 31.252 | 0 | 0 | 0 | 0 | 3 | NA | 269748.4079 | 0 | 0
2 | Fire Hall | 1959-pre | boiler_eff_upgrade | 911.7335 | 911.7335 | 0 | 530.4886 | 1.5355 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.25 | 15.3737 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 6.3402 | 0.13405 | 0.87913 | 31.252 | 0.10271 | 0.015148 | 0.37713 | 0.11786 | 5 | 306.3881 | 269748.4079 | 1251.521 | 0.46396
2 | Fire Hall | 1959-pre | boiler_reset | 911.7335 | 911.7335 | 0 | 389.0821 | 1.5355 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.25 | 15.3737 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 147.7467 | 0.13405 | 20.0807 | 31.252 | 2.3935 | 0.015148 | 7.7072 | 2.4086 | 16 | 0.42309 | 269748.4079 | 26563.2954 | 9.8474
2 | Fire Hall | 1959-pre | cooling_cop_3_0 | 911.7335 | 911.7335 | 0 | 530.4886 | 1.0968 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.25 | 15.3737 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 6.3402 | 0.57278 | 0.93871 | 31.252 | 0.10271 | 0.064724 | 0.53576 | 0.16744 | 8 | 64.3619 | 269748.4079 | 1633.2118 | 0.60546
2 | Fire Hall | 1959-pre | dcv_enabled | 911.7335 | 911.7335 | 0 | 530.4886 | 1.5355 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.25 | 15.3737 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 6.3402 | 0.13405 | 0.87913 | 31.252 | 0.10271 | 0.015148 | 0.37713 | 0.11786 | 6 | 78.3159 | 269748.4079 | 1251.521 | 0.46396
2 | Fire Hall | 1959-pre | ecm_cold_deck_reset_control | 911.7335 | 911.7335 | 0 | 472.3362 | 4.5457 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.2774 | 13.5517 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 64.4926 | -1.0816 | 8.6106 | 31.252 | 1.0448 | -0.12222 | 2.952 | 0.92256 | 15 | 4.1795 | 269748.4079 | 10603.1979 | 3.9308
2 | Fire Hall | 1959-pre | economizers_enabled | 911.7335 | 911.7335 | 0 | 531.232 | 1.4685 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.25 | 14.7034 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 5.5968 | 0.87136 | 0.87831 | 31.252 | 0.090668 | 0.098463 | 0.60518 | 0.18913 | 9 | 6.2158 | 269748.4079 | 1759.9058 | 0.65242
2 | Fire Hall | 1959-pre | elec_reduce | 911.7335 | 911.7335 | 0 | 562.6984 | 1.0328 | 23.6546 | 0 | 64.5291 | 26.4697 | 0 | 40.6674 | 12.2599 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | -25.8695 | 30.991 | 0.69545 | 31.252 | -0.41909 | 3.502 | 9.8647 | 3.0829 | 18 | 12.2842 | 269748.4079 | 22331.564 | 8.2787
2 | Fire Hall | 1959-pre | envelope_ecm_roof | 911.7335 | 911.7335 | 0 | 522.7074 | 1.4929 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 39.9423 | 15.1848 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 14.1215 | 0.67332 | 2.009 | 31.252 | 0.22877 | 0.076085 | 0.97547 | 0.30485 | 10 | 625.0598 | 269748.4079 | 3113.531 | 1.1542
2 | Fire Hall | 1959-pre | envelope_ecm_wall | 911.7335 | 911.7335 | 0 | 517.2324 | 1.5386 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 39.6955 | 14.9867 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 19.5964 | 1.0724 | 2.8066 | 31.252 | 0.31746 | 0.12119 | 1.4036 | 0.43865 | 12 | 679.7319 | 269748.4079 | 4440.7747 | 1.6463
2 | Fire Hall | 1959-pre | envelope_ecm_windows | 911.7335 | 911.7335 | 0 | 520.203 | 1.566 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 39.8387 | 15.0416 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 16.6259 | 0.84698 | 2.3726 | 31.252 | 0.26934 | 0.095709 | 1.1681 | 0.36505 | 11 | 178.6552 | 269748.4079 | 3712.9025 | 1.3764
2 | Fire Hall | 1959-pre | fans_to_variable | 911.7335 | 911.7335 | 0 | 530.6318 | 1.5294 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.1281 | 15.3767 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 6.197 | 0.25897 | 0.87665 | 31.252 | 0.10039 | 0.029264 | 0.41487 | 0.12965 | 7 | 8.9358 | 269748.4079 | 1334.565 | 0.49474
2 | Fire Hall | 1959-pre | hrv_enabled | 911.7335 | 911.7335 | 0 | 460.6735 | 2.6202 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.2347 | 14.6607 | 4.8046 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 76.1554 | -5.0271 | 9.6585 | 31.252 | 1.2337 | -0.56806 | 2.13 | 0.66566 | 14 | 116.6353 | 269748.4079 | 9258.268 | 3.4322
2 | Fire Hall | 1959-pre | infil_reduce | 911.7335 | 911.7335 | 0 | 240.7321 | 2.6994 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 29.1173 | 7.9519 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 296.0967 | 17.5246 | 42.5865 | 31.252 | 4.7968 | 1.9803 | 21.6852 | 6.7771 | 20 | 10.5933 | 269748.4079 | 68247.7424 | 25.3005
2 | Fire Hall | 1959-pre | infil_reduce_plus_setback | 911.7335 | 911.7335 | 0 | 285.2688 | 2.8182 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 30.8204 | 8.5338 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 251.5601 | 15.1208 | 36.2125 | 31.252 | 4.0753 | 1.7086 | 18.5074 | 5.7839 | 19 | 13.3449 | 269748.4079 | 58184.3287 | 21.5699
2 | Fire Hall | 1959-pre | lights_reduce_70p | 911.7335 | 911.7335 | 0 | 562.3541 | 1.0206 | 23.6546 | 0 | 64.5291 | 26.4697 | 0 | 40.646 | 15.6753 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | -25.5253 | 27.6092 | 0.28298 | 31.252 | -0.41351 | 3.1198 | 8.6597 | 2.7063 | 17 | 6.2031 | 269748.4079 | 19450.9899 | 7.2108
2 | Fire Hall | 1959-pre | load_reduce | 911.7335 | 911.7335 | 0 | 207.1452 | 2.8182 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 30.8204 | 8.5338 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 329.6836 | 15.1208 | 46.8208 | 31.252 | 5.3409 | 1.7086 | 22.5571 | 7.0495 | 21 | 11.0936 | 269748.4079 | 72168.4391 | 26.754
2 | Fire Hall | 1959-pre | occupancy_setback | 911.7335 | 911.7335 | 0 | 617.9381 | 1.892 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 44.3752 | 16.8239 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | -81.1093 | -5.7979 | -11.8011 | 31.252 | -1.314 | -0.65516 | -6.3008 | -1.9691 | 1 | 100 | 269748.4079 | -19562.7124 | -7.2522
2 | Fire Hall | 1959-pre | payback_less_than_20 | 911.7335 | 911.7335 | 0 | 184.8647 | 3.1929 | 23.6546 | 0 | 64.5291 | 26.4697 | 0 | 31.3353 | 6.0599 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 351.9641 | 44.363 | 53.8171 | 31.252 | 5.7018 | 5.013 | 34.2853 | 10.7148 | 22 | 12.3759 | 269748.4079 | 101597.4041 | 37.6638
2 | Fire Hall | 1959-pre | plug_loads_90_percent | 911.7335 | 911.7335 | 0 | 530.8329 | 1.5508 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.2683 | 15.3737 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 5.9959 | 0.10054 | 0.82783 | 31.252 | 0.097134 | 0.011361 | 0.34716 | 0.10849 | 4 | 26.9909 | 269748.4079 | 1160.7385 | 0.4303
2 | Fire Hall | 1959-pre | pump_fan_eff_ | 911.7335 | 911.7335 | 0 | 530.4886 | 1.5355 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.25 | 12.0253 | 0 | 0 | 536.8288 | 1.4777 | 23.6546 | 0 | 92.1871 | 26.4697 | 0 | 40.3749 | 15.4407 | 0 | 736.4335 | 6.3402 | 3.4824 | 1.3338 | 31.252 | 0.10271 | 0.39351 | 1.5878 | 0.49622 | 13 | 13.1333 | 269748.4079 | 4164.5638 | 1.5439
3 | Food Service | 1959-pre | air_temp_reset_enabled | 2568 | 2693.605 | 0 | 623.2666 | 9.8365 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 33.8906 | 13.9717 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | -29.5283 | -7.4357 | -4.7091 | 31.2245 | -0.47836 | -0.84023 | -4.2229 | -1.3186 | 2 | 100 | 272626.0852 | -11754.5813 | -4.3116
3 | Food Service | 1959-pre | baseline | 2568 | 2693.605 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 0 | 0 | 0 | 31.2245 | 0 | 0 | 0 | 0 | 16 | NA | 272626.0852 | 0 | 0
3 | Food Service | 1959-pre | boiler_eff_upgrade | 2568 | 2693.605 | 0 | 585.0737 | 4.0064 | 51.8726 | 0 | 77.1428 | 11.9258 | 0 | 33.9142 | 13.8144 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 8.6646 | -1.4728 | 0.91622 | 31.2245 | 0.14037 | -0.16642 | -0.083451 | -0.026057 | 13 | 100 | 272626.0852 | 269.6489 | 0.098908
3 | Food Service | 1959-pre | boiler_reset | 2568 | 2693.605 | 0 | 469.7587 | 4.0064 | 51.8726 | 0 | 77.1428 | 11.9258 | 0 | 33.9142 | 0.73737 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 123.9797 | 11.6043 | 17.2731 | 31.2245 | 2.0085 | 1.3113 | 10.6319 | 3.3198 | 37 | 0.10899 | 272626.0852 | 32288.0658 | 11.8434
3 | Food Service | 1959-pre | cooling_cop_3_0 | 2568 | 2693.605 | 0 | 585.0737 | 2.862 | 51.8726 | 0 | 77.1428 | 11.9258 | 0 | 33.9142 | 13.8144 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 8.6646 | -0.32838 | 1.062 | 31.2245 | 0.14037 | -0.037106 | 0.3307 | 0.10326 | 20 | 74.5074 | 272626.0852 | 1265.2772 | 0.46411
3 | Food Service | 1959-pre | dcv_enabled | 2568 | 2693.605 | 0 | 408.5372 | 6.0012 | 51.8726 | 0 | 77.1428 | 11.9258 | 0 | 33.9171 | 13.5185 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 185.2012 | -3.1746 | 23.1898 | 31.2245 | 3.0003 | -0.35873 | 8.4598 | 2.6415 | 36 | 1.1039 | 272626.0852 | 30389.0788 | 11.1468
3 | Food Service | 1959-pre | ecm_cold_deck_reset_control | 2568 | 2693.605 | 0 | 565.5649 | 5.3307 | 51.8706 | 0 | 77.1428 | 11.9258 | 0 | 33.9987 | 13.6817 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 28.1735 | -2.747 | 3.2393 | 31.2245 | 0.45641 | -0.31041 | 0.4676 | 0.146 | 21 | 37.5076 | 272626.0852 | 2653.2039 | 0.9732
3 | Food Service | 1959-pre | economizers_enabled | 2568 | 2693.605 | 0 | 585.0757 | 3.6387 | 51.8726 | 0 | 77.1428 | 11.9258 | 0 | 33.9142 | 13.7977 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 8.6626 | -1.0884 | 0.96495 | 31.2245 | 0.14033 | -0.12298 | 0.055565 | 0.01735 | 18 | 105.248 | 272626.0852 | 603.7391 | 0.22145
3 | Food Service | 1959-pre | elec_reduce | 2568 | 2693.605 | 0 | 435.8947 | 3.8648 | 51.8736 | 0 | 54.0002 | 11.9258 | 0 | 22.5006 | 10.6594 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 157.8437 | 36.379 | 24.7436 | 31.2245 | 2.5571 | 4.1108 | 21.3546 | 6.6679 | 41 | 7.9013 | 272626.0852 | 59903.7127 | 21.9728
3 | Food Service | 1959-pre | envelope_ecm_roof | 2568 | 2693.605 | 0 | 563.9171 | 3.9208 | 51.8726 | 0 | 77.1428 | 11.9258 | 0 | 33.1542 | 13.2265 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 29.8213 | -0.039326 | 3.7942 | 31.2245 | 0.4831 | -0.0044439 | 1.533 | 0.47866 | 26 | 362.1195 | 272626.0852 | 5303.7926 | 1.9454
3 | Food Service | 1959-pre | envelope_ecm_wall | 2568 | 2693.605 | 0 | 576.3708 | 4.0211 | 51.8726 | 0 | 77.1428 | 11.9258 | 0 | 33.5701 | 13.5254 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 17.3676 | -0.85437 | 2.1037 | 31.2245 | 0.28135 | -0.096544 | 0.59188 | 0.18481 | 22 | 859.0701 | 272626.0852 | 2365.4924 | 0.86767
3 | Food Service | 1959-pre | envelope_ecm_windows | 2568 | 2693.605 | 0 | 564.0724 | 4.0408 | 51.8726 | 0 | 77.1428 | 11.9258 | 0 | 33.224 | 13.2933 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 29.6659 | -0.29593 | 3.7417 | 31.2245 | 0.48059 | -0.03344 | 1.432 | 0.44715 | 25 | 234.8647 | 272626.0852 | 5052.7403 | 1.8534
3 | Food Service | 1959-pre | exhaust_fans_occ_control | 2568 | 2693.605 | 0 | 585.0718 | 4.0064 | 51.8726 | 0 | 77.1428 | 11.9258 | 0 | 22.4043 | 13.8124 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 8.6666 | 10.0391 | 2.3831 | 31.2245 | 0.1404 | 1.1344 | 4.0827 | 1.2748 | 28 | 2.0119 | 272626.0852 | 10285.3038 | 3.7727
3 | Food Service | 1959-pre | fans_to_variable | 2568 | 2693.605 | 0 | 585.3126 | 3.9975 | 51.8726 | 0 | 77.1428 | 11.9258 | 0 | 33.7303 | 13.8144 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 8.4257 | -1.2801 | 0.91034 | 31.2245 | 0.1365 | -0.14465 | -0.026109 | -0.0081524 | 15 | 100 | 272626.0852 | 394.533 | 0.14472
3 | Food Service | 1959-pre | hrv_enabled | 2568 | 2693.605 | 0 | 367.2444 | 6.0651 | 51.8726 | 0 | 77.1428 | 11.9258 | 0 | 33.9122 | 13.3012 | 6.2008 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 226.494 | -9.2171 | 27.6806 | 31.2245 | 3.6692 | -1.0415 | 8.4154 | 2.6277 | 35 | 42.5884 | 272626.0852 | 32523.5036 | 11.9297
3 | Food Service | 1959-pre | infil_reduce | 2568 | 2693.605 | 0 | 327.0252 | 5.139 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 27.9031 | 8.1209 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 266.7131 | 9.1001 | 35.1381 | 31.2245 | 4.3208 | 1.0283 | 17.131 | 5.3491 | 38 | 5.9226 | 272626.0852 | 55658.7795 | 20.4158
3 | Food Service | 1959-pre | infil_reduce_plus_setback | 2568 | 2693.605 | 0 | 297.668 | 2.4068 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 28.0889 | 7.942 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 296.0704 | 11.8255 | 39.2253 | 31.2245 | 4.7963 | 1.3363 | 19.6404 | 6.1326 | 39 | 5.4382 | 272626.0852 | 63284.7533 | 23.213
3 | Food Service | 1959-pre | lights_reduce_70p | 2568 | 2693.605 | 0 | 613.7585 | 2.686 | 51.8736 | 0 | 54.0002 | 11.9258 | 0 | 33.9958 | 13.9589 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | -20.0201 | 22.7631 | 0.34946 | 31.2245 | -0.32433 | 2.5722 | 7.1992 | 2.2479 | 33 | 18.7808 | 272626.0852 | 16220.3356 | 5.9497
3 | Food Service | 1959-pre | load_reduce | 2568 | 2693.605 | 0 | 234.198 | 2.4068 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 28.0889 | 0.42964 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 359.5403 | 19.3378 | 48.2683 | 31.2245 | 5.8246 | 2.1852 | 25.652 | 8.0097 | 43 | 4.2089 | 272626.0852 | 81181.6159 | 29.7776
3 | Food Service | 1959-pre | occupancy_setback | 2568 | 2693.605 | 0 | 547.6792 | 1.7304 | 51.8726 | 0 | 77.1428 | 11.9258 | 0 | 36.9639 | 14.6668 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 46.0592 | -3.0989 | 5.473 | 31.2245 | 0.74616 | -0.35018 | 1.2682 | 0.39598 | 24 | 4.2172 | 272626.0852 | 5548.5252 | 2.0352
3 | Food Service | 1959-pre | payback_less_than_20 | 2568 | 2693.605 | 0 | 143.931 | 7.1722 | 51.8706 | 0 | 54.0002 | 11.9258 | 0 | 14.8172 | 0.17402 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 449.8074 | 51.2434 | 63.8329 | 31.2245 | 7.2869 | 5.7905 | 41.8817 | 13.0774 | 44 | 7.4893 | 272626.0852 | 125097.262 | 45.886
3 | Food Service | 1959-pre | plug_loads_90_percent | 2568 | 2693.605 | 0 | 585.7148 | 3.9366 | 51.8726 | 0 | 77.1428 | 11.9258 | 0 | 33.924 | 13.78 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 8.0236 | -1.3784 | 0.84658 | 31.2245 | 0.12998 | -0.15576 | -0.082552 | -0.025776 | 14 | 100 | 272626.0852 | 237.0197 | 0.086939
3 | Food Service | 1959-pre | pump_fan_eff_ | 2568 | 2693.605 | 0 | 585.0737 | 4.0064 | 51.8726 | 0 | 77.1428 | 11.9258 | 0 | 33.9142 | 10.804 | 0 | 0 | 593.7383 | 2.8797 | 51.8736 | 0 | 77.1428 | 11.9258 | 0 | 33.7775 | 13.604 | 0 | 784.9417 | 8.6646 | 1.5377 | 1.2997 | 31.2245 | 0.14037 | 0.17376 | 1.006 | 0.31412 | 23 | 12.8011 | 272626.0852 | 2888.7331 | 1.0596
4 | Food Service | 2005-2014 | air_temp_reset_enabled | 2568 | 2693.605 | 0 | 392.317 | 5.2127 | 51.8706 | 0 | 77.1428 | 11.9258 | 0 | 26.9632 | 8.701 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | -79.3254 | -7.8555 | -17.9034 | 24.728 | -1.2851 | -0.88767 | -8.7865 | -2.1727 | 1 | 100 | 207371.2662 | -21033.5059 | -10.1429
4 | Food Service | 2005-2014 | baseline | 2568 | 2693.605 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | 0 | 0 | 0 | 24.728 | 0 | 0 | 0 | 0 | 17 | NA | 207371.2662 | 0 | 0
4 | Food Service | 2005-2014 | boiler_eff_upgrade | 2568 | 2693.605 | 0 | 315.8703 | 3.6682 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 27.0104 | 7.8604 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | -2.8787 | -5.5185 | -1.7244 | 24.728 | -0.046635 | -0.62359 | -2.7104 | -0.67022 | 3 | 100 | 207371.2662 | -5316.3712 | -2.5637
4 | Food Service | 2005-2014 | boiler_reset | 2568 | 2693.605 | 0 | 247.3331 | 3.6682 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 27.0104 | 0.46307 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | 65.6585 | 1.8788 | 13.8694 | 24.728 | 1.0637 | 0.21231 | 5.16 | 1.276 | 29 | 0.28356 | 207371.2662 | 13387.447 | 6.4558
4 | Food Service | 2005-2014 | cooling_cop_3_0 | 2568 | 2693.605 | 0 | 315.8703 | 3.6682 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 27.0104 | 7.8604 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | -2.8787 | -5.5185 | -1.7244 | 24.728 | -0.046635 | -0.62359 | -2.7104 | -0.67022 | 4 | 100 | 207371.2662 | -5316.3712 | -2.5637
4 | Food Service | 2005-2014 | dcv_enabled | 2568 | 2693.605 | 0 | 148.6324 | 6.6904 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 27.0124 | 6.9283 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | 164.3591 | -7.6107 | 32.1897 | 24.728 | 2.6626 | -0.86 | 7.2898 | 1.8026 | 31 | 1.6177 | 207371.2662 | 22799.009 | 10.9943
4 | Food Service | 2005-2014 | ecm_cold_deck_reset_control | 2568 | 2693.605 | 0 | 310.6546 | 3.9061 | 51.8706 | 0 | 77.1428 | 11.9258 | 0 | 27.0193 | 7.9115 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | 2.337 | -5.8154 | -0.71433 | 24.728 | 0.037859 | -0.65714 | -2.5044 | -0.61928 | 7 | 100 | 207371.2662 | -4641.0816 | -2.2381
4 | Food Service | 2005-2014 | economizers_enabled | 2568 | 2693.605 | 0 | 315.8762 | 3.0989 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 27.0104 | 7.8496 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | -2.8846 | -4.9384 | -1.6065 | 24.728 | -0.04673 | -0.55804 | -2.4457 | -0.60477 | 9 | 100 | 207371.2662 | -4812.7701 | -2.3208
4 | Food Service | 2005-2014 | elec_reduce | 2568 | 2693.605 | 0 | 158.6194 | 4.3751 | 51.8716 | 0 | 54.0002 | 11.9258 | 0 | 13.4605 | 4.9915 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | 154.3721 | 33.3361 | 38.5476 | 24.728 | 2.5008 | 3.767 | 25.347 | 6.2678 | 40 | 8.4057 | 207371.2662 | 56634.9953 | 27.3109
4 | Food Service | 2005-2014 | envelope_ecm_roof | 2568 | 2693.605 | 0 | 301.9182 | 3.6662 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 26.7105 | 7.5094 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | 11.0734 | -4.8657 | 1.2748 | 24.728 | 0.17939 | -0.54982 | -1.498 | -0.37043 | 12 | 0 | 207371.2662 | -2251.0013 | -1.0855
4 | Food Service | 2005-2014 | envelope_ecm_wall | 2568 | 2693.605 | 0 | 312.9385 | 3.678 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 27.0035 | 7.7906 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | 0.053091 | -5.4516 | -1.1086 | 24.728 | 0.00086007 | -0.61603 | -2.4878 | -0.61517 | 8 | 0 | 207371.2662 | -4733.4172 | -2.2826
4 | Food Service | 2005-2014 | envelope_ecm_windows | 2568 | 2693.605 | 0 | 306.0249 | 3.7753 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 27.0242 | 7.7198 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | 6.9667 | -5.4988 | 0.30144 | 24.728 | 0.11286 | -0.62137 | -2.0564 | -0.50851 | 10 | 100 | 207371.2662 | -3536.9406 | -1.7056
4 | Food Service | 2005-2014 | exhaust_fans_occ_control | 2568 | 2693.605 | 0 | 315.8693 | 3.6682 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 15.5005 | 7.8604 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | -2.8777 | 5.9914 | 0.63942 | 24.728 | -0.046619 | 0.67703 | 2.5494 | 0.63041 | 27 | 4.0685 | 207371.2662 | 4697.3971 | 2.2652
4 | Food Service | 2005-2014 | fans_to_variable | 2568 | 2693.605 | 0 | 316.0118 | 3.6633 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 26.8944 | 7.8614 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | -3.0203 | -5.3985 | -1.7289 | 24.728 | -0.048928 | -0.61004 | -2.6648 | -0.65896 | 5 | 100 | 207371.2662 | -5237.3604 | -2.5256
4 | Food Service | 2005-2014 | hrv_enabled | 2568 | 2693.605 | 0 | 105.5287 | 7.1663 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 27.0055 | 6.8035 | 6.1998 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | 207.4629 | -14.1546 | 39.6976 | 24.728 | 3.3609 | -1.5995 | 7.1232 | 1.7614 | 30 | 63.5324 | 207371.2662 | 24821.371 | 11.9695
4 | Food Service | 2005-2014 | lights_reduce_70p | 2568 | 2693.605 | 0 | 324.3726 | 2.3153 | 51.8716 | 0 | 54.0002 | 11.9258 | 0 | 24.9605 | 7.0149 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | -11.3811 | 21.8724 | 2.1545 | 24.728 | -0.18437 | 2.4716 | 9.2495 | 2.2872 | 34 | 18.4581 | 207371.2662 | 16991.7765 | 8.1939
4 | Food Service | 2005-2014 | load_reduce | 2568 | 2693.605 | 0 | 221.4769 | 1.7333 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 27.034 | 0.41588 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | 91.5147 | 3.8373 | 19.5814 | 24.728 | 1.4825 | 0.43361 | 7.7489 | 1.9162 | 32 | 1.0603 | 207371.2662 | 19719.5611 | 9.5093
4 | Food Service | 2005-2014 | occupancy_setback | 2568 | 2693.605 | 0 | 282.9451 | 1.7333 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 27.034 | 7.7247 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | 30.0464 | -3.4715 | 5.4574 | 24.728 | 0.48675 | -0.39228 | 0.38203 | 0.094467 | 19 | 17.6772 | 207371.2662 | 2358.0636 | 1.1371
4 | Food Service | 2005-2014 | payback_less_than_20 | 2568 | 2693.605 | 0 | 131.7388 | 5.1292 | 51.8706 | 0 | 54.0002 | 11.9258 | 0 | 13.8321 | 0.16812 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | 181.2528 | 37.0347 | 44.8273 | 24.728 | 2.9363 | 4.1849 | 28.7982 | 7.1212 | 42 | 9.3045 | 207371.2662 | 64664.4578 | 31.1829
4 | Food Service | 2005-2014 | plug_loads_90_percent | 2568 | 2693.605 | 0 | 315.7247 | 3.5895 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 27.0035 | 7.8545 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | -2.7332 | -5.4271 | -1.6758 | 24.728 | -0.044278 | -0.61326 | -2.6591 | -0.65753 | 6 | 100 | 207371.2662 | -5210.7777 | -2.5128
4 | Food Service | 2005-2014 | pump_fan_eff_ | 2568 | 2693.605 | 0 | 315.8703 | 3.6682 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 27.0104 | 6.1477 | 0 | 0 | 312.9916 | 2.0617 | 51.8716 | 0 | 77.1428 | 11.9258 | 0 | 24.5407 | 6.4181 | 0 | 486.9522 | -2.8787 | -3.8058 | -1.3727 | 24.728 | -0.046635 | -0.43006 | -1.9277 | -0.47669 | 11 | 100 | 207371.2662 | -3826.3501 | -1.8452
5 | Hangar | 1959-pre | air_temp_reset_enabled | 6423 | 6276.5798 | 0 | 458.2811 | 4.8323 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.6279 | 10.3584 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | -3.763 | -5.7603 | -1.7506 | 16.9077 | -0.060961 | -0.65091 | -4.2103 | -0.71187 | 1 | 100 | 155159.9863 | -5685.0159 | -3.664
5 | Hangar | 1959-pre | baseline | 6423 | 6276.5798 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 0 | 0 | 0 | 16.9077 | 0 | 0 | 0 | 0 | 6 | NA | 155159.9863 | 0 | 0
5 | Hangar | 1959-pre | boiler_eff_upgrade | 6423 | 6276.5798 | 0 | 450.8379 | 0.44021 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.6279 | 9.1166 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 3.6802 | -0.12636 | 0.65329 | 16.9077 | 0.059619 | -0.014278 | 0.26816 | 0.04534 | 17 | 583.535 | 155159.9863 | 548.8191 | 0.35371
5 | Hangar | 1959-pre | boiler_reset | 6423 | 6276.5798 | 0 | 371.8871 | 0.44021 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.6279 | 0.38903 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 82.631 | 8.6012 | 16.771 | 16.9077 | 1.3386 | 0.97194 | 13.6657 | 2.3106 | 59 | 0.062607 | 155159.9863 | 22274.0166 | 14.3555
5 | Hangar | 1959-pre | cooling_cop_3_0 | 6423 | 6276.5798 | 0 | 450.8379 | 0.3143 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.6279 | 9.1166 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 3.6802 | -0.00045289 | 0.67643 | 16.9077 | 0.059619 | -5.1176e-05 | 0.35231 | 0.059567 | 21 | 42.093 | 155159.9863 | 658.3543 | 0.42431
5 | Hangar | 1959-pre | dcv_enabled | 6423 | 6276.5798 | 0 | 387.0688 | 0.54256 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.6279 | 8.8788 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 67.4493 | 0.0090577 | 12.4007 | 16.9077 | 1.0927 | 0.0010235 | 6.4687 | 1.0937 | 48 | 9.12 | 155159.9863 | 12081.3112 | 7.7864
5 | Hangar | 1959-pre | ecm_cold_deck_reset_control | 6423 | 6276.5798 | 0 | 443.4278 | 2.3138 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.6279 | 9.0971 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 11.0903 | -1.9805 | 1.6746 | 16.9077 | 0.17966 | -0.22379 | -0.26101 | -0.044131 | 4 | 100 | 155159.9863 | 262.1499 | 0.16895
5 | Hangar | 1959-pre | economizers_enabled | 6423 | 6276.5798 | 0 | 450.8461 | 0.42707 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.6279 | 9.1143 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 3.672 | -0.11096 | 0.65462 | 16.9077 | 0.059486 | -0.012538 | 0.27767 | 0.046948 | 19 | 9.1115 | 155159.9863 | 560.7563 | 0.36141
5 | Hangar | 1959-pre | elec_reduce | 6423 | 6276.5798 | 0 | 404.0452 | 0.35008 | 0 | 5.8427 | 40.042 | 6.3658 | 0 | 9.7873 | 7.0881 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 50.4729 | 19.9936 | 12.9537 | 16.9077 | 0.81766 | 2.2593 | 18.1985 | 3.0769 | 62 | 11.4057 | 155159.9863 | 26429.0704 | 17.0334
5 | Hangar | 1959-pre | envelope_ecm_roof | 6423 | 6276.5798 | 0 | 418.8659 | 0.39537 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.089 | 8.5541 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 35.6522 | 1.0199 | 6.7413 | 16.9077 | 0.57756 | 0.11525 | 4.0976 | 0.69281 | 42 | 250.9108 | 155159.9863 | 7269.0494 | 4.6849
5 | Hangar | 1959-pre | envelope_ecm_wall | 6423 | 6276.5798 | 0 | 432.8148 | 0.41439 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 9.9332 | 8.4078 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 21.7032 | 1.303 | 4.2292 | 16.9077 | 0.35159 | 0.14723 | 2.9503 | 0.49883 | 40 | 279.5843 | 155159.9863 | 5018.4512 | 3.2344
5 | Hangar | 1959-pre | envelope_ecm_windows | 6423 | 6276.5798 | 0 | 445.8295 | 0.43115 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.4255 | 8.8942 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 8.6886 | 0.30751 | 1.6537 | 16.9077 | 0.14076 | 0.034749 | 1.038 | 0.1755 | 34 | 166.3688 | 155159.9863 | 1822.7991 | 1.1748
5 | Hangar | 1959-pre | exhaust_fans_occ_control | 6423 | 6276.5798 | 0 | 450.8361 | 0.44156 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 9.762 | 9.1166 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 3.682 | 0.73821 | 0.81255 | 16.9077 | 0.059648 | 0.083417 | 0.84615 | 0.14307 | 30 | 3.9821 | 155159.9863 | 1301.3113 | 0.83869
5 | Hangar | 1959-pre | fans_to_variable | 6423 | 6276.5798 | 0 | 450.9847 | 0.43794 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5319 | 9.1171 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 3.5334 | -0.028532 | 0.6443 | 16.9077 | 0.057241 | -0.0032241 | 0.31948 | 0.054017 | 20 | 6.3101 | 155159.9863 | 607.6599 | 0.39163
5 | Hangar | 1959-pre | hrv_enabled | 6423 | 6276.5798 | 0 | 398.1328 | 0.62045 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.6279 | 8.8725 | 1.4284 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 56.3853 | -1.4909 | 10.0911 | 16.9077 | 0.91344 | -0.16847 | 4.4061 | 0.74497 | 43 | 37.9556 | 155159.9863 | 8795.8848 | 5.6689
5 | Hangar | 1959-pre | infil_reduce | 6423 | 6276.5798 | 0 | 260.2817 | 0.47281 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.186 | 5.4351 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 194.2364 | 6.9645 | 36.9863 | 16.9077 | 3.1466 | 0.78699 | 23.2653 | 3.9336 | 65 | 3.7188 | 155159.9863 | 40827.4157 | 26.3131
5 | Hangar | 1959-pre | infil_reduce_plus_setback | 6423 | 6276.5798 | 0 | 225.0766 | 0.29121 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 6.1679 | 4.3038 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 229.4415 | 9.2955 | 43.8865 | 16.9077 | 3.717 | 1.0504 | 28.1963 | 4.7673 | 67 | 4.2666 | 155159.9863 | 49157.1156 | 31.6816
5 | Hangar | 1959-pre | lights_reduce_70p | 6423 | 6276.5798 | 0 | 467.674 | 0.28713 | 0 | 5.8427 | 40.042 | 6.3658 | 0 | 10.6483 | 9.2692 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | -13.1559 | 17.0145 | 0.70932 | 16.9077 | -0.21313 | 1.9226 | 10.1109 | 1.7095 | 55 | 11.823 | 155159.9863 | 12447.7107 | 8.0225
5 | Hangar | 1959-pre | load_reduce | 6423 | 6276.5798 | 0 | 182.7851 | 0.29121 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 6.1679 | 0.29075 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 271.733 | 13.3085 | 52.3985 | 16.9077 | 4.4021 | 1.5039 | 34.9305 | 5.9059 | 70 | 3.4685 | 155159.9863 | 60218.6254 | 38.8107
5 | Hangar | 1959-pre | occupancy_setback | 6423 | 6276.5798 | 0 | 398.6441 | 0.23912 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 8.9916 | 7.4183 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 55.874 | 3.4093 | 10.8979 | 16.9077 | 0.90516 | 0.38525 | 7.6321 | 1.2904 | 51 | 4.4264 | 155159.9863 | 12967.565 | 8.3575
5 | Hangar | 1959-pre | payback_less_than_20 | 6423 | 6276.5798 | 0 | 154.4308 | 1.8971 | 0 | 5.8427 | 40.042 | 6.3658 | 0 | 5.3264 | 0.11096 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 300.0873 | 29.8846 | 60.658 | 16.9077 | 4.8614 | 3.377 | 48.7256 | 8.2384 | 72 | 7.487 | 155159.9863 | 79715.2667 | 51.3762
5 | Hangar | 1959-pre | plug_loads_90_percent | 6423 | 6276.5798 | 0 | 450.977 | 0.43024 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.6333 | 9.1225 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 3.5411 | -0.12771 | 0.62748 | 16.9077 | 0.057366 | -0.014432 | 0.25393 | 0.042934 | 16 | 76.9219 | 155159.9863 | 522.7496 | 0.33691
5 | Hangar | 1959-pre | pumps_to_variable | 6423 | 6276.5798 | 0 | 450.8379 | 0.44021 | 0 | 5.859 | 57.2028 | 6.3658 | 0 | 10.6279 | 9.1003 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 3.6639 | -0.11005 | 0.65329 | 16.9077 | 0.059354 | -0.012436 | 0.2775 | 0.046919 | 18 | 11.366 | 155159.9863 | 560.0851 | 0.36097
5 | Hangar | 1959-pre | pump_fan_eff_ | 6423 | 6276.5798 | 0 | 450.8379 | 0.44021 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.6279 | 7.1302 | 0 | 0 | 454.5181 | 0.35416 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.5853 | 9.1189 | 0 | 543.9877 | 3.6802 | 1.86 | 1.0184 | 16.9077 | 0.059619 | 0.21018 | 1.5957 | 0.2698 | 36 | 3.8405 | 155159.9863 | 2276.9535 | 1.4675
6 | Hangar | 1960-1979 | air_temp_reset_enabled | 6423 | 6276.5798 | 0 | 443.0025 | 4.5628 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0817 | 9.7312 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | -1.716 | -5.4437 | -1.3518 | 16.5661 | -0.027799 | -0.61514 | -3.881 | -0.64294 | 2 | 100 | 151811.634 | -5043.1802 | -3.322
6 | Hangar | 1960-1979 | baseline | 6423 | 6276.5798 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 0 | 0 | 0 | 16.5661 | 0 | 0 | 0 | 0 | 7 | NA | 151811.634 | 0 | 0
6 | Hangar | 1960-1979 | boiler_eff_upgrade | 6423 | 6276.5798 | 0 | 436.3546 | 0.37001 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0817 | 8.5913 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 4.9319 | -0.11096 | 0.91025 | 16.5661 | 0.079897 | -0.012538 | 0.40661 | 0.067359 | 23 | 392.7853 | 151811.634 | 786.2839 | 0.51793
6 | Hangar | 1960-1979 | boiler_reset | 6423 | 6276.5798 | 0 | 360.8131 | 0.37001 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0817 | 0.37816 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 80.4735 | 8.1021 | 16.7241 | 16.5661 | 1.3037 | 0.91554 | 13.3961 | 2.2192 | 58 | 0.065184 | 151811.634 | 21453.614 | 14.1317
6 | Hangar | 1960-1979 | cooling_cop_3_0 | 6423 | 6276.5798 | 0 | 436.3546 | 0.26403 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0817 | 8.5913 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 4.9319 | -0.0049818 | 0.93026 | 16.5661 | 0.079897 | -0.00056294 | 0.4789 | 0.079334 | 27 | 31.6051 | 151811.634 | 878.4826 | 0.57867
6 | Hangar | 1960-1979 | dcv_enabled | 6423 | 6276.5798 | 0 | 372.7947 | 0.44836 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0817 | 8.3653 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 68.4919 | 0.036684 | 12.939 | 16.5661 | 1.1096 | 0.0041453 | 6.7229 | 1.1137 | 49 | 8.9562 | 151811.634 | 12291.9616 | 8.0969
6 | Hangar | 1960-1979 | ecm_cold_deck_reset_control | 6423 | 6276.5798 | 0 | 428.5627 | 2.1675 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0817 | 8.5686 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 12.7239 | -1.8858 | 2.0463 | 16.5661 | 0.20613 | -0.2131 | -0.042082 | -0.0069713 | 5 | 100 | 151811.634 | 636.906 | 0.41954
6 | Hangar | 1960-1979 | economizers_enabled | 6423 | 6276.5798 | 0 | 436.3623 | 0.35823 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0817 | 8.5867 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 4.9242 | -0.094653 | 0.91188 | 16.5661 | 0.079773 | -0.010696 | 0.41698 | 0.069077 | 25 | 6.1927 | 151811.634 | 799.0902 | 0.52637
6 | Hangar | 1960-1979 | elec_reduce | 6423 | 6276.5798 | 0 | 389.4464 | 0.27626 | 0 | 5.8427 | 40.042 | 6.3658 | 0 | 9.2416 | 6.6801 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 51.8401 | 19.8949 | 13.5444 | 16.5661 | 0.83981 | 2.2481 | 18.6401 | 3.0879 | 63 | 11.3651 | 151811.634 | 26587.9164 | 17.5138
6 | Hangar | 1960-1979 | envelope_ecm_roof | 6423 | 6276.5798 | 0 | 396.7166 | 0.31702 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 9.3983 | 7.8829 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 44.5699 | 1.3338 | 8.6671 | 16.5661 | 0.72203 | 0.15071 | 5.2683 | 0.87275 | 46 | 215.5433 | 151811.634 | 9138.3845 | 6.0196
6 | Hangar | 1960-1979 | envelope_ecm_wall | 6423 | 6276.5798 | 0 | 426.1198 | 0.3605 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 9.6746 | 8.1814 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 15.1667 | 0.71556 | 2.9988 | 16.5661 | 0.2457 | 0.080858 | 1.9713 | 0.32656 | 38 | 427.0711 | 151811.634 | 3337.3821 | 2.1984
6 | Hangar | 1960-1979 | envelope_ecm_windows | 6423 | 6276.5798 | 0 | 431.4014 | 0.36004 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 9.8802 | 8.3743 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 9.8852 | 0.31747 | 1.9264 | 16.5661 | 0.16014 | 0.035875 | 1.1832 | 0.19601 | 35 | 148.961 | 151811.634 | 2045.6457 | 1.3475
6 | Hangar | 1960-1979 | exhaust_fans_occ_control | 6423 | 6276.5798 | 0 | 436.3528 | 0.37091 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 9.2158 | 8.5913 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 4.9337 | 0.75406 | 1.0739 | 16.5661 | 0.079927 | 0.085208 | 0.99683 | 0.16514 | 33 | 3.4499 | 151811.634 | 1539.1702 | 1.0139
6 | Hangar | 1960-1979 | fans_to_variable | 6423 | 6276.5798 | 0 | 436.4918 | 0.3682 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 9.9911 | 8.5931 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 4.7947 | -0.02038 | 0.90145 | 16.5661 | 0.077674 | -0.0023029 | 0.45497 | 0.075371 | 26 | 4.5224 | 151811.634 | 840.523 | 0.55366
6 | Hangar | 1960-1979 | hrv_enabled | 6423 | 6276.5798 | 0 | 383.8958 | 0.53078 | 0 | 5.8431 | 57.2028 | 6.3658 | 0 | 10.0817 | 8.3675 | 1.4284 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 57.3903 | -1.4764 | 10.5572 | 16.5661 | 0.92972 | -0.16683 | 4.6051 | 0.76289 | 44 | 37.0642 | 151811.634 | 8988.3802 | 5.9207
6 | Hangar | 1960-1979 | infil_reduce | 6423 | 6276.5798 | 0 | 264.4637 | 0.37544 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 6.9736 | 5.2856 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 176.8229 | 6.2974 | 34.5751 | 16.5661 | 2.8645 | 0.71161 | 21.5871 | 3.5761 | 64 | 4.0906 | 151811.634 | 37130.0208 | 24.458
6 | Hangar | 1960-1979 | infil_reduce_plus_setback | 6423 | 6276.5798 | 0 | 226.1871 | 0.2355 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 5.9695 | 4.1507 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 215.0995 | 8.5763 | 42.2325 | 16.5661 | 3.4846 | 0.96912 | 26.8847 | 4.4537 | 66 | 4.567 | 151811.634 | 45964.2039 | 30.2771
6 | Hangar | 1960-1979 | lights_reduce_70p | 6423 | 6276.5798 | 0 | 452.8768 | 0.23007 | 0 | 5.8427 | 40.042 | 6.3658 | 0 | 10.1021 | 8.7421 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | -11.5903 | 17.0186 | 1.0249 | 16.5661 | -0.18776 | 1.9231 | 10.4753 | 1.7353 | 56 | 11.647 | 151811.634 | 12731.5045 | 8.3864
6 | Hangar | 1960-1979 | load_reduce | 6423 | 6276.5798 | 0 | 185.2696 | 0.2355 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 5.9695 | 0.28849 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 256.0169 | 12.4385 | 50.6874 | 16.5661 | 4.1475 | 1.4056 | 33.5205 | 5.553 | 69 | 3.689 | 151811.634 | 56648.5515 | 37.315
6 | Hangar | 1960-1979 | occupancy_setback | 6423 | 6276.5798 | 0 | 382.8959 | 0.2047 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 8.5179 | 6.9418 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 58.3907 | 3.2676 | 11.6418 | 16.5661 | 0.94593 | 0.36924 | 7.9389 | 1.3152 | 52 | 4.3431 | 151811.634 | 13294.7272 | 8.7574
6 | Hangar | 1960-1979 | payback_less_than_20 | 6423 | 6276.5798 | 0 | 156.4448 | 1.7264 | 0 | 5.8427 | 40.042 | 6.3658 | 0 | 5.128 | 0.10869 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 284.8418 | 29.1297 | 59.2813 | 16.5661 | 4.6144 | 3.2917 | 47.7246 | 7.9061 | 71 | 7.8017 | 151811.634 | 76329.5 | 50.2791
6 | Hangar | 1960-1979 | plug_loads_90_percent | 6423 | 6276.5798 | 0 | 436.5349 | 0.36095 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0871 | 8.599 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 4.7517 | -0.11503 | 0.87545 | 16.5661 | 0.076977 | -0.012999 | 0.3862 | 0.063979 | 22 | 51.6204 | 151811.634 | 750.4733 | 0.49435
6 | Hangar | 1960-1979 | pumps_to_variable | 6423 | 6276.5798 | 0 | 436.3546 | 0.37001 | 0 | 5.859 | 57.2028 | 6.3658 | 0 | 10.0817 | 8.575 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 4.9156 | -0.094653 | 0.91025 | 16.5661 | 0.079633 | -0.010696 | 0.41614 | 0.068937 | 24 | 7.7357 | 151811.634 | 797.5499 | 0.52535
6 | Hangar | 1960-1979 | pump_fan_eff_ | 6423 | 6276.5798 | 0 | 436.3546 | 0.37001 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0817 | 6.7195 | 0 | 0 | 441.2865 | 0.28668 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 10.0441 | 8.6012 | 0 | 529.6298 | 4.9319 | 1.7608 | 1.2637 | 16.5661 | 0.079897 | 0.19897 | 1.6834 | 0.27887 | 37 | 3.7156 | 151811.634 | 2414.7335 | 1.5906
7 | Hangar | 1980-2004 | air_temp_reset_enabled | 6423 | 6276.5798 | 0 | 282.8717 | 2.7291 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.1167 | 6.1257 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | -3.4311 | -3.2848 | -1.8576 | 13.2384 | -0.055583 | -0.37118 | -3.2237 | -0.42676 | 3 | 100 | 117407.8014 | -3471.927 | -2.9572
7 | Hangar | 1980-2004 | baseline | 6423 | 6276.5798 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 0 | 0 | 0 | 13.2384 | 0 | 0 | 0 | 0 | 8 | NA | 117407.8014 | 0 | 0
7 | Hangar | 1980-2004 | boiler_eff_upgrade | 6423 | 6276.5798 | 0 | 277.4996 | 0.32155 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.1167 | 5.4179 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 1.9411 | -0.16938 | 0.49004 | 13.2384 | 0.031445 | -0.01914 | 0.092953 | 0.012305 | 11 | 826.5894 | 117407.8014 | 200.0917 | 0.17042
7 | Hangar | 1980-2004 | boiler_reset | 6423 | 6276.5798 | 0 | 225.6635 | 0.32155 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.1167 | 0.29574 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 53.7771 | 4.9528 | 16.2444 | 13.2384 | 0.87119 | 0.55966 | 10.8083 | 1.4309 | 53 | 0.1011 | 117407.8014 | 13935.0172 | 11.8689
7 | Hangar | 1980-2004 | cooling_cop_3_0 | 6423 | 6276.5798 | 0 | 277.4996 | 0.27581 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.1167 | 5.4179 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 1.9411 | -0.12364 | 0.50269 | 13.2384 | 0.031445 | -0.013971 | 0.132 | 0.017474 | 14 | 143.4893 | 117407.8014 | 239.8869 | 0.20432
7 | Hangar | 1980-2004 | dcv_enabled | 6423 | 6276.5798 | 0 | 215.3789 | 0.48006 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.1167 | 5.0628 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 64.0617 | 0.027173 | 17.7267 | 13.2384 | 1.0378 | 0.0030706 | 7.8625 | 1.0409 | 47 | 9.583 | 117407.8014 | 11490.6925 | 9.787
7 | Hangar | 1980-2004 | ecm_cold_deck_reset_control | 6423 | 6276.5798 | 0 | 270.118 | 1.3849 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.1167 | 5.4713 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 9.3227 | -1.2862 | 2.2229 | 13.2384 | 0.15103 | -0.14534 | 0.042957 | 0.0056869 | 9 | 192.5165 | 117407.8014 | 549.7661 | 0.46825
7 | Hangar | 1980-2004 | economizers_enabled | 6423 | 6276.5798 | 0 | 277.5077 | 0.30615 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.1167 | 5.4156 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 1.9329 | -0.15172 | 0.49267 | 13.2384 | 0.031313 | -0.017144 | 0.10703 | 0.014169 | 13 | 30.19 | 117407.8014 | 213.999 | 0.18227
7 | Hangar | 1980-2004 | elec_reduce | 6423 | 6276.5798 | 0 | 230.5493 | 0.25452 | 0 | 5.8427 | 40.042 | 6.3658 | 0 | 6.2784 | 4.1054 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 48.8914 | 19.2092 | 18.8363 | 13.2384 | 0.79204 | 2.1706 | 22.3794 | 2.9627 | 61 | 11.8456 | 117407.8014 | 25463.5575 | 21.6881
7 | Hangar | 1980-2004 | envelope_ecm_roof | 6423 | 6276.5798 | 0 | 259.5245 | 0.29845 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 6.8028 | 5.1004 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 19.9161 | 0.48504 | 5.6429 | 13.2384 | 0.32264 | 0.05481 | 2.8512 | 0.37745 | 39 | 460.548 | 117407.8014 | 3986.9771 | 3.3958
7 | Hangar | 1980-2004 | envelope_ecm_wall | 6423 | 6276.5798 | 0 | 272.2905 | 0.31476 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 6.9138 | 5.2136 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 7.1502 | 0.24456 | 2.0454 | 13.2384 | 0.11583 | 0.027635 | 1.0837 | 0.14347 | 31 | 972.0917 | 117407.8014 | 1492.6478 | 1.2713
7 | Hangar | 1980-2004 | envelope_ecm_windows | 6423 | 6276.5798 | 0 | 274.0092 | 0.322 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 6.9677 | 5.258 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 5.4315 | 0.13904 | 1.5408 | 13.2384 | 0.08799 | 0.015711 | 0.78333 | 0.1037 | 28 | 281.5642 | 117407.8014 | 1093.1949 | 0.93111
7 | Hangar | 1980-2004 | exhaust_fans_occ_control | 6423 | 6276.5798 | 0 | 277.4978 | 0.32246 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 6.2507 | 5.4179 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 1.9429 | 0.69563 | 0.7298 | 13.2384 | 0.031475 | 0.078607 | 0.83153 | 0.11008 | 29 | 5.1753 | 117407.8014 | 952.978 | 0.81168
7 | Hangar | 1980-2004 | fans_to_variable | 6423 | 6276.5798 | 0 | 277.5847 | 0.32064 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0564 | 5.4197 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 1.8559 | -0.11005 | 0.4829 | 13.2384 | 0.030066 | -0.012436 | 0.13317 | 0.01763 | 15 | 19.3336 | 117407.8014 | 236.4667 | 0.20141
7 | Hangar | 1980-2004 | hrv_enabled | 6423 | 6276.5798 | 0 | 226.1182 | 0.56249 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.1167 | 5.1905 | 1.4284 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 53.3224 | -1.6114 | 14.3031 | 13.2384 | 0.86382 | -0.18208 | 5.1497 | 0.68174 | 41 | 41.476 | 117407.8014 | 8142.8234 | 6.9355
7 | Hangar | 1980-2004 | infil_reduce | 6423 | 6276.5798 | 0 | 221.5183 | 0.36593 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 6.1892 | 4.3944 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 57.9224 | 1.7373 | 16.5016 | 13.2384 | 0.93834 | 0.19631 | 8.5709 | 1.1347 | 50 | 11.8329 | 117407.8014 | 11879.5393 | 10.1182
7 | Hangar | 1980-2004 | infil_reduce_plus_setback | 6423 | 6276.5798 | 0 | 188.4928 | 0.22282 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 5.2621 | 3.4111 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 90.9478 | 3.7907 | 26.2042 | 13.2384 | 1.4734 | 0.42834 | 14.365 | 1.9017 | 57 | 10.0637 | 117407.8014 | 19577.536 | 16.6748
7 | Hangar | 1980-2004 | lights_reduce_70p | 6423 | 6276.5798 | 0 | 292.7782 | 0.16485 | 0 | 5.8427 | 40.042 | 6.3658 | 0 | 7.1393 | 5.5732 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | -13.3375 | 16.9701 | 1.0048 | 13.2384 | -0.21607 | 1.9176 | 12.8531 | 1.7016 | 54 | 11.8782 | 117407.8014 | 12376.5898 | 10.5415
7 | Hangar | 1980-2004 | load_reduce | 6423 | 6276.5798 | 0 | 154.0494 | 0.22282 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 5.2621 | 0.26222 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 125.3912 | 6.9396 | 36.6021 | 13.2384 | 2.0313 | 0.78417 | 21.2677 | 2.8155 | 60 | 6.8488 | 117407.8014 | 28482.4664 | 24.2594
7 | Hangar | 1980-2004 | occupancy_setback | 6423 | 6276.5798 | 0 | 240.2102 | 0.19248 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 6.1122 | 4.2974 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 39.2304 | 2.0846 | 11.4276 | 13.2384 | 0.63553 | 0.23556 | 6.5801 | 0.8711 | 45 | 6.5571 | 117407.8014 | 8835.8788 | 7.5258
7 | Hangar | 1980-2004 | payback_less_than_20 | 6423 | 6276.5798 | 0 | 125.3745 | 1.3713 | 0 | 5.8427 | 40.042 | 6.3658 | 0 | 4.4224 | 0.095106 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 154.0662 | 23.9586 | 49.2409 | 13.2384 | 2.4959 | 2.7073 | 39.3037 | 5.2032 | 68 | 11.6233 | 117407.8014 | 48421.8462 | 41.2424
7 | Hangar | 1980-2004 | plug_loads_90_percent | 6423 | 6276.5798 | 0 | 277.534 | 0.3134 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.1216 | 5.4242 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 1.9067 | -0.17255 | 0.47965 | 13.2384 | 0.030888 | -0.019498 | 0.086035 | 0.01139 | 10 | 289.9653 | 117407.8014 | 191.1726 | 0.16283
7 | Hangar | 1980-2004 | pumps_to_variable | 6423 | 6276.5798 | 0 | 277.4996 | 0.32155 | 0 | 5.859 | 57.2028 | 6.3658 | 0 | 7.1167 | 5.4016 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 1.9248 | -0.15308 | 0.49004 | 13.2384 | 0.031181 | -0.017298 | 0.10487 | 0.013884 | 12 | 38.4103 | 117407.8014 | 211.3577 | 0.18002
7 | Hangar | 1980-2004 | pump_fan_eff_ | 6423 | 6276.5798 | 0 | 277.4996 | 0.32155 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.1167 | 4.2377 | 0 | 0 | 279.4407 | 0.22916 | 0 | 5.8427 | 57.2028 | 6.3658 | 0 | 7.0682 | 5.3894 | 0 | 361.5386 | 1.9411 | 1.0108 | 0.81649 | 13.2384 | 0.031445 | 0.11423 | 1.1004 | 0.14567 | 32 | 7.1131 | 117407.8014 | 1226.8857 | 1.045
10 | Maintenance Shop-Small | 1959-pre | air_temp_reset_enabled | 927 | 923.718 | 0 | 772.7648 | 8.0184 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 28.2924 | 41.4955 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | -15.6235 | -9.0355 | -2.7629 | 27.0928 | -0.2531 | -1.021 | -4.7028 | -1.2741 | 1 | 100 | 249946.6073 | -10657.4541 | -4.2639
10 | Maintenance Shop-Small | 1959-pre | baseline | 927 | 923.718 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 0 | 0 | 0 | 27.0928 | 0 | 0 | 0 | 0 | 17 | NA | 249946.6073 | 0 | 0
10 | Maintenance Shop-Small | 1959-pre | boiler_eff_upgrade | 927 | 923.718 | 0 | 752.5452 | 1.2162 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1305 | 40.7501 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 4.5962 | -0.32593 | 0.47846 | 27.0928 | 0.074458 | -0.03683 | 0.13889 | 0.037628 | 26 | 1872.9664 | 249946.6073 | 539.1615 | 0.21571
10 | Maintenance Shop-Small | 1959-pre | boiler_reset | 927 | 923.718 | 0 | 468.0336 | 1.2162 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1305 | 40.7501 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 289.1078 | -0.32593 | 32.3565 | 27.0928 | 4.6835 | -0.03683 | 17.1511 | 4.6467 | 60 | 0.2157 | 249946.6073 | 51466.7356 | 20.5911
10 | Maintenance Shop-Small | 1959-pre | cooling_cop_3_0 | 927 | 923.718 | 0 | 752.5452 | 0.86914 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1305 | 40.7501 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 4.5962 | 0.021125 | 0.51735 | 27.0928 | 0.074458 | 0.0023871 | 0.28364 | 0.076846 | 36 | 141.0602 | 249946.6073 | 841.0982 | 0.33651
10 | Maintenance Shop-Small | 1959-pre | dcv_enabled | 927 | 923.718 | 0 | 752.5452 | 1.2162 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1305 | 40.7501 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 4.5962 | -0.32593 | 0.47846 | 27.0928 | 0.074458 | -0.03683 | 0.13889 | 0.037628 | 27 | 214.6792 | 249946.6073 | 539.1615 | 0.21571
10 | Maintenance Shop-Small | 1959-pre | ecm_cold_deck_reset_control | 927 | 923.718 | 0 | 750.2486 | 4.5208 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 28.9473 | 40.3125 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 6.8928 | -5.0096 | 0.211 | 27.0928 | 0.11166 | -0.56609 | -1.6773 | -0.45443 | 4 | 100 | 249946.6073 | -3124.5816 | -1.2501
10 | Maintenance Shop-Small | 1959-pre | economizers_enabled | 927 | 923.718 | 0 | 752.6749 | 1.1347 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1336 | 40.6626 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 4.4664 | -0.15995 | 0.48252 | 27.0928 | 0.072356 | -0.018074 | 0.20036 | 0.054282 | 31 | 27.3013 | 249946.6073 | 660.3375 | 0.26419
10 | Maintenance Shop-Small | 1959-pre | elec_reduce | 927 | 923.718 | 0 | 775.6046 | 0.70014 | 0 | 4.8406 | 38.6014 | 6.6061 | 0 | 27.4323 | 32.2247 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | -18.4633 | 24.9547 | 0.72733 | 27.0928 | -0.2991 | 2.8199 | 9.3042 | 2.5208 | 56 | 16.497 | 249946.6073 | 18405.6387 | 7.3638
10 | Maintenance Shop-Small | 1959-pre | envelope_ecm_roof | 927 | 923.718 | 0 | 703.17 | 1.0683 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.522 | 38.1337 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 53.9714 | 4.0469 | 6.5006 | 27.0928 | 0.87434 | 0.45731 | 4.9151 | 1.3316 | 46 | 85.0578 | 249946.6073 | 13181.7204 | 5.2738
10 | Maintenance Shop-Small | 1959-pre | envelope_ecm_wall | 927 | 923.718 | 0 | 656.4445 | 1.1921 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 23.9346 | 36.0362 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 100.6969 | 7.608 | 12.135 | 27.0928 | 1.6313 | 0.85971 | 9.1943 | 2.491 | 54 | 111.3799 | 249946.6073 | 24643.7173 | 9.8596
10 | Maintenance Shop-Small | 1959-pre | envelope_ecm_windows | 927 | 923.718 | 0 | 751.2746 | 1.2162 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1155 | 40.6928 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 5.8667 | -0.2535 | 0.62893 | 27.0928 | 0.095041 | -0.028646 | 0.24507 | 0.066395 | 34 | 108.6366 | 249946.6073 | 829.5971 | 0.33191
10 | Maintenance Shop-Small | 1959-pre | exhaust_fans_occ_control | 927 | 923.718 | 0 | 752.5452 | 1.2162 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1305 | 40.7501 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 4.5962 | -0.32593 | 0.47846 | 27.0928 | 0.074458 | -0.03683 | 0.13889 | 0.037628 | 28 | 20.9864 | 249946.6073 | 539.1615 | 0.21571
10 | Maintenance Shop-Small | 1959-pre | fans_to_variable | 927 | 923.718 | 0 | 752.6719 | 1.2102 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.037 | 40.7562 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 4.4694 | -0.23238 | 0.47474 | 27.0928 | 0.072405 | -0.026258 | 0.17033 | 0.046147 | 30 | 61.4372 | 249946.6073 | 597.8648 | 0.2392
10 | Maintenance Shop-Small | 1959-pre | hrv_enabled | 927 | 923.718 | 0 | 739.1066 | 1.3188 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.0853 | 40.6656 | 2.4022 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 18.0347 | -2.701 | 1.7181 | 27.0928 | 0.29216 | -0.30521 | -0.048163 | -0.013049 | 16 | 100 | 249946.6073 | 878.3597 | 0.35142
10 | Maintenance Shop-Small | 1959-pre | infil_reduce | 927 | 923.718 | 0 | 417.5689 | 1.5451 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 16.1697 | 23.6298 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 339.5724 | 27.4263 | 41.1202 | 27.0928 | 5.5011 | 3.0992 | 31.7437 | 8.6002 | 64 | 5.7365 | 249946.6073 | 84644.3369 | 33.865
10 | Maintenance Shop-Small | 1959-pre | infil_reduce_plus_setback | 927 | 923.718 | 0 | 364.8108 | 1.5119 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 16.9453 | 23.7204 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 392.3306 | 26.5934 | 46.9382 | 27.0928 | 6.3558 | 3.0051 | 34.5509 | 9.3608 | 65 | 5.7646 | 249946.6073 | 93363.4057 | 37.3533
10 | Maintenance Shop-Small | 1959-pre | lights_reduce_70p | 927 | 923.718 | 0 | 775.3903 | 0.72127 | 0 | 4.8406 | 38.6014 | 6.6061 | 0 | 27.4263 | 41.1938 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | -18.249 | 15.9705 | -0.25529 | 27.0928 | -0.29563 | 1.8047 | 5.5699 | 1.509 | 48 | 16.7742 | 249946.6073 | 10627.7705 | 4.252
10 | Maintenance Shop-Small | 1959-pre | load_reduce | 927 | 923.718 | 0 | 225.1775 | 1.5119 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 16.9453 | 23.7204 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 531.9639 | 26.5934 | 62.5834 | 27.0928 | 8.6178 | 3.0051 | 42.9002 | 11.6229 | 67 | 4.7289 | 249946.6073 | 118357.7619 | 47.3532
10 | Maintenance Shop-Small | 1959-pre | occupancy_setback | 927 | 923.718 | 0 | 663.1321 | 1.1166 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 29.1797 | 41.7249 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 94.0093 | -3.2502 | 10.1691 | 27.0928 | 1.523 | -0.36728 | 4.2656 | 1.1557 | 44 | 4.0029 | 249946.6073 | 13999.9613 | 5.6012
10 | Maintenance Shop-Small | 1959-pre | payback_less_than_20 | 927 | 923.718 | 0 | 251.9338 | 5.3627 | 0 | 4.8406 | 38.6014 | 6.6061 | 0 | 18.922 | 18.4482 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 505.2075 | 42.579 | 61.3765 | 27.0928 | 8.1844 | 4.8114 | 47.9677 | 12.9958 | 69 | 8.2215 | 249946.6073 | 127475.8458 | 51.0012
10 | Maintenance Shop-Small | 1959-pre | plug_loads_90_percent | 927 | 923.718 | 0 | 752.7172 | 1.183 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1336 | 40.7622 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 4.4242 | -0.30782 | 0.46122 | 27.0928 | 0.071672 | -0.034784 | 0.13615 | 0.036888 | 25 | 72.5137 | 249946.6073 | 524.1235 | 0.20969
10 | Maintenance Shop-Small | 1959-pre | pump_fan_eff_ | 927 | 923.718 | 0 | 752.5452 | 1.2162 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1305 | 31.8716 | 0 | 0 | 757.1414 | 0.8782 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1487 | 40.7441 | 0 | 892.5013 | 4.5962 | 8.5526 | 1.4733 | 27.0928 | 0.074458 | 0.96644 | 3.842 | 1.0409 | 42 | 4.5439 | 249946.6073 | 8263.4899 | 3.3061
11 | Maintenance Shop-Small | 1960-1979 | air_temp_reset_enabled | 927 | 923.718 | 0 | 713.147 | 7.3123 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 26.2252 | 38.861 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | -9.0626 | -8.4108 | -2.0935 | 25.6928 | -0.14681 | -0.95042 | -4.2706 | -1.0972 | 2 | 100 | 236287.9356 | -8939.5807 | -3.7833
11 | Maintenance Shop-Small | 1960-1979 | baseline | 927 | 923.718 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 0 | 0 | 0 | 25.6928 | 0 | 0 | 0 | 0 | 18 | NA | 236287.9356 | 0 | 0
11 | Maintenance Shop-Small | 1960-1979 | boiler_eff_upgrade | 927 | 923.718 | 0 | 697.6413 | 1.2222 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2534 | 38.1216 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 6.4431 | -0.60961 | 0.69891 | 25.6928 | 0.10438 | -0.068886 | 0.13814 | 0.035493 | 22 | 1985.6533 | 236287.9356 | 622.9614 | 0.26365
11 | Maintenance Shop-Small | 1960-1979 | boiler_reset | 927 | 923.718 | 0 | 433.4368 | 1.2222 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2534 | 38.1216 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 270.6475 | -0.60961 | 32.353 | 25.6928 | 4.3845 | -0.068886 | 16.797 | 4.3156 | 58 | 0.23225 | 236287.9356 | 47915.5526 | 20.2785
11 | Maintenance Shop-Small | 1960-1979 | cooling_cop_3_0 | 927 | 923.718 | 0 | 697.6413 | 0.87216 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2534 | 38.1216 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 6.4431 | -0.25954 | 0.74085 | 25.6928 | 0.10438 | -0.029328 | 0.29211 | 0.075051 | 35 | 144.4329 | 236287.9356 | 927.5236 | 0.39254
11 | Maintenance Shop-Small | 1960-1979 | dcv_enabled | 927 | 923.718 | 0 | 697.6413 | 1.2222 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2534 | 38.1216 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 6.4431 | -0.60961 | 0.69891 | 25.6928 | 0.10438 | -0.068886 | 0.13814 | 0.035493 | 23 | 227.5953 | 236287.9356 | 622.9614 | 0.26365
11 | Maintenance Shop-Small | 1960-1979 | ecm_cold_deck_reset_control | 927 | 923.718 | 0 | 694.7351 | 4.3638 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 26.9253 | 37.6206 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 9.3493 | -4.9221 | 0.53042 | 25.6928 | 0.15146 | -0.5562 | -1.5753 | -0.40474 | 5 | 100 | 236287.9356 | -2608.721 | -1.104
11 | Maintenance Shop-Small | 1960-1979 | economizers_enabled | 927 | 923.718 | 0 | 697.8193 | 1.1377 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2565 | 37.9979 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 6.2651 | -0.40439 | 0.70216 | 25.6928 | 0.10149 | -0.045696 | 0.21717 | 0.055798 | 32 | 26.5597 | 236287.9356 | 769.6262 | 0.32572
11 | Maintenance Shop-Small | 1960-1979 | elec_reduce | 927 | 923.718 | 0 | 720.3537 | 0.68807 | 0 | 4.8406 | 38.6014 | 6.6061 | 0 | 25.5462 | 30.1846 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | -16.2693 | 24.1097 | 0.93935 | 25.6928 | -0.26356 | 2.7244 | 9.5779 | 2.4608 | 53 | 16.8989 | 236287.9356 | 18063.2114 | 7.6446
11 | Maintenance Shop-Small | 1960-1979 | envelope_ecm_roof | 927 | 923.718 | 0 | 619.518 | 0.99891 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 22.7184 | 34.0173 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 84.5664 | 6.253 | 10.881 | 25.6928 | 1.37 | 0.70659 | 8.0823 | 2.0766 | 51 | 79.8734 | 236287.9356 | 20577.5006 | 8.7087
11 | Maintenance Shop-Small | 1960-1979 | envelope_ecm_wall | 927 | 923.718 | 0 | 657.208 | 1.2554 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 23.8652 | 36.0181 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 46.8764 | 2.8489 | 5.9575 | 25.6928 | 0.7594 | 0.32192 | 4.2087 | 1.0813 | 43 | 256.582 | 236287.9356 | 10869.3802 | 4.6001
11 | Maintenance Shop-Small | 1960-1979 | envelope_ecm_windows | 927 | 923.718 | 0 | 696.3919 | 1.2222 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2383 | 38.0582 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 7.6925 | -0.53114 | 0.858 | 25.6928 | 0.12462 | -0.060019 | 0.25143 | 0.0646 | 33 | 111.6562 | 236287.9356 | 914.8667 | 0.38718
11 | Maintenance Shop-Small | 1960-1979 | exhaust_fans_occ_control | 927 | 923.718 | 0 | 697.6413 | 1.2222 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2534 | 38.1216 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 6.4431 | -0.60961 | 0.69891 | 25.6928 | 0.10438 | -0.068886 | 0.13814 | 0.035493 | 24 | 22.2491 | 236287.9356 | 622.9614 | 0.26365
11 | Maintenance Shop-Small | 1960-1979 | fans_to_variable | 927 | 923.718 | 0 | 697.762 | 1.2162 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.1659 | 38.1246 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 6.3224 | -0.51907 | 0.69529 | 25.6928 | 0.10242 | -0.058655 | 0.17035 | 0.043768 | 29 | 64.7762 | 236287.9356 | 680.1196 | 0.28784
11 | Maintenance Shop-Small | 1960-1979 | hrv_enabled | 927 | 923.718 | 0 | 684.1545 | 1.3339 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0582 | 2.4022 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 19.9299 | -3.0179 | 2.0262 | 25.6928 | 0.32286 | -0.34102 | -0.070654 | -0.018153 | 15 | 100 | 236287.9356 | 941.9218 | 0.39863
11 | Maintenance Shop-Small | 1960-1979 | infil_reduce | 927 | 923.718 | 0 | 396.0516 | 1.5029 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 15.4303 | 22.646 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 308.0328 | 24.4084 | 39.8295 | 25.6928 | 4.9901 | 2.7582 | 30.1575 | 7.7483 | 62 | 6.3673 | 236287.9356 | 76373.2058 | 32.3221
11 | Maintenance Shop-Small | 1960-1979 | infil_reduce_plus_setback | 927 | 923.718 | 0 | 341.3409 | 1.4757 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 16.1395 | 22.4951 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 362.7435 | 23.8773 | 46.3207 | 25.6928 | 5.8764 | 2.6981 | 33.3735 | 8.5746 | 63 | 6.2932 | 236287.9356 | 85704.3354 | 36.2711
11 | Maintenance Shop-Small | 1960-1979 | lights_reduce_70p | 927 | 923.718 | 0 | 720.079 | 0.7092 | 0 | 4.8406 | 38.6014 | 6.6061 | 0 | 25.5401 | 38.5924 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | -15.9946 | 15.6868 | -0.03688 | 25.6928 | -0.25911 | 1.7726 | 5.8908 | 1.5135 | 49 | 16.7248 | 236287.9356 | 10784.4969 | 4.5641
11 | Maintenance Shop-Small | 1960-1979 | load_reduce | 927 | 923.718 | 0 | 210.2813 | 1.4757 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 16.1395 | 22.4951 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 493.8031 | 23.8773 | 62.0228 | 25.6928 | 7.9996 | 2.6981 | 41.6372 | 10.6977 | 66 | 5.1379 | 236287.9356 | 109163.9931 | 46.1996
11 | Maintenance Shop-Small | 1960-1979 | occupancy_setback | 927 | 923.718 | 0 | 609.3659 | 1.1257 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 27.1185 | 38.8549 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 94.7185 | -3.1114 | 10.9754 | 25.6928 | 1.5344 | -0.35159 | 4.6038 | 1.1829 | 45 | 3.9109 | 236287.9356 | 14247.6822 | 6.0298
11 | Maintenance Shop-Small | 1960-1979 | payback_less_than_20 | 927 | 923.718 | 0 | 235.4593 | 5.0881 | 0 | 4.8406 | 38.6014 | 6.6061 | 0 | 18.074 | 17.573 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 468.6251 | 39.7935 | 60.9132 | 25.6928 | 7.5917 | 4.4967 | 47.0498 | 12.0884 | 68 | 8.8387 | 236287.9356 | 118504.2125 | 50.1525
11 | Maintenance Shop-Small | 1960-1979 | plug_loads_90_percent | 927 | 923.718 | 0 | 697.8616 | 1.189 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2565 | 38.1367 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 6.2228 | -0.59452 | 0.67432 | 25.6928 | 0.10081 | -0.067181 | 0.13089 | 0.033629 | 21 | 79.5403 | 236287.9356 | 596.6547 | 0.25251
11 | Maintenance Shop-Small | 1960-1979 | pump_fan_eff_ | 927 | 923.718 | 0 | 697.6413 | 1.2222 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2534 | 29.8134 | 0 | 0 | 704.0844 | 0.72429 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 25.2112 | 38.0522 | 0 | 834.6611 | 6.4431 | 7.6986 | 1.6943 | 25.6928 | 0.10438 | 0.86994 | 3.7922 | 0.97432 | 41 | 4.8544 | 236287.9356 | 7851.0634 | 3.3227
12 | Maintenance Shop-Small | 1980-2004 | air_temp_reset_enabled | 927 | 923.718 | 0 | 379.6978 | 3.7572 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.9384 | 21.623 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | -4.7139 | -3.881 | -1.798 | 17.2482 | -0.076365 | -0.43855 | -2.9853 | -0.51491 | 3 | 100 | 153410.4339 | -4220.227 | -2.7509
12 | Maintenance Shop-Small | 1980-2004 | baseline | 927 | 923.718 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 0 | 0 | 0 | 17.2482 | 0 | 0 | 0 | 0 | 19 | NA | 153410.4339 | 0 | 0
12 | Maintenance Shop-Small | 1980-2004 | boiler_eff_upgrade | 927 | 923.718 | 0 | 372.458 | 1.0744 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.6909 | 21.4358 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 2.5259 | -0.76352 | 0.3687 | 17.2482 | 0.04092 | -0.086278 | -0.26297 | -0.045357 | 8 | 100 | 153410.4339 | -212.1162 | -0.13827
12 | Maintenance Shop-Small | 1980-2004 | boiler_reset | 927 | 923.718 | 0 | 230.7997 | 1.0744 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.6909 | 21.4358 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 144.1842 | -0.76352 | 30.0037 | 17.2482 | 2.3358 | -0.086278 | 13.042 | 2.2495 | 52 | 0.44556 | 153410.4339 | 25144.712 | 16.3905
12 | Maintenance Shop-Small | 1980-2004 | cooling_cop_3_0 | 927 | 923.718 | 0 | 372.458 | 0.92045 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.6909 | 21.4358 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 2.5259 | -0.60961 | 0.4009 | 17.2482 | 0.04092 | -0.068886 | -0.16213 | -0.027965 | 13 | 100 | 153410.4339 | -78.2138 | -0.050983
12 | Maintenance Shop-Small | 1980-2004 | dcv_enabled | 927 | 923.718 | 0 | 372.458 | 1.0744 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.6909 | 21.4358 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 2.5259 | -0.76352 | 0.3687 | 17.2482 | 0.04092 | -0.086278 | -0.26297 | -0.045357 | 9 | 100 | 153410.4339 | -212.1162 | -0.13827
12 | Maintenance Shop-Small | 1980-2004 | ecm_cold_deck_reset_control | 927 | 923.718 | 0 | 371.7337 | 2.7674 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 15.3337 | 20.9862 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 3.2502 | -2.6497 | 0.12564 | 17.2482 | 0.052654 | -0.29941 | -1.4306 | -0.24676 | 6 | 100 | 153410.4339 | -1723.4293 | -1.1234
12 | Maintenance Shop-Small | 1980-2004 | economizers_enabled | 927 | 923.718 | 0 | 372.8503 | 0.93252 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.694 | 21.1069 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 2.1336 | -0.29575 | 0.38448 | 17.2482 | 0.034565 | -0.03342 | 0.0066382 | 0.001145 | 20 | 1294.3284 | 153410.4339 | 124.6164 | 0.081231
12 | Maintenance Shop-Small | 1980-2004 | elec_reduce | 927 | 923.718 | 0 | 393.8667 | 0.46475 | 0 | 4.8406 | 38.6014 | 6.6061 | 0 | 15.0138 | 17.2863 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | -18.8827 | 20.2136 | 0.27842 | 17.2482 | -0.3059 | 2.2841 | 11.4693 | 1.9782 | 50 | 21.0213 | 153410.4339 | 14205.8335 | 9.26
12 | Maintenance Shop-Small | 1980-2004 | envelope_ecm_roof | 927 | 923.718 | 0 | 354.6225 | 1.0291 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.0994 | 20.4913 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 20.3615 | 0.81784 | 4.4307 | 17.2482 | 0.32986 | 0.092416 | 2.4482 | 0.42227 | 38 | 340.6289 | 153410.4339 | 4356.2268 | 2.8396
12 | Maintenance Shop-Small | 1980-2004 | envelope_ecm_wall | 927 | 923.718 | 0 | 361.1471 | 1.0985 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.2986 | 20.8081 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 13.8369 | 0.23238 | 2.9433 | 17.2482 | 0.22416 | 0.026258 | 1.4518 | 0.25042 | 37 | 1107.9444 | 153410.4339 | 2678.9677 | 1.7463
12 | Maintenance Shop-Small | 1980-2004 | envelope_ecm_windows | 927 | 923.718 | 0 | 371.4863 | 1.0804 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.6789 | 21.3876 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 3.4977 | -0.7092 | 0.58336 | 17.2482 | 0.056663 | -0.080139 | -0.13611 | -0.023477 | 14 | 100 | 153410.4339 | 9.0868 | 0.0059232
12 | Maintenance Shop-Small | 1980-2004 | exhaust_fans_occ_control | 927 | 923.718 | 0 | 372.458 | 1.0744 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.6909 | 21.4358 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 2.5259 | -0.76352 | 0.3687 | 17.2482 | 0.04092 | -0.086278 | -0.26297 | -0.045357 | 10 | 100 | 153410.4339 | -212.1162 | -0.13827
12 | Maintenance Shop-Small | 1980-2004 | fans_to_variable | 927 | 923.718 | 0 | 372.5214 | 1.0713 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.6426 | 21.4389 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 2.4626 | -0.71523 | 0.36554 | 17.2482 | 0.039894 | -0.080821 | -0.23729 | -0.040928 | 12 | 100 | 153410.4339 | -181.4517 | -0.11828
12 | Maintenance Shop-Small | 1980-2004 | hrv_enabled | 927 | 923.718 | 0 | 358.9018 | 1.2403 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.6306 | 21.3272 | 2.4022 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 16.0822 | -3.1627 | 2.7028 | 17.2482 | 0.26053 | -0.35739 | -0.56154 | -0.096856 | 7 | 100 | 153410.4339 | 127.1454 | 0.082879
12 | Maintenance Shop-Small | 1980-2004 | infil_reduce | 927 | 923.718 | 0 | 272.7359 | 1.2977 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 11.3954 | 16.218 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 102.248 | 7.5265 | 22.9649 | 17.2482 | 1.6564 | 0.8505 | 14.5344 | 2.5069 | 55 | 18.0479 | 153410.4339 | 24850.4889 | 16.1987
12 | Maintenance Shop-Small | 1980-2004 | infil_reduce_plus_setback | 927 | 923.718 | 0 | 234.5479 | 1.2011 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 11.5946 | 15.8347 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 140.436 | 7.8072 | 31.0125 | 17.2482 | 2.2751 | 0.88221 | 18.305 | 3.1573 | 57 | 15.7955 | 153410.4339 | 31930.3115 | 20.8137
12 | Maintenance Shop-Small | 1980-2004 | lights_reduce_70p | 927 | 923.718 | 0 | 393.8003 | 0.48588 | 0 | 4.8406 | 38.6014 | 6.6061 | 0 | 15.0108 | 22.0907 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | -18.8163 | 15.3911 | -0.71657 | 17.2482 | -0.30482 | 1.7392 | 8.316 | 1.4344 | 47 | 17.6474 | 153410.4339 | 10022.1105 | 6.5329
12 | Maintenance Shop-Small | 1980-2004 | load_reduce | 927 | 923.718 | 0 | 145.3793 | 1.2011 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 11.5946 | 15.8347 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 229.6047 | 7.8072 | 49.6667 | 17.2482 | 3.7196 | 0.88221 | 26.68 | 4.6018 | 59 | 11.055 | 153410.4339 | 47891.5003 | 31.2179
12 | Maintenance Shop-Small | 1980-2004 | occupancy_setback | 927 | 923.718 | 0 | 322.4491 | 0.95666 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 15.201 | 21.2186 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 52.5349 | -0.93855 | 10.794 | 17.2482 | 0.85106 | -0.10606 | 4.3193 | 0.74501 | 40 | 6.2094 | 153410.4339 | 8587.2005 | 5.5975
12 | Maintenance Shop-Small | 1980-2004 | payback_less_than_20 | 927 | 923.718 | 0 | 163.07 | 2.8579 | 0 | 4.8406 | 38.6014 | 6.6061 | 0 | 13.013 | 12.3551 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 211.914 | 24.7525 | 49.5107 | 17.2482 | 3.433 | 2.797 | 36.12 | 6.23 | 61 | 16.4934 | 153410.4339 | 59467.2554 | 38.7635
12 | Maintenance Shop-Small | 1980-2004 | plug_loads_90_percent | 927 | 923.718 | 0 | 372.4972 | 1.0442 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.6909 | 21.4449 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 2.4867 | -0.74239 | 0.36491 | 17.2482 | 0.040285 | -0.08389 | -0.25281 | -0.043606 | 11 | 100 | 153410.4339 | -200.76 | -0.13086
12 | Maintenance Shop-Small | 1980-2004 | pump_fan_eff_ | 927 | 923.718 | 0 | 372.458 | 1.0744 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.6909 | 16.7642 | 0 | 0 | 374.984 | 0.56132 | 0 | 4.8406 | 55.1423 | 6.6061 | 0 | 14.5521 | 21.3242 | 0 | 478.0106 | 2.5259 | 3.9081 | 1.346 | 17.2482 | 0.04092 | 0.44162 | 2.7976 | 0.48254 | 39 | 9.8018 | 153410.4339 | 3852.2143 | 2.5111
8 | Maintenance Shop | 1959-pre | air_temp_reset_enabled | 1927 | 2388.545 | 0 | 555.6701 | 0.74871 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 34.0796 | 29.0019 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 2.3662 | -3.2594 | -0.13673 | 19.8025 | 0.038333 | -0.36832 | -1.6664 | -0.32998 | 1 | 100 | 182748.5368 | -2412.1538 | -1.3199
8 | Maintenance Shop | 1959-pre | baseline | 1927 | 2388.545 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 0 | 0 | 0 | 19.8025 | 0 | 0 | 0 | 0 | 13 | NA | 182748.5368 | 0 | 0
8 | Maintenance Shop | 1959-pre | boiler_eff_upgrade | 1927 | 2388.545 | 0 | 556.598 | 0.42502 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.4563 | 29.0019 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 1.4383 | -0.31337 | 0.1722 | 19.8025 | 0.023301 | -0.035411 | -0.061155 | -0.01211 | 11 | 100 | 182748.5368 | -15.1741 | -0.0083033
8 | Maintenance Shop | 1959-pre | boiler_reset | 1927 | 2388.545 | 0 | 351.0087 | 0.42502 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.4563 | 29.0019 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 207.0277 | -0.31337 | 31.6426 | 19.8025 | 3.3538 | -0.035411 | 16.7577 | 3.3184 | 40 | 0.1453 | 182748.5368 | 36785.3252 | 20.1289
8 | Maintenance Shop | 1959-pre | cooling_cop_3_0 | 1927 | 2388.545 | 0 | 556.598 | 0.30305 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.4563 | 29.0019 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 1.4383 | -0.1914 | 0.19087 | 19.8025 | 0.023301 | -0.021628 | 0.0084459 | 0.0016725 | 15 | 1532.7168 | 182748.5368 | 90.9405 | 0.049763
8 | Maintenance Shop | 1959-pre | dcv_enabled | 1927 | 2388.545 | 0 | 427.2583 | 0.46255 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 31.2658 | 29.0009 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 130.7781 | -0.15856 | 19.9945 | 19.8025 | 2.1186 | -0.017918 | 10.6082 | 2.1007 | 37 | 2.261 | 182748.5368 | 23271.3289 | 12.7341
8 | Maintenance Shop | 1959-pre | ecm_cold_deck_reset_control | 1927 | 2388.545 | 0 | 556.9874 | 0.65114 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.4375 | 29.0019 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 1.0489 | -0.52072 | 0.080858 | 19.8025 | 0.016993 | -0.058842 | -0.21133 | -0.041849 | 7 | 100 | 182748.5368 | -265.266 | -0.14515
8 | Maintenance Shop | 1959-pre | economizers_enabled | 1927 | 2388.545 | 0 | 556.6947 | 0.32088 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.4582 | 29.0019 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 1.3417 | -0.2111 | 0.17306 | 19.8025 | 0.021735 | -0.023855 | -0.010703 | -0.0021195 | 12 | 100 | 182748.5368 | 56.5007 | 0.030917
8 | Maintenance Shop | 1959-pre | elec_reduce | 1927 | 2388.545 | 0 | 437.8575 | 0.39312 | 2.1701 | 0 | 19.8981 | 4.0748 | 0 | 30.0067 | 22.6106 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 120.1788 | 16.088 | 20.8589 | 19.8025 | 1.9469 | 1.8179 | 19.012 | 3.7648 | 41 | 8.7864 | 182748.5368 | 35508.5305 | 19.4303
8 | Maintenance Shop | 1959-pre | envelope_ecm_roof | 1927 | 2388.545 | 0 | 526.3136 | 0.42127 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 29.5723 | 27.2061 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 31.7227 | 3.3701 | 5.3718 | 19.8025 | 0.51391 | 0.38083 | 4.5183 | 0.89474 | 31 | 149.6233 | 182748.5368 | 8610.4002 | 4.7116
8 | Maintenance Shop | 1959-pre | envelope_ecm_wall | 1927 | 2388.545 | 0 | 494.3507 | 0.42877 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 27.8966 | 25.4375 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 63.6857 | 6.8069 | 10.7906 | 19.8025 | 1.0317 | 0.76918 | 9.0943 | 1.8009 | 34 | 144.3229 | 182748.5368 | 17321.7491 | 9.4785
8 | Maintenance Shop | 1959-pre | envelope_ecm_windows | 1927 | 2388.545 | 0 | 552.5974 | 0.45035 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3869 | 28.8827 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 5.439 | -0.15012 | 0.80959 | 19.8025 | 0.088111 | -0.016963 | 0.35929 | 0.071148 | 18 | 530.2837 | 182748.5368 | 842.9715 | 0.46127
8 | Maintenance Shop | 1959-pre | exhaust_fans_occ_control | 1927 | 2388.545 | 0 | 555.9432 | 0.42502 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 30.5912 | 29.0019 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 2.0932 | 0.55168 | 0.40486 | 19.8025 | 0.03391 | 0.06234 | 0.48605 | 0.09625 | 20 | 11.8353 | 182748.5368 | 854.6488 | 0.46766
8 | Maintenance Shop | 1959-pre | fans_to_variable | 1927 | 2388.545 | 0 | 557.0024 | 0.42408 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.2123 | 29.0019 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 1.0339 | -0.068491 | 0.14778 | 19.8025 | 0.01675 | -0.0077395 | 0.045501 | 0.0090103 | 16 | 67.939 | 182748.5368 | 125.4874 | 0.068667
8 | Maintenance Shop | 1959-pre | hrv_enabled | 1927 | 2388.545 | 0 | 481.1628 | 0.51509 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.2564 | 29.0019 | 8.8767 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 76.8735 | -9.0803 | 10.3774 | 19.8025 | 1.2454 | -1.0261 | 1.1073 | 0.21928 | 21 | 317.5519 | 182748.5368 | 5860.5363 | 3.2069
8 | Maintenance Shop | 1959-pre | infil_reduce | 1927 | 2388.545 | 0 | 357.5547 | 0.48413 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 20.3344 | 18.5217 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 200.4816 | 21.2304 | 33.9384 | 19.8025 | 3.2478 | 2.399 | 28.5158 | 5.6468 | 43 | 6.6042 | 182748.5368 | 54356.6877 | 29.744
8 | Maintenance Shop | 1959-pre | infil_reduce_plus_setback | 1927 | 2388.545 | 0 | 312.4434 | 0.27866 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 22.6537 | 20.6619 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 245.593 | 16.9765 | 40.1926 | 19.8025 | 3.9786 | 1.9183 | 29.7789 | 5.8969 | 44 | 6.7853 | 182748.5368 | 58730.6742 | 32.1374
8 | Maintenance Shop | 1959-pre | lights_reduce_70p | 1927 | 2388.545 | 0 | 568.1393 | 0.36497 | 2.1711 | 0 | 19.8981 | 4.0748 | 0 | 31.2386 | 28.909 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | -10.1029 | 8.5849 | -0.23238 | 19.8025 | -0.16367 | 0.97009 | 4.0723 | 0.80642 | 30 | 28.4775 | 182748.5368 | 5660.4122 | 3.0974
8 | Maintenance Shop | 1959-pre | load_reduce | 1927 | 2388.545 | 0 | 195.4958 | 0.27866 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 22.6537 | 20.6619 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 362.5405 | 16.9765 | 58.0943 | 19.8025 | 5.8732 | 1.9183 | 39.3461 | 7.7915 | 45 | 5.1973 | 182748.5368 | 79664.2824 | 43.5923
8 | Maintenance Shop | 1959-pre | occupancy_setback | 1927 | 2388.545 | 0 | 487.5109 | 0.24019 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 35.6202 | 32.4471 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 70.5254 | -7.7376 | 9.6112 | 19.8025 | 1.1425 | -0.87435 | 1.3542 | 0.26816 | 24 | 10.142 | 182748.5368 | 5892.3013 | 3.2243
8 | Maintenance Shop | 1959-pre | payback_less_than_20 | 1927 | 2388.545 | 0 | 136.2039 | 0.714 | 2.1701 | 0 | 19.8981 | 4.0748 | 0 | 20.9771 | 15.662 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 421.8324 | 31.7453 | 69.4311 | 19.8025 | 6.8337 | 3.5872 | 52.6242 | 10.4209 | 46 | 7.7482 | 182748.5368 | 103126.3849 | 56.4308
8 | Maintenance Shop | 1959-pre | plug_loads_90_percent | 1927 | 2388.545 | 0 | 556.993 | 0.41845 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.4272 | 29.0047 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 1.0433 | -0.28053 | 0.11676 | 19.8025 | 0.016902 | -0.0317 | -0.07473 | -0.014798 | 10 | 100 | 182748.5368 | -57.3094 | -0.03136
8 | Maintenance Shop | 1959-pre | pump_fan_eff_ | 1927 | 2388.545 | 0 | 556.598 | 0.42502 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.4563 | 22.6828 | 0 | 0 | 558.0364 | 0.38186 | 2.1711 | 0 | 28.4258 | 4.0748 | 0 | 31.3953 | 28.7926 | 0 | 653.2778 | 1.4383 | 6.0057 | 1.1395 | 19.8025 | 0.023301 | 0.67864 | 3.5447 | 0.70194 | 28 | 3.7797 | 182748.5368 | 5482.3807 | 3
9 | Maintenance Shop | 1980-2004 | air_temp_reset_enabled | 1927 | 2388.545 | 0 | 333.5696 | 0.6305 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 18.6052 | 16.3084 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | -9.3167 | -1.245 | -2.6859 | 13.0465 | -0.15093 | -0.14069 | -2.2352 | -0.29162 | 2 | 100 | 118045.0277 | -2750.8744 | -2.3304
9 | Maintenance Shop | 1980-2004 | baseline | 1927 | 2388.545 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 0 | 0 | 0 | 13.0465 | 0 | 0 | 0 | 0 | 14 | NA | 118045.0277 | 0 | 0
9 | Maintenance Shop | 1980-2004 | boiler_eff_upgrade | 1927 | 2388.545 | 0 | 323.9602 | 0.39406 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 18.0798 | 16.3084 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 0.29273 | -0.48319 | -0.048436 | 13.0465 | 0.0047422 | -0.054601 | -0.38216 | -0.049858 | 5 | 100 | 118045.0277 | -367.9786 | -0.31173
9 | Maintenance Shop | 1980-2004 | boiler_reset | 1927 | 2388.545 | 0 | 206.6487 | 0.39406 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 18.0798 | 16.3084 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 117.6043 | -0.48319 | 29.7849 | 13.0465 | 1.9052 | -0.054601 | 14.1846 | 1.8506 | 35 | 0.26055 | 118045.0277 | 20630.7921 | 17.4771
9 | Maintenance Shop | 1980-2004 | cooling_cop_3_0 | 1927 | 2388.545 | 0 | 323.9602 | 0.33777 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 18.0798 | 16.3084 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 0.29273 | -0.4269 | -0.03412 | 13.0465 | 0.0047422 | -0.048239 | -0.3334 | -0.043497 | 6 | 100 | 118045.0277 | -319.0026 | -0.27024
9 | Maintenance Shop | 1980-2004 | dcv_enabled | 1927 | 2388.545 | 0 | 217.383 | 0.44379 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.7683 | 16.3075 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 106.8699 | -0.22049 | 27.1219 | 13.0465 | 1.7313 | -0.024915 | 13.0792 | 1.7064 | 33 | 2.7834 | 118045.0277 | 18937.8939 | 16.0429
9 | Maintenance Shop | 1980-2004 | ecm_cold_deck_reset_control | 1927 | 2388.545 | 0 | 324.419 | 0.57608 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 18.0845 | 16.3084 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | -0.16607 | -0.6699 | -0.21259 | 13.0465 | -0.0026903 | -0.075699 | -0.60084 | -0.078389 | 3 | 100 | 118045.0277 | -612.5404 | -0.5189
9 | Maintenance Shop | 1980-2004 | economizers_enabled | 1927 | 2388.545 | 0 | 324.1741 | 0.28053 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 18.0836 | 16.3084 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 0.078812 | -0.37342 | -0.074921 | 13.0465 | 0.0012768 | -0.042196 | -0.31364 | -0.04092 | 8 | 100 | 118045.0277 | -310.7667 | -0.26326
9 | Maintenance Shop | 1980-2004 | elec_reduce | 1927 | 2388.545 | 0 | 227.2458 | 0.36873 | 2.1701 | 0 | 19.8981 | 4.0748 | 0 | 16.4989 | 12.685 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 97.0072 | 13.2742 | 28.0455 | 13.0465 | 1.5715 | 1.5 | 23.5427 | 3.0715 | 38 | 10.7697 | 118045.0277 | 28912.8224 | 24.493
9 | Maintenance Shop | 1980-2004 | envelope_ecm_roof | 1927 | 2388.545 | 0 | 312.8806 | 0.39218 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.3677 | 15.6573 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 11.3724 | 0.88194 | 3.1164 | 13.0465 | 0.18423 | 0.09966 | 2.176 | 0.28389 | 25 | 471.564 | 118045.0277 | 2802.9456 | 2.3745
9 | Maintenance Shop | 1980-2004 | envelope_ecm_wall | 1927 | 2388.545 | 0 | 312.0211 | 0.39687 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.3283 | 15.6132 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 12.2318 | 0.96076 | 3.355 | 13.0465 | 0.19816 | 0.10857 | 2.351 | 0.30672 | 26 | 847.3823 | 118045.0277 | 3025.3491 | 2.5629
9 | Maintenance Shop | 1980-2004 | envelope_ecm_windows | 1927 | 2388.545 | 0 | 321.0873 | 0.4269 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 18.0179 | 16.2278 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 3.1656 | -0.37342 | 0.71008 | 13.0465 | 0.051283 | -0.042196 | 0.069648 | 0.0090866 | 17 | 4152.0895 | 118045.0277 | 241.7706 | 0.20481
9 | Maintenance Shop | 1980-2004 | exhaust_fans_occ_control | 1927 | 2388.545 | 0 | 323.7651 | 0.39406 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 16.9596 | 16.3084 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 0.48788 | 0.63706 | 0.28608 | 13.0465 | 0.0079037 | 0.071988 | 0.61236 | 0.079892 | 19 | 14.2587 | 118045.0277 | 641.5761 | 0.5435
9 | Maintenance Shop | 1980-2004 | fans_to_variable | 1927 | 2388.545 | 0 | 324.177 | 0.39312 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.9466 | 16.3084 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 0.075997 | -0.34902 | -0.069433 | 13.0465 | 0.0012312 | -0.03944 | -0.29286 | -0.038209 | 9 | 100 | 118045.0277 | -290.0476 | -0.24571
9 | Maintenance Shop | 1980-2004 | hrv_enabled | 1927 | 2388.545 | 0 | 245.1295 | 0.53104 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.7984 | 16.3075 | 8.8767 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 79.1234 | -9.2144 | 17.7785 | 13.0465 | 1.2818 | -1.0412 | 1.8439 | 0.24057 | 23 | 289.4526 | 118045.0277 | 6146.5411 | 5.2069
9 | Maintenance Shop | 1980-2004 | infil_reduce | 1927 | 2388.545 | 0 | 264.7546 | 0.41376 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 14.5952 | 13.1775 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 59.4983 | 6.1126 | 16.6854 | 13.0465 | 0.96387 | 0.69073 | 12.6823 | 1.6546 | 32 | 20.4442 | 118045.0277 | 15968.1757 | 13.5272
9 | Maintenance Shop | 1980-2004 | infil_reduce_plus_setback | 1927 | 2388.545 | 0 | 229.0228 | 0.243 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 16.0861 | 14.659 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 95.2302 | 3.311 | 25.0599 | 13.0465 | 1.5427 | 0.37415 | 14.6927 | 1.9169 | 36 | 19.0657 | 118045.0277 | 19926.8017 | 16.8807
9 | Maintenance Shop | 1980-2004 | lights_reduce_70p | 1927 | 2388.545 | 0 | 334.7471 | 0.3312 | 2.1701 | 0 | 19.8981 | 4.0748 | 0 | 17.9973 | 16.2174 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | -10.4942 | 8.2809 | -0.56286 | 13.0465 | -0.17001 | 0.93574 | 5.8693 | 0.76573 | 29 | 29.9907 | 118045.0277 | 5325.909 | 4.5118
9 | Maintenance Shop | 1980-2004 | load_reduce | 1927 | 2388.545 | 0 | 144.2953 | 0.243 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 16.0861 | 14.659 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 179.9577 | 3.311 | 46.6068 | 13.0465 | 2.9153 | 0.37415 | 25.2134 | 3.2895 | 39 | 11.2568 | 118045.0277 | 35093.0284 | 29.7285
9 | Maintenance Shop | 1980-2004 | occupancy_setback | 1927 | 2388.545 | 0 | 281.2826 | 0.22518 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 20.0013 | 18.1793 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 42.9703 | -4.1067 | 9.8834 | 13.0465 | 0.69612 | -0.46405 | 1.7788 | 0.23207 | 22 | 11.7193 | 118045.0277 | 4118.891 | 3.4893
9 | Maintenance Shop | 1980-2004 | payback_less_than_20 | 1927 | 2388.545 | 0 | 92.6941 | 0.59953 | 2.1701 | 0 | 19.8981 | 4.0748 | 0 | 14.4348 | 11.0872 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 231.5589 | 16.7053 | 63.1358 | 13.0465 | 3.7513 | 1.8877 | 43.222 | 5.639 | 42 | 13.7042 | 118045.0277 | 55982.6596 | 47.4248
9 | Maintenance Shop | 1980-2004 | plug_loads_90_percent | 1927 | 2388.545 | 0 | 324.1526 | 0.38843 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 18.0817 | 16.3103 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 0.10039 | -0.48132 | -0.096872 | 13.0465 | 0.0016263 | -0.054389 | -0.40442 | -0.052762 | 4 | 100 | 118045.0277 | -400.7746 | -0.33951
9 | Maintenance Shop | 1980-2004 | pump_fan_eff_ | 1927 | 2388.545 | 0 | 323.9602 | 0.39406 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 18.0798 | 12.7553 | 0 | 0 | 324.2529 | 0.35278 | 2.1701 | 0 | 28.4258 | 4.0748 | 0 | 17.8556 | 16.0908 | 0 | 393.2228 | 0.29273 | 3.0699 | 0.85515 | 13.0465 | 0.0047422 | 0.3469 | 2.6953 | 0.35164 | 27 | 7.545 | 118045.0277 | 2723.2226 | 2.3069
16 | Office-Small | 1960-1979 | air_temp_reset_enabled | 584 | 1211.4622 | 4.6037 | 53.5144 | 3.7448 | 2.8628 | 0 | 12.8782 | 3.0839 | 0 | 9.1013 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 10.9173 | -7.0144 | 4.1654 | 4.3509 | 0.17686 | -0.79263 | -14.1525 | -0.61577 | 1 | 100 | 36744.4638 | -4148.3347 | -11.2897
16 | Office-Small | 1960-1979 | baseline | 584 | 1211.4622 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 0 | 0 | 0 | 4.3509 | 0 | 0 | 0 | 0 | 41 | NA | 36744.4638 | 0 | 0
16 | Office-Small | 1960-1979 | boiler_reset | 584 | 1211.4622 | 0.65878 | 62.6035 | 1.4093 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.0836 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 1.8282 | -0.70409 | 1.1997 | 4.3509 | 0.029617 | -0.079563 | -1.1479 | -0.049946 | 22 | 100 | 36744.4638 | -285.3115 | -0.77647
16 | Office-Small | 1960-1979 | cooling_cop_3_0 | 584 | 1211.4622 | 0.65878 | 62.6035 | 1.007 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.0836 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 1.8282 | -0.30175 | 1.6291 | 4.3509 | 0.029617 | -0.034098 | -0.10299 | -0.0044812 | 37 | 100 | 36744.4638 | 64.7236 | 0.17615
16 | Office-Small | 1960-1979 | dcv_enabled | 584 | 1211.4622 | 0.65878 | 62.6035 | 1.4093 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.0836 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 1.8282 | -0.70409 | 1.1997 | 4.3509 | 0.029617 | -0.079563 | -1.1479 | -0.049946 | 23 | 100 | 36744.4638 | -285.3115 | -0.77647
16 | Office-Small | 1960-1979 | ecm_cold_deck_reset_control | 584 | 1211.4622 | 7.9993 | 35.1406 | 2.6683 | 2.875 | 0 | 12.8782 | 3.0839 | 0 | 9.1643 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 29.2912 | -9.4085 | 21.2198 | 4.3509 | 0.47452 | -1.0632 | -13.5292 | -0.58865 | 2 | 100 | 36744.4638 | -2942.3153 | -8.0075
16 | Office-Small | 1960-1979 | economizers_enabled | 584 | 1211.4622 | 0.65878 | 62.6035 | 1.4093 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.0836 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 1.8282 | -0.70409 | 1.1997 | 4.3509 | 0.029617 | -0.079563 | -1.1479 | -0.049946 | 24 | 100 | 36744.4638 | -285.3115 | -0.77647
16 | Office-Small | 1960-1979 | elec_reduce | 584 | 1211.4622 | 0.50071 | 65.7615 | 1.0047 | 2.8517 | 0 | 9.0151 | 3.0839 | 0 | 8.1054 | 0.0044213 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | -1.3297 | 4.701 | 3.598 | 4.3509 | -0.021541 | 0.53121 | 11.7139 | 0.50967 | 58 | 135.9994 | 36744.4638 | 3851.8152 | 10.4827
16 | Office-Small | 1960-1979 | envelope_ecm_roof | 584 | 1211.4622 | 0.68751 | 50.7246 | 1.2335 | 2.8352 | 0 | 12.8782 | 3.0839 | 0 | 7.8699 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 13.7072 | 0.67204 | 15.3462 | 4.3509 | 0.22206 | 0.07594 | 6.849 | 0.298 | 52 | 872.7936 | 36744.4638 | 3038.2566 | 8.2686
16 | Office-Small | 1960-1979 | envelope_ecm_wall | 584 | 1211.4622 | 0.6422 | 58.0728 | 1.4292 | 2.8307 | 0 | 12.8782 | 3.0839 | 0 | 8.5829 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 6.3589 | -0.1868 | 6.5872 | 4.3509 | 0.10301 | -0.021108 | 1.8825 | 0.081907 | 48 | 2644.3716 | 36744.4638 | 975.7355 | 2.6555
16 | Office-Small | 1960-1979 | envelope_ecm_windows | 584 | 1211.4622 | 0.65767 | 60.7753 | 1.4215 | 2.8495 | 0 | 12.8782 | 3.0839 | 0 | 8.9432 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 3.6564 | -0.57366 | 3.2901 | 4.3509 | 0.059234 | -0.064824 | -0.12848 | -0.0055901 | 36 | 100 | 36744.4638 | 155.4112 | 0.42295
16 | Office-Small | 1960-1979 | exhaust_fans_occ_control | 584 | 1211.4622 | 0.65878 | 62.6035 | 1.4181 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 8.0733 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 1.8282 | 0.29733 | 2.2685 | 4.3509 | 0.029617 | 0.033599 | 1.4529 | 0.063216 | 47 | 39.6577 | 36744.4638 | 585.9296 | 1.5946
16 | Office-Small | 1960-1979 | fans_to_variable | 584 | 1211.4622 | 0.65988 | 62.6732 | 1.4049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.0084 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 1.7586 | -0.62562 | 1.2092 | 4.3509 | 0.028489 | -0.070695 | -0.97003 | -0.042206 | 28 | 100 | 36744.4638 | -229.5002 | -0.62458
16 | Office-Small | 1960-1979 | hrv_enabled | 584 | 1211.4622 | 0.65878 | 62.6035 | 1.4093 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.0836 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 1.8282 | -0.70409 | 1.1997 | 4.3509 | 0.029617 | -0.079563 | -1.1479 | -0.049946 | 25 | 100 | 36744.4638 | -285.3115 | -0.77647
16 | Office-Small | 1960-1979 | infil_reduce | 584 | 1211.4622 | 0.61898 | 37.548 | 1.7166 | 2.7799 | 0 | 12.8782 | 3.0839 | 0 | 6.622 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 26.8838 | 1.5607 | 30.3574 | 4.3509 | 0.43552 | 0.17636 | 14.0631 | 0.61188 | 61 | 100.4083 | 36744.4638 | 6170.0239 | 16.7917
16 | Office-Small | 1960-1979 | infil_reduce_plus_setback | 584 | 1211.4622 | 0.55487 | 31.6765 | 1.3607 | 2.7876 | 0 | 12.8782 | 3.0839 | 0 | 7.4842 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 32.7553 | 1.1109 | 36.1437 | 4.3509 | 0.53064 | 0.12553 | 15.0809 | 0.65616 | 62 | 113.5258 | 36744.4638 | 6829.6369 | 18.5868
16 | Office-Small | 1960-1979 | lights_reduce_70p | 584 | 1211.4622 | 0.51287 | 65.652 | 1.028 | 2.8517 | 0 | 9.0151 | 3.0839 | 0 | 9.1046 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | -1.2203 | 3.6642 | 2.6082 | 4.3509 | -0.019769 | 0.41405 | 9.062 | 0.39428 | 55 | 85.1252 | 36744.4638 | 2969.3892 | 8.0812
16 | Office-Small | 1960-1979 | load_reduce | 584 | 1211.4622 | 0.55487 | 31.6765 | 1.3607 | 2.7876 | 0 | 12.8782 | 3.0839 | 0 | 7.4842 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 32.7553 | 1.1109 | 36.1437 | 4.3509 | 0.53064 | 0.12553 | 15.0809 | 0.65616 | 63 | 115.9504 | 36744.4638 | 6829.6369 | 18.5868
16 | Office-Small | 1960-1979 | occupancy_setback | 584 | 1211.4622 | 0.57698 | 53.8294 | 1.0998 | 2.8584 | 0 | 12.8782 | 3.0839 | 0 | 10.316 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 10.6023 | -1.553 | 9.6579 | 4.3509 | 0.17176 | -0.17549 | -0.085729 | -0.00373 | 38 | 100 | 36744.4638 | 546.7148 | 1.4879
16 | Office-Small | 1960-1979 | payback_less_than_20 | 584 | 1211.4622 | 3.9571 | 22.8924 | 2.5069 | 2.8086 | 0 | 9.0151 | 3.0839 | 0 | 6.5402 | 0.0044213 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 41.5393 | 1.3507 | 45.7744 | 4.3509 | 0.67294 | 0.15263 | 18.9744 | 0.82557 | 64 | 229.7747 | 36744.4638 | 8610.6543 | 23.4339
16 | Office-Small | 1960-1979 | plug_loads_90_percent | 584 | 1211.4622 | 0.64883 | 62.6898 | 1.3717 | 2.8495 | 0 | 12.8782 | 3.0839 | 0 | 9.0935 | 0.006632 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 1.742 | -0.66541 | 1.149 | 4.3509 | 0.02822 | -0.075191 | -1.0795 | -0.046971 | 27 | 100 | 36744.4638 | -267.0869 | -0.72688
16 | Office-Small | 1960-1979 | pump_fan_eff_ | 584 | 1211.4622 | 0.65878 | 62.6035 | 1.4093 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.0836 | 0.0044213 | 0 | 0.28849 | 64.4317 | 1.049 | 2.8506 | 0 | 12.8782 | 3.0839 | 0 | 9.1101 | 0.006632 | 0 | 93.6986 | 1.8282 | -0.70188 | 1.2021 | 4.3509 | 0.029617 | -0.079313 | -1.1422 | -0.049696 | 26 | 100 | 36744.4638 | -283.3883 | -0.77124
17 | Office-Small | 1980-2004 | air_temp_reset_enabled | 584 | 1211.4622 | 2.812 | 30.3744 | 2.4185 | 2.7887 | 0 | 12.8782 | 3.0839 | 0 | 6.2871 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 5.4802 | -4.0212 | 2.3492 | 3.5475 | 0.088779 | -0.45439 | -10.3062 | -0.36561 | 4 | 100 | 28981.7758 | -2517.4694 | -8.6864
17 | Office-Small | 1980-2004 | baseline | 584 | 1211.4622 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 0 | 0 | 0 | 3.5475 | 0 | 0 | 0 | 0 | 42 | NA | 28981.7758 | 0 | 0
17 | Office-Small | 1980-2004 | boiler_reset | 584 | 1211.4622 | 0.62672 | 34.6376 | 1.2744 | 2.7788 | 0 | 12.8782 | 3.0839 | 0 | 6.286 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 1.217 | -0.68088 | 0.86314 | 3.5475 | 0.019715 | -0.07694 | -1.6131 | -0.057225 | 14 | 100 | 28981.7758 | -374.5303 | -1.2923
17 | Office-Small | 1980-2004 | cooling_cop_3_0 | 584 | 1211.4622 | 0.62672 | 34.6376 | 1.0921 | 2.7788 | 0 | 12.8782 | 3.0839 | 0 | 6.286 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 1.217 | -0.4985 | 1.1568 | 3.5475 | 0.019715 | -0.056331 | -1.0322 | -0.036616 | 31 | 100 | 28981.7758 | -215.8605 | -0.74481
17 | Office-Small | 1980-2004 | dcv_enabled | 584 | 1211.4622 | 0.62672 | 34.6376 | 1.2744 | 2.7788 | 0 | 12.8782 | 3.0839 | 0 | 6.286 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 1.217 | -0.68088 | 0.86314 | 3.5475 | 0.019715 | -0.07694 | -1.6131 | -0.057225 | 15 | 100 | 28981.7758 | -374.5303 | -1.2923
17 | Office-Small | 1980-2004 | ecm_cold_deck_reset_control | 584 | 1211.4622 | 5.216 | 18.5098 | 2.0404 | 2.8053 | 0 | 12.8782 | 3.0839 | 0 | 6.3424 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 17.3448 | -6.1191 | 18.0744 | 3.5475 | 0.28099 | -0.69146 | -11.5707 | -0.41047 | 3 | 100 | 28981.7758 | -2218.8918 | -7.6562
17 | Office-Small | 1980-2004 | economizers_enabled | 584 | 1211.4622 | 0.62672 | 34.6376 | 1.2744 | 2.7788 | 0 | 12.8782 | 3.0839 | 0 | 6.286 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 1.217 | -0.68088 | 0.86314 | 3.5475 | 0.019715 | -0.07694 | -1.6131 | -0.057225 | 16 | 100 | 28981.7758 | -374.5303 | -1.2923
17 | Office-Small | 1980-2004 | elec_reduce | 584 | 1211.4622 | 0.50735 | 37.3369 | 0.84115 | 2.781 | 0 | 9.0151 | 3.0839 | 0 | 5.2989 | 0.0044213 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | -1.4822 | 4.722 | 5.2162 | 3.5475 | -0.024012 | 0.53358 | 14.3641 | 0.50957 | 57 | 136.0255 | 28981.7758 | 3842.7824 | 13.2593
17 | Office-Small | 1980-2004 | envelope_ecm_roof | 584 | 1211.4622 | 0.63114 | 30.6231 | 1.2534 | 2.7711 | 0 | 12.8782 | 3.0839 | 0 | 5.8593 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 5.2315 | -0.22991 | 8.053 | 3.5475 | 0.084751 | -0.02598 | 1.6567 | 0.058771 | 46 | 4425.4782 | 28981.7758 | 736.4211 | 2.541
17 | Office-Small | 1980-2004 | envelope_ecm_wall | 584 | 1211.4622 | 0.61456 | 32.9631 | 1.3032 | 2.7688 | 0 | 12.8782 | 3.0839 | 0 | 6.0926 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 2.8915 | -0.49408 | 3.8601 | 3.5475 | 0.046843 | -0.055831 | -0.25337 | -0.0089883 | 34 | 100 | 28981.7758 | 87.7343 | 0.30272
17 | Office-Small | 1980-2004 | envelope_ecm_windows | 584 | 1211.4622 | 0.62451 | 33.2947 | 1.3032 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.1799 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 2.5599 | -0.60019 | 3.1554 | 3.5475 | 0.041471 | -0.067822 | -0.7428 | -0.026351 | 33 | 100 | 28981.7758 | -63.9388 | -0.22062
17 | Office-Small | 1980-2004 | exhaust_fans_occ_control | 584 | 1211.4622 | 0.62672 | 34.6376 | 1.2811 | 2.7788 | 0 | 12.8782 | 3.0839 | 0 | 5.2768 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 1.217 | 0.32165 | 2.4773 | 3.5475 | 0.019715 | 0.036346 | 1.5803 | 0.056061 | 45 | 44.7186 | 28981.7758 | 497.6726 | 1.7172
17 | Office-Small | 1980-2004 | fans_to_variable | 584 | 1211.4622 | 0.62783 | 34.6774 | 1.2711 | 2.7788 | 0 | 12.8782 | 3.0839 | 0 | 6.2385 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 1.1772 | -0.63114 | 0.87916 | 3.5475 | 0.01907 | -0.071319 | -1.4728 | -0.052249 | 21 | 100 | 28981.7758 | -338.3794 | -1.1676
17 | Office-Small | 1980-2004 | hrv_enabled | 584 | 1211.4622 | 0.62672 | 34.6376 | 1.2744 | 2.7788 | 0 | 12.8782 | 3.0839 | 0 | 6.286 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 1.217 | -0.68088 | 0.86314 | 3.5475 | 0.019715 | -0.07694 | -1.6131 | -0.057225 | 17 | 100 | 28981.7758 | -374.5303 | -1.2923
17 | Office-Small | 1980-2004 | infil_reduce | 584 | 1211.4622 | 0.71515 | 22.3508 | 1.4977 | 2.7357 | 0 | 12.8782 | 3.0839 | 0 | 5.132 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 13.5038 | 0.20449 | 22.0715 | 3.5475 | 0.21876 | 0.023107 | 6.818 | 0.24187 | 49 | 230.6161 | 28981.7758 | 2595.08 | 8.9542
17 | Office-Small | 1980-2004 | infil_reduce_plus_setback | 584 | 1211.4622 | 0.57366 | 18.3871 | 1.2689 | 2.7434 | 0 | 12.8782 | 3.0839 | 0 | 5.6714 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 17.4675 | 0.027633 | 28.1687 | 3.5475 | 0.28297 | 0.0031225 | 8.0647 | 0.2861 | 50 | 240.5917 | 28981.7758 | 3150.7215 | 10.8714
17 | Office-Small | 1980-2004 | lights_reduce_70p | 584 | 1211.4622 | 0.51508 | 37.2993 | 0.86768 | 2.781 | 0 | 9.0151 | 3.0839 | 0 | 6.3037 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | -1.4447 | 3.6807 | 3.6003 | 3.5475 | -0.023404 | 0.41592 | 11.0646 | 0.39252 | 54 | 85.5072 | 28981.7758 | 2943.6494 | 10.1569
17 | Office-Small | 1980-2004 | load_reduce | 584 | 1211.4622 | 0.57366 | 18.3871 | 1.2689 | 2.7434 | 0 | 12.8782 | 3.0839 | 0 | 5.6714 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 17.4675 | 0.027633 | 28.1687 | 3.5475 | 0.28297 | 0.0031225 | 8.0647 | 0.2861 | 51 | 246.1526 | 28981.7758 | 3150.7215 | 10.8714
17 | Office-Small | 1980-2004 | occupancy_setback | 584 | 1211.4622 | 0.57809 | 28.9706 | 1.0755 | 2.7876 | 0 | 12.8782 | 3.0839 | 0 | 7.084 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 6.884 | -1.2402 | 9.087 | 3.5475 | 0.11152 | -0.14014 | -0.80675 | -0.02862 | 32 | 100 | 28981.7758 | 153.278 | 0.52888
17 | Office-Small | 1980-2004 | payback_less_than_20 | 584 | 1211.4622 | 2.8761 | 13.6817 | 1.8768 | 2.7633 | 0 | 9.0151 | 3.0839 | 0 | 4.7087 | 0.0044213 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 22.1729 | 1.9255 | 38.8005 | 3.5475 | 0.3592 | 0.21758 | 16.2587 | 0.57678 | 60 | 319.074 | 28981.7758 | 5644.1113 | 19.4747
17 | Office-Small | 1980-2004 | plug_loads_90_percent | 584 | 1211.4622 | 0.6223 | 34.6421 | 1.2358 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2926 | 0.006632 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 1.2125 | -0.6433 | 0.91653 | 3.5475 | 0.019643 | -0.072693 | -1.4954 | -0.05305 | 20 | 100 | 28981.7758 | -342.6261 | -1.1822
17 | Office-Small | 1980-2004 | pump_fan_eff_ | 584 | 1211.4622 | 0.62672 | 34.6376 | 1.2744 | 2.7788 | 0 | 12.8782 | 3.0839 | 0 | 6.286 | 0.0044213 | 0 | 0.31833 | 35.8546 | 0.89753 | 2.7777 | 0 | 12.8782 | 3.0839 | 0 | 6.2915 | 0.006632 | 0 | 62.1083 | 1.217 | -0.67867 | 0.8667 | 3.5475 | 0.019715 | -0.07669 | -1.6061 | -0.056975 | 19 | 100 | 28981.7758 | -372.607 | -1.2857
18 | Office-Small | 2005-2014 | air_temp_reset_enabled | 584 | 1211.4622 | 1.6304 | 16.9988 | 1.7862 | 2.7202 | 0 | 12.8782 | 3.0839 | 0 | 4.5893 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 1.5397 | -1.8614 | -0.74161 | 3.1065 | 0.024943 | -0.21033 | -5.9679 | -0.18539 | 6 | 100 | 24325.3143 | -1343.783 | -5.5242
18 | Office-Small | 2005-2014 | baseline | 584 | 1211.4622 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 0 | 0 | 0 | 3.1065 | 0 | 0 | 0 | 0 | 43 | NA | 24325.3143 | 0 | 0
18 | Office-Small | 2005-2014 | boiler_reset | 584 | 1211.4622 | 0.7892 | 18.3551 | 1.3297 | 2.7169 | 0 | 12.8782 | 3.0839 | 0 | 4.6048 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 0.18348 | -0.57588 | -0.90471 | 3.1065 | 0.0029724 | -0.065074 | -1.9991 | -0.062101 | 7 | 100 | 24325.3143 | -468.1681 | -1.9246
18 | Office-Small | 2005-2014 | cooling_cop_3_0 | 584 | 1211.4622 | 0.7892 | 18.3551 | 1.3297 | 2.7169 | 0 | 12.8782 | 3.0839 | 0 | 4.6048 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 0.18348 | -0.57588 | -0.90471 | 3.1065 | 0.0029724 | -0.065074 | -1.9991 | -0.062101 | 8 | 100 | 24325.3143 | -468.1681 | -1.9246
18 | Office-Small | 2005-2014 | dcv_enabled | 584 | 1211.4622 | 0.7892 | 18.3551 | 1.3297 | 2.7169 | 0 | 12.8782 | 3.0839 | 0 | 4.6048 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 0.18348 | -0.57588 | -0.90471 | 3.1065 | 0.0029724 | -0.065074 | -1.9991 | -0.062101 | 9 | 100 | 24325.3143 | -468.1681 | -1.9246
18 | Office-Small | 2005-2014 | ecm_cold_deck_reset_control | 584 | 1211.4622 | 3.379 | 9.3345 | 1.8536 | 2.739 | 0 | 12.8782 | 3.0839 | 0 | 4.6335 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 9.2041 | -3.7404 | 12.5972 | 3.1065 | 0.14911 | -0.42267 | -8.8061 | -0.27356 | 5 | 100 | 24325.3143 | -1606.6454 | -6.6048
18 | Office-Small | 2005-2014 | economizers_enabled | 584 | 1211.4622 | 0.7892 | 18.3551 | 1.3297 | 2.7169 | 0 | 12.8782 | 3.0839 | 0 | 4.6048 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 0.18348 | -0.57588 | -0.90471 | 3.1065 | 0.0029724 | -0.065074 | -1.9991 | -0.062101 | 10 | 100 | 24325.3143 | -468.1681 | -1.9246
18 | Office-Small | 2005-2014 | elec_reduce | 584 | 1211.4622 | 0.58361 | 20.7249 | 0.85221 | 2.7191 | 0 | 9.0151 | 3.0839 | 0 | 3.4088 | 0.0044213 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | -2.1863 | 5.1663 | 6.8707 | 3.1065 | -0.035419 | 0.58379 | 17.6525 | 0.54837 | 59 | 126.4 | 24325.3143 | 4103.3269 | 16.8685
18 | Office-Small | 2005-2014 | envelope_ecm_roof | 584 | 1211.4622 | 0.77373 | 16.1875 | 1.354 | 2.7114 | 0 | 12.8782 | 3.0839 | 0 | 4.4346 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 2.351 | -0.40897 | 4.4777 | 3.1065 | 0.038087 | -0.046214 | -0.26161 | -0.008127 | 35 | 0 | 24325.3143 | 65.0297 | 0.26733
18 | Office-Small | 2005-2014 | envelope_ecm_wall | 584 | 1211.4622 | 0.77926 | 17.4918 | 1.3507 | 2.7103 | 0 | 12.8782 | 3.0839 | 0 | 4.5407 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 1.0467 | -0.51619 | 1.2233 | 3.1065 | 0.016957 | -0.058329 | -1.3318 | -0.041372 | 29 | 0 | 24325.3143 | -261.7161 | -1.0759
18 | Office-Small | 2005-2014 | envelope_ecm_windows | 584 | 1211.4622 | 0.81794 | 17.0331 | 1.3783 | 2.7169 | 0 | 12.8782 | 3.0839 | 0 | 4.5329 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 1.5055 | -0.5814 | 2.1305 | 3.1065 | 0.024388 | -0.065698 | -1.3298 | -0.04131 | 30 | 100 | 24325.3143 | -236.3433 | -0.97159
18 | Office-Small | 2005-2014 | exhaust_fans_occ_control | 584 | 1211.4622 | 0.7892 | 18.3551 | 1.3374 | 2.7169 | 0 | 12.8782 | 3.0839 | 0 | 3.5945 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 0.18348 | 0.42666 | 1.4068 | 3.1065 | 0.0029724 | 0.048212 | 1.6477 | 0.051185 | 44 | 48.9793 | 24325.3143 | 404.0348 | 1.661
18 | Office-Small | 2005-2014 | fans_to_variable | 584 | 1211.4622 | 0.7892 | 18.3772 | 1.3275 | 2.7169 | 0 | 12.8782 | 3.0839 | 0 | 4.5738 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 0.16138 | -0.54272 | -0.87923 | 3.1065 | 0.0026143 | -0.061327 | -1.89 | -0.058713 | 13 | 100 | 24325.3143 | -443.2761 | -1.8223
18 | Office-Small | 2005-2014 | hrv_enabled | 584 | 1211.4622 | 0.7892 | 18.3551 | 1.3297 | 2.7169 | 0 | 12.8782 | 3.0839 | 0 | 4.6048 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 0.18348 | -0.57588 | -0.90471 | 3.1065 | 0.0029724 | -0.065074 | -1.9991 | -0.062101 | 11 | 100 | 24325.3143 | -468.1681 | -1.9246
18 | Office-Small | 2005-2014 | lights_reduce_70p | 584 | 1211.4622 | 0.58361 | 20.7238 | 0.87652 | 2.7202 | 0 | 9.0151 | 3.0839 | 0 | 4.4169 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | -2.1852 | 4.1306 | 4.4853 | 3.1065 | -0.035401 | 0.46676 | 13.8857 | 0.43136 | 56 | 77.8085 | 24325.3143 | 3202.4729 | 13.1652
18 | Office-Small | 2005-2014 | load_reduce | 584 | 1211.4622 | 0.68088 | 14.7473 | 1.1097 | 2.7257 | 0 | 12.8782 | 3.0839 | 0 | 4.9088 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 3.7913 | -0.5604 | 7.4492 | 3.1065 | 0.061419 | -0.063325 | -0.061377 | -0.0019067 | 39 | 100 | 24325.3143 | 191.089 | 0.78556
18 | Office-Small | 2005-2014 | occupancy_setback | 584 | 1211.4622 | 0.68088 | 14.7473 | 1.1097 | 2.7257 | 0 | 12.8782 | 3.0839 | 0 | 4.9088 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 3.7913 | -0.5604 | 7.4492 | 3.1065 | 0.061419 | -0.063325 | -0.061377 | -0.0019067 | 40 | 100 | 24325.3143 | 191.089 | 0.78556
18 | Office-Small | 2005-2014 | payback_less_than_20 | 584 | 1211.4622 | 2.5588 | 11.1848 | 1.5309 | 2.7456 | 0 | 9.0151 | 3.0839 | 0 | 3.9339 | 0.0044213 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 7.3537 | 1.9609 | 21.4761 | 3.1065 | 0.11913 | 0.22158 | 10.9676 | 0.34071 | 53 | 376.4432 | 24325.3143 | 3022.2603 | 12.4243
18 | Office-Small | 2005-2014 | plug_loads_90_percent | 584 | 1211.4622 | 0.78589 | 18.3285 | 1.2921 | 2.7169 | 0 | 12.8782 | 3.0839 | 0 | 4.6048 | 0.006632 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 0.21001 | -0.53498 | -0.74925 | 3.1065 | 0.0034022 | -0.060453 | -1.8365 | -0.05705 | 18 | 100 | 24325.3143 | -427.8391 | -1.7588
18 | Office-Small | 2005-2014 | pump_fan_eff_ | 584 | 1211.4622 | 0.7892 | 18.3551 | 1.3297 | 2.7169 | 0 | 12.8782 | 3.0839 | 0 | 4.6048 | 0.0044213 | 0 | 0.68751 | 18.5386 | 1.018 | 2.7125 | 0 | 12.8782 | 3.0839 | 0 | 4.4467 | 0.006632 | 0 | 43.3719 | 0.18348 | -0.57366 | -0.89962 | 3.1065 | 0.0029724 | -0.064824 | -1.991 | -0.061852 | 12 | 100 | 24325.3143 | -466.2448 | -1.9167
13 | Office | 1959-pre | air_temp_reset_enabled | 3418.6207 | 3418.6207 | 0 | 358.3888 | 3.5208 | 0 | 45.3879 | 37.75 | 11.426 | 0 | 30.9717 | 12.7334 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 82.4838 | 17.2877 | 16.63 | 20.7243 | 1.3362 | 1.9535 | 15.8738 | 3.2897 | 60 | 1.563 | 185950.5308 | 29804.8861 | 16.0284
13 | Office | 1959-pre | baseline | 3418.6207 | 3418.6207 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 0 | 0 | 0 | 20.7243 | 0 | 0 | 0 | 0 | 17 | NA | 185950.5308 | 0 | 0
13 | Office | 1959-pre | boiler_eff_upgrade | 3418.6207 | 3418.6207 | 0 | 433.4963 | 21.3577 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.8677 | 12.7439 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 7.3722 | -0.45584 | 1.1528 | 20.7243 | 0.11943 | -0.05151 | 0.32773 | 0.06792 | 21 | 731.8803 | 185950.5308 | 923.0476 | 0.49639
13 | Office | 1959-pre | boiler_reset | 3418.6207 | 3418.6207 | 0 | 306.0244 | 21.3577 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.8677 | 10.5996 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 134.8441 | 1.6885 | 22.7573 | 20.7243 | 2.1845 | 0.1908 | 11.4613 | 2.3753 | 56 | 0.11442 | 185950.5308 | 25606.0646 | 13.7704
13 | Office | 1959-pre | cooling_cop_3_0 | 3418.6207 | 3418.6207 | 0 | 433.4963 | 15.2555 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.8677 | 12.7439 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 7.3722 | 5.6464 | 2.1699 | 20.7243 | 0.11943 | 0.63804 | 3.655 | 0.75747 | 39 | 7.761 | 185950.5308 | 6231.9668 | 3.3514
13 | Office | 1959-pre | dcv_enabled | 3418.6207 | 3418.6207 | 0 | 372.6197 | 21.4349 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.8677 | 12.7049 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 68.2488 | -0.49403 | 11.2934 | 20.7243 | 1.1056 | -0.055825 | 5.0656 | 1.0498 | 45 | 11.8237 | 185950.5308 | 11786.7367 | 6.3386
13 | Office | 1959-pre | ecm_cold_deck_reset_control | 3418.6207 | 3418.6207 | 0 | 342.1566 | 2.4449 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.8986 | 12.6123 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 98.7119 | 18.5577 | 19.5466 | 20.7243 | 1.5991 | 2.097 | 17.8348 | 3.6962 | 62 | 1.3912 | 185950.5308 | 33814.627 | 18.1847
13 | Office | 1959-pre | economizers_enabled | 3418.6207 | 3418.6207 | 0 | 433.5183 | 21.2074 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.8677 | 12.7448 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 7.3503 | -0.30633 | 1.1741 | 20.7243 | 0.11907 | -0.034615 | 0.40754 | 0.084459 | 24 | 23.7898 | 185950.5308 | 1049.1927 | 0.56423
13 | Office | 1959-pre | elec_reduce | 3418.6207 | 3418.6207 | 0 | 387.3836 | 21.2326 | 0 | 45.392 | 26.4256 | 11.426 | 0 | 14.911 | 9.987 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 53.4849 | 29.7074 | 13.8665 | 20.7243 | 0.86646 | 3.3569 | 20.3789 | 4.2234 | 65 | 10.4164 | 185950.5308 | 35419.2561 | 19.0477
13 | Office | 1959-pre | envelope_ecm_roof | 3418.6207 | 3418.6207 | 0 | 405.7049 | 19.5921 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.2754 | 12.0281 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 35.1637 | 2.618 | 6.2975 | 20.7243 | 0.56965 | 0.29584 | 4.1762 | 0.86549 | 41 | 304.9303 | 185950.5308 | 8571.9695 | 4.6098
13 | Office | 1959-pre | envelope_ecm_wall | 3418.6207 | 3418.6207 | 0 | 413.0259 | 20.2307 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.3599 | 12.1516 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 27.8426 | 1.7713 | 4.9361 | 20.7243 | 0.45105 | 0.20016 | 3.1423 | 0.65121 | 37 | 173.1346 | 185950.5308 | 6524.9028 | 3.5089
13 | Office | 1959-pre | envelope_ecm_windows | 3418.6207 | 3418.6207 | 0 | 431.3171 | 21.3626 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.7735 | 12.644 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 9.5515 | -0.26651 | 1.5476 | 20.7243 | 0.15473 | -0.030116 | 0.60131 | 0.12462 | 28 | 7121.1538 | 185950.5308 | 1477.843 | 0.79475
13 | Office | 1959-pre | exhaust_fans_occ_control | 3418.6207 | 3418.6207 | 0 | 433.4963 | 21.3577 | 0 | 45.392 | 37.75 | 11.426 | 0 | 14.7517 | 12.7439 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 7.3722 | 15.6602 | 3.839 | 20.7243 | 0.11943 | 1.7696 | 9.115 | 1.889 | 53 | 0.79319 | 185950.5308 | 14943.9669 | 8.0365
13 | Office | 1959-pre | fans_to_variable | 3418.6207 | 3418.6207 | 0 | 433.5743 | 21.3561 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.8084 | 12.7439 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 7.2942 | -0.3949 | 1.15 | 20.7243 | 0.11817 | -0.044623 | 0.35486 | 0.073543 | 22 | 20.0805 | 185950.5308 | 962.1034 | 0.5174
13 | Office | 1959-pre | hrv_enabled | 3418.6207 | 3418.6207 | 0 | 368.7122 | 21.6827 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.8685 | 12.7114 | 6.4053 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 72.1564 | -7.1545 | 10.8346 | 20.7243 | 1.1689 | -0.80845 | 1.7394 | 0.36048 | 31 | 247.0073 | 185950.5308 | 6691.6149 | 3.5986
13 | Office | 1959-pre | infil_reduce | 3418.6207 | 3418.6207 | 0 | 261.987 | 17.8248 | 0 | 45.3895 | 37.75 | 11.426 | 0 | 27.1861 | 8.4196 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 178.884 | 11.0831 | 31.6638 | 20.7243 | 2.8979 | 1.2524 | 20.0263 | 4.1503 | 64 | 3.7287 | 185950.5308 | 41662.5368 | 22.4052
13 | Office | 1959-pre | infil_reduce_plus_setback | 3418.6207 | 3418.6207 | 0 | 236.4706 | 17.5103 | 0 | 45.3887 | 37.75 | 11.426 | 0 | 27.1495 | 8.6195 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 204.4011 | 11.2342 | 35.9422 | 20.7243 | 3.3113 | 1.2695 | 22.1033 | 4.5808 | 68 | 4.93 | 185950.5308 | 46361.5896 | 24.9322
13 | Office | 1959-pre | lights_reduce_70p | 3418.6207 | 3418.6207 | 0 | 447.4136 | 21.1562 | 0 | 45.392 | 26.4256 | 11.426 | 0 | 31.0189 | 12.7951 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | -6.545 | 10.8678 | 0.72052 | 20.7243 | -0.10603 | 1.2281 | 5.4141 | 1.122 | 47 | 21.0526 | 185950.5308 | 8283.4034 | 4.4546
13 | Office | 1959-pre | load_reduce | 3418.6207 | 3418.6207 | 0 | 160.0939 | 17.5103 | 0 | 45.3887 | 37.75 | 11.426 | 0 | 27.1503 | 7.6493 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 280.7779 | 12.2036 | 48.8343 | 20.7243 | 4.5486 | 1.379 | 28.6022 | 5.9276 | 69 | 3.8557 | 185950.5308 | 60876.3675 | 32.7379
13 | Office | 1959-pre | occupancy_setback | 3418.6207 | 3418.6207 | 0 | 414.5592 | 24.6591 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 31.7932 | 13.7547 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 26.311 | -5.6935 | 3.4365 | 20.7243 | 0.42624 | -0.64337 | -1.0477 | -0.21713 | 13 | 100 | 185950.5308 | -243.6747 | -0.13104
13 | Office | 1959-pre | payback_less_than_20 | 3418.6207 | 3418.6207 | 0 | 73.3045 | 2.514 | 0 | 45.3887 | 26.4256 | 11.426 | 0 | 10.8434 | 5.5416 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 367.5673 | 56.939 | 70.7569 | 20.7243 | 5.9546 | 6.4341 | 59.7785 | 12.3887 | 72 | 6.4812 | 185950.5308 | 115331.5015 | 62.0227
13 | Office | 1959-pre | plug_loads_90_percent | 3418.6207 | 3418.6207 | 0 | 434.1366 | 21.361 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.8775 | 12.7504 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 6.7319 | -0.47534 | 1.0429 | 20.7243 | 0.10906 | -0.053713 | 0.26705 | 0.055344 | 20 | 74.2574 | 185950.5308 | 791.4707 | 0.42564
13 | Office | 1959-pre | pumps_to_variable | 3418.6207 | 3418.6207 | 0 | 442.8926 | 21.3577 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.8677 | 2.9698 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | -2.024 | 9.3183 | 1.2158 | 20.7243 | -0.03279 | 1.053 | 4.9226 | 1.0202 | 44 | 0.98212 | 185950.5308 | 7744.5778 | 4.1649
13 | Office | 1959-pre | pump_fan_eff_ | 3418.6207 | 3418.6207 | 0 | 433.4963 | 21.3577 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.8677 | 9.9675 | 0 | 0 | 440.8685 | 20.91 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.9279 | 12.6757 | 0 | 599.95 | 7.3722 | 2.3206 | 1.6156 | 20.7243 | 0.11943 | 0.26223 | 1.8416 | 0.38166 | 33 | 6.1582 | 185950.5308 | 3338.5705 | 1.7954
14 | Office | 1960-1979 | air_temp_reset_enabled | 3418.6207 | 3418.6207 | 0 | 333.8825 | 3.3932 | 0 | 45.3879 | 37.75 | 11.426 | 0 | 30.199 | 11.838 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 77.5614 | 16.2525 | 16.5255 | 19.9277 | 1.2565 | 1.8365 | 15.5212 | 3.093 | 59 | 1.6625 | 178219.9036 | 28023.1703 | 15.7239
14 | Office | 1960-1979 | baseline | 3418.6207 | 3418.6207 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 0 | 0 | 0 | 19.9277 | 0 | 0 | 0 | 0 | 18 | NA | 178219.9036 | 0 | 0
14 | Office | 1960-1979 | boiler_eff_upgrade | 3418.6207 | 3418.6207 | 0 | 402.865 | 20.13 | 0 | 45.3911 | 37.75 | 11.426 | 0 | 30.0698 | 11.8859 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 8.5756 | -0.40302 | 1.4396 | 19.9277 | 0.13892 | -0.045541 | 0.46861 | 0.093383 | 25 | 204.6478 | 178219.9036 | 1184.4016 | 0.66457
14 | Office | 1960-1979 | boiler_reset | 3418.6207 | 3418.6207 | 0 | 285.103 | 20.13 | 0 | 45.3911 | 37.75 | 11.426 | 0 | 30.0698 | 9.9309 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 126.3376 | 1.552 | 22.528 | 19.9277 | 2.0467 | 0.17537 | 11.1505 | 2.222 | 55 | 0.12231 | 178219.9036 | 23964.6354 | 13.4467
14 | Office | 1960-1979 | cooling_cop_3_0 | 3418.6207 | 3418.6207 | 0 | 402.865 | 14.3788 | 0 | 45.3911 | 37.75 | 11.426 | 0 | 30.0698 | 11.8859 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 8.5756 | 5.3482 | 2.4527 | 19.9277 | 0.13892 | 0.60434 | 3.7298 | 0.74327 | 38 | 7.9093 | 178219.9036 | 6187.9343 | 3.4721
14 | Office | 1960-1979 | dcv_enabled | 3418.6207 | 3418.6207 | 0 | 342.5345 | 20.2226 | 0 | 45.3911 | 37.75 | 11.426 | 0 | 30.0698 | 11.838 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 68.9062 | -0.44771 | 12.0591 | 19.9277 | 1.1163 | -0.050591 | 5.3478 | 1.0657 | 46 | 11.6475 | 178219.9036 | 11944.6961 | 6.7022
14 | Office | 1960-1979 | ecm_cold_deck_reset_control | 3418.6207 | 3418.6207 | 0 | 317.9396 | 2.4523 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1064 | 11.7404 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 93.5003 | 17.3836 | 19.5324 | 19.9277 | 1.5147 | 1.9643 | 17.4583 | 3.479 | 61 | 1.478 | 178219.9036 | 31860.2504 | 17.8769
14 | Office | 1960-1979 | economizers_enabled | 3418.6207 | 3418.6207 | 0 | 402.8821 | 19.9918 | 0 | 45.3911 | 37.75 | 11.426 | 0 | 30.069 | 11.8867 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 8.5585 | -0.26489 | 1.4609 | 19.9277 | 0.13865 | -0.029932 | 0.54555 | 0.10872 | 27 | 18.4819 | 178219.9036 | 1301.5225 | 0.73029
14 | Office | 1960-1979 | elec_reduce | 3418.6207 | 3418.6207 | 0 | 356.7142 | 20.0251 | 0 | 45.3911 | 26.4256 | 11.426 | 0 | 14.0895 | 9.2996 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 54.7265 | 29.5929 | 14.853 | 19.9277 | 0.88657 | 3.344 | 21.2296 | 4.2306 | 66 | 10.3988 | 178219.9036 | 35541.8218 | 19.9427
14 | Office | 1960-1979 | envelope_ecm_roof | 3418.6207 | 3418.6207 | 0 | 340.356 | 16.7969 | 0 | 45.3911 | 37.75 | 11.426 | 0 | 28.7023 | 10.2299 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 71.0846 | 5.9535 | 13.5704 | 19.9277 | 1.1516 | 0.67275 | 9.1547 | 1.8243 | 52 | 133.0595 | 178219.9036 | 17903.6985 | 10.0458
14 | Office | 1960-1979 | envelope_ecm_wall | 3418.6207 | 3418.6207 | 0 | 383.6727 | 19.0509 | 0 | 45.3911 | 37.75 | 11.426 | 0 | 29.67 | 11.3846 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 27.7679 | 1.5771 | 5.1692 | 19.9277 | 0.44984 | 0.17822 | 3.1517 | 0.62806 | 36 | 179.5178 | 178219.9036 | 6342.5695 | 3.5588
14 | Office | 1960-1979 | envelope_ecm_windows | 3418.6207 | 3418.6207 | 0 | 400.8971 | 20.13 | 0 | 45.3911 | 37.75 | 11.426 | 0 | 30.0048 | 11.8103 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 10.5436 | -0.26245 | 1.811 | 19.9277 | 0.17081 | -0.029657 | 0.7083 | 0.14115 | 29 | 6287.1232 | 178219.9036 | 1658.9664 | 0.93085
14 | Office | 1960-1979 | exhaust_fans_occ_control | 3418.6207 | 3418.6207 | 0 | 402.865 | 20.13 | 0 | 45.3911 | 37.75 | 11.426 | 0 | 13.953 | 11.8859 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 8.5756 | 15.7138 | 4.2786 | 19.9277 | 0.13892 | 1.7757 | 9.6076 | 1.9146 | 54 | 0.7826 | 178219.9036 | 15206.0278 | 8.5322
14 | Office | 1960-1979 | fans_to_variable | 3418.6207 | 3418.6207 | 0 | 402.9357 | 20.1275 | 0 | 45.3911 | 37.75 | 11.426 | 0 | 30.0154 | 11.8867 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 8.5049 | -0.34696 | 1.437 | 19.9277 | 0.13778 | -0.039206 | 0.49465 | 0.098573 | 26 | 14.9815 | 178219.9036 | 1220.5249 | 0.68484
14 | Office | 1960-1979 | hrv_enabled | 3418.6207 | 3418.6207 | 0 | 338.5611 | 20.4737 | 0 | 45.3911 | 37.75 | 11.426 | 0 | 30.0706 | 11.8485 | 6.4053 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 72.8795 | -7.1154 | 11.5845 | 19.9277 | 1.1806 | -0.80405 | 1.8898 | 0.3766 | 32 | 236.4328 | 178219.9036 | 6854.9931 | 3.8464
14 | Office | 1960-1979 | infil_reduce | 3418.6207 | 3418.6207 | 0 | 302.3281 | 18.4317 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.737 | 9.2216 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 109.1133 | 6.2923 | 20.329 | 19.9277 | 1.7676 | 0.71103 | 12.4383 | 2.4787 | 57 | 6.2434 | 178219.9036 | 25005.6165 | 14.0308
14 | Office | 1960-1979 | infil_reduce_plus_setback | 3418.6207 | 3418.6207 | 0 | 271.6245 | 18.1181 | 0 | 45.3887 | 37.75 | 11.426 | 0 | 27.9263 | 9.614 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 139.8185 | 6.0242 | 25.6905 | 19.9277 | 2.2651 | 0.68073 | 14.7824 | 2.9458 | 58 | 7.6662 | 178219.9036 | 30268.5709 | 16.9838
14 | Office | 1960-1979 | lights_reduce_70p | 3418.6207 | 3418.6207 | 0 | 415.8958 | 19.9203 | 0 | 45.3911 | 26.4256 | 11.426 | 0 | 30.1925 | 11.9216 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | -4.4552 | 10.9726 | 1.1481 | 19.9277 | -0.072174 | 1.2399 | 5.8598 | 1.1677 | 48 | 20.2287 | 178219.9036 | 8748.6807 | 4.9089
14 | Office | 1960-1979 | load_reduce | 3418.6207 | 3418.6207 | 0 | 185.6891 | 18.1181 | 0 | 45.3887 | 37.75 | 11.426 | 0 | 27.9263 | 8.3765 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 225.754 | 7.2617 | 41.0463 | 19.9277 | 3.6572 | 0.82057 | 22.4702 | 4.4778 | 67 | 5.104 | 178219.9036 | 46727.6497 | 26.2191
14 | Office | 1960-1979 | occupancy_setback | 3418.6207 | 3418.6207 | 0 | 383.3737 | 23.3257 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 30.9132 | 12.8926 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 28.0677 | -5.4489 | 3.9844 | 19.9277 | 0.4547 | -0.61573 | -0.80808 | -0.16103 | 14 | 100 | 178219.9036 | 283.5592 | 0.15911
14 | Office | 1960-1979 | payback_less_than_20 | 3418.6207 | 3418.6207 | 0 | 95.3626 | 2.4003 | 0 | 45.3887 | 26.4256 | 11.426 | 0 | 11.7486 | 6.2176 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 316.0805 | 52.6407 | 64.9511 | 19.9277 | 5.1205 | 5.9484 | 55.5453 | 11.0689 | 71 | 7.254 | 178219.9036 | 102375.7828 | 57.4435
14 | Office | 1960-1979 | plug_loads_90_percent | 3418.6207 | 3418.6207 | 0 | 403.6394 | 20.1527 | 0 | 45.3911 | 37.75 | 11.426 | 0 | 30.0723 | 11.8883 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 7.8012 | -0.43065 | 1.2983 | 19.9277 | 0.12638 | -0.048663 | 0.38999 | 0.077717 | 23 | 52.8805 | 178219.9036 | 1021.7571 | 0.57331
14 | Office | 1960-1979 | pumps_to_variable | 3418.6207 | 3418.6207 | 0 | 411.5747 | 20.13 | 0 | 45.3911 | 37.75 | 11.426 | 0 | 30.0698 | 2.7366 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | -0.13407 | 8.7462 | 1.5171 | 19.9277 | -0.0021719 | 0.98832 | 4.9486 | 0.98615 | 43 | 1.016 | 178219.9036 | 7585.2167 | 4.2561
14 | Office | 1960-1979 | pump_fan_eff_ | 3418.6207 | 3418.6207 | 0 | 402.865 | 20.13 | 0 | 45.3911 | 37.75 | 11.426 | 0 | 30.0698 | 9.2963 | 0 | 0 | 411.4398 | 19.7115 | 0 | 45.392 | 37.75 | 11.426 | 0 | 30.1308 | 11.8404 | 0 | 567.6904 | 8.5756 | 2.1866 | 1.8958 | 19.9277 | 0.13892 | 0.24708 | 1.937 | 0.38601 | 34 | 6.0889 | 178219.9036 | 3437.3344 | 1.9287
15 | Office | 1980-2004 | air_temp_reset_enabled | 3418.6207 | 3418.6207 | 0 | 235.6597 | 2.553 | 0 | 45.3879 | 37.75 | 11.426 | 0 | 27.7427 | 8.8047 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | 33.6735 | 6.1347 | 9.7299 | 15.7669 | 0.54551 | 0.69322 | 7.8565 | 1.2387 | 49 | 4.151 | 138472.7469 | 11364.7436 | 8.2072
15 | Office | 1980-2004 | baseline | 3418.6207 | 3418.6207 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | 0 | 0 | 0 | 15.7669 | 0 | 0 | 0 | 0 | 19 | NA | 138472.7469 | 0 | 0
15 | Office | 1980-2004 | boiler_eff_upgrade | 3418.6207 | 3418.6207 | 0 | 288.8147 | 14.8289 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.5062 | 8.877 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | -19.484 | -5.9771 | -6.2232 | 15.7669 | -0.31564 | -0.67541 | -6.2856 | -0.99105 | 1 | 100 | 138472.7469 | -8687.6895 | -6.2739
15 | Office | 1980-2004 | boiler_reset | 3418.6207 | 3418.6207 | 0 | 202.681 | 14.8289 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.5062 | 7.7557 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | 66.6497 | -4.8558 | 15.1037 | 15.7669 | 1.0797 | -0.5487 | 3.368 | 0.53102 | 35 | 0.51181 | 138472.7469 | 7705.7893 | 5.5648
15 | Office | 1980-2004 | cooling_cop_3_0 | 3418.6207 | 3418.6207 | 0 | 288.8147 | 12.7106 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.5062 | 8.877 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | -19.484 | -3.8588 | -5.7054 | 15.7669 | -0.31564 | -0.43604 | -4.7675 | -0.75168 | 8 | 100 | 138472.7469 | -6844.7665 | -4.943
15 | Office | 1980-2004 | dcv_enabled | 3418.6207 | 3418.6207 | 0 | 227.1605 | 14.976 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.5062 | 8.8202 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | 42.1702 | -6.0673 | 8.8243 | 15.7669 | 0.68316 | -0.6856 | -0.015498 | -0.0024435 | 16 | 100 | 138472.7469 | 2269.9483 | 1.6393
15 | Office | 1980-2004 | ecm_cold_deck_reset_control | 3418.6207 | 3418.6207 | 0 | 218.1331 | 2.1159 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.5696 | 8.7909 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | 51.1976 | 6.7587 | 14.1657 | 15.7669 | 0.8294 | 0.76374 | 10.1043 | 1.5931 | 51 | 3.2276 | 138472.7469 | 15044.4737 | 10.8646
15 | Office | 1980-2004 | economizers_enabled | 3418.6207 | 3418.6207 | 0 | 288.8448 | 14.6485 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.5062 | 8.8779 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | -19.5141 | -5.7975 | -6.1866 | 15.7669 | -0.31613 | -0.65512 | -6.16 | -0.97125 | 5 | 100 | 138472.7469 | -8536.8432 | -6.165
15 | Office | 1980-2004 | elec_reduce | 3418.6207 | 3418.6207 | 0 | 217.6351 | 11.1611 | 0 | 45.3903 | 26.4256 | 11.426 | 0 | 11.2204 | 6.6661 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | 51.6957 | 27.5119 | 19.3599 | 15.7669 | 0.83747 | 3.1088 | 25.0291 | 3.9463 | 63 | 11.1478 | 138472.7469 | 33188.9054 | 23.9678
15 | Office | 1980-2004 | envelope_ecm_roof | 3418.6207 | 3418.6207 | 0 | 270.3651 | 14.3503 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.2544 | 8.483 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | -1.0344 | -4.8525 | -1.4389 | 15.7669 | -0.016757 | -0.54833 | -3.584 | -0.56509 | 11 | 100 | 138472.7469 | -4406.8385 | -3.1825
15 | Office | 1980-2004 | envelope_ecm_wall | 3418.6207 | 3418.6207 | 0 | 283.8972 | 14.8647 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.4494 | 8.7722 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | -14.5665 | -5.8511 | -4.9905 | 15.7669 | -0.23598 | -0.66118 | -5.6901 | -0.89715 | 6 | 100 | 138472.7469 | -7697.8825 | -5.5591
15 | Office | 1980-2004 | envelope_ecm_windows | 3418.6207 | 3418.6207 | 0 | 287.5626 | 14.8444 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.5103 | 8.8657 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | -18.2319 | -5.9852 | -5.9191 | 15.7669 | -0.29536 | -0.67633 | -6.1628 | -0.97168 | 4 | 100 | 138472.7469 | -8470.6273 | -6.1172
15 | Office | 1980-2004 | exhaust_fans_occ_control | 3418.6207 | 3418.6207 | 0 | 288.8155 | 14.8289 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 11.3902 | 8.877 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | -19.4848 | 10.1389 | -2.2843 | 15.7669 | -0.31565 | 1.1457 | 5.2645 | 0.83004 | 40 | 1.8052 | 138472.7469 | 5333.0843 | 3.8514
15 | Office | 1980-2004 | fans_to_variable | 3418.6207 | 3418.6207 | 0 | 288.8684 | 14.8273 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.4648 | 8.877 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | -19.5376 | -5.934 | -6.2258 | 15.7669 | -0.31651 | -0.67054 | -6.2603 | -0.98705 | 2 | 100 | 138472.7469 | -8659.8225 | -6.2538
15 | Office | 1980-2004 | hrv_enabled | 3418.6207 | 3418.6207 | 0 | 222.984 | 15.3278 | 0 | 45.3895 | 37.75 | 11.426 | 0 | 27.5079 | 8.8389 | 6.4053 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | 46.3475 | -12.8447 | 8.1888 | 15.7669 | 0.75083 | -1.4515 | -4.4436 | -0.70062 | 9 | 100 | 138472.7469 | -2878.6811 | -2.0789
15 | Office | 1980-2004 | infil_reduce | 3418.6207 | 3418.6207 | 0 | 242.6899 | 14.7777 | 0 | 45.3895 | 37.75 | 11.426 | 0 | 27.1081 | 8.0783 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | 26.6417 | -4.729 | 5.3559 | 15.7669 | 0.4316 | -0.53438 | -0.65188 | -0.10278 | 15 | 100 | 138472.7469 | 654.6278 | 0.47275
15 | Office | 1980-2004 | infil_reduce_plus_setback | 3418.6207 | 3418.6207 | 0 | 219.3 | 14.5145 | 0 | 45.3887 | 37.75 | 11.426 | 0 | 26.9033 | 8.2051 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | 50.0324 | -4.3877 | 11.1565 | 15.7669 | 0.81052 | -0.49581 | 1.996 | 0.31471 | 30 | 67.6162 | 138472.7469 | 5138.4678 | 3.7108
15 | Office | 1980-2004 | lights_reduce_70p | 3418.6207 | 3418.6207 | 0 | 280.1619 | 11.1497 | 0 | 45.3903 | 26.4256 | 11.426 | 0 | 27.3332 | 8.5707 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | -10.8312 | 9.506 | -0.32392 | 15.7669 | -0.17547 | 1.0742 | 5.6999 | 0.89871 | 42 | 26.284 | 138472.7469 | 6331.3922 | 4.5723
15 | Office | 1980-2004 | load_reduce | 3418.6207 | 3418.6207 | 0 | 147.1907 | 14.5145 | 0 | 45.3887 | 37.75 | 11.426 | 0 | 26.9033 | 7.4096 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | 122.1416 | -3.5923 | 28.9758 | 15.7669 | 1.9787 | -0.40593 | 9.9751 | 1.5728 | 50 | 13.7028 | 138472.7469 | 18738.087 | 13.532
15 | Office | 1980-2004 | occupancy_setback | 3418.6207 | 3418.6207 | 0 | 260.76 | 14.612 | 0 | 45.3887 | 37.75 | 11.426 | 0 | 27.7013 | 9.2378 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | 8.5723 | -6.3159 | 0.55152 | 15.7669 | 0.13887 | -0.7137 | -3.6458 | -0.57483 | 10 | 100 | 138472.7469 | -3960.3886 | -2.86
15 | Office | 1980-2004 | payback_less_than_20 | 3418.6207 | 3418.6207 | 0 | 66.9878 | 2.1232 | 0 | 45.3887 | 26.4256 | 11.426 | 0 | 10.3916 | 0.15195 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | 202.3446 | 43.8928 | 60.1853 | 15.7669 | 3.278 | 4.9599 | 52.2478 | 8.2379 | 70 | 9.5886 | 138472.7469 | 74406.4354 | 53.7336
15 | Office | 1980-2004 | plug_loads_90_percent | 3418.6207 | 3418.6207 | 0 | 288.5173 | 14.7192 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.4989 | 8.8722 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | -19.1866 | -5.8552 | -6.1207 | 15.7669 | -0.31082 | -0.66164 | -6.1677 | -0.97246 | 3 | 100 | 138472.7469 | -8528.4195 | -6.1589
15 | Office | 1980-2004 | pumps_to_variable | 3418.6207 | 3418.6207 | 0 | 295.9164 | 14.8289 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.5062 | 1.7291 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | -26.5856 | 1.1709 | -6.2119 | 15.7669 | -0.43069 | 0.13231 | -1.8924 | -0.29838 | 12 | 100 | 138472.7469 | -3740.1656 | -2.701
15 | Office | 1980-2004 | pump_fan_eff_ | 3418.6207 | 3418.6207 | 0 | 288.8147 | 14.8289 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.5062 | 6.9432 | 0 | 0 | 269.3307 | 9.7887 | 0 | 45.3903 | 37.75 | 11.426 | 0 | 27.0821 | 8.3643 | 0 | 409.1322 | -19.484 | -4.0432 | -5.7505 | 15.7669 | -0.31564 | -0.45688 | -4.8996 | -0.77252 | 7 | 100 | 138472.7469 | -7005.2358 | -5.0589
19 | Recreation Center | 1980-2004 | air_temp_reset_enabled | 12612.7339 | 12612.7339 | 8.6969 | 416.0644 | 1.5595 | 0 | 23.3928 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.1924 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | -63.746 | 3.3471 | -12.7125 | 16.8267 | -1.0327 | 0.37823 | -3.8894 | -0.65446 | 2 | 100 | 143044.5256 | -8498.5203 | -5.9412
19 | Recreation Center | 1980-2004 | baseline | 12612.7339 | 12612.7339 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 0 | 0 | 0 | 16.8267 | 0 | 0 | 0 | 0 | 5 | NA | 143044.5256 | 0 | 0
19 | Recreation Center | 1980-2004 | boiler_eff_upgrade | 12612.7339 | 12612.7339 | 12.1808 | 346.3912 | 1.4655 | 0 | 23.3941 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.1902 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 5.9259 | -0.040523 | 1.2387 | 16.8267 | 0.095999 | -0.0045792 | 0.5433 | 0.09142 | 7 | 56.6597 | 143044.5256 | 1025.4797 | 0.7169
19 | Recreation Center | 1980-2004 | boiler_reset | 12612.7339 | 12612.7339 | 12.1808 | 319.971 | 1.4655 | 0 | 23.3941 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.1902 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 32.3461 | -0.040523 | 6.7996 | 16.8267 | 0.52401 | -0.0045792 | 3.0869 | 0.51943 | 16 | 0.14182 | 143044.5256 | 5754.6936 | 4.023
19 | Recreation Center | 1980-2004 | cooling_cop_3_0 | 12612.7339 | 12612.7339 | 12.1808 | 346.3912 | 1.2562 | 0 | 23.3941 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.1902 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 5.9259 | 0.1687 | 1.2828 | 16.8267 | 0.095999 | 0.019063 | 0.68381 | 0.11506 | 11 | 29.8871 | 143044.5256 | 1207.5048 | 0.84415
19 | Recreation Center | 1980-2004 | dcv_enabled | 12612.7339 | 12612.7339 | 11.8245 | 252.0942 | 2.4506 | 0 | 23.3937 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.1869 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 100.2233 | -0.66599 | 20.9545 | 16.8267 | 1.6236 | -0.075257 | 9.2018 | 1.5484 | 19 | 1.3634 | 143044.5256 | 17360.5571 | 12.1365
19 | Recreation Center | 1980-2004 | ecm_cold_deck_reset_control | 12612.7339 | 12612.7339 | 12.3729 | 344.7583 | 1.3956 | 0 | 23.3939 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.1896 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 7.5589 | -0.16209 | 1.5569 | 16.8267 | 0.12245 | -0.018317 | 0.61889 | 0.10414 | 9 | 24.0902 | 143044.5256 | 1212.0296 | 0.84731
19 | Recreation Center | 1980-2004 | economizers_enabled | 12612.7339 | 12612.7339 | 12.1841 | 346.4892 | 1.4351 | 0 | 23.3941 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.1722 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 5.8279 | 0.004625 | 1.2276 | 16.8267 | 0.094412 | 0.00052262 | 0.56419 | 0.094934 | 8 | 6.8839 | 143044.5256 | 1047.2159 | 0.73209
19 | Recreation Center | 1980-2004 | elec_reduce | 12612.7339 | 12612.7339 | 12.8895 | 263.4372 | 2.1691 | 0 | 23.3948 | 37.28 | 6.6082 | 5.0846 | 16.6162 | 3.269 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 88.8792 | 15.485 | 21.9662 | 16.8267 | 1.4398 | 1.7498 | 18.9559 | 3.1897 | 22 | 7.4878 | 143044.5256 | 29381.3412 | 20.54
19 | Recreation Center | 1980-2004 | envelope_ecm_roof | 12612.7339 | 12612.7339 | 11.678 | 352.9315 | 1.5498 | 0 | 23.3917 | 53.2573 | 6.6082 | 5.0846 | 14.6849 | 4.3314 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | -0.61204 | 2.2074 | 0.33579 | 16.8267 | -0.009915 | 0.24944 | 1.4235 | 0.23952 | 14 | 477.2006 | 143044.5256 | 1810.907 | 1.266
19 | Recreation Center | 1980-2004 | envelope_ecm_wall | 12612.7339 | 12612.7339 | 13.223 | 363.9642 | 1.6663 | 0 | 23.3919 | 53.2573 | 6.6082 | 5.0846 | 16.0041 | 4.6739 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | -11.645 | -1.1157 | -2.6858 | 16.8267 | -0.18865 | -0.12608 | -1.8704 | -0.31472 | 4 | 100 | 143044.5256 | -3055.1258 | -2.1358
19 | Recreation Center | 1980-2004 | envelope_ecm_windows | 12612.7339 | 12612.7339 | 13.9947 | 365.7435 | 1.6637 | 0 | 23.3919 | 53.2573 | 6.6082 | 5.0846 | 16.2962 | 4.7051 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | -13.4243 | -2.2081 | -3.2902 | 16.8267 | -0.21747 | -0.24951 | -2.7753 | -0.46699 | 3 | 100 | 143044.5256 | -4323.9814 | -3.0228
19 | Recreation Center | 1980-2004 | fans_to_variable | 12612.7339 | 12612.7339 | 12.1813 | 346.5277 | 1.4641 | 0 | 23.3941 | 53.2573 | 6.6082 | 5.0846 | 16.4862 | 4.1902 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 5.7893 | 0.12972 | 1.2458 | 16.8267 | 0.093787 | 0.014658 | 0.64449 | 0.10845 | 10 | 8.4559 | 143044.5256 | 1149.1489 | 0.80335
19 | Recreation Center | 1980-2004 | hrv_enabled | 12612.7339 | 12612.7339 | 11.3979 | 222.0346 | 3.1787 | 0 | 23.3937 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.1909 | 3.1137 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 130.2829 | -4.0852 | 26.5616 | 16.8267 | 2.1106 | -0.46162 | 9.7997 | 1.649 | 21 | 37.1721 | 143044.5256 | 19766.5494 | 13.8185
19 | Recreation Center | 1980-2004 | infil_reduce | 12612.7339 | 12612.7339 | 8.347 | 314.7124 | 1.3963 | 0 | 23.393 | 53.2573 | 6.6082 | 5.0846 | 14.2427 | 3.3152 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 37.6058 | 7.1504 | 9.4201 | 16.8267 | 0.60921 | 0.808 | 8.4224 | 1.4172 | 18 | 6.1294 | 143044.5256 | 12952.286 | 9.0547
19 | Recreation Center | 1980-2004 | infil_reduce_plus_setback | 12612.7339 | 12612.7339 | 9.7265 | 392.2093 | 3.5729 | 0 | 23.3878 | 53.2573 | 6.6082 | 5.0846 | 10.8471 | 3.4581 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | -39.8859 | 6.8469 | -6.9539 | 16.8267 | -0.64615 | 0.7737 | 0.75803 | 0.12755 | 12 | 77.5809 | 143044.5256 | -1182.7485 | -0.82684
19 | Recreation Center | 1980-2004 | lights_reduce_70p | 12612.7339 | 12612.7339 | 13.1386 | 357.1294 | 1.31 | 0 | 23.395 | 37.28 | 6.6082 | 5.0846 | 16.6256 | 4.1832 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | -4.8133 | 15.1714 | 2.1801 | 16.8267 | -0.077975 | 1.7144 | 9.725 | 1.6364 | 20 | 10.9292 | 143044.5256 | 12337.5512 | 8.625
19 | Recreation Center | 1980-2004 | load_reduce | 12612.7339 | 12612.7339 | 9.7265 | 362.3581 | 3.5729 | 0 | 23.3878 | 53.2573 | 6.6082 | 5.0846 | 10.8471 | 3.4581 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | -10.0346 | 6.8469 | -0.67093 | 16.8267 | -0.16256 | 0.7737 | 3.632 | 0.61114 | 17 | 16.3124 | 143044.5256 | 4160.625 | 2.9086
19 | Recreation Center | 1980-2004 | occupancy_setback | 12612.7339 | 12612.7339 | 16.0107 | 429.244 | 3.5665 | 0 | 23.3886 | 53.2573 | 6.6082 | 5.0846 | 12.5116 | 4.1413 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | -76.9214 | -1.7786 | -16.5645 | 16.8267 | -1.2461 | -0.20098 | -8.6001 | -1.4471 | 1 | 100 | 143044.5256 | -15316.3436 | -10.7074
19 | Recreation Center | 1980-2004 | payback_less_than_20 | 12612.7339 | 12612.7339 | 10.8101 | 274.0605 | 4.9732 | 0 | 23.3882 | 37.28 | 6.6082 | 5.0846 | 10.8592 | 2.6433 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 78.2625 | 21.1431 | 20.9225 | 16.8267 | 1.2679 | 2.3892 | 21.7334 | 3.657 | 23 | 10.5529 | 143044.5256 | 32403.4869 | 22.6527
19 | Recreation Center | 1980-2004 | plug_loads_90_percent | 12612.7339 | 12612.7339 | 12.1782 | 346.725 | 1.4538 | 0 | 23.3941 | 53.2573 | 6.6082 | 5.0846 | 16.6461 | 4.1882 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 5.592 | -0.014756 | 1.1739 | 16.8267 | 0.090591 | -0.0016674 | 0.52846 | 0.088923 | 6 | 7.86 | 143044.5256 | 988.1333 | 0.69079
19 | Recreation Center | 1980-2004 | pumps_to_variable | 12612.7339 | 12612.7339 | 12.1808 | 349.604 | 1.4575 | 0 | 23.4393 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 0.46712 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 2.6679 | 3.6905 | 1.3383 | 16.8267 | 0.043221 | 0.41703 | 2.7352 | 0.46025 | 15 | 2.3602 | 143044.5256 | 3688.294 | 2.5784
19 | Recreation Center | 1980-2004 | pump_fan_eff_ | 12612.7339 | 12612.7339 | 12.1808 | 346.3912 | 1.4655 | 0 | 23.3941 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 3.2773 | 0 | 12.2841 | 352.3166 | 1.3459 | 0 | 23.3946 | 53.2573 | 6.6082 | 5.0846 | 16.6556 | 4.166 | 0 | 475.1128 | 5.9259 | 0.87236 | 1.4309 | 16.8267 | 0.095999 | 0.098576 | 1.1563 | 0.19458 | 13 | 14.0037 | 143044.5256 | 1819.6843 | 1.2721
20 | Storage Building | 1959-pre | baseline | 1171 | 965.1569 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | 0 | 0 | 0 | 12.6056 | 0 | 0 | 0 | 0 | 2 | NA | 118625.8777 | 0 | 0
20 | Storage Building | 1959-pre | dcv_enabled | 1171 | 965.1569 | 0 | 394.0618 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.2477 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | 3.436 | 0.22348 | 0.8095 | 12.6056 | 0.055663 | 0.025253 | 0.64191 | 0.080917 | 20 | 8.7811 | 118625.8777 | 809.4729 | 0.68237
20 | Storage Building | 1959-pre | ecm_cold_deck_reset_control | 1171 | 965.1569 | 0 | 394.0618 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.2477 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | 3.436 | 0.22348 | 0.8095 | 12.6056 | 0.055663 | 0.025253 | 0.64191 | 0.080917 | 21 | 0 | 118625.8777 | 809.4729 | 0.68237
20 | Storage Building | 1959-pre | elec_reduce | 1171 | 965.1569 | 0 | 404.8447 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 16.6353 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | -7.3469 | 10.2941 | 0.65193 | 12.6056 | -0.11902 | 1.1632 | 8.2837 | 1.0442 | 47 | 36.8129 | 118625.8777 | 7640.729 | 6.441
20 | Storage Building | 1959-pre | envelope_ecm_roof | 1171 | 965.1569 | 0 | 367.5305 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.1547 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | 29.9673 | 1.3164 | 6.9202 | 12.6056 | 0.48547 | 0.14876 | 5.0313 | 0.63423 | 40 | 376.6664 | 118625.8777 | 6509.4448 | 5.4874
20 | Storage Building | 1959-pre | envelope_ecm_wall | 1171 | 965.1569 | 0 | 382.0113 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.7274 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | 15.4865 | 0.74377 | 3.5902 | 12.6056 | 0.25088 | 0.084046 | 2.657 | 0.33493 | 33 | 398.3362 | 118625.8777 | 3419.1584 | 2.8823
20 | Storage Building | 1959-pre | envelope_ecm_windows | 1171 | 965.1569 | 0 | 394.0618 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.2477 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | 3.436 | 0.22348 | 0.8095 | 12.6056 | 0.055663 | 0.025253 | 0.64191 | 0.080917 | 22 | 0 | 118625.8777 | 809.4729 | 0.68237
20 | Storage Building | 1959-pre | exhaust_fans_occ_control | 1171 | 965.1569 | 0 | 394.0618 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.2477 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | 3.436 | 0.22348 | 0.8095 | 12.6056 | 0.055663 | 0.025253 | 0.64191 | 0.080917 | 23 | 7.7257 | 118625.8777 | 809.4729 | 0.68237
20 | Storage Building | 1959-pre | hrv_enabled | 1171 | 965.1569 | 0 | 394.0618 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.2477 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | 3.436 | 0.22348 | 0.8095 | 12.6056 | 0.055663 | 0.025253 | 0.64191 | 0.080917 | 24 | 0 | 118625.8777 | 809.4729 | 0.68237
20 | Storage Building | 1959-pre | infil_reduce | 1171 | 965.1569 | 0 | 204.9627 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 8.6424 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | 192.5351 | 7.8288 | 44.3219 | 12.6056 | 3.1191 | 0.88465 | 31.7615 | 4.0037 | 59 | 7.7364 | 118625.8777 | 41274.8275 | 34.7941
20 | Storage Building | 1959-pre | infil_reduce_plus_setback | 1171 | 965.1569 | 0 | 177.7714 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 8.8903 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | 219.7263 | 7.5809 | 50.2819 | 12.6056 | 3.5596 | 0.85664 | 35.0337 | 4.4162 | 60 | 7.106 | 118625.8777 | 45926.3669 | 38.7153
20 | Storage Building | 1959-pre | lights_reduce_70p | 1171 | 965.1569 | 0 | 404.6841 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 16.6178 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | -7.1863 | 10.3115 | 0.69132 | 12.6056 | -0.11642 | 1.1652 | 8.32 | 1.0488 | 50 | 19.3175 | 118625.8777 | 7684.6708 | 6.4781
20 | Storage Building | 1959-pre | load_reduce | 1171 | 965.1569 | 0 | 177.7714 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 8.8903 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | 219.7263 | 7.5809 | 50.2819 | 12.6056 | 3.5596 | 0.85664 | 35.0337 | 4.4162 | 61 | 7.106 | 118625.8777 | 45926.3669 | 38.7153
20 | Storage Building | 1959-pre | occupancy_setback | 1171 | 965.1569 | 0 | 347.0262 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 17.407 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | 50.4716 | -0.93582 | 10.9577 | 12.6056 | 0.81764 | -0.10575 | 5.6474 | 0.71189 | 41 | 0.57184 | 118625.8777 | 8220.2479 | 6.9296
20 | Storage Building | 1959-pre | payback_less_than_20 | 1171 | 965.1569 | 0 | 188.7324 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 9.1732 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | 208.7653 | 17.7562 | 50.1081 | 12.6056 | 3.382 | 2.0064 | 42.7465 | 5.3884 | 62 | 10.0624 | 118625.8777 | 52816.8837 | 44.5239
20 | Storage Building | 1959-pre | plug_loads_90_percent | 1171 | 965.1569 | 0 | 394.2015 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.2617 | 0 | 0 | 0 | 397.4978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 16.4712 | 0 | 0 | 452.0653 | 3.2963 | 0.20951 | 0.77552 | 12.6056 | 0.053401 | 0.023675 | 0.61144 | 0.077075 | 18 | 3.055 | 118625.8777 | 772.3193 | 0.65105
21 | Storage Building | 1960-1979 | baseline | 1171 | 965.1569 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | 0 | 0 | 0 | 11.8781 | 0 | 0 | 0 | 0 | 3 | NA | 111139.2277 | 0 | 0
21 | Storage Building | 1960-1979 | dcv_enabled | 1171 | 965.1569 | 0 | 357.7882 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 14.7741 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | 4.962 | 0.24094 | 1.2511 | 11.8781 | 0.080384 | 0.027226 | 0.90595 | 0.10761 | 26 | 6.6029 | 111139.2277 | 1097.8076 | 0.98778
21 | Storage Building | 1960-1979 | ecm_cold_deck_reset_control | 1171 | 965.1569 | 0 | 357.7882 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 14.7741 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | 4.962 | 0.24094 | 1.2511 | 11.8781 | 0.080384 | 0.027226 | 0.90595 | 0.10761 | 27 | 0 | 111139.2277 | 1097.8076 | 0.98778
21 | Storage Building | 1960-1979 | elec_reduce | 1171 | 965.1569 | 0 | 368.3232 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 15.1373 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | -5.573 | 10.336 | 1.1453 | 11.8781 | -0.090283 | 1.168 | 9.0728 | 1.0777 | 51 | 35.6695 | 111139.2277 | 7994.7075 | 7.1934
21 | Storage Building | 1960-1979 | envelope_ecm_roof | 1171 | 965.1569 | 0 | 281.1659 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 11.6873 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | 81.5842 | 3.3278 | 20.4183 | 11.8781 | 1.3217 | 0.37604 | 14.2926 | 1.6977 | 53 | 92.1921 | 111139.2277 | 17498.7229 | 15.7449
21 | Storage Building | 1960-1979 | envelope_ecm_wall | 1171 | 965.1569 | 0 | 353.57 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 14.5891 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | 9.1801 | 0.42601 | 2.3099 | 11.8781 | 0.14872 | 0.048139 | 1.6573 | 0.19686 | 32 | 677.7165 | 111139.2277 | 2013.8735 | 1.812
21 | Storage Building | 1960-1979 | envelope_ecm_windows | 1171 | 965.1569 | 0 | 357.7882 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 14.7741 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | 4.962 | 0.24094 | 1.2511 | 11.8781 | 0.080384 | 0.027226 | 0.90595 | 0.10761 | 28 | 0 | 111139.2277 | 1097.8076 | 0.98778
21 | Storage Building | 1960-1979 | exhaust_fans_occ_control | 1171 | 965.1569 | 0 | 357.7882 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 14.7741 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | 4.962 | 0.24094 | 1.2511 | 11.8781 | 0.080384 | 0.027226 | 0.90595 | 0.10761 | 29 | 5.8093 | 111139.2277 | 1097.8076 | 0.98778
21 | Storage Building | 1960-1979 | hrv_enabled | 1171 | 965.1569 | 0 | 357.7882 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 14.7741 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | 4.962 | 0.24094 | 1.2511 | 11.8781 | 0.080384 | 0.027226 | 0.90595 | 0.10761 | 30 | 0 | 111139.2277 | 1097.8076 | 0.98778
21 | Storage Building | 1960-1979 | infil_reduce | 1171 | 965.1569 | 0 | 263.5529 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 10.9435 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | 99.1972 | 4.0715 | 24.8325 | 11.8781 | 1.607 | 0.46008 | 17.4024 | 2.0671 | 55 | 14.9846 | 111139.2277 | 21298.5342 | 19.1638
21 | Storage Building | 1960-1979 | infil_reduce_plus_setback | 1171 | 965.1569 | 0 | 228.7598 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 11.4743 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | 133.9903 | 3.5408 | 33.0714 | 11.8781 | 2.1706 | 0.40011 | 21.6427 | 2.5707 | 56 | 12.2071 | 111139.2277 | 27064.7261 | 24.3521
21 | Storage Building | 1960-1979 | lights_reduce_70p | 1171 | 965.1569 | 0 | 368.1032 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 15.1233 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | -5.353 | 10.3499 | 1.2016 | 11.8781 | -0.086719 | 1.1695 | 9.1161 | 1.0828 | 52 | 18.7102 | 111139.2277 | 8046.2372 | 7.2398
21 | Storage Building | 1960-1979 | load_reduce | 1171 | 965.1569 | 0 | 228.7598 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 11.4743 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | 133.9903 | 3.5408 | 33.0714 | 11.8781 | 2.1706 | 0.40011 | 21.6427 | 2.5707 | 57 | 12.2071 | 111139.2277 | 27064.7261 | 24.3521
21 | Storage Building | 1960-1979 | occupancy_setback | 1171 | 965.1569 | 0 | 313.0502 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.7903 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | 49.6999 | -0.7752 | 11.7647 | 11.8781 | 0.80514 | -0.087597 | 6.0408 | 0.71754 | 42 | 0.56734 | 111139.2277 | 8221.8576 | 7.3978
21 | Storage Building | 1960-1979 | payback_less_than_20 | 1171 | 965.1569 | 0 | 239.7557 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 11.7921 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | 122.9944 | 13.6812 | 32.8656 | 11.8781 | 1.9925 | 1.546 | 29.7898 | 3.5385 | 58 | 15.3231 | 111139.2277 | 33918.6131 | 30.519
21 | Storage Building | 1960-1979 | plug_loads_90_percent | 1171 | 965.1569 | 0 | 357.9837 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 14.7916 | 0 | 0 | 0 | 362.7501 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 15.0151 | 0 | 0 | 415.8616 | 4.7664 | 0.22348 | 1.1999 | 11.8781 | 0.077216 | 0.025253 | 0.86267 | 0.10247 | 25 | 2.2979 | 111139.2277 | 1047.6154 | 0.94262
22 | Storage Building | 1980-2004 | baseline | 1171 | 965.1569 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | 0 | 0 | 0 | 8.9168 | 0 | 0 | 0 | 0 | 4 | NA | 80588.4389 | 0 | 0
22 | Storage Building | 1980-2004 | dcv_enabled | 1171 | 965.1569 | 0 | 216.9119 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.0998 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | 3.0309 | 0.18158 | 1.2018 | 8.9168 | 0.049101 | 0.020518 | 0.78077 | 0.06962 | 13 | 10.206 | 80588.4389 | 700.5124 | 0.86925
22 | Storage Building | 1980-2004 | ecm_cold_deck_reset_control | 1171 | 965.1569 | 0 | 216.9119 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.0998 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | 3.0309 | 0.18158 | 1.2018 | 8.9168 | 0.049101 | 0.020518 | 0.78077 | 0.06962 | 14 | 0 | 80588.4389 | 700.5124 | 0.86925
22 | Storage Building | 1980-2004 | elec_reduce | 1171 | 965.1569 | 0 | 227.0558 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 9.4804 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | -7.113 | 10.2591 | 1.1769 | 8.9168 | -0.11523 | 1.1593 | 11.7089 | 1.0441 | 46 | 36.8184 | 80588.4389 | 7652.2278 | 9.4954
22 | Storage Building | 1980-2004 | envelope_ecm_roof | 1171 | 965.1569 | 0 | 190.0978 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 8.0383 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | 29.8451 | 1.2431 | 11.6295 | 8.9168 | 0.48349 | 0.14047 | 6.9976 | 0.62396 | 39 | 217.5335 | 80588.4389 | 6423.7716 | 7.9711
22 | Storage Building | 1980-2004 | envelope_ecm_wall | 1171 | 965.1569 | 0 | 213.9997 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 8.9706 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | 5.9432 | 0.31078 | 2.3395 | 8.9168 | 0.096279 | 0.035118 | 1.4736 | 0.1314 | 31 | 1015.3447 | 80588.4389 | 1334.2042 | 1.6556
22 | Storage Building | 1980-2004 | envelope_ecm_windows | 1171 | 965.1569 | 0 | 216.9119 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.0998 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | 3.0309 | 0.18158 | 1.2018 | 8.9168 | 0.049101 | 0.020518 | 0.78077 | 0.06962 | 15 | 0 | 80588.4389 | 700.5124 | 0.86925
22 | Storage Building | 1980-2004 | exhaust_fans_occ_control | 1171 | 965.1569 | 0 | 216.9119 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.0998 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | 3.0309 | 0.18158 | 1.2018 | 8.9168 | 0.049101 | 0.020518 | 0.78077 | 0.06962 | 16 | 8.9794 | 80588.4389 | 700.5124 | 0.86925
22 | Storage Building | 1980-2004 | hrv_enabled | 1171 | 965.1569 | 0 | 216.9119 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.0998 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | 3.0309 | 0.18158 | 1.2018 | 8.9168 | 0.049101 | 0.020518 | 0.78077 | 0.06962 | 17 | 0 | 80588.4389 | 700.5124 | 0.86925
22 | Storage Building | 1980-2004 | infil_reduce | 1171 | 965.1569 | 0 | 193.4081 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 8.164 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | 26.5348 | 1.1174 | 10.3442 | 8.9168 | 0.42986 | 0.12627 | 6.2369 | 0.55613 | 38 | 49.9803 | 80588.4389 | 5721.8625 | 7.1001
22 | Storage Building | 1980-2004 | infil_reduce_plus_setback | 1171 | 965.1569 | 0 | 167.2574 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 8.377 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | 52.6854 | 0.9044 | 20.047 | 8.9168 | 0.8535 | 0.1022 | 10.718 | 0.9557 | 43 | 29.5099 | 80588.4389 | 10217.5175 | 12.6786
22 | Storage Building | 1980-2004 | lights_reduce_70p | 1171 | 965.1569 | 0 | 226.9266 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 9.4665 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | -6.9838 | 10.2731 | 1.2305 | 8.9168 | -0.11314 | 1.1609 | 11.75 | 1.0477 | 49 | 19.337 | 80588.4389 | 7687.5062 | 9.5392
22 | Storage Building | 1980-2004 | load_reduce | 1171 | 965.1569 | 0 | 167.2574 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 8.377 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | 52.6854 | 0.9044 | 20.047 | 8.9168 | 0.8535 | 0.1022 | 10.718 | 0.9557 | 44 | 29.5099 | 80588.4389 | 10217.5175 | 12.6786
22 | Storage Building | 1980-2004 | occupancy_setback | 1171 | 965.1569 | 0 | 188.1528 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.4106 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | 31.79 | -0.1292 | 11.8438 | 8.9168 | 0.515 | -0.0146 | 5.6119 | 0.5004 | 37 | 0.81353 | 80588.4389 | 5578.0146 | 6.9216
22 | Storage Building | 1980-2004 | payback_less_than_20 | 1171 | 965.1569 | 0 | 178.194 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 8.6599 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | 41.7489 | 11.0797 | 19.7623 | 8.9168 | 0.67633 | 1.252 | 21.626 | 1.9283 | 54 | 26.4693 | 80588.4389 | 17112.4096 | 21.2343
22 | Storage Building | 1980-2004 | plug_loads_90_percent | 1171 | 965.1569 | 0 | 217.0236 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.1103 | 0 | 0 | 0 | 219.9428 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 9.2814 | 0 | 0 | 267.3206 | 2.9192 | 0.1711 | 1.156 | 8.9168 | 0.047291 | 0.019335 | 0.7472 | 0.066626 | 12 | 3.5342 | 80588.4389 | 671.3971 | 0.83312
23 | Storage Building | 2005-2014 | baseline | 1171 | 965.1569 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 175.4249 | 0 | 0 | 0 | 7.0474 | 0 | 0 | 0 | 0 | 5 | NA | 61422.1947 | 0 | 0
23 | Storage Building | 2005-2014 | dcv_enabled | 1171 | 965.1569 | 0 | 129.5416 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.1994 | 0 | 0 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 175.4249 | 2.4373 | 0.15015 | 1.475 | 7.0474 | 0.039485 | 0.016967 | 0.80102 | 0.056452 | 7 | 12.5866 | 61422.1947 | 566.9132 | 0.92298
23 | Storage Building | 2005-2014 | ecm_cold_deck_reset_control | 1171 | 965.1569 | 0 | 129.5416 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.1994 | 0 | 0 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 175.4249 | 2.4373 | 0.15015 | 1.475 | 7.0474 | 0.039485 | 0.016967 | 0.80102 | 0.056452 | 8 | 0 | 61422.1947 | 566.9132 | 0.92298
23 | Storage Building | 2005-2014 | elec_reduce | 1171 | 965.1569 | 0 | 139.0989 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 5.5626 | 0 | 0 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 175.4249 | -7.1199 | 10.2452 | 1.7815 | 7.0474 | -0.11534 | 1.1577 | 14.7906 | 1.0424 | 45 | 23.6076 | 61422.1947 | 7638.8259 | 12.4366
23 | Storage Building | 2005-2014 | envelope_ecm_roof | 1171 | 965.1569 | 0 | 111.5305 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 4.515 | 0 | 0 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 175.4249 | 20.4484 | 0.83456 | 12.1323 | 7.0474 | 0.33126 | 0.094305 | 6.0386 | 0.42557 | 35 | 0 | 61422.1947 | 4386.3349 | 7.1413
23 | Storage Building | 2005-2014 | envelope_ecm_wall | 1171 | 965.1569 | 0 | 128.529 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.1575 | 0 | 0 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 175.4249 | 3.45 | 0.19205 | 2.0761 | 7.0474 | 0.05589 | 0.021702 | 1.101 | 0.077592 | 19 | 0 | 61422.1947 | 784.6317 | 1.2774
23 | Storage Building | 2005-2014 | envelope_ecm_windows | 1171 | 965.1569 | 0 | 129.5416 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.1994 | 0 | 0 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 175.4249 | 2.4373 | 0.15015 | 1.475 | 7.0474 | 0.039485 | 0.016967 | 0.80102 | 0.056452 | 9 | 0 | 61422.1947 | 566.9132 | 0.92298
23 | Storage Building | 2005-2014 | exhaust_fans_occ_control | 1171 | 965.1569 | 0 | 129.5416 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.1994 | 0 | 0 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 175.4249 | 2.4373 | 0.15015 | 1.475 | 7.0474 | 0.039485 | 0.016967 | 0.80102 | 0.056452 | 10 | 11.0739 | 61422.1947 | 566.9132 | 0.92298
23 | Storage Building | 2005-2014 | hrv_enabled | 1171 | 965.1569 | 0 | 129.5416 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.1994 | 0 | 0 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 175.4249 | 2.4373 | 0.15015 | 1.475 | 7.0474 | 0.039485 | 0.016967 | 0.80102 | 0.056452 | 11 | 0 | 61422.1947 | 566.9132 | 0.92298
23 | Storage Building | 2005-2014 | lights_reduce_70p | 1171 | 965.1569 | 0 | 138.9907 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 5.5521 | 0 | 0 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 175.4249 | -7.0117 | 10.2556 | 1.8492 | 7.0474 | -0.11359 | 1.1589 | 14.8323 | 1.0453 | 48 | 19.3819 | 61422.1947 | 7667.3162 | 12.483
23 | Storage Building | 2005-2014 | load_reduce | 1171 | 965.1569 | 0 | 151.6662 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 7.1409 | 0 | 0 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 175.4249 | -19.6872 | -1.7913 | -12.2437 | 7.0474 | -0.31893 | -0.20242 | -7.3978 | -0.52135 | 1 | 100 | 61422.1947 | -5082.4684 | -8.2746
23 | Storage Building | 2005-2014 | occupancy_setback | 1171 | 965.1569 | 0 | 110.2106 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.2518 | 0 | 0 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 175.4249 | 21.7684 | 0.097773 | 12.4647 | 7.0474 | 0.35265 | 0.011048 | 5.1607 | 0.3637 | 34 | 1.1193 | 61422.1947 | 3981.5984 | 6.4823
23 | Storage Building | 2005-2014 | payback_less_than_20 | 1171 | 965.1569 | 0 | 162.6237 | 0 | 0 | 0 | 24.4082 | 3.23 | 0 | 7.4063 | 0 | 0 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 175.4249 | -30.6447 | 8.4015 | -12.6796 | 7.0474 | -0.49644 | 0.94936 | 6.4267 | 0.45292 | 36 | 51.3253 | 61422.1947 | 1823.8631 | 2.9694
23 | Storage Building | 2005-2014 | plug_loads_90_percent | 1171 | 965.1569 | 0 | 129.6289 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.2099 | 0 | 0 | 0 | 131.979 | 0 | 0 | 0 | 34.8664 | 3.23 | 0 | 5.3496 | 0 | 0 | 175.4249 | 2.35 | 0.13968 | 1.4192 | 7.0474 | 0.038071 | 0.015783 | 0.76416 | 0.053854 | 6 | 4.3723 | 61422.1947 | 542.1732 | 0.8827
24 | Training Building | 1959-pre | air_temp_reset_enabled | 3699.8929 | 3699.8929 | 0 | 541.2008 | 14.1641 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.3469 | 0.54131 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | -24.9257 | -12.3292 | -6.1995 | 17.93 | -0.4038 | -1.3932 | -10.0223 | -1.797 | 1 | 100 | 166065.6394 | -15188.0944 | -9.1458
24 | Training Building | 1959-pre | baseline | 3699.8929 | 3699.8929 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 0 | 0 | 0 | 17.93 | 0 | 0 | 0 | 0 | 38 | NA | 166065.6394 | 0 | 0
24 | Training Building | 1959-pre | boiler_eff_upgrade | 3699.8929 | 3699.8929 | 0 | 512.9942 | 3.0511 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.3469 | 0.74477 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 3.2809 | -1.4197 | 0.30971 | 17.93 | 0.05315 | -0.16043 | -0.59831 | -0.10728 | 29 | 100 | 166065.6394 | -647.8721 | -0.39013
24 | Training Building | 1959-pre | boiler_reset | 3699.8929 | 3699.8929 | 0 | 321.7821 | 3.0511 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.3469 | 0.74477 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 194.493 | -1.4197 | 32.1289 | 17.93 | 3.1508 | -0.16043 | 16.678 | 2.9904 | 65 | 0.083978 | 166065.6394 | 33579.1017 | 20.2204
24 | Training Building | 1959-pre | cooling_cop_3_0 | 3699.8929 | 3699.8929 | 0 | 512.9942 | 2.1795 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.3469 | 0.74477 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 3.2809 | -0.54806 | 0.45476 | 17.93 | 0.05315 | -0.061931 | -0.048974 | -0.008781 | 37 | 100 | 166065.6394 | 110.4612 | 0.066517
24 | Training Building | 1959-pre | dcv_enabled | 3699.8929 | 3699.8929 | 0 | 437.4762 | 3.1517 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.2283 | 0.60813 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 78.7989 | -1.2651 | 12.9022 | 17.93 | 1.2765 | -0.14295 | 6.3223 | 1.1336 | 57 | 8.1336 | 166065.6394 | 13004.4056 | 7.8309
24 | Training Building | 1959-pre | ecm_cold_deck_reset_control | 3699.8929 | 3699.8929 | 0 | 491.5341 | 7.4754 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.3469 | 0.41743 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 24.741 | -5.5167 | 3.1991 | 17.93 | 0.4008 | -0.62338 | -1.2414 | -0.22258 | 25 | 100 | 166065.6394 | -370.8774 | -0.22333
24 | Training Building | 1959-pre | economizers_enabled | 3699.8929 | 3699.8929 | 0 | 512.7472 | 2.5549 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.3469 | 0.74477 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 3.5279 | -0.92345 | 0.4334 | 17.93 | 0.057152 | -0.10435 | -0.26324 | -0.047198 | 36 | 100 | 166065.6394 | -171.9113 | -0.10352
24 | Training Building | 1959-pre | elec_reduce | 3699.8929 | 3699.8929 | 0 | 452.3228 | 1.9107 | 7.7112 | 0 | 26.5706 | 9.2653 | 0 | 27.1945 | 0.49401 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 63.9524 | 11.5116 | 12.5578 | 17.93 | 1.036 | 1.3008 | 13.0331 | 2.3368 | 62 | 23.7984 | 166065.6394 | 21462.5663 | 12.9241
24 | Training Building | 1959-pre | envelope_ecm_roof | 3699.8929 | 3699.8929 | 0 | 466.592 | 2.922 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 24.5863 | 0.75002 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 49.6832 | 1.4648 | 8.5114 | 17.93 | 0.80487 | 0.16552 | 5.4121 | 0.97038 | 54 | 141.4559 | 166065.6394 | 10167.6253 | 6.1227
24 | Training Building | 1959-pre | envelope_ecm_wall | 3699.8929 | 3699.8929 | 0 | 491.5859 | 3.1735 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 26.1156 | 0.74702 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 24.6892 | -0.31307 | 4.0564 | 17.93 | 0.39996 | -0.035377 | 2.0334 | 0.36459 | 44 | 327.8265 | 166065.6394 | 4146.989 | 2.4972
24 | Training Building | 1959-pre | envelope_ecm_windows | 3699.8929 | 3699.8929 | 0 | 504.8679 | 3.0804 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 26.9708 | 0.74176 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 11.4072 | -1.0699 | 1.7202 | 17.93 | 0.1848 | -0.12089 | 0.35641 | 0.063904 | 41 | 679.0164 | 166065.6394 | 1111.1261 | 0.66909
24 | Training Building | 1959-pre | exhaust_fans_occ_control | 3699.8929 | 3699.8929 | 0 | 513.004 | 3.0444 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.3266 | 0.74402 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 3.2711 | -1.3919 | 0.31271 | 17.93 | 0.052992 | -0.15729 | -0.58169 | -0.1043 | 32 | 100 | 166065.6394 | -625.4518 | -0.37663
24 | Training Building | 1959-pre | fans_to_variable | 3699.8929 | 3699.8929 | 0 | 512.9942 | 3.0511 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.3469 | 0.74477 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 3.2809 | -1.4197 | 0.30971 | 17.93 | 0.05315 | -0.16043 | -0.59831 | -0.10728 | 30 | 100 | 166065.6394 | -647.8721 | -0.39013
24 | Training Building | 1959-pre | hrv_enabled | 3699.8929 | 3699.8929 | 0 | 437.7968 | 3.4911 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.3387 | 0.61188 | 1.184 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 78.4783 | -2.9025 | 12.5764 | 17.93 | 1.2713 | -0.32798 | 5.2614 | 0.94337 | 53 | 70.7305 | 166065.6394 | 11522.4523 | 6.9385
24 | Training Building | 1959-pre | infil_reduce | 3699.8929 | 3699.8929 | 0 | 283.6331 | 5.0159 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 16.5598 | 0.65392 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 232.6421 | 7.4935 | 39.9604 | 17.93 | 3.7688 | 0.84676 | 25.7421 | 4.6156 | 67 | 6.6201 | 166065.6394 | 48162.2434 | 29.0019
24 | Training Building | 1959-pre | infil_reduce_plus_setback | 3699.8929 | 3699.8929 | 0 | 241.2009 | 4.3184 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 20.9413 | 0.36863 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 275.0742 | 4.0947 | 46.4559 | 17.93 | 4.4562 | 0.4627 | 27.4339 | 4.9189 | 68 | 7.2853 | 166065.6394 | 52800.6937 | 31.7951
24 | Training Building | 1959-pre | lights_reduce_70p | 3699.8929 | 3699.8929 | 0 | 527.7972 | 1.9355 | 7.7112 | 0 | 26.5706 | 9.2653 | 0 | 27.2501 | 0.76879 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | -11.5221 | 11.1565 | -0.060843 | 17.93 | -0.18666 | 1.2607 | 5.9901 | 1.074 | 56 | 39.1662 | 166065.6394 | 7643.6861 | 4.6028
24 | Training Building | 1959-pre | load_reduce | 3699.8929 | 3699.8929 | 0 | 149.045 | 4.3184 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 20.9413 | 0.36863 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 367.2301 | 4.0947 | 61.7914 | 17.93 | 5.9491 | 0.4627 | 35.7603 | 6.4118 | 69 | 5.589 | 166065.6394 | 69296.5988 | 41.7284
24 | Training Building | 1959-pre | occupancy_setback | 3699.8929 | 3699.8929 | 0 | 460.1316 | 2.4265 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.4768 | 0.60212 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 56.1436 | -0.78231 | 9.2125 | 17.93 | 0.90953 | -0.088401 | 4.5796 | 0.82113 | 49 | 6.43 | 166065.6394 | 9369.0918 | 5.6418
24 | Training Building | 1959-pre | payback_less_than_20 | 3699.8929 | 3699.8929 | 0 | 111.6437 | 8.245 | 7.7112 | 0 | 26.5706 | 9.2653 | 0 | 22.0998 | 0.13589 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 404.6314 | 10.6302 | 69.1028 | 17.93 | 6.555 | 1.2012 | 43.2584 | 7.7562 | 70 | 13.5337 | 166065.6394 | 81677.2921 | 49.1837
24 | Training Building | 1959-pre | plug_loads_90_percent | 3699.8929 | 3699.8929 | 0 | 513.2593 | 2.9168 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.3116 | 0.74552 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 3.0159 | -1.2508 | 0.29372 | 17.93 | 0.048857 | -0.14134 | -0.5158 | -0.092482 | 33 | 100 | 166065.6394 | -548.3474 | -0.3302
24 | Training Building | 1959-pre | pumps_to_variable | 3699.8929 | 3699.8929 | 0 | 512.9942 | 3.0511 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.3469 | 0.74477 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 3.2809 | -1.4197 | 0.30971 | 17.93 | 0.05315 | -0.16043 | -0.59831 | -0.10728 | 31 | 100 | 166065.6394 | -647.8721 | -0.39013
24 | Training Building | 1959-pre | pump_fan_eff_ | 3699.8929 | 3699.8929 | 0 | 512.9942 | 3.0511 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.3469 | 0.5826 | 0 | 0 | 516.2751 | 1.9182 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 27.0496 | 0.75528 | 0 | 600.933 | 3.2809 | -1.2575 | 0.3367 | 17.93 | 0.05315 | -0.1421 | -0.49611 | -0.088952 | 34 | 100 | 166065.6394 | -506.7868 | -0.30517
25 | Training Building | 1980-2004 | air_temp_reset_enabled | 3699.8929 | 3699.8929 | 0 | 320.7963 | 9.2082 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 16.556 | 0.45572 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | -19.1365 | -8.3876 | -7.351 | 13.1096 | -0.31001 | -0.9478 | -9.5946 | -1.2578 | 3 | 100 | 117304.5636 | -10722.6696 | -9.1409
25 | Training Building | 1980-2004 | baseline | 3699.8929 | 3699.8929 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 0 | 0 | 0 | 13.1096 | 0 | 0 | 0 | 0 | 39 | NA | 117304.5636 | 0 | 0
25 | Training Building | 1980-2004 | boiler_eff_upgrade | 3699.8929 | 3699.8929 | 0 | 300.8032 | 3.6946 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 16.556 | 0.70197 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 0.85663 | -3.1202 | -0.60455 | 13.1096 | 0.013877 | -0.35258 | -2.5837 | -0.33871 | 16 | 100 | 117304.5636 | -2561.2481 | -2.1834
25 | Training Building | 1980-2004 | boiler_reset | 3699.8929 | 3699.8929 | 0 | 193.0515 | 3.6946 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 16.556 | 0.70197 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 108.6083 | -3.1202 | 28.1732 | 13.1096 | 1.7595 | -0.35258 | 10.7316 | 1.4069 | 59 | 0.1785 | 117304.5636 | 16726.3068 | 14.2589
25 | Training Building | 1980-2004 | cooling_cop_3_0 | 3699.8929 | 3699.8929 | 0 | 300.8032 | 3.1668 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 16.556 | 0.70197 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 0.85663 | -2.5924 | -0.46358 | 13.1096 | 0.013877 | -0.29294 | -2.1287 | -0.27907 | 22 | 100 | 117304.5636 | -2102.0678 | -1.792
25 | Training Building | 1980-2004 | dcv_enabled | 3699.8929 | 3699.8929 | 0 | 225.6816 | 3.913 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 16.4367 | 0.40467 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 75.9782 | -2.922 | 19.5115 | 13.1096 | 1.2308 | -0.33019 | 6.8702 | 0.90066 | 52 | 10.2371 | 117304.5636 | 11057.9566 | 9.4267
25 | Training Building | 1980-2004 | ecm_cold_deck_reset_control | 3699.8929 | 3699.8929 | 0 | 286.0956 | 5.9018 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 16.556 | 0.26502 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 15.5643 | -4.8905 | 2.8507 | 13.1096 | 0.25214 | -0.55263 | -2.2921 | -0.30049 | 20 | 100 | 117304.5636 | -1468.7607 | -1.2521
25 | Training Building | 1980-2004 | economizers_enabled | 3699.8929 | 3699.8929 | 0 | 300.4481 | 2.5804 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 16.556 | 0.70122 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 1.2117 | -2.0053 | -0.21194 | 13.1096 | 0.01963 | -0.2266 | -1.5788 | -0.20697 | 26 | 100 | 117304.5636 | -1527.7211 | -1.3024
25 | Training Building | 1980-2004 | elec_reduce | 3699.8929 | 3699.8929 | 0 | 238.3307 | 2.1878 | 7.7112 | 0 | 26.5706 | 9.2653 | 0 | 15.6213 | 0.47224 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 63.3292 | 10.9388 | 19.8351 | 13.1096 | 1.0259 | 1.2361 | 17.2547 | 2.262 | 61 | 25.3804 | 117304.5636 | 20852.6533 | 17.7765
25 | Training Building | 1980-2004 | envelope_ecm_roof | 3699.8929 | 3699.8929 | 0 | 275.6989 | 3.8087 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.3533 | 0.68846 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 25.961 | -2.0181 | 6.3945 | 13.1096 | 0.42057 | -0.22804 | 1.4686 | 0.19253 | 42 | 712.9805 | 117304.5636 | 2891.288 | 2.4648
25 | Training Building | 1980-2004 | envelope_ecm_wall | 3699.8929 | 3699.8929 | 0 | 293.1198 | 3.8079 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 16.2302 | 0.69822 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 8.54 | -2.904 | 1.5052 | 13.1096 | 0.13835 | -0.32815 | -1.4478 | -0.1898 | 28 | 100 | 117304.5636 | -997.8037 | -0.85061
25 | Training Building | 1980-2004 | envelope_ecm_windows | 3699.8929 | 3699.8929 | 0 | 295.1109 | 3.7816 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 16.4172 | 0.69296 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 6.549 | -3.0594 | 0.93198 | 13.1096 | 0.10609 | -0.34571 | -1.8278 | -0.23962 | 24 | 100 | 117304.5636 | -1489.4084 | -1.2697
25 | Training Building | 1980-2004 | exhaust_fans_occ_control | 3699.8929 | 3699.8929 | 0 | 300.6253 | 3.6878 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 16.5358 | 0.70122 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 1.0346 | -3.0924 | -0.5496 | 13.1096 | 0.01676 | -0.34945 | -2.5377 | -0.33269 | 18 | 100 | 117304.5636 | -2505.2307 | -2.1357
25 | Training Building | 1980-2004 | fans_to_variable | 3699.8929 | 3699.8929 | 0 | 303.2433 | 3.675 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.1589 | 0.47449 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | -1.5834 | -1.476 | -0.81709 | 13.1096 | -0.025651 | -0.16679 | -1.4679 | -0.19244 | 27 | 100 | 117304.5636 | -1567.5624 | -1.3363
25 | Training Building | 1980-2004 | hrv_enabled | 3699.8929 | 3699.8929 | 0 | 227.705 | 4.4476 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 16.5478 | 0.42794 | 1.1832 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 73.9549 | -4.7742 | 18.4764 | 13.1096 | 1.1981 | -0.53948 | 5.0237 | 0.65859 | 47 | 101.3149 | 117304.5636 | 9084.4031 | 7.7443
25 | Training Building | 1980-2004 | infil_reduce | 3699.8929 | 3699.8929 | 0 | 233.5933 | 4.3793 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.0507 | 0.52104 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 68.0666 | -2.1187 | 17.613 | 13.1096 | 1.1027 | -0.23941 | 6.585 | 0.86327 | 51 | 31.5528 | 117304.5636 | 10340.6664 | 8.8152
25 | Training Building | 1980-2004 | infil_reduce_plus_setback | 3699.8929 | 3699.8929 | 0 | 197.3137 | 4.0872 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 17.9532 | 0.33259 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 104.3462 | -4.5407 | 26.6555 | 13.1096 | 1.6904 | -0.5131 | 8.9805 | 1.1773 | 58 | 27.6209 | 117304.5636 | 14727.5815 | 12.555
25 | Training Building | 1980-2004 | lights_reduce_70p | 3699.8929 | 3699.8929 | 0 | 311.9537 | 2.145 | 7.7112 | 0 | 26.5706 | 9.2653 | 0 | 15.758 | 0.75378 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | -10.2938 | 10.5634 | 0.071984 | 13.1096 | -0.16676 | 1.1937 | 7.8332 | 1.0269 | 55 | 40.9635 | 117304.5636 | 7347.5391 | 6.2636
25 | Training Building | 1980-2004 | load_reduce | 3699.8929 | 3699.8929 | 0 | 122.6666 | 4.0872 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 17.9532 | 0.33259 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 178.9933 | -4.5407 | 46.5919 | 13.1096 | 2.8997 | -0.5131 | 18.205 | 2.3866 | 63 | 13.6254 | 117304.5636 | 28089.4151 | 23.9457
25 | Training Building | 1980-2004 | occupancy_setback | 3699.8929 | 3699.8929 | 0 | 257.6263 | 3.1427 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 21.2514 | 0.39341 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 44.0336 | -6.9552 | 9.9027 | 13.1096 | 0.71334 | -0.78593 | -0.55371 | -0.072589 | 35 | 100 | 117304.5636 | 1831.0222 | 1.5609
25 | Training Building | 1980-2004 | payback_less_than_20 | 3699.8929 | 3699.8929 | 0 | 84.4169 | 6.3508 | 7.7112 | 0 | 26.5706 | 9.2653 | 0 | 18.3121 | 0.11637 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 217.2429 | 4.4408 | 59.2061 | 13.1096 | 3.5193 | 0.50181 | 30.6734 | 4.0211 | 66 | 25.2798 | 117304.5636 | 42750.0036 | 36.4436
25 | Training Building | 1980-2004 | plug_loads_90_percent | 3699.8929 | 3699.8929 | 0 | 300.3821 | 3.4926 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 16.3616 | 0.70648 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 1.2778 | -2.7283 | -0.38739 | 13.1096 | 0.020701 | -0.3083 | -2.1938 | -0.2876 | 21 | 100 | 117304.5636 | -2144.9001 | -1.8285
25 | Training Building | 1980-2004 | pumps_to_variable | 3699.8929 | 3699.8929 | 0 | 300.8032 | 3.6946 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 16.556 | 0.70197 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 0.85663 | -3.1202 | -0.60455 | 13.1096 | 0.013877 | -0.35258 | -2.5837 | -0.33871 | 17 | 100 | 117304.5636 | -2561.2481 | -2.1834
25 | Training Building | 1980-2004 | pump_fan_eff_ | 3699.8929 | 3699.8929 | 0 | 300.8032 | 3.6946 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 16.556 | 0.54882 | 0 | 0 | 301.6599 | 1.8559 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.2317 | 0.74477 | 0 | 374.4271 | 0.85663 | -2.9671 | -0.56364 | 13.1096 | 0.013877 | -0.33528 | -2.4516 | -0.3214 | 19 | 100 | 117304.5636 | -2428.0009 | -2.0698
26 | Training Building | 2005-2014 | air_temp_reset_enabled | 3699.8929 | 3699.8929 | 0 | 235.3659 | 7.4251 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 13.5147 | 0.37013 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | -26.8454 | -9.3389 | -13.1375 | 10.9384 | -0.4349 | -1.0553 | -13.6235 | -1.4902 | 2 | 100 | 95533.2914 | -12930.1391 | -13.5347
26 | Training Building | 2005-2014 | baseline | 3699.8929 | 3699.8929 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | 0 | 0 | 0 | 10.9384 | 0 | 0 | 0 | 0 | 40 | NA | 95533.2914 | 0 | 0
26 | Training Building | 2005-2014 | boiler_eff_upgrade | 3699.8929 | 3699.8929 | 0 | 210.3081 | 3.8192 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 13.5147 | 0.45797 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | -1.7876 | -5.8207 | -2.7624 | 10.9384 | -0.028959 | -0.65774 | -6.2779 | -0.6867 | 4 | 100 | 95533.2914 | -5384.0258 | -5.6358
26 | Training Building | 2005-2014 | boiler_reset | 3699.8929 | 3699.8929 | 0 | 132.5618 | 3.8192 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 13.5147 | 0.45797 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | 75.9587 | -5.8207 | 25.4652 | 10.9384 | 1.2305 | -0.65774 | 5.2365 | 0.57279 | 45 | 0.43842 | 95533.2914 | 8532.5631 | 8.9315
26 | Training Building | 2005-2014 | cooling_cop_3_0 | 3699.8929 | 3699.8929 | 0 | 210.3081 | 3.8192 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 13.5147 | 0.45797 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | -1.7876 | -5.8207 | -2.7624 | 10.9384 | -0.028959 | -0.65774 | -6.2779 | -0.6867 | 5 | 100 | 95533.2914 | -5384.0258 | -5.6358
26 | Training Building | 2005-2014 | dcv_enabled | 3699.8929 | 3699.8929 | 0 | 132.5377 | 4.1548 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 13.4028 | 0.22523 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | 75.9827 | -5.8117 | 25.4772 | 10.9384 | 1.2309 | -0.65673 | 5.2493 | 0.57419 | 46 | 16.0576 | 95533.2914 | 8544.7016 | 8.9442
26 | Training Building | 2005-2014 | ecm_cold_deck_reset_control | 3699.8929 | 3699.8929 | 0 | 200.6914 | 5.2772 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 13.5147 | 0.18995 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | 7.8291 | -7.0107 | 0.29712 | 10.9384 | 0.12683 | -0.79221 | -6.083 | -0.66538 | 9 | 100 | 95533.2914 | -4697.9235 | -4.9176
26 | Training Building | 2005-2014 | economizers_enabled | 3699.8929 | 3699.8929 | 0 | 209.8959 | 2.3867 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 13.5147 | 0.45797 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | -1.3754 | -4.3883 | -2.0926 | 10.9384 | -0.022282 | -0.49587 | -4.737 | -0.51816 | 14 | 100 | 95533.2914 | -4063.9933 | -4.254
26 | Training Building | 2005-2014 | elec_reduce | 3699.8929 | 3699.8929 | 0 | 147.9166 | 2.5128 | 7.7112 | 0 | 26.5706 | 9.2653 | 0 | 10.9162 | 0.40317 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | 60.6039 | 9.5266 | 25.4625 | 10.9384 | 0.98178 | 1.0765 | 18.8171 | 2.0583 | 60 | 27.8925 | 95533.2914 | 19136.2059 | 20.0309
26 | Training Building | 2005-2014 | envelope_ecm_roof | 3699.8929 | 3699.8929 | 0 | 195.8452 | 3.868 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 13.0252 | 0.42344 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | 12.6753 | -5.3455 | 2.6613 | 10.9384 | 0.20534 | -0.60404 | -3.645 | -0.3987 | 15 | 0 | 95533.2914 | -2381.7097 | -2.4931
26 | Training Building | 2005-2014 | envelope_ecm_wall | 3699.8929 | 3699.8929 | 0 | 205.9693 | 3.8462 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 13.4651 | 0.44371 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | 2.5511 | -5.784 | -1.1738 | 10.9384 | 0.041328 | -0.65359 | -5.5973 | -0.61226 | 11 | 0 | 95533.2914 | -4575.3899 | -4.7893
26 | Training Building | 2005-2014 | envelope_ecm_windows | 3699.8929 | 3699.8929 | 0 | 204.2478 | 3.8875 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 13.5019 | 0.4362 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | 4.2726 | -5.8545 | -0.57434 | 10.9384 | 0.069217 | -0.66156 | -5.4153 | -0.59234 | 12 | 100 | 95533.2914 | -4328.6355 | -4.531
26 | Training Building | 2005-2014 | exhaust_fans_occ_control | 3699.8929 | 3699.8929 | 0 | 210.2172 | 3.8312 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 13.4944 | 0.45797 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | -1.6967 | -5.8125 | -2.7264 | 10.9384 | -0.027487 | -0.65681 | -6.2559 | -0.6843 | 7 | 100 | 95533.2914 | -5360.5799 | -5.6112
26 | Training Building | 2005-2014 | fans_to_variable | 3699.8929 | 3699.8929 | 0 | 211.1151 | 3.7974 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 12.7301 | 0.29355 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | -2.5947 | -4.85 | -2.703 | 10.9384 | -0.042034 | -0.54805 | -5.3946 | -0.59008 | 13 | 100 | 95533.2914 | -4683.9411 | -4.9029
26 | Training Building | 2005-2014 | hrv_enabled | 3699.8929 | 3699.8929 | 0 | 137.1482 | 4.9108 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 13.5072 | 0.241 | 1.1825 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | 71.3722 | -7.8704 | 23.0559 | 10.9384 | 1.1562 | -0.88935 | 2.4398 | 0.26688 | 43 | 250.0178 | 95533.2914 | 5928.4233 | 6.2056
26 | Training Building | 2005-2014 | lights_reduce_70p | 3699.8929 | 3699.8929 | 0 | 220.2385 | 2.3522 | 7.7112 | 0 | 26.5706 | 9.2653 | 0 | 11.1873 | 0.65017 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | -11.7181 | 9.1692 | -0.92543 | 10.9384 | -0.18983 | 1.0361 | 7.7368 | 0.84629 | 50 | 49.706 | 95533.2914 | 5879.6629 | 6.1546
26 | Training Building | 2005-2014 | load_reduce | 3699.8929 | 3699.8929 | 0 | 108.1076 | 3.5151 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.6746 | 0.29505 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | 100.4129 | -7.5137 | 33.7292 | 10.9384 | 1.6267 | -0.84905 | 7.1092 | 0.77764 | 48 | 6.7896 | 95533.2914 | 11436.9573 | 11.9717
26 | Training Building | 2005-2014 | occupancy_setback | 3699.8929 | 3699.8929 | 0 | 173.1876 | 3.5151 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 15.6746 | 0.29505 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | 35.3329 | -7.5137 | 10.1004 | 10.9384 | 0.57239 | -0.84905 | -2.5293 | -0.27666 | 23 | 100 | 95533.2914 | -212.3652 | -0.22229
26 | Training Building | 2005-2014 | payback_less_than_20 | 3699.8929 | 3699.8929 | 0 | 71.8077 | 5.0722 | 7.7112 | 0 | 26.5706 | 9.2653 | 0 | 15.1739 | 0.10811 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | 136.7128 | 3.0046 | 50.7277 | 10.9384 | 2.2147 | 0.33952 | 23.3514 | 2.5543 | 64 | 29.1337 | 95533.2914 | 27085.5834 | 28.352
26 | Training Building | 2005-2014 | plug_loads_90_percent | 3699.8929 | 3699.8929 | 0 | 210.0168 | 3.651 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 13.2114 | 0.47073 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | -1.4963 | -5.362 | -2.4901 | 10.9384 | -0.02424 | -0.60591 | -5.7609 | -0.63015 | 10 | 100 | 95533.2914 | -4932.7946 | -5.1634
26 | Training Building | 2005-2014 | pumps_to_variable | 3699.8929 | 3699.8929 | 0 | 210.3081 | 3.8192 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 13.5147 | 0.45797 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | -1.7876 | -5.8207 | -2.7624 | 10.9384 | -0.028959 | -0.65774 | -6.2779 | -0.6867 | 6 | 100 | 95533.2914 | -5384.0258 | -5.6358
26 | Training Building | 2005-2014 | pump_fan_eff_ | 3699.8929 | 3699.8929 | 0 | 210.3081 | 3.8192 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 13.5147 | 0.35812 | 0 | 0 | 208.5205 | 1.7666 | 7.7112 | 0 | 37.9583 | 9.2653 | 0 | 9.492 | 0.71248 | 0 | 275.4264 | -1.7876 | -5.7209 | -2.7261 | 10.9384 | -0.028959 | -0.64646 | -6.1748 | -0.67542 | 8 | 100 | 95533.2914 | -5297.1538 | -5.5448
27 | Vehicle Garage | 1959-pre | air_temp_reset_enabled | 2270 | 3744.5971 | 0 | 117.9902 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 8.3638 | 7.6052 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 3.2558 | -1.2506 | 1.3431 | 5.133 | 0.052743 | -0.14132 | -1.7256 | -0.088573 | 2 | 100 | 46100.1604 | -505.2315 | -1.0959
27 | Vehicle Garage | 1959-pre | baseline | 2270 | 3744.5971 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 0 | 0 | 0 | 5.133 | 0 | 0 | 0 | 0 | 4 | NA | 46100.1604 | 0 | 0
27 | Vehicle Garage | 1959-pre | boiler_eff_upgrade | 2270 | 3744.5971 | 0 | 117.8584 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.1442 | 7.6002 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 3.3875 | -0.026082 | 2.2516 | 5.133 | 0.054878 | -0.0029473 | 1.0117 | 0.051931 | 16 | 554.2144 | 46100.1604 | 583.6742 | 1.2661
27 | Vehicle Garage | 1959-pre | boiler_reset | 2270 | 3744.5971 | 0 | 72.8512 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.1442 | 7.6002 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 48.3948 | -0.026082 | 32.3994 | 5.133 | 0.784 | -0.0029473 | 15.2162 | 0.78105 | 37 | 0.52405 | 46100.1604 | 8639.9722 | 18.7417
27 | Vehicle Garage | 1959-pre | dcv_enabled | 2270 | 3744.5971 | 0 | 102.1462 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.1276 | 7.6002 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 19.0997 | -0.0094435 | 12.7875 | 5.133 | 0.30942 | -0.0010671 | 6.0072 | 0.30835 | 31 | 12.1368 | 46100.1604 | 3410.6296 | 7.3983
27 | Vehicle Garage | 1959-pre | ecm_cold_deck_reset_control | 2270 | 3744.5971 | 0 | 117.8584 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.1442 | 7.6002 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 3.3875 | -0.026082 | 2.2516 | 5.133 | 0.054878 | -0.0029473 | 1.0117 | 0.051931 | 17 | 76.718 | 46100.1604 | 583.6742 | 1.2661
27 | Vehicle Garage | 1959-pre | economizers_enabled | 2270 | 3744.5971 | 0 | 118.0536 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.1451 | 7.4595 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 3.1924 | 0.11377 | 2.2146 | 5.133 | 0.051716 | 0.012856 | 1.258 | 0.064572 | 21 | 23.9971 | 46100.1604 | 670.4122 | 1.4543
27 | Vehicle Garage | 1959-pre | elec_reduce | 2270 | 3744.5971 | 0 | 106.8325 | 0 | 0.74873 | 0 | 7.2414 | 2.2309 | 0 | 7.1083 | 5.9611 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 14.4135 | 4.7523 | 12.8381 | 5.133 | 0.2335 | 0.53701 | 15.0109 | 0.77051 | 36 | 27.0337 | 46100.1604 | 6714.536 | 14.5651
27 | Vehicle Garage | 1959-pre | envelope_ecm_roof | 2270 | 3744.5971 | 0 | 115.5209 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 6.9653 | 7.4203 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 5.725 | 0.33277 | 4.0578 | 5.133 | 0.092745 | 0.037603 | 2.5394 | 0.13035 | 24 | 1171.3729 | 46100.1604 | 1314.2868 | 2.8509
27 | Vehicle Garage | 1959-pre | envelope_ecm_wall | 2270 | 3744.5971 | 0 | 111.0991 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 6.7121 | 7.1047 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 10.1468 | 0.90163 | 7.4007 | 5.133 | 0.16438 | 0.10188 | 5.1873 | 0.26626 | 28 | 610.8266 | 46100.1604 | 2600.6965 | 5.6414
27 | Vehicle Garage | 1959-pre | envelope_ecm_windows | 2270 | 3744.5971 | 0 | 117.7397 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.1379 | 7.5935 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 3.5062 | -0.013041 | 2.3399 | 5.133 | 0.056801 | -0.0014736 | 1.0779 | 0.055327 | 18 | 34.5081 | 46100.1604 | 616.2704 | 1.3368
27 | Vehicle Garage | 1959-pre | exhaust_fans_occ_control | 2270 | 3744.5971 | 0 | 117.8584 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.0781 | 7.6002 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 3.3875 | 0.040022 | 2.2959 | 5.133 | 0.054878 | 0.0045225 | 1.1572 | 0.0594 | 20 | 5.429 | 46100.1604 | 641.185 | 1.3909
27 | Vehicle Garage | 1959-pre | fans_to_variable | 2270 | 3744.5971 | 0 | 117.9722 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.0777 | 7.6002 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 3.2737 | 0.040472 | 2.22 | 5.133 | 0.053035 | 0.0045734 | 1.1223 | 0.057608 | 19 | 23.1638 | 46100.1604 | 621.2111 | 1.3475
27 | Vehicle Garage | 1959-pre | hrv_enabled | 2270 | 3744.5971 | 0 | 104.8975 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.1199 | 7.6016 | 2.127 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 16.3485 | -2.1302 | 9.524 | 5.133 | 0.26485 | -0.24071 | 0.47019 | 0.024135 | 12 | 2904.1238 | 46100.1604 | 1073.1207 | 2.3278
27 | Vehicle Garage | 1959-pre | infil_reduce | 2270 | 3744.5971 | 0 | 74.2834 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.474 | 4.8886 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 46.9625 | 5.3558 | 35.0451 | 5.133 | 0.76079 | 0.60521 | 26.6121 | 1.366 | 40 | 21.0555 | 46100.1604 | 13065.8441 | 28.3423
27 | Vehicle Garage | 1959-pre | infil_reduce_plus_setback | 2270 | 3744.5971 | 0 | 67.7904 | 0 | 0.74918 | 0 | 10.3447 | 2.2309 | 0 | 5.283 | 0.070152 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 53.4556 | 9.3648 | 42.0798 | 5.133 | 0.86598 | 1.0582 | 37.4868 | 1.9242 | 42 | 16.0383 | 46100.1604 | 17715.9254 | 38.4292
27 | Vehicle Garage | 1959-pre | lights_reduce_70p | 2270 | 3744.5971 | 0 | 122.5136 | 0 | 0.74873 | 0 | 7.2414 | 2.2309 | 0 | 7.1703 | 7.6191 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | -1.2677 | 3.0323 | 1.182 | 5.133 | -0.020536 | 0.34265 | 6.2753 | 0.32211 | 32 | 34.7353 | 46100.1604 | 2411.1534 | 5.2302
27 | Vehicle Garage | 1959-pre | load_reduce | 2270 | 3744.5971 | 0 | 42.6122 | 0 | 0.74918 | 0 | 10.3447 | 2.2309 | 0 | 5.283 | 0.070152 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 78.6337 | 9.3648 | 58.9452 | 5.133 | 1.2739 | 1.0582 | 45.4332 | 2.3321 | 43 | 13.4087 | 46100.1604 | 22222.8158 | 48.2055
27 | Vehicle Garage | 1959-pre | occupancy_setback | 2270 | 3744.5971 | 0 | 99.8964 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 8.322 | 8.6183 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 21.3495 | -2.2219 | 12.8125 | 5.133 | 0.34586 | -0.25108 | 1.8466 | 0.094785 | 23 | 22.1464 | 46100.1604 | 1888.4896 | 4.0965
27 | Vehicle Garage | 1959-pre | payback_less_than_20 | 2270 | 3744.5971 | 0 | 32.733 | 0 | 0.74873 | 0 | 7.2414 | 2.2309 | 0 | 5.2092 | 4.2518 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 88.513 | 8.3606 | 64.8902 | 5.133 | 1.4339 | 0.94475 | 46.3405 | 2.3787 | 44 | 24.114 | 46100.1604 | 23117.583 | 50.1464
27 | Vehicle Garage | 1959-pre | plug_loads_90_percent | 2270 | 3744.5971 | 0 | 117.9592 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.1573 | 7.6029 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 3.2868 | -0.041821 | 2.1736 | 5.133 | 0.053246 | -0.0047258 | 0.94526 | 0.04852 | 14 | 25.0165 | 46100.1604 | 551.9503 | 1.1973
27 | Vehicle Garage | 1959-pre | pump_fan_eff_ | 2270 | 3744.5971 | 0 | 117.8584 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.1442 | 5.944 | 0 | 0 | 121.2459 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 7.151 | 7.5674 | 0 | 149.2886 | 3.3875 | 1.6301 | 3.361 | 5.133 | 0.054878 | 0.1842 | 4.6577 | 0.23908 | 27 | 5.9911 | 46100.1604 | 2024.5762 | 4.3917
28 | Vehicle Garage | 1980-2004 | air_temp_reset_enabled | 2270 | 3744.5971 | 0 | 83.0061 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 5.6531 | 5.2938 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | -0.079145 | -0.82968 | -0.85441 | 3.9923 | -0.0012822 | -0.093754 | -2.3805 | -0.095036 | 1 | 100 | 35237.987 | -735.9874 | -2.0886
28 | Vehicle Garage | 1980-2004 | baseline | 2270 | 3744.5971 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 0 | 0 | 0 | 3.9923 | 0 | 0 | 0 | 0 | 5 | NA | 35237.987 | 0 | 0
28 | Vehicle Garage | 1980-2004 | boiler_eff_upgrade | 2270 | 3744.5971 | 0 | 81.6458 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8778 | 5.2866 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 1.2812 | -0.047217 | 1.1601 | 3.9923 | 0.020755 | -0.0053356 | 0.38623 | 0.015419 | 7 | 940.6146 | 35237.987 | 188.2498 | 0.53422
28 | Vehicle Garage | 1980-2004 | boiler_reset | 2270 | 3744.5971 | 0 | 50.7192 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8778 | 5.2866 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 32.2077 | -0.047217 | 30.235 | 3.9923 | 0.52177 | -0.0053356 | 12.9356 | 0.51643 | 34 | 0.79257 | 35237.987 | 5724.1022 | 16.2441
28 | Vehicle Garage | 1980-2004 | dcv_enabled | 2270 | 3744.5971 | 0 | 66.2533 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8391 | 5.2866 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 16.6736 | -0.0085441 | 15.6673 | 3.9923 | 0.27011 | -0.00096548 | 6.7417 | 0.26915 | 29 | 13.9045 | 35237.987 | 2977.1439 | 8.4487
28 | Vehicle Garage | 1980-2004 | ecm_cold_deck_reset_control | 2270 | 3744.5971 | 0 | 81.6458 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8778 | 5.2866 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 1.2812 | -0.047217 | 1.1601 | 3.9923 | 0.020755 | -0.0053356 | 0.38623 | 0.015419 | 8 | 258.3771 | 35237.987 | 188.2498 | 0.53422
28 | Vehicle Garage | 1980-2004 | economizers_enabled | 2270 | 3744.5971 | 0 | 81.8679 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8782 | 5.1301 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 1.059 | 0.10883 | 1.0979 | 3.9923 | 0.017156 | 0.012297 | 0.73775 | 0.029453 | 13 | 52.6103 | 35237.987 | 284.2425 | 0.80664
28 | Vehicle Garage | 1980-2004 | elec_reduce | 2270 | 3744.5971 | 0 | 70.6891 | 0 | 0.74873 | 0 | 7.2414 | 2.2309 | 0 | 4.8225 | 4.1551 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 12.2379 | 4.2428 | 15.494 | 3.9923 | 0.19825 | 0.47944 | 16.975 | 0.67769 | 35 | 28.1613 | 35237.987 | 5881.8391 | 16.6918
28 | Vehicle Garage | 1980-2004 | envelope_ecm_roof | 2270 | 3744.5971 | 0 | 79.4769 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.7258 | 5.1269 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 3.45 | 0.26442 | 3.4921 | 3.9923 | 0.05589 | 0.029879 | 2.1484 | 0.08577 | 22 | 1780.192 | 35237.987 | 847.5978 | 2.4054
28 | Vehicle Garage | 1980-2004 | envelope_ecm_wall | 2270 | 3744.5971 | 0 | 77.6714 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.6152 | 4.9907 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 5.2555 | 0.5113 | 5.4216 | 3.9923 | 0.08514 | 0.057777 | 3.5798 | 0.14292 | 25 | 1138.0104 | 35237.987 | 1385.5691 | 3.932
28 | Vehicle Garage | 1980-2004 | envelope_ecm_windows | 2270 | 3744.5971 | 0 | 81.5536 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8737 | 5.2816 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 1.3734 | -0.038224 | 1.2552 | 3.9923 | 0.022248 | -0.0043193 | 0.44909 | 0.017929 | 9 | 106.4887 | 35237.987 | 212.5758 | 0.60326
28 | Vehicle Garage | 1980-2004 | exhaust_fans_occ_control | 2270 | 3744.5971 | 0 | 81.6458 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8117 | 5.2866 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 1.2812 | 0.018887 | 1.2222 | 3.9923 | 0.020755 | 0.0021342 | 0.57333 | 0.022889 | 11 | 14.089 | 35237.987 | 245.7607 | 0.69743
28 | Vehicle Garage | 1980-2004 | fans_to_variable | 2270 | 3744.5971 | 0 | 81.7213 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8319 | 5.2866 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 1.2056 | -0.0013491 | 1.1322 | 3.9923 | 0.019531 | -0.00015244 | 0.4854 | 0.019379 | 10 | 68.8604 | 35237.987 | 214.6322 | 0.60909
28 | Vehicle Garage | 1980-2004 | hrv_enabled | 2270 | 3744.5971 | 0 | 68.8813 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8441 | 5.2938 | 2.127 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 14.0456 | -2.1477 | 11.1856 | 3.9923 | 0.22754 | -0.24269 | -0.37956 | -0.015153 | 3 | 100 | 35237.987 | 645.65 | 1.8323
28 | Vehicle Garage | 1980-2004 | infil_reduce | 2270 | 3744.5971 | 0 | 67.5606 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.0211 | 4.4034 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 15.3664 | 1.6926 | 16.0377 | 3.9923 | 0.24894 | 0.19127 | 11.0263 | 0.4402 | 33 | 60.3748 | 35237.987 | 4223.1714 | 11.9847
28 | Vehicle Garage | 1980-2004 | infil_reduce_plus_setback | 2270 | 3744.5971 | 0 | 61.2118 | 0 | 0.74918 | 0 | 10.3447 | 2.2309 | 0 | 4.7667 | 0.064306 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 21.7151 | 5.2857 | 25.3842 | 3.9923 | 0.35178 | 0.59728 | 23.7724 | 0.94906 | 38 | 30.2153 | 35237.987 | 8485.5256 | 24.0806
28 | Vehicle Garage | 1980-2004 | lights_reduce_70p | 2270 | 3744.5971 | 0 | 86.1211 | 0 | 0.74873 | 0 | 7.2414 | 2.2309 | 0 | 4.912 | 5.3099 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | -3.1942 | 2.9985 | -0.1839 | 3.9923 | -0.051745 | 0.33883 | 7.1911 | 0.28709 | 30 | 38.9725 | 35237.987 | 2036.9724 | 5.7806
28 | Vehicle Garage | 1980-2004 | load_reduce | 2270 | 3744.5971 | 0 | 38.5956 | 0 | 0.74918 | 0 | 10.3447 | 2.2309 | 0 | 4.7667 | 0.064306 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 44.3314 | 5.2857 | 46.6464 | 3.9923 | 0.71817 | 0.59728 | 32.9496 | 1.3154 | 39 | 22.1108 | 35237.987 | 12533.8385 | 35.5691
28 | Vehicle Garage | 1980-2004 | occupancy_setback | 2270 | 3744.5971 | 0 | 68.3781 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 5.7367 | 6.0214 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 14.5488 | -1.6409 | 12.1351 | 3.9923 | 0.23569 | -0.18542 | 1.2591 | 0.050267 | 15 | 41.7597 | 35237.987 | 1176.6402 | 3.3391
28 | Vehicle Garage | 1980-2004 | payback_less_than_20 | 2270 | 3744.5971 | 0 | 29.1408 | 0 | 0.74873 | 0 | 7.2414 | 2.2309 | 0 | 4.6876 | 3.8381 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 53.7861 | 4.6948 | 54.9796 | 3.9923 | 0.87133 | 0.53051 | 35.1137 | 1.4018 | 41 | 39.3584 | 35237.987 | 13712.1597 | 38.913
28 | Vehicle Garage | 1980-2004 | plug_loads_90_percent | 2270 | 3744.5971 | 0 | 81.7604 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8769 | 5.2902 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 1.1665 | -0.049916 | 1.0497 | 3.9923 | 0.018897 | -0.0056405 | 0.33206 | 0.013257 | 6 | 91.5612 | 35237.987 | 165.3763 | 0.46931
28 | Vehicle Garage | 1980-2004 | pump_fan_eff_ | 2270 | 3744.5971 | 0 | 81.6458 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8778 | 4.1345 | 0 | 0 | 82.9269 | 0 | 0.74873 | 0 | 10.3447 | 2.2309 | 0 | 4.8652 | 5.2519 | 0 | 106.3684 | 1.2812 | 1.1049 | 2.2432 | 3.9923 | 0.020755 | 0.12485 | 3.6472 | 0.14561 | 26 | 9.8371 | 35237.987 | 1190.5824 | 3.3787
Note on AN1: Lubun, Mike: includes gas space heating

## base_building_arch_areas
baseline_id | Type | Arch | Vintage | scenario_year | Total Area (m2) | Space DES Area (m2) | Space Gas Area (m2) | Space Elec Area (m2) | Water DES Area (m2) | Water Gas Area (m2) | Water Elec Area (m2) | Total Area Percentage | Area Used to Apply ECMS (m2) | Year | Total Area (m2) | DES Area (m2) | Gas/Propane Area (m2) | Elec Area (m2)
5 | 1A | Hangar | 1959-pre | 2015 | 62176 | 62176 | 0 | 0 | 0 | 0 | 0 | 0.26866 | 21679 | 2015 | 231427 | 139442 | 90255 | 1730
6 | 1A | Hangar | 1960-1979 | 2015 | 6231 | 0 | 6231 | 0 | 0 | 0 | 0 | 0.026924 | 6231 | 2018 | 231983 | 139499 | 91267 | 1217
7 | 1A | Hangar | 1980-2004 | 2015 | 7269 | 0 | 7269 | 0 | 0 | 0 | 0 | 0.031409 | 7269 | 2020 | 224290 | 138091 | 84982 | 1217
24 | 2A | Training Building | 1959-pre | 2015 | 6832 | 3118 | 3714 | 0 | 0 | 0 | 0 | 0.029521 | 6832 | 2023 | 202852 | 108609 | 93026 | 1217
25 | 2A | Training Building | 1980-2004 | 2015 | 4831 | 4831 | 0 | 0 | 0 | 0 | 0 | 0.020875 | 4831 | 2025 | 197069 | 102443 | 93409 | 1217
26 | 2A | Training Building | 2005-2014 | 2015 | 1869 | 0 | 1869 | 0 | 0 | 0 | 0 | 0.008076 | 1869 | 2028 | 197069 | 102443 | 93409 | 1217
20 | 3B | Storage Building | 1959-pre | 2015 | 330 | 249 | 81 | 0 | 0 | 0 | 0 | 0.0014259 | 330 | 2030 | 197069 | 102443 | 93409 | 1217
21 | 3B | Storage Building | 1960-1979 | 2015 | 832 | 326 | 506 | 0 | 0 | 0 | 0 | 0.0035951 | 832 | 2033 | 197069 | 102443 | 93409 | 1217
22 | 3B | Storage Building | 1980-2004 | 2015 | 10124 | 1376 | 8006 | 742 | 0 | 0 | 0 | 0.043746 | 8824 | 2035 | 197069 | 102443 | 93409 | 1217
23 | 3B | Storage Building | 2005-2014 | 2015 | 501 | 0 | 428 | 73 | 0 | 0 | 0 | 0.0021648 | 501
1 | 4C | Barracks | 1959-pre | 2015 | 20067 | 20067 | 0 | 0 | 0 | 0 | 0 | 0.08671 | 20067
NA | 5E | Recreation Center | 1959-pre | 2015 | 294 | 0 | 294 | 0 | 0 | 0 | 0 | 0.0012704 | 294
NA | 5E | Recreation Center | 1960-1979 | 2015 | 101 | 0 | 101 | 0 | 0 | 0 | 0 | 0.00043642 | 101
19 | 5E | Recreation Center | 1980-2004 | 2015 | 15831 | 0 | 15831 | 0 | 0 | 0 | 0 | 0.068406 | 15831
13 | 6A | Office | 1959-pre | 2015 | 16513 | 10502 | 6011 | 0 | 0 | 0 | 0 | 0.071353 | 11035
14 | 6A | Office | 1960-1979 | 2015 | 3480 | 0 | 3480 | 0 | 0 | 0 | 0 | 0.015037 | 2220
15 | 6A | Office | 1980-2004 | 2015 | 17682 | 11024 | 6658 | 0 | 0 | 0 | 0 | 0.076404 | 17682
16 | 6B | Office-Small | 1960-1979 | 2015 | 1148 | 0 | 1136 | 12 | 0 | 0 | 0 | 0.0049605 | 815
17 | 6B | Office-Small | 1980-2004 | 2015 | 4356 | 0 | 3453 | 903 | 0 | 0 | 0 | 0.018822 | 3259
18 | 6B | Office-Small | 2005-2014 | 2015 | 501 | 0 | 501 | 0 | 0 | 0 | 0 | 0.0021648 | 501
3 | 7A | Food Service | 1959-pre | 2015 | 10012 | 10012 | 0 | 0 | 0 | 0 | 0 | 0.043262 | 0
4 | 7A | Food Service | 2005-2014 | 2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4000
27 | 8B | Vehicle Garage | 1959-pre | 2015 | 5221 | 3443 | 1778 | 0 | 0 | 0 | 0 | 0.02256 | 1778
28 | 8B | Vehicle Garage | 1980-2004 | 2015 | 11811 | 0 | 11811 | 0 | 0 | 0 | 0 | 0.051036 | 11711
8 | 9A | Maintenance Shop | 1959-pre | 2015 | 3983 | 1504 | 2479 | 0 | 0 | 0 | 0 | 0.017211 | 1504
9 | 9A | Maintenance Shop | 1980-2004 | 2015 | 10986 | 7670 | 3316 | 0 | 0 | 0 | 0 | 0.047471 | 10986
10 | 9B | Maintenance Shop-Small | 1959-pre | 2015 | 1564 | 805 | 759 | 0 | 0 | 0 | 0 | 0.0067581 | 1127
11 | 9B | Maintenance Shop-Small | 1960-1979 | 2015 | 724 | 0 | 724 | 0 | 0 | 0 | 0 | 0.0031284 | 724
12 | 9B | Maintenance Shop-Small | 1980-2004 | 2015 | 4869 | 1050 | 3819 | 0 | 0 | 0 | 0 | 0.021039 | 4736
2 | 13B | Fire Hall | 1959-pre | 2015 | 1289 | 1289 | 0 | 0 | 0 | 0 | 0 | 0.0055698 | 0
5 | 1A | Hangar | 1959-pre | 2018 | 56669 | 56669 | 0 | 0 | 0 | 0 | 0 | 0.24428
6 | 1A | Hangar | 1960-1979 | 2018 | 6231 | 0 | 6231 | 0 | 0 | 0 | 0 | 0.02686
7 | 1A | Hangar | 1980-2004 | 2018 | 6551 | 0 | 6551 | 0 | 0 | 0 | 0 | 0.028239
29 | 1A | Hangar | 2005-2014 | 2018 | 6000 | 6000 | 0 | 0 | 0 | 0 |  | 0.025864
24 | 2A | Training Building | 1959-pre | 2018 | 6832 | 3118 | 3714 | 0 | 0 | 0 | 0 | 0.02945
25 | 2A | Training Building | 1980-2004 | 2018 | 4831 | 4831 | 0 | 0 | 0 | 0 | 0 | 0.020825
26 | 2A | Training Building | 2005-2014 | 2018 | 1869 | 0 | 1869 | 0 | 0 | 0 | 0 | 0.0080566
20 | 3B | Storage Building | 1959-pre | 2018 | 330 | 249 | 81 | 0 | 0 | 0 | 0 | 0.0014225
21 | 3B | Storage Building | 1960-1979 | 2018 | 832 | 326 | 506 | 0 | 0 | 0 | 0 | 0.0035865
22 | 3B | Storage Building | 1980-2004 | 2018 | 10125 | 1377 | 8006 | 742 | 0 | 0 | 0 | 0.043645
23 | 3B | Storage Building | 2005-2014 | 2018 | 501 | 0 | 428 | 73 | 0 | 0 | 0 | 0.0021596
1 | 4C | Barracks | 1959-pre | 2018 | 20067 | 20067 | 0 | 0 | 0 | 0 | 0 | 0.086502
| 4C | Barracks | 2005-2014 | 2018 | 5000 | 0 | 5000 | 0 | 0 | 0 | 0 | 0.021553
NA | 5E | Recreation Center | 1959-pre | 2018 | 294 | 0 | 294 | 0 | 0 | 0 | 0 | 0.0012673
NA | 5E | Recreation Center | 1960-1979 | 2018 | 101 | 0 | 101 | 0 | 0 | 0 | 0 | 0.00043538
19 | 5E | Recreation Center | 1980-2004 | 2018 | 15724 | 0 | 15724 | 0 | 0 | 0 | 0 | 0.067781
NA | 6A | Office | pre-1960 | 2018 | 16513 | 10502 | 6011 | 0 | 0 | 0 | 0 | 0.071182
14 | 6A | Office | 1960-1979 | 2018 | 3480 | 0 | 3480 | 0 | 0 | 0 | 0 | 0.015001
15 | 6A | Office | 1980-2004 | 2018 | 17682 | 11024 | 6658 | 0 | 0 | 0 | 0 | 0.076221
16 | 6B | Office-Small | 1960-1979 | 2018 | 1148 | 0 | 1136 | 12 | 0 | 0 | 0 | 0.0049486
17 | 6B | Office-Small | 1980-2004 | 2018 | 3259 | 0 | 2869 | 390 | 0 | 0 | 0 | 0.014048
18 | 6B | Office-Small | 2005-2014 | 2018 | 501 | 0 | 501 | 0 | 0 | 0 | 0 | 0.0021596
3 | 7A | Food Service | 1959-pre | 2018 | 10012 | 10012 | 0 | 0 | 0 | 0 | 0 | 0.043158
| 7A | Food Service | 2005-2014 | 2018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 8B | Vehicle Garage | 1959-pre | 2018 | 5221 | 3443 | 1778 | 0 | 0 | 0 | 0 | 0.022506
28 | 8B | Vehicle Garage | 1980-2004 | 2018 | 11711 | 0 | 11711 | 0 | 0 | 0 | 0 | 0.050482
8 | 9A | Maintenance Shop | 1959-pre | 2018 | 1504 | 1504 | 0 | 0 | 0 | 0 | 0 | 0.0064832
9 | 9A | Maintenance Shop | 1980-2004 | 2018 | 10986 | 7670 | 3316 | 0 | 0 | 0 | 0 | 0.047357
10 | 9B | Maintenance Shop-Small | 1959-pre | 2018 | 1127 | 368 | 759 | 0 | 0 | 0 | 0 | 0.0048581
11 | 9B | Maintenance Shop-Small | 1960-1979 | 2018 | 724 | 0 | 724 | 0 | 0 | 0 | 0 | 0.0031209
12 | 9B | Maintenance Shop-Small | 1980-2004 | 2018 | 4869 | 1050 | 3819 | 0 | 0 | 0 | 0 | 0.020989
2 | 13B | Fire Hall | 1959-pre | 2018 | 1289 | 1289 | 0 | 0 | 0 | 0 | 0 | 0.0055564
5 | 1A | Hangar | 1959-pre | 2020 | 50266 | 50266 | 0 | 0 | 0 | 0 | 0 | 0.22411
6 | 1A | Hangar | 1960-1979 | 2020 | 6231 | 0 | 6231 | 0 | 0 | 0 | 0 | 0.027781
7 | 1A | Hangar | 1980-2004 | 2020 | 6551 | 0 | 6551 | 0 | 0 | 0 | 0 | 0.029208
29 | 1A | Hangar | 2005-2014 | 2020 | 12000 | 12000 | 0 | 0 | 0 | 0 | 0 | 0.053502
24 | 2A | Training Building | 1959-pre | 2020 | 6832 | 3118 | 3714 | 0 | 0 | 0 | 0 | 0.030461
25 | 2A | Training Building | 1980-2004 | 2020 | 4831 | 4831 | 0 | 0 | 0 | 0 | 0 | 0.021539
26 | 2A | Training Building | 2005-2014 | 2020 | 1869 | 0 | 1869 | 0 | 0 | 0 | 0 | 0.008333
20 | 3B | Storage Building | 1959-pre | 2020 | 330 | 249 | 81 | 0 | 0 | 0 | 0 | 0.0014713
21 | 3B | Storage Building | 1960-1979 | 2020 | 833 | 326 | 507 | 0 | 0 | 0 | 0 | 0.0037139
22 | 3B | Storage Building | 1980-2004 | 2020 | 10125 | 1377 | 8006 | 742 | 0 | 0 | 0 | 0.045142
23 | 3B | Storage Building | 2005-2014 | 2020 | 501 | 0 | 428 | 73 | 0 | 0 | 0 | 0.0022337
1 | 4C | Barracks | 1959-pre | 2020 | 20067 | 20067 | 0 | 0 | 0 | 0 | 0 | 0.089469
| 4C | Barracks | 2005-2014 | 2020 | 5000 | 5000 | 0 | 0 | 0 | 0 | 0 | 0.022293
NA | 5E | Recreation Center | 1959-pre | 2020 | 294 | 0 | 294 | 0 | 0 | 0 | 0 | 0.0013108
NA | 5E | Recreation Center | 1960-1979 | 2020 | 101 | 0 | 101 | 0 | 0 | 0 | 0 | 0.00045031
19 | 5E | Recreation Center | 1980-2004 | 2020 | 15831 | 0 | 15831 | 0 | 0 | 0 | 0 | 0.070583
NA | 6A | Office | pre-1960 | 2020 | 13740 | 7729 | 6011 | 0 | 0 | 0 | 0 | 0.06126
14 | 6A | Office | 1960-1979 | 2020 | 2220 | 0 | 2220 | 0 | 0 | 0 | 0 | 0.0098979
15 | 6A | Office | 1980-2004 | 2020 | 17683 | 11025 | 6658 | 0 | 0 | 0 | 0 | 0.07884
16 | 6B | Office-Small | 1960-1979 | 2020 | 1148 | 0 | 1136 | 12 | 0 | 0 | 0 | 0.0051184
17 | 6B | Office-Small | 1980-2004 | 2020 | 3259 | 0 | 2869 | 390 | 0 | 0 | 0 | 0.01453
18 | 6B | Office-Small | 2005-2014 | 2020 | 501 | 0 | 501 | 0 | 0 | 0 | 0 | 0.0022337
3 | 7A | Food Service | 1959-pre | 2020 | 2568 | 2568 | 0 | 0 | 0 | 0 | 0 | 0.011449
| 7A | Food Service | 2005-2014 | 2020 | 4000 | 4000 | 0 | 0 | 0 | 0 | 0 | 0.017834
27 | 8B | Vehicle Garage | 1959-pre | 2020 | 5221 | 3443 | 1778 | 0 | 0 | 0 | 0 | 0.023278
28 | 8B | Vehicle Garage | 1980-2004 | 2020 | 11711 | 0 | 11711 | 0 | 0 | 0 | 0 | 0.052214
8 | 9A | Maintenance Shop | 1959-pre | 2020 | 1504 | 1504 | 0 | 0 | 0 | 0 | 0 | 0.0067056
9 | 9A | Maintenance Shop | 1980-2004 | 2020 | 10986 | 7670 | 3316 | 0 | 0 | 0 | 0 | 0.048981
10 | 9B | Maintenance Shop-Small | 1959-pre | 2020 | 1127 | 368 | 759 | 0 | 0 | 0 | 0 | 0.0050247
11 | 9B | Maintenance Shop-Small | 1960-1979 | 2020 | 724 | 0 | 724 | 0 | 0 | 0 | 0 | 0.003228
12 | 9B | Maintenance Shop-Small | 1980-2004 | 2020 | 4736 | 1050 | 3686 | 0 | 0 | 0 | 0 | 0.021116
2 | 13B | Fire Hall | 1959-pre | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 13B | Fire Hall | 2005-2014 | 2020 | 1500 | 1500 | 0 | 0 | 0 | 0 | 0 | 0.0066878
5 | 1A | Hangar | 1959-pre | 2023 | 21697 | 21697 | 0 | 0 | 0 | 0 | 0 | 0.10696
6 | 1A | Hangar | 1960-1979 | 2023 | 6231 | 0 | 6231 | 0 | 0 | 0 | 0 | 0.030717
7 | 1A | Hangar | 1980-2004 | 2023 | 6551 | 0 | 6551 | 0 | 0 | 0 | 0 | 0.032294
| 1A | Hangar | 2005-2014 | 2023 | 23000 | 23000 | 0 | 0 | 0 | 0 | 0 | 0.11338
24 | 2A | Training Building | 1959-pre | 2023 | 6832 | 3118 | 3714 | 0 | 0 | 0 | 0 | 0.03368
25 | 2A | Training Building | 1980-2004 | 2023 | 4831 | 4831 | 0 | 0 | 0 | 0 | 0 | 0.023815
26 | 2A | Training Building | 2005-2014 | 2023 | 1869 | 0 | 1869 | 0 | 0 | 0 | 0 | 0.0092136
20 | 3B | Storage Building | 1959-pre | 2023 | 330 | 249 | 81 | 0 | 0 | 0 | 0 | 0.0016268
21 | 3B | Storage Building | 1960-1979 | 2023 | 833 | 326 | 507 | 0 | 0 | 0 | 0 | 0.0041064
22 | 3B | Storage Building | 1980-2004 | 2023 | 8824 | 76 | 8006 | 742 | 0 | 0 | 0 | 0.0435
23 | 3B | Storage Building | 2005-2014 | 2023 | 501 | 0 | 428 | 73 | 0 | 0 | 0 | 0.0024698
1 | 4C | Barracks | 1959-pre | 2023 | 20067 | 17024 | 3043 | 0 | 0 | 0 | 0 | 0.098924
| 4C | Barracks | 2005-2014 | 2023 | 5000 | 0 | 5000 | 0 | 0 | 0 | 0 | 0.024649
NA | 5E | Recreation Center | 1959-pre | 2023 | 294 | 0 | 294 | 0 | 0 | 0 | 0 | 0.0014493
NA | 5E | Recreation Center | 1960-1979 | 2023 | 101 | 0 | 101 | 0 | 0 | 0 | 0 | 0.0004979
19 | 5E | Recreation Center | 1980-2004 | 2023 | 15831 | 0 | 15831 | 0 | 0 | 0 | 0 | 0.078042
NA | 6A | Office | pre-1960 | 2023 | 13740 | 7729 | 6011 | 0 | 0 | 0 | 0 | 0.067734
14 | 6A | Office | 1960-1979 | 2023 | 2220 | 0 | 2220 | 0 | 0 | 0 | 0 | 0.010944
15 | 6A | Office | 1980-2004 | 2023 | 17682 | 11024 | 6658 | 0 | 0 | 0 | 0 | 0.087167
16 | 6B | Office-Small | 1960-1979 | 2023 | 815 | 0 | 803 | 12 | 0 | 0 | 0 | 0.0040177
17 | 6B | Office-Small | 1980-2004 | 2023 | 3259 | 0 | 2869 | 390 | 0 | 0 | 0 | 0.016066
18 | 6B | Office-Small | 2005-2014 | 2023 | 501 | 0 | 501 | 0 | 0 | 0 | 0 | 0.0024698
3 | 7A | Food Service | 1959-pre | 2023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7A | Food Service | 2005-2014 | 2023 | 4000 | 4000 | 0 | 0 | 0 | 0 | 0 | 0.019719
27 | 8B | Vehicle Garage | 1959-pre | 2023 | 5221 | 3443 | 1778 | 0 | 0 | 0 | 0 | 0.025738
28 | 8B | Vehicle Garage | 1980-2004 | 2023 | 12045 | 0 | 12045 | 0 | 0 | 0 | 0 | 0.059378
8 | 9A | Maintenance Shop | 1959-pre | 2023 | 1504 | 1504 | 0 | 0 | 0 | 0 | 0 | 0.0074143
9 | 9A | Maintenance Shop | 1980-2004 | 2023 | 10986 | 7670 | 3316 | 0 | 0 | 0 | 0 | 0.054158
10 | 9B | Maintenance Shop-Small | 1959-pre | 2023 | 1127 | 368 | 759 | 0 | 0 | 0 | 0 | 0.0055558
11 | 9B | Maintenance Shop-Small | 1960-1979 | 2023 | 724 | 0 | 724 | 0 | 0 | 0 | 0 | 0.0035691
12 | 9B | Maintenance Shop-Small | 1980-2004 | 2023 | 4736 | 1050 | 3686 | 0 | 0 | 0 | 0 | 0.023347
2 | 13B | Fire Hall | 1959-pre | 2023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 13B | Fire Hall | 2015-2014 | 2023 | 1500 | 1500 | 0 | 0 | 0 | 0 | 0 | 0.0073946
5 | 1A | Hangar | 1959-pre | 2025 | 21679 | 21679 | 0 | 0 | 0 | 0 | 0 | 0.11001
6 | 1A | Hangar | 1960-1979 | 2025 | 6231 | 0 | 6231 | 0 | 0 | 0 | 0 | 0.031618
7 | 1A | Hangar | 1980-2004 | 2025 | 7269 | 0 | 7269 | 0 | 0 | 0 | 0 | 0.036886
| 1A | Hangar | 2005-2014 | 2025 | 23000 | 23000 | 0 | 0 | 0 | 0 | 0 | 0.11671
24 | 2A | Training Building | 1959-pre | 2025 | 6832 | 3118 | 3714 | 0 | 0 | 0 | 0 | 0.034668
25 | 2A | Training Building | 1980-2004 | 2025 | 4831 | 4831 | 0 | 0 | 0 | 0 | 0 | 0.024514
26 | 2A | Training Building | 2005-2014 | 2025 | 1869 | 0 | 1869 | 0 | 0 | 0 | 0 | 0.009484
20 | 3B | Storage Building | 1959-pre | 2025 | 330 | 249 | 81 | 0 | 0 | 0 | 0 | 0.0016745
21 | 3B | Storage Building | 1960-1979 | 2025 | 832 | 326 | 506 | 0 | 0 | 0 | 0 | 0.0042219
22 | 3B | Storage Building | 1980-2004 | 2025 | 8824 | 76 | 8006 | 742 | 0 | 0 | 0 | 0.044776
23 | 3B | Storage Building | 2005-2014 | 2025 | 501 | 0 | 428 | 73 | 0 | 0 | 0 | 0.0025423
1 | 4C | Barracks | 1959-pre | 2025 | 20067 | 17024 | 3043 | 0 | 0 | 0 | 0 | 0.10183
| 4C | Barracks | 2015-2014 | 2025 | 5000 | 0 | 5000 | 0 | 0 | 0 | 0 | 0.025372
NA | 5E | Recreation Center | 1959-pre | 2025 | 294 | 0 | 294 | 0 | 0 | 0 | 0 | 0.0014919
NA | 5E | Recreation Center | 1960-1979 | 2025 | 101 | 0 | 101 | 0 | 0 | 0 | 0 | 0.00051251
19 | 5E | Recreation Center | 1980-2004 | 2025 | 15831 | 0 | 15831 | 0 | 0 | 0 | 0 | 0.080332
NA | 6A | Office | pre-1960 | 2025 | 11035 | 5024 | 6011 | 0 | 0 | 0 | 0 | 0.055996
14 | 6A | Office | 1960-1979 | 2025 | 2220 | 0 | 2220 | 0 | 0 | 0 | 0 | 0.011265
15 | 6A | Office | 1980-2004 | 2025 | 17682 | 11024 | 6658 | 0 | 0 | 0 | 0 | 0.089725
16 | 6B | Office-Small | 1960-1979 | 2025 | 815 | 0 | 803 | 12 | 0 | 0 | 0 | 0.0041356
17 | 6B | Office-Small | 1980-2004 | 2025 | 3259 | 0 | 2869 | 390 | 0 | 0 | 0 | 0.016537
18 | 6B | Office-Small | 2005-2014 | 2025 | 501 | 0 | 501 | 0 | 0 | 0 | 0 | 0.0025423
3 | 7A | Food Service | 1959-pre | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7A | Food Service | 2005-2014 | 2025 | 4000 | 4000 | 0 | 0 | 0 | 0 | 0 | 0.020297
27 | 8B | Vehicle Garage | 1959-pre | 2025 | 1778 | 0 | 1778 | 0 | 0 | 0 | 0 | 0.0090222
28 | 8B | Vehicle Garage | 1980-2004 | 2025 | 11711 | 0 | 11711 | 0 | 0 | 0 | 0 | 0.059426
8 | 9A | Maintenance Shop | 1959-pre | 2025 | 1504 | 1504 | 0 | 0 | 0 | 0 | 0 | 0.0076318
9 | 9A | Maintenance Shop | 1980-2004 | 2025 | 10986 | 7670 | 3316 | 0 | 0 | 0 | 0 | 0.055747
10 | 9B | Maintenance Shop-Small | 1959-pre | 2025 | 1127 | 368 | 759 | 0 | 0 | 0 | 0 | 0.0057188
11 | 9B | Maintenance Shop-Small | 1960-1979 | 2025 | 724 | 0 | 724 | 0 | 0 | 0 | 0 | 0.0036738
12 | 9B | Maintenance Shop-Small | 1980-2004 | 2025 | 4736 | 1050 | 3686 | 0 | 0 | 0 | 0 | 0.024032
2 | 13B | Fire Hall | 1959-pre | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 13B | Fire Hall | 1959-pre | 2025 | 1500 | 1500 | 0 | 0 | 0 | 0 | 0 | 0.0076115
5 | 1A | Hangar | 1959-pre | 2028 | 21679 | 21679 | 0 | 0 | 0 | 0 | 0 | 0.11001
6 | 1A | Hangar | 1960-1979 | 2028 | 6231 | 0 | 6231 | 0 | 0 | 0 | 0 | 0.031618
7 | 1A | Hangar | 1980-2004 | 2028 | 7269 | 0 | 7269 | 0 | 0 | 0 | 0 | 0.036886
| 1A | Hangar | 2005-2014 | 2028 | 23000 | 23000 | 0 | 0 | 0 | 0 | 0 | 0.11671
24 | 2A | Training Building | 1959-pre | 2028 | 6832 | 3118 | 3714 | 0 | 0 | 0 | 0 | 0.034668
25 | 2A | Training Building | 1980-2004 | 2028 | 4831 | 4831 | 0 | 0 | 0 | 0 | 0 | 0.024514
26 | 2A | Training Building | 2005-2014 | 2028 | 1869 | 0 | 1869 | 0 | 0 | 0 | 0 | 0.009484
20 | 3B | Storage Building | 1959-pre | 2028 | 330 | 249 | 81 | 0 | 0 | 0 | 0 | 0.0016745
21 | 3B | Storage Building | 1960-1979 | 2028 | 832 | 326 | 506 | 0 | 0 | 0 | 0 | 0.0042219
22 | 3B | Storage Building | 1980-2004 | 2028 | 8824 | 76 | 8006 | 742 | 0 | 0 | 0 | 0.044776
23 | 3B | Storage Building | 2005-2014 | 2028 | 501 | 0 | 428 | 73 | 0 | 0 | 0 | 0.0025423
1 | 4C | Barracks | 1959-pre | 2028 | 20067 | 17024 | 3043 | 0 | 0 | 0 | 0 | 0.10183
| 4C | Barracks | 2015-2014 | 2028 | 5000 | 0 | 5000 | 0 | 0 | 0 | 0 | 0.025372
NA | 5E | Recreation Center | 1959-pre | 2028 | 294 | 0 | 294 | 0 | 0 | 0 | 0 | 0.0014919
NA | 5E | Recreation Center | 1960-1979 | 2028 | 101 | 0 | 101 | 0 | 0 | 0 | 0 | 0.00051251
19 | 5E | Recreation Center | 1980-2004 | 2028 | 15831 | 0 | 15831 | 0 | 0 | 0 | 0 | 0.080332
NA | 6A | Office | pre-1960 | 2028 | 11035 | 5024 | 6011 | 0 | 0 | 0 | 0 | 0.055996
14 | 6A | Office | 1960-1979 | 2028 | 2220 | 0 | 2220 | 0 | 0 | 0 | 0 | 0.011265
15 | 6A | Office | 1980-2004 | 2028 | 17682 | 11024 | 6658 | 0 | 0 | 0 | 0 | 0.089725
16 | 6B | Office-Small | 1960-1979 | 2028 | 815 | 0 | 803 | 12 | 0 | 0 | 0 | 0.0041356
17 | 6B | Office-Small | 1980-2004 | 2028 | 3259 | 0 | 2869 | 390 | 0 | 0 | 0 | 0.016537
18 | 6B | Office-Small | 2005-2014 | 2028 | 501 | 0 | 501 | 0 | 0 | 0 | 0 | 0.0025423
3 | 7A | Food Service | 1959-pre | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7A | Food Service | 2005-2014 | 2028 | 4000 | 4000 | 0 | 0 | 0 | 0 | 0 | 0.020297
27 | 8B | Vehicle Garage | 1959-pre | 2028 | 1778 | 0 | 1778 | 0 | 0 | 0 | 0 | 0.0090222
28 | 8B | Vehicle Garage | 1980-2004 | 2028 | 11711 | 0 | 11711 | 0 | 0 | 0 | 0 | 0.059426
8 | 9A | Maintenance Shop | 1959-pre | 2028 | 1504 | 1504 | 0 | 0 | 0 | 0 | 0 | 0.0076318
9 | 9A | Maintenance Shop | 1980-2004 | 2028 | 10986 | 7670 | 3316 | 0 | 0 | 0 | 0 | 0.055747
10 | 9B | Maintenance Shop-Small | 1959-pre | 2028 | 1127 | 368 | 759 | 0 | 0 | 0 | 0 | 0.0057188
11 | 9B | Maintenance Shop-Small | 1960-1979 | 2028 | 724 | 0 | 724 | 0 | 0 | 0 | 0 | 0.0036738
12 | 9B | Maintenance Shop-Small | 1980-2004 | 2028 | 4736 | 1050 | 3686 | 0 | 0 | 0 | 0 | 0.024032
2 | 13B | Fire Hall | 1959-pre | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 13B | Fire Hall | 1959-pre | 2028 | 1500 | 1500 | 0 | 0 | 0 | 0 | 0 | 0.0076115
5 | 1A | Hangar | 1959-pre | 2030 | 21679 | 21679 | 0 | 0 | 0 | 0 | 0 | 0.11001
6 | 1A | Hangar | 1960-1979 | 2030 | 6231 | 0 | 6231 | 0 | 0 | 0 | 0 | 0.031618
7 | 1A | Hangar | 1980-2004 | 2030 | 7269 | 0 | 7269 | 0 | 0 | 0 | 0 | 0.036886
| 1A | Hangar | 2005-2014 | 2030 | 23000 | 23000 | 0 | 0 | 0 | 0 | 0 | 0.11671
24 | 2A | Training Building | 1959-pre | 2030 | 6832 | 3118 | 3714 | 0 | 0 | 0 | 0 | 0.034668
25 | 2A | Training Building | 1980-2004 | 2030 | 4831 | 4831 | 0 | 0 | 0 | 0 | 0 | 0.024514
26 | 2A | Training Building | 2005-2014 | 2030 | 1869 | 0 | 1869 | 0 | 0 | 0 | 0 | 0.009484
20 | 3B | Storage Building | 1959-pre | 2030 | 330 | 249 | 81 | 0 | 0 | 0 | 0 | 0.0016745
21 | 3B | Storage Building | 1960-1979 | 2030 | 832 | 326 | 506 | 0 | 0 | 0 | 0 | 0.0042219
22 | 3B | Storage Building | 1980-2004 | 2030 | 8824 | 76 | 8006 | 742 | 0 | 0 | 0 | 0.044776
23 | 3B | Storage Building | 2005-2014 | 2030 | 501 | 0 | 428 | 73 | 0 | 0 | 0 | 0.0025423
1 | 4C | Barracks | 1959-pre | 2030 | 20067 | 17024 | 3043 | 0 | 0 | 0 | 0 | 0.10183
| 4C | Barracks | 2015-2014 | 2030 | 5000 | 0 | 5000 | 0 | 0 | 0 | 0 | 0.025372
NA | 5E | Recreation Center | 1959-pre | 2030 | 294 | 0 | 294 | 0 | 0 | 0 | 0 | 0.0014919
NA | 5E | Recreation Center | 1960-1979 | 2030 | 101 | 0 | 101 | 0 | 0 | 0 | 0 | 0.00051251
19 | 5E | Recreation Center | 1980-2004 | 2030 | 15831 | 0 | 15831 | 0 | 0 | 0 | 0 | 0.080332
NA | 6A | Office | pre-1960 | 2030 | 11035 | 5024 | 6011 | 0 | 0 | 0 | 0 | 0.055996
14 | 6A | Office | 1960-1979 | 2030 | 2220 | 0 | 2220 | 0 | 0 | 0 | 0 | 0.011265
15 | 6A | Office | 1980-2004 | 2030 | 17682 | 11024 | 6658 | 0 | 0 | 0 | 0 | 0.089725
16 | 6B | Office-Small | 1960-1979 | 2030 | 815 | 0 | 803 | 12 | 0 | 0 | 0 | 0.0041356
17 | 6B | Office-Small | 1980-2004 | 2030 | 3259 | 0 | 2869 | 390 | 0 | 0 | 0 | 0.016537
18 | 6B | Office-Small | 2005-2014 | 2030 | 501 | 0 | 501 | 0 | 0 | 0 | 0 | 0.0025423
3 | 7A | Food Service | 1959-pre | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7A | Food Service | 2005-2014 | 2030 | 4000 | 4000 | 0 | 0 | 0 | 0 | 0 | 0.020297
27 | 8B | Vehicle Garage | 1959-pre | 2030 | 1778 | 0 | 1778 | 0 | 0 | 0 | 0 | 0.0090222
28 | 8B | Vehicle Garage | 1980-2004 | 2030 | 11711 | 0 | 11711 | 0 | 0 | 0 | 0 | 0.059426
8 | 9A | Maintenance Shop | 1959-pre | 2030 | 1504 | 1504 | 0 | 0 | 0 | 0 | 0 | 0.0076318
9 | 9A | Maintenance Shop | 1980-2004 | 2030 | 10986 | 7670 | 3316 | 0 | 0 | 0 | 0 | 0.055747
10 | 9B | Maintenance Shop-Small | 1959-pre | 2030 | 1127 | 368 | 759 | 0 | 0 | 0 | 0 | 0.0057188
11 | 9B | Maintenance Shop-Small | 1960-1979 | 2030 | 724 | 0 | 724 | 0 | 0 | 0 | 0 | 0.0036738
12 | 9B | Maintenance Shop-Small | 1980-2004 | 2030 | 4736 | 1050 | 3686 | 0 | 0 | 0 | 0 | 0.024032
2 | 13B | Fire Hall | 1959-pre | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 13B | Fire Hall | 1959-pre | 2030 | 1500 | 1500 | 0 | 0 | 0 | 0 | 0 | 0.0076115
5 | 1A | Hangar | 1959-pre | 2033 | 21679 | 21679 | 0 | 0 | 0 | 0 | 0 | 0.11001
6 | 1A | Hangar | 1960-1979 | 2033 | 6231 | 0 | 6231 | 0 | 0 | 0 | 0 | 0.031618
7 | 1A | Hangar | 1980-2004 | 2033 | 7269 | 0 | 7269 | 0 | 0 | 0 | 0 | 0.036886
| 1A | Hangar | 2005-2014 | 2033 | 23000 | 23000 | 0 | 0 | 0 | 0 | 0 | 0.11671
24 | 2A | Training Building | 1959-pre | 2033 | 6832 | 3118 | 3714 | 0 | 0 | 0 | 0 | 0.034668
25 | 2A | Training Building | 1980-2004 | 2033 | 4831 | 4831 | 0 | 0 | 0 | 0 | 0 | 0.024514
26 | 2A | Training Building | 2005-2014 | 2033 | 1869 | 0 | 1869 | 0 | 0 | 0 | 0 | 0.009484
20 | 3B | Storage Building | 1959-pre | 2033 | 330 | 249 | 81 | 0 | 0 | 0 | 0 | 0.0016745
21 | 3B | Storage Building | 1960-1979 | 2033 | 832 | 326 | 506 | 0 | 0 | 0 | 0 | 0.0042219
22 | 3B | Storage Building | 1980-2004 | 2033 | 8824 | 76 | 8006 | 742 | 0 | 0 | 0 | 0.044776
23 | 3B | Storage Building | 2005-2014 | 2033 | 501 | 0 | 428 | 73 | 0 | 0 | 0 | 0.0025423
1 | 4C | Barracks | 1959-pre | 2033 | 20067 | 17024 | 3043 | 0 | 0 | 0 | 0 | 0.10183
| 4C | Barracks | 2015-2014 | 2033 | 5000 | 0 | 5000 | 0 | 0 | 0 | 0 | 0.025372
NA | 5E | Recreation Center | 1959-pre | 2033 | 294 | 0 | 294 | 0 | 0 | 0 | 0 | 0.0014919
NA | 5E | Recreation Center | 1960-1979 | 2033 | 101 | 0 | 101 | 0 | 0 | 0 | 0 | 0.00051251
19 | 5E | Recreation Center | 1980-2004 | 2033 | 15831 | 0 | 15831 | 0 | 0 | 0 | 0 | 0.080332
NA | 6A | Office | pre-1960 | 2033 | 11035 | 5024 | 6011 | 0 | 0 | 0 | 0 | 0.055996
14 | 6A | Office | 1960-1979 | 2033 | 2220 | 0 | 2220 | 0 | 0 | 0 | 0 | 0.011265
15 | 6A | Office | 1980-2004 | 2033 | 17682 | 11024 | 6658 | 0 | 0 | 0 | 0 | 0.089725
16 | 6B | Office-Small | 1960-1979 | 2033 | 815 | 0 | 803 | 12 | 0 | 0 | 0 | 0.0041356
17 | 6B | Office-Small | 1980-2004 | 2033 | 3259 | 0 | 2869 | 390 | 0 | 0 | 0 | 0.016537
18 | 6B | Office-Small | 2005-2014 | 2033 | 501 | 0 | 501 | 0 | 0 | 0 | 0 | 0.0025423
3 | 7A | Food Service | 1959-pre | 2033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7A | Food Service | 2005-2014 | 2033 | 4000 | 4000 | 0 | 0 | 0 | 0 | 0 | 0.020297
27 | 8B | Vehicle Garage | 1959-pre | 2033 | 1778 | 0 | 1778 | 0 | 0 | 0 | 0 | 0.0090222
28 | 8B | Vehicle Garage | 1980-2004 | 2033 | 11711 | 0 | 11711 | 0 | 0 | 0 | 0 | 0.059426
8 | 9A | Maintenance Shop | 1959-pre | 2033 | 1504 | 1504 | 0 | 0 | 0 | 0 | 0 | 0.0076318
9 | 9A | Maintenance Shop | 1980-2004 | 2033 | 10986 | 7670 | 3316 | 0 | 0 | 0 | 0 | 0.055747
10 | 9B | Maintenance Shop-Small | 1959-pre | 2033 | 1127 | 368 | 759 | 0 | 0 | 0 | 0 | 0.0057188
11 | 9B | Maintenance Shop-Small | 1960-1979 | 2033 | 724 | 0 | 724 | 0 | 0 | 0 | 0 | 0.0036738
12 | 9B | Maintenance Shop-Small | 1980-2004 | 2033 | 4736 | 1050 | 3686 | 0 | 0 | 0 | 0 | 0.024032
2 | 13B | Fire Hall | 1959-pre | 2033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 13B | Fire Hall | 1959-pre | 2033 | 1500 | 1500 | 0 | 0 | 0 | 0 | 0 | 0.0076115
5 | 1A | Hangar | 1959-pre | 2035 | 21679 | 21679 | 0 | 0 | 0 | 0 | 0 | 0.11001
6 | 1A | Hangar | 1960-1979 | 2035 | 6231 | 0 | 6231 | 0 | 0 | 0 | 0 | 0.031618
7 | 1A | Hangar | 1980-2004 | 2035 | 7269 | 0 | 7269 | 0 | 0 | 0 | 0 | 0.036886
| 1A | Hangar | 2005-2014 | 2035 | 23000 | 23000 | 0 | 0 | 0 | 0 | 0 | 0.11671
24 | 2A | Training Building | 1959-pre | 2035 | 6832 | 3118 | 3714 | 0 | 0 | 0 | 0 | 0.034668
25 | 2A | Training Building | 1980-2004 | 2035 | 4831 | 4831 | 0 | 0 | 0 | 0 | 0 | 0.024514
26 | 2A | Training Building | 2005-2014 | 2035 | 1869 | 0 | 1869 | 0 | 0 | 0 | 0 | 0.009484
20 | 3B | Storage Building | 1959-pre | 2035 | 330 | 249 | 81 | 0 | 0 | 0 | 0 | 0.0016745
21 | 3B | Storage Building | 1960-1979 | 2035 | 832 | 326 | 506 | 0 | 0 | 0 | 0 | 0.0042219
22 | 3B | Storage Building | 1980-2004 | 2035 | 8824 | 76 | 8006 | 742 | 0 | 0 | 0 | 0.044776
23 | 3B | Storage Building | 2005-2014 | 2035 | 501 | 0 | 428 | 73 | 0 | 0 | 0 | 0.0025423
1 | 4C | Barracks | 1959-pre | 2035 | 20067 | 17024 | 3043 | 0 | 0 | 0 | 0 | 0.10183
| 4C | Barracks | 2015-2014 | 2035 | 5000 | 0 | 5000 | 0 | 0 | 0 | 0 | 0.025372
NA | 5E | Recreation Center | 1959-pre | 2035 | 294 | 0 | 294 | 0 | 0 | 0 | 0 | 0.0014919
NA | 5E | Recreation Center | 1960-1979 | 2035 | 101 | 0 | 101 | 0 | 0 | 0 | 0 | 0.00051251
19 | 5E | Recreation Center | 1980-2004 | 2035 | 15831 | 0 | 15831 | 0 | 0 | 0 | 0 | 0.080332
NA | 6A | Office | pre-1960 | 2035 | 11035 | 5024 | 6011 | 0 | 0 | 0 | 0 | 0.055996
14 | 6A | Office | 1960-1979 | 2035 | 2220 | 0 | 2220 | 0 | 0 | 0 | 0 | 0.011265
15 | 6A | Office | 1980-2004 | 2035 | 17682 | 11024 | 6658 | 0 | 0 | 0 | 0 | 0.089725
16 | 6B | Office-Small | 1960-1979 | 2035 | 815 | 0 | 803 | 12 | 0 | 0 | 0 | 0.0041356
17 | 6B | Office-Small | 1980-2004 | 2035 | 3259 | 0 | 2869 | 390 | 0 | 0 | 0 | 0.016537
18 | 6B | Office-Small | 2005-2014 | 2035 | 501 | 0 | 501 | 0 | 0 | 0 | 0 | 0.0025423
3 | 7A | Food Service | 1959-pre | 2035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7A | Food Service | 2005-2014 | 2035 | 4000 | 4000 | 0 | 0 | 0 | 0 | 0 | 0.020297
27 | 8B | Vehicle Garage | 1959-pre | 2035 | 1778 | 0 | 1778 | 0 | 0 | 0 | 0 | 0.0090222
28 | 8B | Vehicle Garage | 1980-2004 | 2035 | 11711 | 0 | 11711 | 0 | 0 | 0 | 0 | 0.059426
8 | 9A | Maintenance Shop | 1959-pre | 2035 | 1504 | 1504 | 0 | 0 | 0 | 0 | 0 | 0.0076318
9 | 9A | Maintenance Shop | 1980-2004 | 2035 | 10986 | 7670 | 3316 | 0 | 0 | 0 | 0 | 0.055747
10 | 9B | Maintenance Shop-Small | 1959-pre | 2035 | 1127 | 368 | 759 | 0 | 0 | 0 | 0 | 0.0057188
11 | 9B | Maintenance Shop-Small | 1960-1979 | 2035 | 724 | 0 | 724 | 0 | 0 | 0 | 0 | 0.0036738
12 | 9B | Maintenance Shop-Small | 1980-2004 | 2035 | 4736 | 1050 | 3686 | 0 | 0 | 0 | 0 | 0.024032
2 | 13B | Fire Hall | 1959-pre | 2035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 13B | Fire Hall | 1959-pre | 2035 | 1500 | 1500 | 0 | 0 | 0 | 0 | 0 | 0.0076115
Note on H1: Lubun, Mike: includes propane
Note on C4: Lubun, Mike: includes 1b
Note on C12: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C43: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C44: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C75: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C76: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C108: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C109: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C141: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C142: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C174: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C175: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C207: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C208: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C240: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C241: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C273: Lubun, Mike: excludes bunkhouse and seasonal barracks
Note on C274: Lubun, Mike: excludes bunkhouse and seasonal barracks

## base_scenario_arch_measures
baseline_id | building_name | vintage_name | year | measure_id | Percent of Total Base Area | Electricity-Heating KWh/m2 | Natural Gas-Heating KWh/m2 | Electricity-Cooling KWh/m2 | Electricity-Water Systems KWh/m2 | Natural Gas-Water Systems KWh/m2 | Electricity-Interior Lighting KWh/m2 | Electricity-Interior Equipment KWh/m2 | District Heating-Interior Equipment KWh/m2 | Electricity-Fans KWh/m2 | Electricity-Pumps KWh/m2 | Electricity-Heat Recovery KWh/m2 | baseline-Electricity-heating kWh | baseline-Natural Gas-heating kWh | baseline-Electricity-Cooling kWh | baseline-Electricity-Water Systems kWh | baseline-Natural Gas - Water Systems kWh | baseline-Electricty-Interior Lighting kWh | baseline-Electricity-Interior Equipment kWh | baseline-District Heating-Interior Equipment kWh | baseline-Electricity-Fans kWh | baseline-Electricity-Pumps kWh | baseline-Electricity-Heat Recovery kWh | baseline total energy kWh | Gas Energy Savings kWh | Electric Energy Savings kWh | Total Savings kWh | Gas Energy Savings $ | Electric Energy Savings $ | Total Savings $ | Base Total ECM Cost $ | Base Total ECM Payback | Base baseline GHG tonnes
1 | Barracks | 1959-pre | 2015 | air_temp_reset_enabled | 0.08671 | 0 | 7.9332 | 0.22144 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.51458 | 0.3797 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | -84419.7817 | -45298.2399 | -129718.0216 | -1367.6005 | -5118.7011 | -6486.3016 | 54343.7628 | -8.3782
1 | Barracks | 1959-pre | 2015 | baseline | 0.08671 | 0 | 7.5684 | 0.076442 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.50192 | 0.34162 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | Barracks | 1959-pre | 2015 | boiler_eff_upgrade | 0.08671 | 0 | 7.4524 | 0.09343 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.51458 | 0.34938 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 26841.7654 | -8657.6841 | 18184.0813 | 434.8366 | -978.3183 | -543.4817 | 336607.2832 | -619.3535
1 | Barracks | 1959-pre | 2015 | boiler_reset | 0.08671 | 0 | 4.9507 | 0.09343 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.51458 | 0.0088753 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 605794.9399 | 70144.9097 | 675939.8497 | 9813.878 | 7926.3748 | 17740.2528 | 4787.114 | 0.26984
1 | Barracks | 1959-pre | 2015 | cooling_cop_3_0 | 0.08671 | 0 | 7.4524 | 0.06674 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.51458 | 0.34938 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 26841.7654 | -2480.986 | 24360.7794 | 434.8366 | -280.3514 | 154.4852 | 76348.4226 | 494.2119
1 | Barracks | 1959-pre | 2015 | dcv_enabled | 0.08671 | 0 | 7.1981 | 0.10475 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.51458 | 0.3462 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 85700.7656 | -10542.35 | 75158.4156 | 1388.3524 | -1191.2855 | 197.0669 | 321515.6606 | 1631.5055
1 | Barracks | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.08671 | 0 | 7.4339 | 0.18934 | 0 | 1.9301 | 0.90283 | 0.24934 | 0 | 0.51458 | 0.35552 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 31148.5215 | -32274.9039 | -1126.3824 | 504.606 | -3647.0641 | -3142.4581 | 54343.7628 | -17.2934
1 | Barracks | 1959-pre | 2015 | economizers_enabled | 0.08671 | 0 | 7.4517 | 0.072116 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.51458 | 0.34849 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 27011.0909 | -3519.0246 | 23492.0662 | 437.5797 | -397.6498 | 39.9299 | 21234.2947 | 531.7895
1 | Barracks | 1959-pre | 2015 | elec_reduce | 0.08671 | 0 | 7.5467 | 0.078637 | 0 | 1.9302 | 0.63196 | 0.24934 | 0 | 0.50383 | 0.27145 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 5028.2298 | 77978.0525 | 83006.2823 | 81.4573 | 8811.5199 | 8892.9773 | 963141.3954 | 108.3036
1 | Barracks | 1959-pre | 2015 | envelope_ecm_roof | 0.08671 | 0 | 7.4136 | 0.09308 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.51308 | 0.3477 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 35823.3764 | -7840.5047 | 27982.8717 | 580.3387 | -885.977 | -305.6383 | 1161908.3587 | -3801.5793
1 | Barracks | 1959-pre | 2015 | envelope_ecm_wall | 0.08671 | 0 | 7.0751 | 0.094352 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.50484 | 0.33631 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 114154.8038 | -3592.6444 | 110562.1594 | 1849.3078 | -405.9688 | 1443.339 | 2565337.4475 | 1777.3631
1 | Barracks | 1959-pre | 2015 | envelope_ecm_windows | 0.08671 | 0 | 6.7435 | 0.10227 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.49699 | 0.32597 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 190896.0442 | -1214.7261 | 189681.3182 | 3092.5159 | -137.264 | 2955.2519 | 1891737.6986 | 640.1274
1 | Barracks | 1959-pre | 2015 | fans_to_variable | 0.08671 | 0 | 7.4574 | 0.09308 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.51054 | 0.34945 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 25678.5732 | -7656.4553 | 18022.1179 | 415.9929 | -865.1794 | -449.1866 | 15606.848 | -34.7447
1 | Barracks | 1959-pre | 2015 | hrv_enabled | 0.08671 | 0 | 6.8872 | 0.1052 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.51458 | 0.34595 | 0.15047 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 157649.3595 | -45408.6695 | 112240.69 | 2553.9196 | -5131.1797 | -2577.26 | 1357924.1213 | -526.8867
1 | Barracks | 1959-pre | 2015 | infil_reduce | 0.08671 | 0 | 3.5463 | 0.15613 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.46324 | 0.22471 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 930840.9154 | 17565.6753 | 948406.5908 | 15079.6228 | 1984.9213 | 17064.5441 | 610327.0265 | 35.7658
1 | Barracks | 1959-pre | 2015 | infil_reduce_plus_setback | 0.08671 | 0 | 3.9735 | 0.14671 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.29467 | 0.14296 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 831962.2124 | 77676.2114 | 909638.4238 | 13477.7878 | 8777.4119 | 22255.1997 | 978548.1298 | 43.9694
1 | Barracks | 1959-pre | 2015 | lights_reduce_70p | 0.08671 | 0 | 7.7972 | 0.071003 | 0 | 1.9302 | 0.63196 | 0.24934 | 0 | 0.5036 | 0.35015 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | -52947.3332 | 61582.9314 | 8635.5981 | -857.7468 | 6958.8712 | 6101.1244 | 461526.9343 | 75.6462
1 | Barracks | 1959-pre | 2015 | load_reduce | 0.08671 | 0 | 2.8217 | 0.14671 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.29467 | 0.007921 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 1098517.2866 | 108927.8006 | 1207445.0872 | 17795.98 | 12308.8415 | 30104.8215 | 983335.2439 | 32.6637
1 | Barracks | 1959-pre | 2015 | occupancy_setback | 0.08671 | 0 | 7.9855 | 0.10087 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.42907 | 0.29813 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | -96537.5946 | 21268.7494 | -75268.8452 | -1563.909 | 2403.3687 | 839.4596 | 184110.5517 | 219.3203
1 | Barracks | 1959-pre | 2015 | payback_less_than_20 | 0.08671 | 0 | 2.9543 | 0.19456 | 0 | 1.9301 | 0.63196 | 0.24934 | 0 | 0.29613 | 0.0069985 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 1067832.5696 | 160417.4626 | 1228250.0321 | 17298.8876 | 18127.1733 | 35426.0609 | 1988855.1673 | 56.141
1 | Barracks | 1959-pre | 2015 | plug_loads_90_percent | 0.08671 | 0 | 7.4627 | 0.091998 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.51464 | 0.3497 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 24456.4851 | -8414.7389 | 16041.7463 | 396.1951 | -950.8655 | -554.6704 | 106451.6017 | -191.9187
1 | Barracks | 1959-pre | 2015 | pump_fan_eff_ | 0.08671 | 0 | 7.4524 | 0.09343 | 0 | 1.9302 | 0.90283 | 0.24934 | 0 | 0.51458 | 0.27326 | 0 | 0 | 1751531.9422 | 17690.8289 | 0 | 446702.6331 | 208940.248 | 57703.1699 | 0 | 116157.2613 | 79060.263 | 0 | 2677786.3464 | 26841.7654 | 8959.5251 | 35801.2905 | 434.8366 | 1012.4263 | 1447.2629 | 51022.3105 | 35.2543
2 | Fire Hall | 1959-pre | 2015 | air_temp_reset_enabled | 0.0055698 | 0 | 2.8978 | 0.038538 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.22434 | 0.077177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | baseline | 0.0055698 | 0 | 2.99 | 0.0082302 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.22488 | 0.086001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | boiler_eff_upgrade | 0.0055698 | 0 | 2.9547 | 0.0085526 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.22418 | 0.085628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | boiler_reset | 0.0055698 | 0 | 2.1671 | 0.0085526 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.22418 | 0.085628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | cooling_cop_3_0 | 0.0055698 | 0 | 2.9547 | 0.006109 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.22418 | 0.085628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | dcv_enabled | 0.0055698 | 0 | 2.9547 | 0.0085526 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.22418 | 0.085628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.0055698 | 0 | 2.6308 | 0.025318 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.22434 | 0.07548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | economizers_enabled | 0.0055698 | 0 | 2.9589 | 0.0081793 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.22418 | 0.081895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | elec_reduce | 0.0055698 | 0 | 3.1341 | 0.0057527 | 0.13175 | 0 | 0.35941 | 0.14743 | 0 | 0.22651 | 0.068285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | envelope_ecm_roof | 0.0055698 | 0 | 2.9114 | 0.0083151 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.22247 | 0.084576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | envelope_ecm_wall | 0.0055698 | 0 | 2.8809 | 0.0085696 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.2211 | 0.083473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | envelope_ecm_windows | 0.0055698 | 0 | 2.8974 | 0.0087223 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.22189 | 0.083778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | fans_to_variable | 0.0055698 | 0 | 2.9555 | 0.0085187 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.22351 | 0.085645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | hrv_enabled | 0.0055698 | 0 | 2.5659 | 0.014594 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.2241 | 0.081657 | 0.026761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | infil_reduce | 0.0055698 | 0 | 1.3408 | 0.015035 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.16218 | 0.04429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | infil_reduce_plus_setback | 0.0055698 | 0 | 1.5889 | 0.015697 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.17166 | 0.047532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | lights_reduce_70p | 0.0055698 | 0 | 3.1322 | 0.0056848 | 0.13175 | 0 | 0.35941 | 0.14743 | 0 | 0.22639 | 0.087308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | load_reduce | 0.0055698 | 0 | 1.1538 | 0.015697 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.17166 | 0.047532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | occupancy_setback | 0.0055698 | 0 | 3.4418 | 0.010538 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.24716 | 0.093706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | payback_less_than_20 | 0.0055698 | 0 | 1.0297 | 0.017784 | 0.13175 | 0 | 0.35941 | 0.14743 | 0 | 0.17453 | 0.033752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | plug_loads_90_percent | 0.0055698 | 0 | 2.9566 | 0.0086375 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.22429 | 0.085628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Fire Hall | 1959-pre | 2015 | pump_fan_eff_ | 0.0055698 | 0 | 2.9547 | 0.0085526 | 0.13175 | 0 | 0.51346 | 0.14743 | 0 | 0.22418 | 0.066979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | air_temp_reset_enabled | 0.043262 | 0 | 26.9638 | 0.42555 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.4662 | 0.60444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | baseline | 0.043262 | 0 | 25.6863 | 0.12458 | 2.2442 | 0 | 3.3374 | 0.51593 | 0 | 1.4613 | 0.58854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | boiler_eff_upgrade | 0.043262 | 0 | 25.3115 | 0.17332 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.4672 | 0.59764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | boiler_reset | 0.043262 | 0 | 20.3227 | 0.17332 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.4672 | 0.0319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | cooling_cop_3_0 | 0.043262 | 0 | 25.3115 | 0.12382 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.4672 | 0.59764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | dcv_enabled | 0.043262 | 0 | 17.6741 | 0.25962 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.4673 | 0.58484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.043262 | 0 | 24.4675 | 0.23062 | 2.244 | 0 | 3.3374 | 0.51593 | 0 | 1.4709 | 0.5919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | economizers_enabled | 0.043262 | 0 | 25.3116 | 0.15742 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.4672 | 0.59692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | elec_reduce | 0.043262 | 0 | 18.8577 | 0.1672 | 2.2442 | 0 | 2.3362 | 0.51593 | 0 | 0.97342 | 0.46115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | envelope_ecm_roof | 0.043262 | 0 | 24.3962 | 0.16962 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.4343 | 0.5722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | envelope_ecm_wall | 0.043262 | 0 | 24.935 | 0.17396 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.4523 | 0.58513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | envelope_ecm_windows | 0.043262 | 0 | 24.4029 | 0.17481 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.4373 | 0.5751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | exhaust_fans_occ_control | 0.043262 | 0 | 25.3114 | 0.17332 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 0.96926 | 0.59755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | fans_to_variable | 0.043262 | 0 | 25.3218 | 0.17294 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.4592 | 0.59764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | hrv_enabled | 0.043262 | 0 | 15.8877 | 0.26239 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.4671 | 0.57544 | 0.26826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | infil_reduce | 0.043262 | 0 | 14.1478 | 0.22232 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.2071 | 0.35133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | infil_reduce_plus_setback | 0.043262 | 0 | 12.8777 | 0.10412 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.2152 | 0.34359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | lights_reduce_70p | 0.043262 | 0 | 26.5524 | 0.1162 | 2.2442 | 0 | 2.3362 | 0.51593 | 0 | 1.4707 | 0.60389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | load_reduce | 0.043262 | 0 | 10.1319 | 0.10412 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.2152 | 0.018587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | occupancy_setback | 0.043262 | 0 | 23.6937 | 0.074859 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.5991 | 0.63452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | payback_less_than_20 | 0.043262 | 0 | 6.2267 | 0.31028 | 2.244 | 0 | 2.3362 | 0.51593 | 0 | 0.64102 | 0.0075284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | plug_loads_90_percent | 0.043262 | 0 | 25.3392 | 0.1703 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.4676 | 0.59615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Food Service | 1959-pre | 2015 | pump_fan_eff_ | 0.043262 | 0 | 25.3115 | 0.17332 | 2.2441 | 0 | 3.3374 | 0.51593 | 0 | 1.4672 | 0.4674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Food Service | 2005-2014 | 2015 | air_temp_reset_enabled | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | -317301.7351 | -31421.8539 | -348723.5891 | -5140.2881 | -3550.6695 | -8690.9576 | 25452.7866 | -2.9287
4 | Food Service | 2005-2014 | 2015 | baseline | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Food Service | 2005-2014 | 2015 | boiler_eff_upgrade | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | -11514.792 | -22073.9507 | -33588.7427 | -186.5396 | -2494.3564 | -2680.8961 | 59587.7959 | -22.2268
4 | Food Service | 2005-2014 | 2015 | boiler_reset | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | 262634.0015 | 7515.2895 | 270149.291 | 4254.6708 | 849.2277 | 5103.8985 | 1681.63 | 0.32948
4 | Food Service | 2005-2014 | 2015 | cooling_cop_3_0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | -11514.792 | -22073.9507 | -33588.7427 | -186.5396 | -2494.3564 | -2680.8961 | 35758.6502 | -13.3383
4 | Food Service | 2005-2014 | 2015 | dcv_enabled | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | 657436.4219 | -30442.6247 | 626993.7972 | 10650.47 | -3440.0166 | 7210.4534 | 13553.1454 | 1.8797
4 | Food Service | 2005-2014 | 2015 | ecm_cold_deck_reset_control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | 9347.9032 | -23261.6103 | -13913.707 | 151.436 | -2628.562 | -2477.1259 | 25452.7866 | -10.2751
4 | Food Service | 2005-2014 | 2015 | economizers_enabled | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | -11538.3879 | -19753.6887 | -31292.0766 | -186.9219 | -2232.1668 | -2419.0887 | 8487.1882 | -3.5084
4 | Food Service | 2005-2014 | 2015 | elec_reduce | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | 617488.5881 | 133344.2806 | 750832.8686 | 10003.3151 | 15067.9037 | 25071.2188 | 244870.3435 | 9.767
4 | Food Service | 2005-2014 | 2015 | envelope_ecm_roof | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | 44293.4094 | -19462.6727 | 24830.7366 | 717.5532 | -2199.282 | -1481.7288 | 0 | 0
4 | Food Service | 2005-2014 | 2015 | envelope_ecm_wall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | 212.363 | -21806.5307 | -21594.1677 | 3.4403 | -2464.138 | -2460.6977 | 0 | 0
4 | Food Service | 2005-2014 | 2015 | envelope_ecm_windows | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | 27866.7406 | -21995.2978 | 5871.4428 | 451.4412 | -2485.4686 | -2034.0274 | 488110.0056 | -239.9722
4 | Food Service | 2005-2014 | 2015 | exhaust_fans_occ_control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | -11510.8594 | 23965.5542 | 12454.6948 | -186.4759 | 2708.1076 | 2521.6317 | 11920.7265 | 4.7274
4 | Food Service | 2005-2014 | 2015 | fans_to_variable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | -12081.0933 | -21594.1677 | -33675.261 | -195.7137 | -2440.141 | -2635.8547 | 7309.868 | -2.7732
4 | Food Service | 2005-2014 | 2015 | hrv_enabled | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | 829851.5559 | -56618.3268 | 773233.2291 | 13443.5952 | -6397.8709 | 7045.7243 | 520127.6159 | 73.8217
4 | Food Service | 2005-2014 | 2015 | lights_reduce_70p | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | -45524.3281 | 87489.6101 | 41965.282 | -737.4941 | 9886.3259 | 9148.8318 | 196219.2329 | 21.4475
4 | Food Service | 2005-2014 | 2015 | load_reduce | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | 366058.6995 | 15349.1234 | 381407.8229 | 5930.1509 | 1734.4509 | 7664.6019 | 9443.1036 | 1.232
4 | Food Service | 2005-2014 | 2015 | occupancy_setback | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | 120185.6418 | -13886.1785 | 106299.4633 | 1947.0074 | -1569.1382 | 377.8692 | 7761.4736 | 20.5401
4 | Food Service | 2005-2014 | 2015 | payback_less_than_20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | 725011.1048 | 148138.9006 | 873150.0054 | 11745.1799 | 16739.6958 | 28484.8757 | 307961.956 | 10.8114
4 | Food Service | 2005-2014 | 2015 | plug_loads_90_percent | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | -10932.7602 | -21708.2145 | -32640.9747 | -177.1107 | -2453.0282 | -2630.139 | 4487.8398 | -1.7063
4 | Food Service | 2005-2014 | 2015 | pump_fan_eff_ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251966.2136 | 8246.7619 | 207486.4849 | 0 | 308571.2575 | 47703.0148 | 0 | 98162.8156 | 25672.3232 | 0 | 1947808.8715 | -11514.792 | -15223.2787 | -26738.0707 | -186.5396 | -1720.2305 | -1906.7701 | 18689.3809 | -9.8016
5 | Hangar | 1959-pre | 2015 | air_temp_reset_enabled | 0.26866 | 0 | 123.1234 | 1.2983 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.8553 | 2.7829 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | -81578.8646 | -124876.8298 | -206455.6945 | -1321.5776 | -14111.0818 | -15432.6594 | 24802.221 | -1.6071
5 | Hangar | 1959-pre | 2015 | baseline | 0.26866 | 0 | 122.1124 | 0.095149 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.8439 | 2.4499 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Hangar | 1959-pre | 2015 | boiler_eff_upgrade | 0.26866 | 0 | 121.1237 | 0.11827 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.8553 | 2.4493 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 79782.1463 | -2739.259 | 77042.8873 | 1292.4708 | -309.5363 | 982.9345 | 599376.0491 | 609.7823
5 | Hangar | 1959-pre | 2015 | boiler_reset | 0.26866 | 0 | 99.9125 | 0.11827 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.8553 | 0.10452 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 1791357.5842 | 186465.9763 | 1977823.5605 | 29019.9929 | 21070.6553 | 50090.6482 | 3277.07 | 0.065423
5 | Hangar | 1959-pre | 2015 | cooling_cop_3_0 | 0.26866 | 0 | 121.1237 | 0.084442 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.8553 | 2.4493 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 79782.1463 | -9.8181 | 79772.3282 | 1292.4708 | -1.1094 | 1291.3613 | 56802.3003 | 43.9864
5 | Hangar | 1959-pre | 2015 | dcv_enabled | 0.26866 | 0 | 103.9913 | 0.14577 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.8553 | 2.3854 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 1462234.1397 | 196.3627 | 1462430.5024 | 23688.1931 | 22.189 | 23710.382 | 225966.2405 | 9.5303
5 | Hangar | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.26866 | 0 | 119.1329 | 0.62163 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.8553 | 2.4441 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 240426.4336 | -42934.6943 | 197491.7393 | 3894.9082 | -4851.6205 | -956.7122 | 24802.221 | -25.9244
5 | Hangar | 1959-pre | 2015 | economizers_enabled | 0.26866 | 0 | 121.1259 | 0.11474 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.8553 | 2.4487 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 79605.42 | -2405.4425 | 77199.9774 | 1289.6078 | -271.815 | 1017.7928 | 9690.7637 | 9.5214
5 | Hangar | 1959-pre | 2015 | elec_reduce | 0.26866 | 0 | 108.5522 | 0.094054 | 0 | 1.5697 | 10.7578 | 1.7103 | 0 | 2.6295 | 1.9043 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 1094201.4353 | 433441.1044 | 1527642.5398 | 17726.0633 | 48978.8448 | 66704.9081 | 795037.2306 | 11.9187
5 | Hangar | 1959-pre | 2015 | envelope_ecm_roof | 0.26866 | 0 | 112.534 | 0.10622 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.7105 | 2.2982 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 772903.0426 | 22110.4348 | 795013.4775 | 12521.0293 | 2498.4791 | 15019.5084 | 3938066.7296 | 262.1968
5 | Hangar | 1959-pre | 2015 | envelope_ecm_wall | 0.26866 | 0 | 116.2816 | 0.11133 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.6687 | 2.2589 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 470504.5554 | 28246.7678 | 498751.3232 | 7622.1738 | 3191.8848 | 10814.0586 | 3159435.3412 | 292.16
5 | Hangar | 1959-pre | 2015 | envelope_ecm_windows | 0.26866 | 0 | 119.7781 | 0.11583 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.8009 | 2.3896 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 188360.8759 | 6666.5121 | 195027.388 | 3051.4462 | 753.3159 | 3804.7621 | 661465.5095 | 173.852
5 | Hangar | 1959-pre | 2015 | exhaust_fans_occ_control | 0.26866 | 0 | 121.1232 | 0.11863 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.6227 | 2.4493 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 79821.4189 | 16003.5563 | 95824.9752 | 1293.107 | 1808.4019 | 3101.5088 | 12906.1813 | 4.1613
5 | Hangar | 1959-pre | 2015 | fans_to_variable | 0.26866 | 0 | 121.1631 | 0.11766 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.8295 | 2.4494 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 76601.0713 | -618.5424 | 75982.529 | 1240.9374 | -69.8953 | 1171.0421 | 7721.7988 | 6.594
5 | Hangar | 1959-pre | 2015 | hrv_enabled | 0.26866 | 0 | 106.9638 | 0.16669 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.8553 | 2.3837 | 0.38376 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 1222377.1578 | -32321.2929 | 1190055.8649 | 19802.51 | -3652.3061 | 16150.2039 | 640563.5497 | 39.6629
5 | Hangar | 1959-pre | 2015 | infil_reduce | 0.26866 | 0 | 69.9282 | 0.12703 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 1.9306 | 1.4602 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 4210849.8443 | 150983.2447 | 4361833.089 | 68215.7675 | 17061.1067 | 85276.8741 | 331393.6321 | 3.8861
5 | Hangar | 1959-pre | 2015 | infil_reduce_plus_setback | 0.26866 | 0 | 60.4699 | 0.078236 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 1.6571 | 1.1563 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 4974062.3899 | 201517.1737 | 5175579.5636 | 80579.8107 | 22771.4406 | 103351.2513 | 460791.1477 | 4.4585
5 | Hangar | 1959-pre | 2015 | lights_reduce_70p | 0.26866 | 0 | 125.647 | 0.077141 | 0 | 1.5697 | 10.7578 | 1.7103 | 0 | 2.8608 | 2.4903 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | -285206.9369 | 368857.4275 | 83650.4906 | -4620.3524 | 41680.8893 | 37060.5369 | 457873.6584 | 12.3547
5 | Hangar | 1959-pre | 2015 | load_reduce | 0.26866 | 0 | 49.1077 | 0.078236 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 1.6571 | 0.078115 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 5890899.258 | 288515.6476 | 6179414.9056 | 95432.568 | 32602.2682 | 128034.8362 | 464068.2177 | 3.6245
5 | Hangar | 1959-pre | 2015 | occupancy_setback | 0.26866 | 0 | 107.1011 | 0.064244 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.4157 | 1.993 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 1211292.4859 | 73910.903 | 1285203.3889 | 19622.9383 | 8351.932 | 27974.8703 | 129397.5155 | 4.6255
5 | Hangar | 1959-pre | 2015 | payback_less_than_20 | 0.26866 | 0 | 41.4899 | 0.50969 | 0 | 1.5697 | 10.7578 | 1.7103 | 0 | 1.431 | 0.02981 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 6505592.9102 | 647869.1227 | 7153462.0329 | 105390.6051 | 73209.2109 | 178599.816 | 1397320.5405 | 7.8238
5 | Hangar | 1959-pre | 2015 | plug_loads_90_percent | 0.26866 | 0 | 121.1611 | 0.11559 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.8568 | 2.4509 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 76767.9796 | -2768.7134 | 73999.2662 | 1243.6413 | -312.8646 | 930.7767 | 74817.5619 | 80.3819
5 | Hangar | 1959-pre | 2015 | pumps_to_variable | 0.26866 | 0 | 121.1237 | 0.11827 | 0 | 1.5741 | 15.3683 | 1.7103 | 0 | 2.8553 | 2.4449 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 79428.6936 | -2385.8062 | 77042.8873 | 1286.7448 | -269.5961 | 1017.1487 | 12080.9266 | 11.8772
5 | Hangar | 1959-pre | 2015 | pump_fan_eff_ | 0.26866 | 0 | 121.1237 | 0.11827 | 0 | 1.5697 | 15.3683 | 1.7103 | 0 | 2.8553 | 1.9156 | 0 | 0 | 9853497.6168 | 7677.7798 | 0 | 126663.73 | 1240098.8873 | 138003.6733 | 0 | 229479.2157 | 197688.102 | 0 | 11793109.0048 | 79782.1463 | 40323.071 | 120105.2174 | 1292.4708 | 4556.507 | 5848.9778 | 23473.5885 | 4.0133
6 | Hangar | 1960-1979 | 2015 | air_temp_reset_enabled | 0.026924 | 0 | 11.9275 | 0.12285 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.27144 | 0.262 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | -10692.3215 | -33919.6898 | -44612.0113 | -173.2156 | -3832.9249 | -4006.1406 | 7128.6793 | -1.7794
6 | Hangar | 1960-1979 | 2015 | baseline | 0.026924 | 0 | 11.8813 | 0.0077186 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.27043 | 0.23158 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Hangar | 1960-1979 | 2015 | boiler_eff_upgrade | 0.026924 | 0 | 11.7485 | 0.0099622 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.27144 | 0.23131 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 30730.9003 | -691.3747 | 30039.5256 | 497.8406 | -78.1253 | 419.7152 | 172273.2673 | 410.4527
6 | Hangar | 1960-1979 | 2015 | boiler_reset | 0.026924 | 0 | 9.7146 | 0.0099622 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.27144 | 0.010182 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 501430.0892 | 50484.4634 | 551914.5526 | 8123.1674 | 5704.7444 | 13827.9118 | 941.8988 | 0.068116
6 | Hangar | 1960-1979 | 2015 | cooling_cop_3_0 | 0.026924 | 0 | 11.7485 | 0.0071089 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.27144 | 0.23131 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 30730.9003 | -31.0413 | 30699.859 | 497.8406 | -3.5077 | 494.3329 | 16326.1743 | 33.0267
6 | Hangar | 1960-1979 | 2015 | dcv_enabled | 0.026924 | 0 | 10.0372 | 0.012072 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.27144 | 0.22523 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 426772.9085 | 228.5769 | 427001.4854 | 6913.7211 | 25.8292 | 6939.5503 | 64947.4443 | 9.359
6 | Hangar | 1960-1979 | 2015 | ecm_cold_deck_reset_control | 0.026924 | 0 | 11.5387 | 0.058359 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.27144 | 0.2307 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 79282.3364 | -11750.5481 | 67531.7883 | 1284.3738 | -1327.8119 | -43.4381 | 7128.6793 | -164.1113
6 | Hangar | 1960-1979 | 2015 | economizers_enabled | 0.026924 | 0 | 11.7487 | 0.0096452 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.27144 | 0.23119 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 30682.9273 | -589.785 | 30093.1424 | 497.0634 | -66.6457 | 430.4177 | 2785.3291 | 6.4712
6 | Hangar | 1960-1979 | 2015 | elec_reduce | 0.026924 | 0 | 10.4856 | 0.0074381 | 0 | 0.15731 | 1.0781 | 0.17139 | 0 | 0.24882 | 0.17986 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 323015.9074 | 123964.8961 | 446980.8035 | 5232.8577 | 14008.0333 | 19240.891 | 228510.401 | 11.8763
6 | Hangar | 1960-1979 | 2015 | envelope_ecm_roof | 0.026924 | 0 | 10.6813 | 0.0085355 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.25304 | 0.21224 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 277715.3434 | 8310.6062 | 286025.9496 | 4498.9886 | 939.0985 | 5438.0871 | 1224865.9569 | 225.2384
6 | Hangar | 1960-1979 | 2015 | envelope_ecm_wall | 0.026924 | 0 | 11.473 | 0.0097061 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.26048 | 0.22028 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 94503.8677 | 4458.6614 | 98962.5291 | 1530.9627 | 503.8287 | 2034.7914 | 908088.0858 | 446.2807
6 | Hangar | 1960-1979 | 2015 | envelope_ecm_windows | 0.026924 | 0 | 11.6152 | 0.0096939 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.26602 | 0.22547 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 61594.4316 | 1978.1782 | 63572.6099 | 997.8298 | 223.5341 | 1221.3639 | 190119.0825 | 155.6613
6 | Hangar | 1960-1979 | 2015 | exhaust_fans_occ_control | 0.026924 | 0 | 11.7485 | 0.0099866 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.24813 | 0.23131 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 30742.188 | 4698.5261 | 35440.7141 | 498.0234 | 530.9334 | 1028.9569 | 3709.5076 | 3.6051
6 | Hangar | 1960-1979 | 2015 | fans_to_variable | 0.026924 | 0 | 11.7522 | 0.0099134 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.269 | 0.23136 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 29875.8532 | -126.9872 | 29748.866 | 483.9888 | -14.3496 | 469.6393 | 2219.4072 | 4.7258
6 | Hangar | 1960-1979 | 2015 | hrv_enabled | 0.026924 | 0 | 10.3361 | 0.014291 | 0 | 0.15732 | 1.5401 | 0.17139 | 0 | 0.27144 | 0.22529 | 0.038459 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 357598.7525 | -9199.5165 | 348399.236 | 5793.0998 | -1039.5454 | 4753.5544 | 184111.4202 | 38.7313
6 | Hangar | 1960-1979 | 2015 | infil_reduce | 0.026924 | 0 | 7.1205 | 0.010109 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.18776 | 0.14231 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 1101783.2004 | 39239.0421 | 1141022.2425 | 17848.8878 | 4434.0118 | 22282.8996 | 95249.4913 | 4.2746
6 | Hangar | 1960-1979 | 2015 | infil_reduce_plus_setback | 0.026924 | 0 | 6.0899 | 0.0063407 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.16072 | 0.11175 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 1340284.8991 | 53439.032 | 1393723.9311 | 21712.6154 | 6038.6106 | 27751.226 | 132441.0554 | 4.7724
6 | Hangar | 1960-1979 | 2015 | lights_reduce_70p | 0.026924 | 0 | 12.1934 | 0.0061944 | 0 | 0.15731 | 1.0781 | 0.17139 | 0 | 0.27199 | 0.23537 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | -72219.0266 | 106042.7705 | 33823.7439 | -1169.9482 | 11982.8331 | 10812.8848 | 131602.5077 | 12.1709
6 | Hangar | 1960-1979 | 2015 | load_reduce | 0.026924 | 0 | 4.9882 | 0.0063407 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.16072 | 0.0077673 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 1595241.3159 | 77504.5157 | 1672745.8316 | 25842.9093 | 8758.0103 | 34600.9196 | 133382.9542 | 3.8549
6 | Hangar | 1960-1979 | 2015 | occupancy_setback | 0.026924 | 0 | 10.3092 | 0.0055115 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.22934 | 0.1869 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 363832.4126 | 20360.2797 | 384192.6923 | 5894.0851 | 2300.7116 | 8194.7967 | 37191.5641 | 4.5384
6 | Hangar | 1960-1979 | 2015 | payback_less_than_20 | 0.026924 | 0 | 4.2122 | 0.046482 | 0 | 0.15731 | 1.0781 | 0.17139 | 0 | 0.13807 | 0.0029265 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 1774849.1773 | 181507.0254 | 1956356.2027 | 28752.5567 | 20510.2939 | 49262.8505 | 401619.2762 | 8.1526
6 | Hangar | 1960-1979 | 2015 | plug_loads_90_percent | 0.026924 | 0 | 11.7534 | 0.0097183 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.27159 | 0.23152 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 29607.7691 | -716.7721 | 28890.997 | 479.6459 | -80.9953 | 398.6506 | 21504.139 | 53.9423
6 | Hangar | 1960-1979 | 2015 | pumps_to_variable | 0.026924 | 0 | 11.7485 | 0.0099622 | 0 | 0.15775 | 1.5401 | 0.17139 | 0 | 0.27144 | 0.23087 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 30629.3105 | -589.785 | 30039.5256 | 496.1948 | -66.6457 | 429.5491 | 3472.3121 | 8.0836
6 | Hangar | 1960-1979 | 2015 | pump_fan_eff_ | 0.026924 | 0 | 11.7485 | 0.0099622 | 0 | 0.15731 | 1.5401 | 0.17139 | 0 | 0.27144 | 0.18092 | 0 | 0 | 2749656.4742 | 1786.2865 | 0 | 36405.8168 | 356430.4704 | 39665.1547 | 0 | 62584.9317 | 53594.2386 | 0 | 3300123.3728 | 30730.9003 | 10971.6933 | 41702.5936 | 497.8406 | 1239.8013 | 1737.6419 | 6746.8024 | 3.8827
7 | Hangar | 1980-2004 | 2015 | air_temp_reset_enabled | 0.031409 | 0 | 8.8849 | 0.085719 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.22353 | 0.19241 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | -24940.4501 | -23877.1231 | -48817.5732 | -404.0353 | -2698.1149 | -3102.1502 | 8316.2205 | -2.6808
7 | Hangar | 1980-2004 | 2015 | baseline | 0.031409 | 0 | 8.7771 | 0.0071978 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.22201 | 0.16928 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Hangar | 1980-2004 | 2015 | boiler_eff_upgrade | 0.031409 | 0 | 8.7161 | 0.0101 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.22353 | 0.17017 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 14109.658 | -1231.2207 | 12878.4373 | 228.5765 | -139.1279 | 89.4485 | 77262.8782 | 863.7693
7 | Hangar | 1980-2004 | 2015 | boiler_reset | 0.031409 | 0 | 7.088 | 0.0101 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.22353 | 0.0092889 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 390906.0016 | 36001.6846 | 426907.6862 | 6332.6772 | 4068.1904 | 10400.8676 | 1098.8063 | 0.10565
7 | Hangar | 1980-2004 | 2015 | cooling_cop_3_0 | 0.031409 | 0 | 8.7161 | 0.008663 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.22353 | 0.17017 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 14109.658 | -898.7253 | 13210.9327 | 228.5765 | -101.556 | 127.0205 | 19045.8933 | 149.9435
7 | Hangar | 1980-2004 | 2015 | dcv_enabled | 0.031409 | 0 | 6.7649 | 0.015078 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.22353 | 0.15902 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 465664.8034 | 197.522 | 465862.3254 | 7543.7698 | 22.32 | 7566.0898 | 75766.8067 | 10.014
7 | Hangar | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.031409 | 0 | 8.4843 | 0.0435 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.22353 | 0.17185 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 67766.5213 | -9349.3768 | 58417.1446 | 1097.8176 | -1056.4796 | 41.3381 | 8316.2205 | 201.1758
7 | Hangar | 1980-2004 | 2015 | economizers_enabled | 0.031409 | 0 | 8.7164 | 0.0096161 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.22353 | 0.1701 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 14050.4014 | -1102.8314 | 12947.57 | 227.6165 | -124.6199 | 102.9966 | 3249.3271 | 31.5479
7 | Hangar | 1980-2004 | 2015 | elec_reduce | 0.031409 | 0 | 7.2414 | 0.0079944 | 0 | 0.18352 | 1.2577 | 0.19995 | 0 | 0.1972 | 0.12895 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 355391.5381 | 139631.6251 | 495023.1632 | 5757.3429 | 15778.3736 | 21535.7166 | 266577.1313 | 12.3784
7 | Hangar | 1980-2004 | 2015 | envelope_ecm_roof | 0.031409 | 0 | 8.1515 | 0.0093742 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.21367 | 0.1602 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 144770.4903 | 3525.7685 | 148296.2588 | 2345.2819 | 398.4118 | 2743.6938 | 1320439.4602 | 481.2634
7 | Hangar | 1980-2004 | 2015 | envelope_ecm_wall | 0.031409 | 0 | 8.5525 | 0.0098863 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.21716 | 0.16376 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 51974.6339 | 1777.6984 | 53752.3323 | 841.9891 | 200.8799 | 1042.869 | 1059363.2315 | 1015.8162
7 | Hangar | 1980-2004 | 2015 | envelope_ecm_windows | 0.031409 | 0 | 8.6065 | 0.010114 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.21885 | 0.16515 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 39481.3646 | 1010.6545 | 40492.0191 | 639.5981 | 114.204 | 753.8021 | 221790.3404 | 294.2289
7 | Hangar | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.031409 | 0 | 8.7161 | 0.010128 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.19633 | 0.17017 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 14122.8262 | 5056.5643 | 19179.3905 | 228.7898 | 571.3918 | 800.1816 | 4327.4612 | 5.4081
7 | Hangar | 1980-2004 | 2015 | fans_to_variable | 0.031409 | 0 | 8.7188 | 0.010071 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.22164 | 0.17023 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 13490.7556 | -799.9643 | 12690.7913 | 218.5502 | -90.396 | 128.1543 | 2589.1303 | 20.2032
7 | Hangar | 1980-2004 | 2015 | hrv_enabled | 0.031409 | 0 | 7.1023 | 0.017667 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.22353 | 0.16303 | 0.044865 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 387600.7994 | -11713.0572 | 375887.7422 | 6279.133 | -1323.5755 | 4955.5575 | 214781.883 | 43.3416
7 | Hangar | 1980-2004 | 2015 | infil_reduce | 0.031409 | 0 | 6.9578 | 0.011494 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.1944 | 0.13802 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 421037.9895 | 12628.2427 | 433666.2322 | 6820.8154 | 1426.9914 | 8247.8069 | 101985.3403 | 12.3651
7 | Hangar | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.031409 | 0 | 5.9205 | 0.0069987 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.16528 | 0.10714 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 661099.698 | 27554.3252 | 688654.0232 | 10709.8151 | 3113.6387 | 13823.4539 | 145372.514 | 10.5164
7 | Hangar | 1980-2004 | 2015 | lights_reduce_70p | 0.031409 | 0 | 9.196 | 0.0051779 | 0 | 0.18352 | 1.2577 | 0.19995 | 0 | 0.22424 | 0.17505 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | -96950.4034 | 123355.8087 | 26405.4053 | -1570.5965 | 13939.2064 | 12368.6098 | 153525.6987 | 12.4125
7 | Hangar | 1980-2004 | 2015 | load_reduce | 0.031409 | 0 | 4.8386 | 0.0069987 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.16528 | 0.0082362 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 911468.7652 | 50443.8381 | 961912.6032 | 14765.794 | 5700.1537 | 20465.9477 | 146471.3203 | 7.1568
7 | Hangar | 1980-2004 | 2015 | occupancy_setback | 0.031409 | 0 | 7.5449 | 0.0060456 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.19198 | 0.13498 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 285165.8673 | 15153.2328 | 300319.1001 | 4619.6871 | 1712.3153 | 6332.0024 | 43387.1738 | 6.852
7 | Hangar | 1980-2004 | 2015 | payback_less_than_20 | 0.031409 | 0 | 3.9379 | 0.043073 | 0 | 0.18352 | 1.2577 | 0.19995 | 0 | 0.13891 | 0.0029872 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 1119907.1944 | 174155.1864 | 1294062.3808 | 18142.4965 | 19679.5361 | 37822.0326 | 459392.1716 | 12.1462
7 | Hangar | 1980-2004 | 2015 | plug_loads_90_percent | 0.031409 | 0 | 8.7172 | 0.0098437 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.22369 | 0.17037 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 13859.4634 | -1254.265 | 12605.1985 | 224.5233 | -141.7319 | 82.7914 | 25086.4365 | 303.0079
7 | Hangar | 1980-2004 | 2015 | pumps_to_variable | 0.031409 | 0 | 8.7161 | 0.0101 | 0 | 0.18403 | 1.7967 | 0.19995 | 0 | 0.22353 | 0.16966 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 13991.1448 | -1112.7075 | 12878.4373 | 226.6565 | -125.7359 | 100.9206 | 4050.7521 | 40.138
7 | Hangar | 1980-2004 | 2015 | pump_fan_eff_ | 0.031409 | 0 | 8.7161 | 0.0101 | 0 | 0.18352 | 1.7967 | 0.19995 | 0 | 0.22353 | 0.1331 | 0 | 0 | 2031254.1543 | 1665.7692 | 0 | 42470.5315 | 415806.9474 | 46272.8309 | 0 | 51378.7757 | 39175.2054 | 0 | 2628024.2145 | 14109.658 | 7347.82 | 21457.4781 | 228.5765 | 830.3037 | 1058.8801 | 7870.7281 | 7.4331
10 | Maintenance Shop-Small | 1959-pre | 2015 | air_temp_reset_enabled | 0.0067581 | 0 | 5.2224 | 0.054189 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.1912 | 0.28043 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | -17607.6295 | -10182.9714 | -27790.6009 | -285.2436 | -1150.6758 | -1435.9194 | 4410.9585 | -3.0719
10 | Maintenance Shop-Small | 1959-pre | 2015 | baseline | 0.0067581 | 0 | 5.1168 | 0.0059349 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.18347 | 0.27535 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Maintenance Shop-Small | 1959-pre | 2015 | boiler_eff_upgrade | 0.0067581 | 0 | 5.0858 | 0.0082191 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.18335 | 0.27539 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 5179.915 | -367.3216 | 4812.5934 | 83.9146 | -41.5073 | 42.4073 | 81972.5379 | 1932.9827
10 | Maintenance Shop-Small | 1959-pre | 2015 | boiler_reset | 0.0067581 | 0 | 3.163 | 0.0082191 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.18335 | 0.27539 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 325824.4739 | -367.3216 | 325457.1523 | 5278.3565 | -41.5073 | 5236.8491 | 1165.7855 | 0.22261
10 | Maintenance Shop-Small | 1959-pre | 2015 | cooling_cop_3_0 | 0.0067581 | 0 | 5.0858 | 0.0058737 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.18335 | 0.27539 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 5179.915 | 23.8079 | 5203.7228 | 83.9146 | 2.6903 | 86.6049 | 12607.9689 | 145.5803
10 | Maintenance Shop-Small | 1959-pre | 2015 | dcv_enabled | 0.0067581 | 0 | 5.0858 | 0.0082191 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.18335 | 0.27539 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 5179.915 | -367.3216 | 4812.5934 | 83.9146 | -41.5073 | 42.4073 | 9395.6817 | 221.5582
10 | Maintenance Shop-Small | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.0067581 | 0 | 5.0702 | 0.030552 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.19563 | 0.27244 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 7768.1719 | -5645.8692 | 2122.3027 | 125.8444 | -637.9832 | -512.1388 | 4410.9585 | -8.6128
10 | Maintenance Shop-Small | 1959-pre | 2015 | economizers_enabled | 0.0067581 | 0 | 5.0866 | 0.0076685 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.18337 | 0.2748 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 5033.6665 | -180.2597 | 4853.4069 | 81.5454 | -20.3693 | 61.1761 | 1723.7033 | 28.1761
10 | Maintenance Shop-Small | 1959-pre | 2015 | elec_reduce | 0.0067581 | 0 | 5.2416 | 0.0047316 | 0 | 0.032713 | 0.26087 | 0.044644 | 0 | 0.18539 | 0.21778 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | -20808.0891 | 28123.9113 | 7315.8221 | -337.091 | 3178.002 | 2840.9109 | 48368.3224 | 17.0256
10 | Maintenance Shop-Small | 1959-pre | 2015 | envelope_ecm_roof | 0.0067581 | 0 | 4.7521 | 0.0072198 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.17248 | 0.25771 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 60825.7382 | 4560.91 | 65386.6482 | 985.377 | 515.3828 | 1500.7598 | 131741.7527 | 87.7834
10 | Maintenance Shop-Small | 1959-pre | 2015 | envelope_ecm_wall | 0.0067581 | 0 | 4.4363 | 0.008056 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.16175 | 0.24354 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 113485.3727 | 8574.2388 | 122059.6115 | 1838.463 | 968.889 | 2807.352 | 322701.9904 | 114.9489
10 | Maintenance Shop-Small | 1959-pre | 2015 | envelope_ecm_windows | 0.0067581 | 0 | 5.0772 | 0.0082191 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.18325 | 0.275 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 6611.789 | -285.6946 | 6326.0944 | 107.111 | -32.2835 | 74.8275 | 8389.4824 | 112.1176
10 | Maintenance Shop-Small | 1959-pre | 2015 | exhaust_fans_occ_control | 0.0067581 | 0 | 5.0858 | 0.0082191 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.18335 | 0.27539 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 5179.915 | -367.3216 | 4812.5934 | 83.9146 | -41.5073 | 42.4073 | 918.4954 | 21.6589
10 | Maintenance Shop-Small | 1959-pre | 2015 | fans_to_variable | 0.0067581 | 0 | 5.0866 | 0.0081784 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.18272 | 0.27543 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 5037.0677 | -261.8867 | 4775.181 | 81.6005 | -29.5932 | 52.0073 | 3297.5695 | 63.4059
10 | Maintenance Shop-Small | 1959-pre | 2015 | hrv_enabled | 0.0067581 | 0 | 4.9949 | 0.0089126 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.18304 | 0.27482 | 0.016234 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 20325.1292 | -3044.0078 | 17281.1214 | 329.2671 | -343.9729 | -14.7058 | 59513.2908 | -4046.9295
10 | Maintenance Shop-Small | 1959-pre | 2015 | infil_reduce | 0.0067581 | 0 | 2.822 | 0.010442 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.10928 | 0.15969 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 382698.1036 | 30909.4335 | 413607.5371 | 6199.7093 | 3492.766 | 9692.4753 | 57382.7239 | 5.9203
10 | Maintenance Shop-Small | 1959-pre | 2015 | infil_reduce_plus_setback | 0.0067581 | 0 | 2.4654 | 0.010218 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.11452 | 0.1603 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 442156.5891 | 29970.7227 | 472127.3118 | 7162.9367 | 3386.6917 | 10549.6284 | 62763.3447 | 5.9493
10 | Maintenance Shop-Small | 1959-pre | 2015 | lights_reduce_70p | 0.0067581 | 0 | 5.2401 | 0.0048744 | 0 | 0.032713 | 0.26087 | 0.044644 | 0 | 0.18535 | 0.27839 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | -20566.6092 | 17998.759 | -2567.8502 | -333.1791 | 2033.8598 | 1700.6807 | 29441.7517 | 17.3117
10 | Maintenance Shop-Small | 1959-pre | 2015 | load_reduce | 0.0067581 | 0 | 1.5218 | 0.010218 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.11452 | 0.1603 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 599523.29 | 29970.7227 | 629494.0127 | 9712.2773 | 3386.6917 | 13098.969 | 63929.1301 | 4.8805
10 | Maintenance Shop-Small | 1959-pre | 2015 | occupancy_setback | 0.0067581 | 0 | 4.4815 | 0.0075461 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.1972 | 0.28198 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 105948.4774 | -3663.0127 | 102285.4646 | 1716.3653 | -413.9204 | 1302.4449 | 5380.6208 | 4.1312
10 | Maintenance Shop-Small | 1959-pre | 2015 | payback_less_than_20 | 0.0067581 | 0 | 1.7026 | 0.036242 | 0 | 0.032713 | 0.26087 | 0.044644 | 0 | 0.12788 | 0.12467 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 569368.9065 | 47986.4874 | 617355.3939 | 9223.7763 | 5422.4731 | 14646.2494 | 124273.1998 | 8.485
10 | Maintenance Shop-Small | 1959-pre | 2015 | plug_loads_90_percent | 0.0067581 | 0 | 5.0869 | 0.0079948 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.18337 | 0.27547 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 4986.0508 | -346.9149 | 4639.1359 | 80.774 | -39.2014 | 41.5726 | 3111.1829 | 74.8373
10 | Maintenance Shop-Small | 1959-pre | 2015 | pump_fan_eff_ | 0.0067581 | 0 | 5.0858 | 0.0082191 | 0 | 0.032713 | 0.37266 | 0.044644 | 0 | 0.18335 | 0.21539 | 0 | 0 | 853298.3098 | 989.7277 | 0 | 5455.4062 | 62145.3751 | 7445.0649 | 0 | 30596.5299 | 45918.6027 | 0 | 1005849.0163 | 5179.915 | 9638.7912 | 14818.7062 | 83.9146 | 1089.1834 | 1173.098 | 5501.2232 | 4.6895
11 | Maintenance Shop-Small | 1960-1979 | 2015 | air_temp_reset_enabled | 0.0031284 | 0 | 2.231 | 0.022876 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.082043 | 0.12157 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | -6561.3425 | -6089.3978 | -12650.7403 | -106.2937 | -688.102 | -794.3957 | 2833.6592 | -3.5671
11 | Maintenance Shop-Small | 1960-1979 | 2015 | baseline | 0.0031284 | 0 | 2.2027 | 0.0022659 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.078871 | 0.11904 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Maintenance Shop-Small | 1960-1979 | 2015 | boiler_eff_upgrade | 0.0031284 | 0 | 2.1825 | 0.0038237 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.079003 | 0.11926 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 4664.8239 | -441.3557 | 4223.4682 | 75.5701 | -49.8732 | 25.697 | 52660.2639 | 2049.2805
11 | Maintenance Shop-Small | 1960-1979 | 2015 | boiler_reset | 0.0031284 | 0 | 1.356 | 0.0038237 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.079003 | 0.11926 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 195948.8243 | -441.3557 | 195507.4686 | 3174.371 | -49.8732 | 3124.4978 | 748.9163 | 0.23969
11 | Maintenance Shop-Small | 1960-1979 | 2015 | cooling_cop_3_0 | 0.0031284 | 0 | 2.1825 | 0.0027285 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.079003 | 0.11926 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 4664.8239 | -187.9039 | 4476.92 | 75.5701 | -21.2331 | 54.337 | 8099.5292 | 149.061
11 | Maintenance Shop-Small | 1960-1979 | 2015 | dcv_enabled | 0.0031284 | 0 | 2.1825 | 0.0038237 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.079003 | 0.11926 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 4664.8239 | -441.3557 | 4223.4682 | 75.5701 | -49.8732 | 25.697 | 6035.9127 | 234.8883
11 | Maintenance Shop-Small | 1960-1979 | 2015 | ecm_cold_deck_reset_control | 0.0031284 | 0 | 2.1734 | 0.013652 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.084234 | 0.11769 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 6768.9108 | -3563.6196 | 3205.2912 | 109.6564 | -402.689 | -293.0327 | 2833.6592 | -9.6701
11 | Maintenance Shop-Small | 1960-1979 | 2015 | economizers_enabled | 0.0031284 | 0 | 2.1831 | 0.0035593 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.079013 | 0.11887 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 4535.9131 | -292.7805 | 4243.1326 | 73.4818 | -33.0842 | 40.3976 | 1107.3302 | 27.4108
11 | Maintenance Shop-Small | 1960-1979 | 2015 | elec_reduce | 0.0031284 | 0 | 2.2536 | 0.0021526 | 0 | 0.015144 | 0.12076 | 0.020667 | 0 | 0.079919 | 0.09443 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | -11778.9535 | 17455.3997 | 5676.4462 | -190.819 | 1972.4602 | 1781.6411 | 31072.4626 | 17.4404
11 | Maintenance Shop-Small | 1960-1979 | 2015 | envelope_ecm_roof | 0.0031284 | 0 | 1.9381 | 0.003125 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.071073 | 0.10642 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 61226.0872 | 4527.1734 | 65753.2606 | 991.8626 | 511.5706 | 1503.4332 | 123932.2346 | 82.4328
11 | Maintenance Shop-Small | 1960-1979 | 2015 | envelope_ecm_wall | 0.0031284 | 0 | 2.056 | 0.0039275 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.07466 | 0.11268 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 33938.5059 | 2062.5732 | 36001.0791 | 549.8038 | 233.0708 | 782.8746 | 207308.1109 | 264.8037
11 | Maintenance Shop-Small | 1960-1979 | 2015 | envelope_ecm_windows | 0.0031284 | 0 | 2.1786 | 0.0038237 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.078956 | 0.11906 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 5569.3846 | -384.5475 | 5184.8371 | 90.224 | -43.4539 | 46.7702 | 5389.5166 | 115.2341
11 | Maintenance Shop-Small | 1960-1979 | 2015 | exhaust_fans_occ_control | 0.0031284 | 0 | 2.1825 | 0.0038237 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.079003 | 0.11926 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 4664.8239 | -441.3557 | 4223.4682 | 75.5701 | -49.8732 | 25.697 | 590.0538 | 22.962
11 | Maintenance Shop-Small | 1960-1979 | 2015 | fans_to_variable | 0.0031284 | 0 | 2.1829 | 0.0038048 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.078729 | 0.11927 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 4577.4268 | -375.8078 | 4201.6189 | 74.1543 | -42.4663 | 31.688 | 2118.4031 | 66.8518
11 | Maintenance Shop-Small | 1960-1979 | 2015 | hrv_enabled | 0.0031284 | 0 | 2.1403 | 0.004173 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.078871 | 0.11906 | 0.0075151 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 14429.2727 | -2184.9292 | 12244.3435 | 233.7542 | -246.897 | -13.1428 | 38232.1407 | -2908.9829
11 | Maintenance Shop-Small | 1960-1979 | 2015 | infil_reduce | 0.0031284 | 0 | 1.239 | 0.0047017 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.048272 | 0.070846 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 223015.7277 | 17671.7077 | 240687.4355 | 3612.8548 | 1996.903 | 5609.7578 | 36863.4357 | 6.5713
11 | Maintenance Shop-Small | 1960-1979 | 2015 | infil_reduce_plus_setback | 0.0031284 | 0 | 1.0679 | 0.0046167 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.050491 | 0.070374 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 262626.31 | 17287.1602 | 279913.4701 | 4254.5462 | 1953.4491 | 6207.9953 | 40320.0191 | 6.4949
11 | Maintenance Shop-Small | 1960-1979 | 2015 | lights_reduce_70p | 0.0031284 | 0 | 2.2527 | 0.0022187 | 0 | 0.015144 | 0.12076 | 0.020667 | 0 | 0.0799 | 0.12073 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | -11580.125 | 11357.2622 | -222.8628 | -187.598 | 1283.3706 | 1095.7726 | 18913.7784 | 17.2607
11 | Maintenance Shop-Small | 1960-1979 | 2015 | load_reduce | 0.0031284 | 0 | 0.65785 | 0.0046167 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.050491 | 0.070374 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 357513.4171 | 17287.1602 | 374800.5773 | 5791.7174 | 1953.4491 | 7745.1665 | 41068.9354 | 5.3025
11 | Maintenance Shop-Small | 1960-1979 | 2015 | occupancy_setback | 0.0031284 | 0 | 1.9064 | 0.0035215 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.084838 | 0.12155 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 68576.1892 | -2252.662 | 66323.5271 | 1110.9343 | -254.5508 | 856.3835 | 3456.5834 | 4.0363
11 | Maintenance Shop-Small | 1960-1979 | 2015 | payback_less_than_20 | 0.0031284 | 0 | 0.73661 | 0.015918 | 0 | 0.015144 | 0.12076 | 0.020667 | 0 | 0.056543 | 0.054976 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 339284.5524 | 28810.477 | 368095.0294 | 5496.4097 | 3255.5839 | 8751.9936 | 79834.7797 | 9.1219
11 | Maintenance Shop-Small | 1960-1979 | 2015 | plug_loads_90_percent | 0.0031284 | 0 | 2.1832 | 0.0037198 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.079013 | 0.11931 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 4505.3241 | -430.4311 | 4074.893 | 72.9863 | -48.6387 | 24.3475 | 1998.6658 | 82.089
11 | Maintenance Shop-Small | 1960-1979 | 2015 | pump_fan_eff_ | 0.0031284 | 0 | 2.1825 | 0.0038237 | 0 | 0.015144 | 0.17251 | 0.020667 | 0 | 0.079003 | 0.093269 | 0 | 0 | 509757.1018 | 524.383 | 0 | 3504.6265 | 39923.0271 | 4782.8101 | 0 | 18252.8989 | 27549.7728 | 0 | 604294.6202 | 4664.8239 | 5573.7545 | 10238.5784 | 75.5701 | 629.8343 | 705.4044 | 3534.06 | 5.01
12 | Maintenance Shop-Small | 1980-2004 | 2015 | air_temp_reset_enabled | 0.021039 | 0 | 7.9885 | 0.079049 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.31429 | 0.45493 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | -22325.0034 | -18380.2525 | -40705.2559 | -361.6651 | -2076.9685 | -2438.6336 | 18536.2018 | -7.6011
12 | Maintenance Shop-Small | 1980-2004 | 2015 | baseline | 0.021039 | 0 | 7.8893 | 0.01181 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.30616 | 0.44864 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Maintenance Shop-Small | 1980-2004 | 2015 | boiler_eff_upgrade | 0.021039 | 0 | 7.8362 | 0.022603 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.30908 | 0.45099 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 11962.886 | -3616.0217 | 8346.8643 | 193.7988 | -408.6105 | -214.8117 | 173593.4359 | -808.1191
12 | Maintenance Shop-Small | 1980-2004 | 2015 | boiler_reset | 0.021039 | 0 | 4.8558 | 0.022603 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.30908 | 0.45099 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 682856.3948 | -3616.0217 | 679240.3731 | 11062.2736 | -408.6105 | 10653.6631 | 4898.9885 | 0.45984
12 | Maintenance Shop-Small | 1980-2004 | 2015 | cooling_cop_3_0 | 0.021039 | 0 | 7.8362 | 0.019365 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.30908 | 0.45099 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 11962.886 | -2887.1003 | 9075.7856 | 193.7988 | -326.2423 | -132.4436 | 52982.5559 | -400.0387
12 | Maintenance Shop-Small | 1980-2004 | 2015 | dcv_enabled | 0.021039 | 0 | 7.8362 | 0.022603 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.30908 | 0.45099 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 11962.886 | -3616.0217 | 8346.8643 | 193.7988 | -408.6105 | -214.8117 | 39483.5392 | -183.8053
12 | Maintenance Shop-Small | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.021039 | 0 | 7.8209 | 0.058223 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.32261 | 0.44153 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 15393.1042 | -12548.8816 | 2844.2226 | 249.3683 | -1418.0236 | -1168.6553 | 18536.2018 | -15.8611
12 | Maintenance Shop-Small | 1980-2004 | 2015 | economizers_enabled | 0.021039 | 0 | 7.8444 | 0.019619 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.30915 | 0.44407 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 10104.8511 | -1400.6724 | 8704.1787 | 163.6986 | -158.276 | 5.4226 | 7243.5305 | 1335.8031
12 | Maintenance Shop-Small | 1980-2004 | 2015 | elec_reduce | 0.021039 | 0 | 8.2866 | 0.0097779 | 0 | 0.10184 | 0.81214 | 0.13899 | 0 | 0.31588 | 0.36369 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | -89428.6469 | 95731.6728 | 6303.0259 | -1448.7441 | 10817.679 | 9368.9349 | 203258.5401 | 21.6949
12 | Maintenance Shop-Small | 1980-2004 | 2015 | envelope_ecm_roof | 0.021039 | 0 | 7.4609 | 0.021651 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.29664 | 0.43112 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 96432.009 | 3873.288 | 100305.2971 | 1562.1985 | 437.6815 | 1999.8801 | 703045.48 | 351.5438
12 | Maintenance Shop-Small | 1980-2004 | 2015 | envelope_ecm_wall | 0.021039 | 0 | 7.5982 | 0.023111 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.30083 | 0.43778 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 65531.4601 | 1100.5283 | 66631.9885 | 1061.6097 | 124.3597 | 1185.9694 | 1356092.8363 | 1143.4468
12 | Maintenance Shop-Small | 1980-2004 | 2015 | envelope_ecm_windows | 0.021039 | 0 | 7.8157 | 0.02273 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.30883 | 0.44997 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 16565.0954 | -3358.7553 | 13206.3401 | 268.3545 | -379.5394 | -111.1848 | 35255.1805 | -317.0863
12 | Maintenance Shop-Small | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.021039 | 0 | 7.8362 | 0.022603 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.30908 | 0.45099 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 11962.886 | -3616.0217 | 8346.8643 | 193.7988 | -408.6105 | -214.8117 | 3859.7996 | -17.9683
12 | Maintenance Shop-Small | 1980-2004 | 2015 | fans_to_variable | 0.021039 | 0 | 7.8375 | 0.02254 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.30807 | 0.45105 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 11662.7419 | -3387.3405 | 8275.4014 | 188.9364 | -382.7695 | -193.8331 | 13857.3996 | -71.4914
12 | Maintenance Shop-Small | 1980-2004 | 2015 | hrv_enabled | 0.021039 | 0 | 7.5509 | 0.026096 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.30781 | 0.4487 | 0.05054 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 76165.1365 | -14978.6195 | 61186.5171 | 1233.8752 | -1692.584 | -458.7088 | 250093.1193 | -545.2111
12 | Maintenance Shop-Small | 1980-2004 | 2015 | infil_reduce | 0.021039 | 0 | 5.7381 | 0.027302 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.23975 | 0.34121 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 484246.7612 | 35645.6841 | 519892.4453 | 7844.7975 | 4027.9623 | 11872.7598 | 221144.6753 | 18.6262
12 | Maintenance Shop-Small | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.021039 | 0 | 4.9347 | 0.02527 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.24394 | 0.33315 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 665105.0156 | 36974.8936 | 702079.9092 | 10774.7013 | 4178.163 | 14952.8642 | 243755.6958 | 16.3016
12 | Maintenance Shop-Small | 1980-2004 | 2015 | lights_reduce_70p | 0.021039 | 0 | 8.2852 | 0.010222 | 0 | 0.10184 | 0.81214 | 0.13899 | 0 | 0.31581 | 0.46477 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | -89114.2102 | 72892.1367 | -16222.0736 | -1443.6502 | 8236.8114 | 6793.1612 | 123723.2796 | 18.2129
12 | Maintenance Shop-Small | 1980-2004 | 2015 | load_reduce | 0.021039 | 0 | 3.0586 | 0.02527 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.24394 | 0.33315 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 1087407.7532 | 36974.8936 | 1124382.6469 | 17616.0056 | 4178.163 | 21794.1686 | 248654.6316 | 11.4092
12 | Maintenance Shop-Small | 1980-2004 | 2015 | occupancy_setback | 0.021039 | 0 | 6.784 | 0.020127 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.31981 | 0.44642 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 248805.1598 | -4444.9911 | 244360.1687 | 4030.6436 | -502.284 | 3528.3596 | 22611.0205 | 6.4084
12 | Maintenance Shop-Small | 1980-2004 | 2015 | payback_less_than_20 | 0.021039 | 0 | 3.4308 | 0.060128 | 0 | 0.10184 | 0.81214 | 0.13899 | 0 | 0.27378 | 0.25994 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 1003624.6738 | 117227.7068 | 1120852.3806 | 16258.7197 | 13246.7309 | 29505.4506 | 502238.9914 | 17.0219
12 | Maintenance Shop-Small | 1980-2004 | 2015 | plug_loads_90_percent | 0.021039 | 0 | 7.837 | 0.021969 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.30908 | 0.45118 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 11777.0825 | -3515.9737 | 8261.1088 | 190.7887 | -397.305 | -206.5163 | 13074.1457 | -63.3081
12 | Maintenance Shop-Small | 1980-2004 | 2015 | pump_fan_eff_ | 0.021039 | 0 | 7.8362 | 0.022603 | 0 | 0.10184 | 1.1601 | 0.13899 | 0 | 0.30908 | 0.3527 | 0 | 0 | 1775924.008 | 2658.4191 | 0 | 22925.2916 | 261153.9453 | 31286.4485 | 0 | 68918.8006 | 100991.3407 | 0 | 2263858.2538 | 11962.886 | 18508.8857 | 30471.7716 | 193.7988 | 2091.5041 | 2285.3028 | 23117.8288 | 10.1159
8 | Maintenance Shop | 1959-pre | 2015 | air_temp_reset_enabled | 0.017211 | 0 | 9.5634 | 0.012886 | 0.037349 | 0 | 0.48922 | 0.070129 | 0 | 0.58653 | 0.49914 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 3558.8168 | -4902.1925 | -1343.3757 | 57.6528 | -553.9478 | -496.2949 | 2213.6356 | -4.4603
8 | Maintenance Shop | 1959-pre | 2015 | baseline | 0.017211 | 0 | 9.6041 | 0.0065721 | 0.037366 | 0 | 0.48922 | 0.070129 | 0 | 0.54033 | 0.49554 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Maintenance Shop | 1959-pre | 2015 | boiler_eff_upgrade | 0.017211 | 0 | 9.5794 | 0.0073149 | 0.037366 | 0 | 0.48922 | 0.070129 | 0 | 0.54138 | 0.49914 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 2163.23 | -471.3104 | 1691.9197 | 35.0443 | -53.2581 | -18.2137 | 41137.8449 | -2258.615
8 | Maintenance Shop | 1959-pre | 2015 | boiler_reset | 0.017211 | 0 | 6.0411 | 0.0073149 | 0.037366 | 0 | 0.48922 | 0.070129 | 0 | 0.54138 | 0.49914 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 311369.6601 | -471.3104 | 310898.3497 | 5044.1885 | -53.2581 | 4990.9304 | 585.0484 | 0.11722
8 | Maintenance Shop | 1959-pre | 2015 | cooling_cop_3_0 | 0.017211 | 0 | 9.5794 | 0.0052157 | 0.037366 | 0 | 0.48922 | 0.070129 | 0 | 0.54138 | 0.49914 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 2163.23 | -287.8662 | 1875.3638 | 35.0443 | -32.5289 | 2.5154 | 3110.4667 | 1236.5484
8 | Maintenance Shop | 1959-pre | 2015 | dcv_enabled | 0.017211 | 0 | 7.3534 | 0.0079608 | 0.037349 | 0 | 0.48922 | 0.070129 | 0 | 0.5381 | 0.49912 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 196690.2455 | -238.4774 | 196451.7681 | 3186.382 | -26.9479 | 3159.434 | 5763.0413 | 1.8241
8 | Maintenance Shop | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.017211 | 0 | 9.5861 | 0.011206 | 0.037366 | 0 | 0.48922 | 0.070129 | 0 | 0.54106 | 0.49914 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 1577.6198 | -783.1655 | 794.4543 | 25.5574 | -88.4977 | -62.9403 | 2213.6356 | -35.1704
8 | Maintenance Shop | 1959-pre | 2015 | economizers_enabled | 0.017211 | 0 | 9.5811 | 0.0055225 | 0.037366 | 0 | 0.48922 | 0.070129 | 0 | 0.54141 | 0.49914 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 2017.8858 | -317.4995 | 1700.3863 | 32.6898 | -35.8774 | -3.1877 | 738.4935 | -231.6701
8 | Maintenance Shop | 1959-pre | 2015 | elec_reduce | 0.017211 | 0 | 7.5358 | 0.0067659 | 0.037349 | 0 | 0.34246 | 0.070129 | 0 | 0.51643 | 0.38914 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 180748.9475 | 24196.2854 | 204945.233 | 2928.1329 | 2734.1803 | 5662.3132 | 40137.7033 | 7.0886
8 | Maintenance Shop | 1959-pre | 2015 | envelope_ecm_roof | 0.017211 | 0 | 9.0582 | 0.0072503 | 0.037366 | 0 | 0.48922 | 0.070129 | 0 | 0.50896 | 0.46823 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 47711.0053 | 5068.7034 | 52779.7087 | 772.9183 | 572.7635 | 1345.6818 | 162439.2224 | 120.7115
8 | Maintenance Shop | 1959-pre | 2015 | envelope_ecm_wall | 0.017211 | 0 | 8.5081 | 0.0073795 | 0.037366 | 0 | 0.48922 | 0.070129 | 0 | 0.48012 | 0.43779 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 95783.2544 | 10237.5956 | 106020.85 | 1551.6887 | 1156.8483 | 2708.537 | 315369.1492 | 116.4352
8 | Maintenance Shop | 1959-pre | 2015 | envelope_ecm_windows | 0.017211 | 0 | 9.5105 | 0.0077509 | 0.037366 | 0 | 0.48922 | 0.070129 | 0 | 0.54019 | 0.49709 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 8180.1987 | -225.7774 | 7954.4212 | 132.5192 | -25.5129 | 107.0064 | 45779.0854 | 427.8165
8 | Maintenance Shop | 1959-pre | 2015 | exhaust_fans_occ_control | 0.017211 | 0 | 9.5681 | 0.0073149 | 0.037366 | 0 | 0.48922 | 0.070129 | 0 | 0.52649 | 0.49914 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 3148.1841 | 829.7321 | 3977.9162 | 51.0006 | 93.7597 | 144.7603 | 1382.2275 | 9.5484
8 | Maintenance Shop | 1959-pre | 2015 | fans_to_variable | 0.017211 | 0 | 9.5864 | 0.0072987 | 0.037366 | 0 | 0.48922 | 0.070129 | 0 | 0.53718 | 0.49914 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 1555.0421 | -103.011 | 1452.0311 | 25.1917 | -11.6402 | 13.5514 | 742.769 | 54.8111
8 | Maintenance Shop | 1959-pre | 2015 | hrv_enabled | 0.017211 | 0 | 8.2811 | 0.0088651 | 0.037366 | 0 | 0.48922 | 0.070129 | 0 | 0.53794 | 0.49914 | 0.15277 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 115617.8021 | -13656.7126 | 101961.0895 | 1873.0084 | -1543.2085 | 329.7999 | 84491.7749 | 256.191
8 | Maintenance Shop | 1959-pre | 2015 | infil_reduce | 0.017211 | 0 | 6.1537 | 0.0083322 | 0.037349 | 0 | 0.48922 | 0.070129 | 0 | 0.34997 | 0.31877 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 301524.3528 | 31930.5737 | 333454.9265 | 4884.6945 | 3608.1548 | 8492.8493 | 45250.2857 | 5.328
8 | Maintenance Shop | 1959-pre | 2015 | infil_reduce_plus_setback | 0.017211 | 0 | 5.3773 | 0.0047958 | 0.037349 | 0 | 0.48922 | 0.070129 | 0 | 0.38988 | 0.3556 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 369371.883 | 25532.6056 | 394904.4887 | 5983.8245 | 2885.1844 | 8869.0089 | 48550.259 | 5.4741
8 | Maintenance Shop | 1959-pre | 2015 | lights_reduce_70p | 0.017211 | 0 | 9.778 | 0.0062814 | 0.037366 | 0 | 0.34246 | 0.070129 | 0 | 0.53764 | 0.49754 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | -15194.8214 | 12911.647 | -2283.1743 | -246.1561 | 1459.0161 | 1212.86 | 27865.1869 | 22.9748
8 | Maintenance Shop | 1959-pre | 2015 | load_reduce | 0.017211 | 0 | 3.3646 | 0.0047958 | 0.037349 | 0 | 0.48922 | 0.070129 | 0 | 0.38988 | 0.3556 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 545260.9713 | 25532.6056 | 570793.5769 | 8833.2277 | 2885.1844 | 11718.4122 | 49135.3074 | 4.193
8 | Maintenance Shop | 1959-pre | 2015 | occupancy_setback | 0.017211 | 0 | 8.3904 | 0.0041338 | 0.037366 | 0 | 0.48922 | 0.070129 | 0 | 0.61305 | 0.55843 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 106070.2388 | -11637.4156 | 94432.8231 | 1718.3379 | -1315.028 | 403.3099 | 3299.9795 | 8.1822
8 | Maintenance Shop | 1959-pre | 2015 | payback_less_than_20 | 0.017211 | 0 | 2.3442 | 0.012288 | 0.037349 | 0 | 0.34246 | 0.070129 | 0 | 0.36103 | 0.26955 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 634436.0024 | 47744.8719 | 682180.8743 | 10277.8632 | 5395.1705 | 15673.0338 | 97972.2818 | 6.251
8 | Maintenance Shop | 1959-pre | 2015 | plug_loads_90_percent | 0.017211 | 0 | 9.5862 | 0.0072018 | 0.037366 | 0 | 0.48922 | 0.070129 | 0 | 0.54088 | 0.49919 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 1569.1532 | -421.9216 | 1147.2316 | 25.4203 | -47.6771 | -22.2569 | 1907.9732 | -85.7252
8 | Maintenance Shop | 1959-pre | 2015 | pump_fan_eff_ | 0.017211 | 0 | 9.5794 | 0.0073149 | 0.037366 | 0 | 0.48922 | 0.070129 | 0 | 0.54138 | 0.39039 | 0 | 0 | 839286.691 | 574.3213 | 3265.3061 | 0 | 42752.3684 | 6128.4462 | 0 | 47218.5282 | 43304.112 | 0 | 982529.7733 | 2163.23 | 9032.5085 | 11195.7385 | 35.0443 | 1020.6735 | 1055.7178 | 3219.2806 | 3.0494
9 | Maintenance Shop | 1980-2004 | 2015 | air_temp_reset_enabled | 0.047471 | 0 | 15.8348 | 0.02993 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.8832 | 0.77417 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | -102353.2314 | -13678.0199 | -116031.2513 | -1658.1223 | -1545.6163 | -3203.7386 | 16169.5482 | -5.0471
9 | Maintenance Shop | 1980-2004 | 2015 | baseline | 0.047471 | 0 | 15.3925 | 0.016747 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.84762 | 0.76384 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Maintenance Shop | 1980-2004 | 2015 | boiler_eff_upgrade | 0.047471 | 0 | 15.3786 | 0.018706 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.85826 | 0.77417 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 3215.9323 | -5308.3499 | -2092.4175 | 52.0981 | -599.8435 | -547.7454 | 151429.4815 | -276.4596
9 | Maintenance Shop | 1980-2004 | 2015 | boiler_reset | 0.047471 | 0 | 9.8098 | 0.018706 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.85826 | 0.77417 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 1292000.8201 | -5308.3499 | 1286692.4702 | 20930.4133 | -599.8435 | 20330.5698 | 4273.4985 | 0.2102
9 | Maintenance Shop | 1980-2004 | 2015 | cooling_cop_3_0 | 0.047471 | 0 | 15.3786 | 0.016034 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.85826 | 0.77417 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 3215.9323 | -4689.9013 | -1473.969 | 52.0981 | -529.9589 | -477.8607 | 22720.4705 | -47.5462
9 | Maintenance Shop | 1980-2004 | 2015 | dcv_enabled | 0.047471 | 0 | 10.3193 | 0.021067 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.84348 | 0.77413 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 1174072.9932 | -2422.2567 | 1171650.7365 | 19019.9825 | -273.715 | 18746.2675 | 42096.258 | 2.2456
9 | Maintenance Shop | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.047471 | 0 | 15.4004 | 0.027347 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.85848 | 0.77417 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | -1824.4232 | -7359.5375 | -9183.9606 | -29.5557 | -831.6277 | -861.1834 | 16169.5482 | -18.776
9 | Maintenance Shop | 1980-2004 | 2015 | economizers_enabled | 0.047471 | 0 | 15.3888 | 0.013317 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.85844 | 0.77417 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 865.8279 | -4102.3752 | -3236.5473 | 14.0264 | -463.5684 | -449.542 | 5394.3415 | -11.9996
9 | Maintenance Shop | 1980-2004 | 2015 | elec_reduce | 0.047471 | 0 | 10.7875 | 0.017504 | 0.10302 | 0 | 0.94458 | 0.19343 | 0 | 0.78321 | 0.60216 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 1065720.8111 | 145830.1629 | 1211550.974 | 17264.6771 | 16478.8084 | 33743.4856 | 293186.7075 | 8.6887
9 | Maintenance Shop | 1980-2004 | 2015 | envelope_ecm_roof | 0.047471 | 0 | 14.8527 | 0.018617 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.82446 | 0.74326 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 124936.9102 | 9689.0269 | 134625.9371 | 2023.9779 | 1094.86 | 3118.838 | 1186540.7558 | 380.4432
9 | Maintenance Shop | 1980-2004 | 2015 | envelope_ecm_wall | 0.047471 | 0 | 14.8119 | 0.01884 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.82259 | 0.74117 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 134378.5577 | 10554.8549 | 144933.4126 | 2176.9326 | 1192.6986 | 3369.6312 | 2303620.66 | 683.6418
9 | Maintenance Shop | 1980-2004 | 2015 | envelope_ecm_windows | 0.047471 | 0 | 15.2422 | 0.020265 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.85532 | 0.77034 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 34777.4222 | -4102.3752 | 30675.047 | 563.3942 | -463.5684 | 99.8258 | 334394.3033 | 3349.7771
9 | Maintenance Shop | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.047471 | 0 | 15.3694 | 0.018706 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.80508 | 0.77417 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 5359.8872 | 6998.7758 | 12358.6631 | 86.8302 | 790.8617 | 877.6918 | 10096.51 | 11.5035
9 | Maintenance Shop | 1980-2004 | 2015 | fans_to_variable | 0.047471 | 0 | 15.3889 | 0.018662 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.85194 | 0.77417 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 834.9055 | -3834.3809 | -2999.4754 | 13.5255 | -433.285 | -419.7596 | 5425.5719 | -12.9254
9 | Maintenance Shop | 1980-2004 | 2015 | hrv_enabled | 0.047471 | 0 | 11.6365 | 0.025209 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.8449 | 0.77413 | 0.42138 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 869250.0212 | -101229.7166 | 768020.3046 | 14081.8503 | -11438.958 | 2642.8924 | 617171.9674 | 233.5214
9 | Maintenance Shop | 1980-2004 | 2015 | infil_reduce | 0.047471 | 0 | 12.5681 | 0.019642 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.69285 | 0.62555 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 653648.5568 | 67153.2027 | 720801.7595 | 10589.1066 | 7588.3119 | 18177.4185 | 299813.521 | 16.4937
9 | Maintenance Shop | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.047471 | 0 | 10.8719 | 0.011536 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.76362 | 0.69587 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 1046198.4526 | 36375.0809 | 1082573.5335 | 16948.4149 | 4110.3841 | 21058.7991 | 323918.2457 | 15.3816
9 | Maintenance Shop | 1980-2004 | 2015 | lights_reduce_70p | 0.047471 | 0 | 15.8907 | 0.015722 | 0.10302 | 0 | 0.94458 | 0.19343 | 0 | 0.85434 | 0.76985 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | -115289.1131 | 90973.7785 | -24315.3346 | -1867.6836 | 10280.037 | 8412.3533 | 203541.8508 | 24.1956
9 | Maintenance Shop | 1980-2004 | 2015 | load_reduce | 0.047471 | 0 | 6.8498 | 0.011536 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.76362 | 0.69587 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 1977015.0248 | 36375.0809 | 2013390.1057 | 32027.6434 | 4110.3841 | 36138.0275 | 328191.7443 | 9.0816
9 | Maintenance Shop | 1980-2004 | 2015 | occupancy_setback | 0.047471 | 0 | 13.3527 | 0.010689 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.94948 | 0.86298 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 472072.069 | -45115.8201 | 426956.2489 | 7647.5675 | -5098.0877 | 2549.4798 | 24104.7707 | 9.4548
9 | Maintenance Shop | 1980-2004 | 2015 | payback_less_than_20 | 0.047471 | 0 | 4.4003 | 0.02846 | 0.10302 | 0 | 0.94458 | 0.19343 | 0 | 0.68523 | 0.52631 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 2543905.5606 | 183524.6007 | 2727430.1613 | 41211.2701 | 20738.2799 | 61949.55 | 684922.463 | 11.0561
9 | Maintenance Shop | 1980-2004 | 2015 | plug_loads_90_percent | 0.047471 | 0 | 15.3877 | 0.018439 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.85835 | 0.77426 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 1102.8999 | -5287.7349 | -4184.835 | 17.867 | -597.514 | -579.6471 | 13936.8311 | -24.0436
9 | Maintenance Shop | 1980-2004 | 2015 | pump_fan_eff_ | 0.047471 | 0 | 15.3786 | 0.018706 | 0.10302 | 0 | 1.3494 | 0.19343 | 0 | 0.85826 | 0.6055 | 0 | 0 | 3562242.907 | 3875.6108 | 23841.1908 | 0 | 312285.5843 | 44765.366 | 0 | 196161.5656 | 176773.2043 | 0 | 4319945.4287 | 3215.9323 | 33726.0597 | 36941.9921 | 52.0981 | 3811.0447 | 3863.1429 | 23515.3036 | 6.0871
16 | Office-Small | 1960-1979 | 2015 | air_temp_reset_enabled | 0.0049605 | 0.022837 | 0.26546 | 0.018576 | 0.014201 | 0 | 0.063883 | 0.015298 | 0 | 0.045147 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 8897.615 | -5716.7424 | 3180.8726 | 144.1414 | -645.9919 | -501.8505 | 19401.4975 | -38.6599
16 | Office-Small | 1960-1979 | 2015 | baseline | 0.0049605 | 0.0014311 | 0.31962 | 0.0052034 | 0.014141 | 0 | 0.063883 | 0.015298 | 0 | 0.045191 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | Office-Small | 1960-1979 | 2015 | boiler_reset | 0.0049605 | 0.0032679 | 0.31055 | 0.0069908 | 0.014141 | 0 | 0.063883 | 0.015298 | 0 | 0.045059 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 1489.9924 | -573.8363 | 916.1562 | 24.1379 | -64.8435 | -40.7056 | 1281.8298 | -31.4902
16 | Office-Small | 1960-1979 | 2015 | cooling_cop_3_0 | 0.0049605 | 0.0032679 | 0.31055 | 0.004995 | 0.014141 | 0 | 0.063883 | 0.015298 | 0 | 0.045059 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 1489.9924 | -245.9298 | 1244.0626 | 24.1379 | -27.7901 | -3.6522 | 23104.9844 | -6326.3316
16 | Office-Small | 1960-1979 | 2015 | dcv_enabled | 0.0049605 | 0.0032679 | 0.31055 | 0.0069908 | 0.014141 | 0 | 0.063883 | 0.015298 | 0 | 0.045059 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 1489.9924 | -573.8363 | 916.1562 | 24.1379 | -64.8435 | -40.7056 | 18366.1198 | -451.1937
16 | Office-Small | 1960-1979 | 2015 | ecm_cold_deck_reset_control | 0.0049605 | 0.039681 | 0.17432 | 0.013236 | 0.014261 | 0 | 0.063883 | 0.015298 | 0 | 0.04546 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 23872.3091 | -7667.9659 | 16204.3433 | 386.7314 | -866.4801 | -479.7487 | 19401.4975 | -40.441
16 | Office-Small | 1960-1979 | 2015 | economizers_enabled | 0.0049605 | 0.0032679 | 0.31055 | 0.0069908 | 0.014141 | 0 | 0.063883 | 0.015298 | 0 | 0.045059 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 1489.9924 | -573.8363 | 916.1562 | 24.1379 | -64.8435 | -40.7056 | 7581.121 | -186.2426
16 | Office-Small | 1960-1979 | 2015 | elec_reduce | 0.0049605 | 0.0024838 | 0.32621 | 0.0049841 | 0.014146 | 0 | 0.044719 | 0.015298 | 0 | 0.040207 | 2.1932e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | -1083.7128 | 3831.2804 | 2747.5677 | -17.5561 | 432.9347 | 415.3785 | 55845.759 | 134.4455
16 | Office-Small | 1960-1979 | 2015 | envelope_ecm_roof | 0.0049605 | 0.0034104 | 0.25162 | 0.006119 | 0.014064 | 0 | 0.063883 | 0.015298 | 0 | 0.039039 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 11171.3398 | 547.7118 | 11719.0517 | 180.9757 | 61.8914 | 242.8671 | 209550.8548 | 862.8209
16 | Office-Small | 1960-1979 | 2015 | envelope_ecm_wall | 0.0049605 | 0.0031856 | 0.28807 | 0.0070895 | 0.014042 | 0 | 0.063883 | 0.015298 | 0 | 0.042576 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 5182.5432 | -152.2423 | 5030.3009 | 83.9572 | -17.2034 | 66.7538 | 174504.9442 | 2614.1566
16 | Office-Small | 1960-1979 | 2015 | envelope_ecm_windows | 0.0049605 | 0.0032624 | 0.30148 | 0.0070511 | 0.014135 | 0 | 0.063883 | 0.015298 | 0 | 0.044363 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 2979.9849 | -467.5369 | 2512.4479 | 48.2758 | -52.8317 | -4.5559 | 65296.7101 | -14332.2852
16 | Office-Small | 1960-1979 | 2015 | exhaust_fans_occ_control | 0.0049605 | 0.0032679 | 0.31055 | 0.0070347 | 0.014141 | 0 | 0.063883 | 0.015298 | 0 | 0.040048 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 1489.9924 | 242.3265 | 1732.3189 | 24.1379 | 27.3829 | 51.5208 | 2019.848 | 39.2045
16 | Office-Small | 1960-1979 | 2015 | fans_to_variable | 0.0049605 | 0.0032734 | 0.31089 | 0.0069689 | 0.014141 | 0 | 0.063883 | 0.015298 | 0 | 0.044687 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 1433.2394 | -509.8765 | 923.3629 | 23.2185 | -57.616 | -34.3976 | 5571.9788 | -161.9876
16 | Office-Small | 1960-1979 | 2015 | hrv_enabled | 0.0049605 | 0.0032679 | 0.31055 | 0.0069908 | 0.014141 | 0 | 0.063883 | 0.015298 | 0 | 0.045059 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 1489.9924 | -573.8363 | 916.1562 | 24.1379 | -64.8435 | -40.7056 | 223716.555 | -5495.9623
16 | Office-Small | 1960-1979 | 2015 | infil_reduce | 0.0049605 | 0.0030705 | 0.18626 | 0.0085151 | 0.01379 | 0 | 0.063883 | 0.015298 | 0 | 0.032849 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 21910.2756 | 1271.9887 | 23182.2643 | 354.9465 | 143.7347 | 498.6812 | 49499.5889 | 99.261
16 | Office-Small | 1960-1979 | 2015 | infil_reduce_plus_setback | 0.0049605 | 0.0027525 | 0.15713 | 0.0067496 | 0.013828 | 0 | 0.063883 | 0.015298 | 0 | 0.037125 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 26695.5475 | 905.3461 | 27600.8936 | 432.4679 | 102.3041 | 534.772 | 60016.7104 | 112.2286
16 | Office-Small | 1960-1979 | 2015 | lights_reduce_70p | 0.0049605 | 0.0025441 | 0.32567 | 0.0050992 | 0.014146 | 0 | 0.044719 | 0.015298 | 0 | 0.045164 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | -994.5294 | 2986.2907 | 1991.7613 | -16.1114 | 337.4509 | 321.3395 | 27041.5413 | 84.1526
16 | Office-Small | 1960-1979 | 2015 | load_reduce | 0.0049605 | 0.0027525 | 0.15713 | 0.0067496 | 0.013828 | 0 | 0.063883 | 0.015298 | 0 | 0.037125 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 26695.5475 | 905.3461 | 27600.8936 | 432.4679 | 102.3041 | 534.772 | 61298.5402 | 114.6256
16 | Office-Small | 1960-1979 | 2015 | occupancy_setback | 0.0049605 | 0.0028621 | 0.26702 | 0.0054556 | 0.014179 | 0 | 0.063883 | 0.015298 | 0 | 0.051173 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 8640.8751 | -1265.6828 | 7375.1923 | 139.9822 | -143.0222 | -3.04 | 10517.1215 | -3459.6011
16 | Office-Small | 1960-1979 | 2015 | payback_less_than_20 | 0.0049605 | 0.019629 | 0.11356 | 0.012435 | 0.013932 | 0 | 0.044719 | 0.015298 | 0 | 0.032443 | 2.1932e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 33854.5377 | 1100.8287 | 34955.3665 | 548.4435 | 124.3936 | 672.8372 | 152834.4702 | 227.1493
16 | Office-Small | 1960-1979 | 2015 | plug_loads_90_percent | 0.0049605 | 0.0032185 | 0.31097 | 0.0068044 | 0.014135 | 0 | 0.063883 | 0.015298 | 0 | 0.045109 | 3.2898e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 1419.7268 | -542.3068 | 877.42 | 22.9996 | -61.2807 | -38.2811 | 6080.9692 | -158.8505
16 | Office-Small | 1960-1979 | 2015 | pump_fan_eff_ | 0.0049605 | 0.0032679 | 0.31055 | 0.0069908 | 0.014141 | 0 | 0.063883 | 0.015298 | 0 | 0.045059 | 2.1932e-05 | 0 | 235.1197 | 52511.8734 | 854.8989 | 2323.2711 | 0 | 10495.7084 | 2513.3488 | 0 | 7424.7386 | 5.4051 | 0 | 76364.364 | 1489.9924 | -572.0346 | 917.9578 | 24.1379 | -64.6399 | -40.502 | 2337.2807 | -57.7077
17 | Office-Small | 1980-2004 | 2015 | air_temp_reset_enabled | 0.018822 | 0.052928 | 0.57172 | 0.045521 | 0.052491 | 0 | 0.2424 | 0.058046 | 0 | 0.11834 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 17860.0154 | -13105.0295 | 4754.986 | 289.3323 | -1480.8683 | -1191.5361 | 77582.1845 | -65.1111
17 | Office-Small | 1980-2004 | 2015 | baseline | 0.018822 | 0.0059918 | 0.67487 | 0.016894 | 0.052283 | 0 | 0.2424 | 0.058046 | 0 | 0.11842 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | Office-Small | 1980-2004 | 2015 | boiler_reset | 0.018822 | 0.011796 | 0.65196 | 0.023988 | 0.052303 | 0 | 0.2424 | 0.058046 | 0 | 0.11832 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 3966.0906 | -2218.9934 | 1747.0971 | 64.2507 | -250.7463 | -186.4956 | 5125.7464 | -27.4845
17 | Office-Small | 1980-2004 | 2015 | cooling_cop_3_0 | 0.018822 | 0.011796 | 0.65196 | 0.020555 | 0.052303 | 0 | 0.2424 | 0.058046 | 0 | 0.11832 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 3966.0906 | -1624.6202 | 2341.4704 | 64.2507 | -183.5821 | -119.3314 | 92391.588 | -774.2436
17 | Office-Small | 1980-2004 | 2015 | dcv_enabled | 0.018822 | 0.011796 | 0.65196 | 0.023988 | 0.052303 | 0 | 0.2424 | 0.058046 | 0 | 0.11832 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 3966.0906 | -2218.9934 | 1747.0971 | 64.2507 | -250.7463 | -186.4956 | 73441.9443 | -393.7999
17 | Office-Small | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.018822 | 0.098178 | 0.3484 | 0.038406 | 0.052803 | 0 | 0.2424 | 0.058046 | 0 | 0.11938 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 56526.6967 | -19942.1229 | 36584.5738 | 915.7325 | -2253.4599 | -1337.7274 | 77582.1845 | -57.9955
17 | Office-Small | 1980-2004 | 2015 | economizers_enabled | 0.018822 | 0.011796 | 0.65196 | 0.023988 | 0.052303 | 0 | 0.2424 | 0.058046 | 0 | 0.11832 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 3966.0906 | -2218.9934 | 1747.0971 | 64.2507 | -250.7463 | -186.4956 | 30315.1821 | -162.5517
17 | Office-Small | 1980-2004 | 2015 | elec_reduce | 0.018822 | 0.0095494 | 0.70277 | 0.015832 | 0.052345 | 0 | 0.16968 | 0.058046 | 0 | 0.099738 | 8.3219e-05 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | -4830.6335 | 15388.8637 | 10558.2302 | -78.2563 | 1738.9416 | 1660.6853 | 223314.5137 | 134.4713
17 | Office-Small | 1980-2004 | 2015 | envelope_ecm_roof | 0.018822 | 0.01188 | 0.5764 | 0.023593 | 0.052158 | 0 | 0.2424 | 0.058046 | 0 | 0.11029 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 17049.5065 | -749.2705 | 16300.236 | 276.202 | -84.6676 | 191.5344 | 837946.3014 | 4374.912
17 | Office-Small | 1980-2004 | 2015 | envelope_ecm_wall | 0.018822 | 0.011568 | 0.62044 | 0.024529 | 0.052116 | 0 | 0.2424 | 0.058046 | 0 | 0.11468 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 9423.5176 | -1610.2112 | 7813.3065 | 152.661 | -181.9539 | -29.2929 | 697805.6604 | -23821.6858
17 | Office-Small | 1980-2004 | 2015 | envelope_ecm_windows | 0.018822 | 0.011755 | 0.62668 | 0.024529 | 0.052283 | 0 | 0.2424 | 0.058046 | 0 | 0.11632 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 8342.839 | -1956.0283 | 6386.8107 | 135.154 | -221.0312 | -85.8772 | 261106.7218 | -3040.4659
17 | Office-Small | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.018822 | 0.011796 | 0.65196 | 0.024113 | 0.052303 | 0 | 0.2424 | 0.058046 | 0 | 0.099322 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 3966.0906 | 1048.2583 | 5014.3488 | 64.2507 | 118.4532 | 182.7039 | 8076.9136 | 44.2077
17 | Office-Small | 1980-2004 | 2015 | fans_to_variable | 0.018822 | 0.011817 | 0.65271 | 0.023926 | 0.052303 | 0 | 0.2424 | 0.058046 | 0 | 0.11742 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 3836.4091 | -2056.8917 | 1779.5175 | 62.1498 | -232.4288 | -170.2789 | 22281.0782 | -130.8505
17 | Office-Small | 1980-2004 | 2015 | hrv_enabled | 0.018822 | 0.011796 | 0.65196 | 0.023988 | 0.052303 | 0 | 0.2424 | 0.058046 | 0 | 0.11832 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 3966.0906 | -2218.9934 | 1747.0971 | 64.2507 | -250.7463 | -186.4956 | 894591.721 | -4796.8518
17 | Office-Small | 1980-2004 | 2015 | infil_reduce | 0.018822 | 0.013461 | 0.4207 | 0.028191 | 0.051492 | 0 | 0.2424 | 0.058046 | 0 | 0.096597 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 44008.836 | 666.4185 | 44675.2545 | 712.9431 | 75.3053 | 788.2484 | 179705.701 | 227.981
17 | Office-Small | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.018822 | 0.010798 | 0.34609 | 0.023884 | 0.051638 | 0 | 0.2424 | 0.058046 | 0 | 0.10675 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 56926.5478 | 90.0566 | 57016.6044 | 922.2101 | 10.1764 | 932.3865 | 221761.2823 | 237.8427
17 | Office-Small | 1980-2004 | 2015 | lights_reduce_70p | 0.018822 | 0.0096951 | 0.70206 | 0.016332 | 0.052345 | 0 | 0.16968 | 0.058046 | 0 | 0.11865 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | -4708.1566 | 11995.5328 | 7287.3762 | -76.2721 | 1355.4952 | 1279.2231 | 108132.9856 | 84.5302
17 | Office-Small | 1980-2004 | 2015 | load_reduce | 0.018822 | 0.010798 | 0.34609 | 0.023884 | 0.051638 | 0 | 0.2424 | 0.058046 | 0 | 0.10675 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 56926.5478 | 90.0566 | 57016.6044 | 922.2101 | 10.1764 | 932.3865 | 226886.9735 | 243.3401
17 | Office-Small | 1980-2004 | 2015 | occupancy_setback | 0.018822 | 0.010881 | 0.5453 | 0.020243 | 0.05247 | 0 | 0.2424 | 0.058046 | 0 | 0.13334 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 22434.8883 | -4041.7381 | 18393.1502 | 363.4452 | -456.7164 | -93.2712 | 42055.5814 | -450.8956
17 | Office-Small | 1980-2004 | 2015 | payback_less_than_20 | 0.018822 | 0.054134 | 0.25752 | 0.035327 | 0.052012 | 0 | 0.16968 | 0.058046 | 0 | 0.088629 | 8.3219e-05 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 72261.3775 | 6275.1406 | 78536.5181 | 1170.6343 | 709.0909 | 1879.7252 | 592918.4347 | 315.4283
17 | Office-Small | 1980-2004 | 2015 | plug_loads_90_percent | 0.018822 | 0.011713 | 0.65205 | 0.02326 | 0.052283 | 0 | 0.2424 | 0.058046 | 0 | 0.11844 | 0.00012483 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 3951.6815 | -2096.5165 | 1855.165 | 64.0172 | -236.9064 | -172.8891 | 24316.4155 | -140.6475
17 | Office-Small | 1980-2004 | 2015 | pump_fan_eff_ | 0.018822 | 0.011796 | 0.65196 | 0.023988 | 0.052303 | 0 | 0.2424 | 0.058046 | 0 | 0.11832 | 8.3219e-05 | 0 | 1037.4515 | 116850.1777 | 2925.0368 | 9052.4846 | 0 | 41969.9556 | 10050.3112 | 0 | 20504.0758 | 21.6136 | 0 | 202411.1069 | 3966.0906 | -2211.7889 | 1754.3016 | 64.2507 | -249.9321 | -185.6815 | 9346.2548 | -50.3349
18 | Office-Small | 2005-2014 | 2015 | air_temp_reset_enabled | 0.0021648 | 0.0035294 | 0.0368 | 0.0038668 | 0.0058888 | 0 | 0.027879 | 0.006676 | 0 | 0.0099351 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 771.4003 | -932.5471 | -161.1468 | 12.4967 | -105.3778 | -92.8811 | 11926.5647 | -128.4068
18 | Office-Small | 2005-2014 | 2015 | baseline | 0.0021648 | 0.0014883 | 0.040133 | 0.0022038 | 0.005872 | 0 | 0.027879 | 0.006676 | 0 | 0.0096264 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | Office-Small | 2005-2014 | 2015 | boiler_reset | 0.0021648 | 0.0017085 | 0.039736 | 0.0028786 | 0.0058816 | 0 | 0.027879 | 0.006676 | 0 | 0.0099686 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 91.9257 | -288.5137 | -196.588 | 1.4892 | -32.602 | -31.1128 | 787.9714 | -25.3262
18 | Office-Small | 2005-2014 | 2015 | cooling_cop_3_0 | 0.0021648 | 0.0017085 | 0.039736 | 0.0028786 | 0.0058816 | 0 | 0.027879 | 0.006676 | 0 | 0.0099686 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 91.9257 | -288.5137 | -196.588 | 1.4892 | -32.602 | -31.1128 | 14203.1867 | -456.5055
18 | Office-Small | 2005-2014 | 2015 | dcv_enabled | 0.0021648 | 0.0017085 | 0.039736 | 0.0028786 | 0.0058816 | 0 | 0.027879 | 0.006676 | 0 | 0.0099686 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 91.9257 | -288.5137 | -196.588 | 1.4892 | -32.602 | -31.1128 | 11290.0933 | -362.8756
18 | Office-Small | 2005-2014 | 2015 | ecm_cold_deck_reset_control | 0.0021648 | 0.0073149 | 0.020208 | 0.0040128 | 0.0059295 | 0 | 0.027879 | 0.006676 | 0 | 0.010031 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 4611.2348 | -1873.9544 | 2737.2804 | 74.702 | -211.7569 | -137.0548 | 11926.5647 | -87.0204
18 | Office-Small | 2005-2014 | 2015 | economizers_enabled | 0.0021648 | 0.0017085 | 0.039736 | 0.0028786 | 0.0058816 | 0 | 0.027879 | 0.006676 | 0 | 0.0099686 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 91.9257 | -288.5137 | -196.588 | 1.4892 | -32.602 | -31.1128 | 4660.2965 | -149.7869
18 | Office-Small | 2005-2014 | 2015 | elec_reduce | 0.0021648 | 0.0012634 | 0.044866 | 0.0018449 | 0.0058864 | 0 | 0.019516 | 0.006676 | 0 | 0.0073795 | 9.5714e-06 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | -1095.3552 | 2588.3165 | 1492.9613 | -17.7448 | 292.4798 | 274.735 | 34329.7243 | 124.9558
18 | Office-Small | 2005-2014 | 2015 | envelope_ecm_roof | 0.0021648 | 0.001675 | 0.035043 | 0.0029312 | 0.0058696 | 0 | 0.027879 | 0.006676 | 0 | 0.0096001 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 1177.8668 | -204.8945 | 972.9722 | 19.0814 | -23.1531 | -4.0716 | 0 | 0
18 | Office-Small | 2005-2014 | 2015 | envelope_ecm_wall | 0.0021648 | 0.001687 | 0.037867 | 0.0029241 | 0.0058673 | 0 | 0.027879 | 0.006676 | 0 | 0.0098298 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 524.4193 | -258.6101 | 265.8091 | 8.4956 | -29.2229 | -20.7274 | 0 | 0
18 | Office-Small | 2005-2014 | 2015 | envelope_ecm_windows | 0.0021648 | 0.0017707 | 0.036874 | 0.0029839 | 0.0058816 | 0 | 0.027879 | 0.006676 | 0 | 0.0098131 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 754.2334 | -291.2825 | 462.9509 | 12.2186 | -32.9149 | -20.6963 | 40139.45 | -1939.4465
18 | Office-Small | 2005-2014 | 2015 | exhaust_fans_occ_control | 0.0021648 | 0.0017085 | 0.039736 | 0.0028953 | 0.0058816 | 0 | 0.027879 | 0.006676 | 0 | 0.0077815 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 91.9257 | 213.7549 | 305.6805 | 1.4892 | 24.1543 | 25.6435 | 1241.6489 | 48.4196
18 | Office-Small | 2005-2014 | 2015 | fans_to_variable | 0.0021648 | 0.0017085 | 0.039783 | 0.0028738 | 0.0058816 | 0 | 0.027879 | 0.006676 | 0 | 0.0099016 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 80.8503 | -271.9006 | -191.0503 | 1.3098 | -30.7248 | -29.415 | 3425.2287 | -116.445
18 | Office-Small | 2005-2014 | 2015 | hrv_enabled | 0.0021648 | 0.0017085 | 0.039736 | 0.0028786 | 0.0058816 | 0 | 0.027879 | 0.006676 | 0 | 0.0099686 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 91.9257 | -288.5137 | -196.588 | 1.4892 | -32.602 | -31.1128 | 137523.9191 | -4420.1648
18 | Office-Small | 2005-2014 | 2015 | lights_reduce_70p | 0.0021648 | 0.0012634 | 0.044863 | 0.0018975 | 0.0058888 | 0 | 0.019516 | 0.006676 | 0 | 0.0095618 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | -1094.8014 | 2069.4349 | 974.6335 | -17.7358 | 233.8461 | 216.1104 | 16623.0825 | 76.9194
18 | Office-Small | 2005-2014 | 2015 | load_reduce | 0.0021648 | 0.001474 | 0.031925 | 0.0024024 | 0.0059008 | 0 | 0.027879 | 0.006676 | 0 | 0.010627 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 1899.4278 | -280.7609 | 1618.6669 | 30.7707 | -31.726 | -0.95525 | 7253.0976 | -7592.8663
18 | Office-Small | 2005-2014 | 2015 | occupancy_setback | 0.0021648 | 0.001474 | 0.031925 | 0.0024024 | 0.0059008 | 0 | 0.027879 | 0.006676 | 0 | 0.010627 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 1899.4278 | -280.7609 | 1618.6669 | 30.7707 | -31.726 | -0.95525 | 6465.1262 | -6767.9826
18 | Office-Small | 2005-2014 | 2015 | payback_less_than_20 | 0.0021648 | 0.0055394 | 0.024213 | 0.0033141 | 0.0059438 | 0 | 0.019516 | 0.006676 | 0 | 0.0085161 | 9.5714e-06 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 3684.2254 | 982.3863 | 4666.6117 | 59.6845 | 111.0096 | 170.6941 | 63522.4239 | 372.1419
18 | Office-Small | 2005-2014 | 2015 | plug_loads_90_percent | 0.0021648 | 0.0017013 | 0.039678 | 0.0027972 | 0.0058816 | 0 | 0.027879 | 0.006676 | 0 | 0.0099686 | 1.4357e-05 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 105.2161 | -268.0242 | -162.8081 | 1.7045 | -30.2867 | -28.5822 | 3738.1173 | -130.7846
18 | Office-Small | 2005-2014 | 2015 | pump_fan_eff_ | 0.0021648 | 0.0017085 | 0.039736 | 0.0028786 | 0.0058816 | 0 | 0.027879 | 0.006676 | 0 | 0.0099686 | 9.5714e-06 | 0 | 344.4443 | 9287.8144 | 510.0213 | 1358.9492 | 0 | 6451.9631 | 1545.0156 | 0 | 2227.8129 | 3.3226 | 0 | 21729.3434 | 91.9257 | -287.4061 | -195.4805 | 1.4892 | -32.4769 | -30.9877 | 1436.7823 | -46.3662
13 | Office | 1959-pre | 2015 | air_temp_reset_enabled | 0.071353 | 0 | 25.5721 | 0.25122 | 0 | 3.2386 | 2.6936 | 0.81528 | 0 | 2.2099 | 0.90856 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 910208.5842 | 190769.6338 | 1100978.218 | 14745.3791 | 21556.9686 | 36302.3477 | 71825.3993 | 1.9785
13 | Office | 1959-pre | 2015 | baseline | 0.071353 | 0 | 31.4573 | 1.492 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 2.2068 | 0.90445 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | Office | 1959-pre | 2015 | boiler_eff_upgrade | 0.071353 | 0 | 30.9312 | 1.5239 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 2.2025 | 0.90932 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 81352.3636 | -5030.1638 | 76322.1998 | 1317.9083 | -568.4085 | 749.4998 | 694357.1659 | 926.4274
13 | Office | 1959-pre | 2015 | boiler_reset | 0.071353 | 0 | 21.8357 | 1.5239 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 2.2025 | 0.75632 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 1488004.937 | 18632.2288 | 1506637.1658 | 24105.68 | 2105.4418 | 26211.1218 | 3796.3764 | 0.14484
13 | Office | 1959-pre | 2015 | cooling_cop_3_0 | 0.071353 | 0 | 30.9312 | 1.0885 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 2.2025 | 0.90932 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 81352.3636 | 62307.6793 | 143660.0429 | 1317.9083 | 7040.7678 | 8358.6761 | 82115.6537 | 9.824
13 | Office | 1959-pre | 2015 | dcv_enabled | 0.071353 | 0 | 26.5875 | 1.5294 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 2.2025 | 0.90653 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 753125.8048 | -5451.5857 | 747674.2191 | 12200.638 | -616.0292 | 11584.6089 | 173383.0124 | 14.9667
13 | Office | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.071353 | 0 | 24.4139 | 0.17445 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 2.2047 | 0.89993 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 1089286.0013 | 204784.1543 | 1294070.1556 | 17646.4332 | 23140.6094 | 40787.0427 | 71825.3993 | 1.761
13 | Office | 1959-pre | 2015 | economizers_enabled | 0.071353 | 0 | 30.9328 | 1.5132 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 2.2025 | 0.90938 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 81110.2701 | -3380.3418 | 77729.9283 | 1313.9864 | -381.9786 | 932.0078 | 28066.087 | 30.1136
13 | Office | 1959-pre | 2015 | elec_reduce | 0.071353 | 0 | 27.641 | 1.515 | 0 | 3.2389 | 1.8855 | 0.81528 | 0 | 1.0639 | 0.7126 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 590205.8834 | 327821.4223 | 918027.3058 | 9561.3353 | 37043.8207 | 46605.156 | 614502.6756 | 13.1853
13 | Office | 1959-pre | 2015 | envelope_ecm_roof | 0.071353 | 0 | 28.9482 | 1.398 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 2.1602 | 0.85824 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 388030.9585 | 28889.8176 | 416920.7761 | 6286.1015 | 3264.5494 | 9550.6509 | 3686421.1394 | 385.9864
13 | Office | 1959-pre | 2015 | envelope_ecm_wall | 0.071353 | 0 | 29.4706 | 1.4435 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 2.1663 | 0.86705 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 307243.4796 | 19546.804 | 326790.2836 | 4977.3444 | 2208.7889 | 7186.1332 | 1574890.7726 | 219.1569
13 | Office | 1959-pre | 2015 | envelope_ecm_windows | 0.071353 | 0 | 30.7757 | 1.5243 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 2.1958 | 0.90219 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 105400.3123 | -2940.987 | 102459.3253 | 1707.4851 | -332.3315 | 1375.1535 | 12395753.0085 | 9014.0866
13 | Office | 1959-pre | 2015 | exhaust_fans_occ_control | 0.071353 | 0 | 30.9312 | 1.5239 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 1.0526 | 0.90932 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 81352.3636 | 172809.8868 | 254162.2504 | 1317.9083 | 19527.5172 | 20845.4255 | 20929.5712 | 1.004
13 | Office | 1959-pre | 2015 | fans_to_variable | 0.071353 | 0 | 30.9368 | 1.5238 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 2.1983 | 0.90932 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 80491.5869 | -4357.682 | 76133.9049 | 1303.9637 | -492.4181 | 811.5456 | 20628.0691 | 25.4182
13 | Office | 1959-pre | 2015 | hrv_enabled | 0.071353 | 0 | 26.3087 | 1.5471 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 2.2026 | 0.907 | 0.45704 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 796245.3371 | -78949.362 | 717295.9751 | 12899.1745 | -8921.2779 | 3977.8966 | 1243754.4774 | 312.6664
13 | Office | 1959-pre | 2015 | infil_reduce | 0.071353 | 0 | 18.6935 | 1.2719 | 0 | 3.2387 | 2.6936 | 0.81528 | 0 | 1.9398 | 0.60076 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 1973985.1096 | 122302.0213 | 2096287.1309 | 31978.5588 | 13820.1284 | 45798.6872 | 216162.4736 | 4.7198
13 | Office | 1959-pre | 2015 | infil_reduce_plus_setback | 0.071353 | 0 | 16.8729 | 1.2494 | 0 | 3.2386 | 2.6936 | 0.81528 | 0 | 1.9372 | 0.61502 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 2255566.6842 | 123969.7761 | 2379536.4603 | 36540.1803 | 14008.5847 | 50548.765 | 315447.0333 | 6.2404
13 | Office | 1959-pre | 2015 | lights_reduce_70p | 0.071353 | 0 | 31.9243 | 1.5096 | 0 | 3.2389 | 1.8855 | 0.81528 | 0 | 2.2133 | 0.91297 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | -72224.5441 | 119925.919 | 47701.3749 | -1170.0376 | 13551.6288 | 12381.5912 | 329954.1489 | 26.6488
13 | Office | 1959-pre | 2015 | load_reduce | 0.071353 | 0 | 11.4232 | 1.2494 | 0 | 3.2386 | 2.6936 | 0.81528 | 0 | 1.9373 | 0.5458 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 3098383.6267 | 134666.7198 | 3233050.3465 | 50193.8148 | 15217.3393 | 65411.1541 | 319243.4097 | 4.8806
13 | Office | 1959-pre | 2015 | occupancy_setback | 0.071353 | 0 | 29.58 | 1.7595 | 0 | 3.2387 | 2.6936 | 0.81528 | 0 | 2.2685 | 0.98144 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 290341.7707 | -62827.7319 | 227514.0387 | 4703.5367 | -7099.5337 | -2395.997 | 99284.5597 | -41.4377
13 | Office | 1959-pre | 2015 | payback_less_than_20 | 0.071353 | 0 | 5.2305 | 0.17938 | 0 | 3.2386 | 1.8855 | 0.81528 | 0 | 0.77371 | 0.39541 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 4056105.2909 | 628322.1512 | 4684427.4421 | 65708.9057 | 71000.4031 | 136709.3088 | 1121560.8275 | 8.204
13 | Office | 1959-pre | 2015 | plug_loads_90_percent | 0.071353 | 0 | 30.9769 | 1.5242 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 2.2032 | 0.90978 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 74286.8216 | -5245.358 | 69041.4636 | 1203.4465 | -592.7254 | 610.7211 | 57405.5596 | 93.9964
13 | Office | 1959-pre | 2015 | pumps_to_variable | 0.071353 | 0 | 31.6017 | 1.5239 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 2.2025 | 0.21191 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | -22335.3618 | 102826.9487 | 80491.5869 | -361.8329 | 11619.4452 | 11257.6123 | 13995.3506 | 1.2432
13 | Office | 1959-pre | 2015 | pump_fan_eff_ | 0.071353 | 0 | 30.9312 | 1.5239 | 0 | 3.2389 | 2.6936 | 0.81528 | 0 | 2.2025 | 0.71121 | 0 | 0 | 4864984.3191 | 230741.9513 | 0 | 500900.3019 | 416571.0856 | 126085.8522 | 0 | 341288.991 | 139876.212 | 0 | 6620448.7131 | 81352.3636 | 25608.1065 | 106960.4701 | 1317.9083 | 2893.716 | 4211.6243 | 32830.3835 | 7.7952
14 | Office | 1960-1979 | 2015 | air_temp_reset_enabled | 0.015037 | 0 | 5.0206 | 0.051024 | 0 | 0.6825 | 0.56765 | 0.17181 | 0 | 0.45411 | 0.17801 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 172186.2958 | 36080.5646 | 208266.8604 | 2789.418 | 4077.1038 | 6866.5218 | 14449.6952 | 2.1044
14 | Office | 1960-1979 | 2015 | baseline | 0.015037 | 0 | 6.1869 | 0.2964 | 0 | 0.68257 | 0.56765 | 0.17181 | 0 | 0.45308 | 0.17805 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | Office | 1960-1979 | 2015 | boiler_eff_upgrade | 0.015037 | 0 | 6.0579 | 0.3027 | 0 | 0.68255 | 0.56765 | 0.17181 | 0 | 0.45216 | 0.17873 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 19037.8101 | -894.7085 | 18143.1016 | 308.4125 | -101.1021 | 207.3105 | 53703.1343 | 259.0469
14 | Office | 1960-1979 | 2015 | boiler_reset | 0.015037 | 0 | 4.2871 | 0.3027 | 0 | 0.68255 | 0.56765 | 0.17181 | 0 | 0.45216 | 0.14933 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 280469.478 | 3445.3494 | 283914.8274 | 4543.6055 | 389.3245 | 4932.93 | 763.7477 | 0.15483
14 | Office | 1960-1979 | 2015 | cooling_cop_3_0 | 0.015037 | 0 | 6.0579 | 0.21622 | 0 | 0.68255 | 0.56765 | 0.17181 | 0 | 0.45216 | 0.17873 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 19037.8101 | 11872.9265 | 30910.7366 | 308.4125 | 1341.6407 | 1650.0532 | 16519.8687 | 10.0117
14 | Office | 1960-1979 | 2015 | dcv_enabled | 0.015037 | 0 | 5.1507 | 0.30409 | 0 | 0.68255 | 0.56765 | 0.17181 | 0 | 0.45216 | 0.17801 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 152971.7086 | -993.9202 | 151977.7884 | 2478.1417 | -112.313 | 2365.8287 | 34880.8598 | 14.7436
14 | Office | 1960-1979 | 2015 | ecm_cold_deck_reset_control | 0.015037 | 0 | 4.7809 | 0.036875 | 0 | 0.68257 | 0.56765 | 0.17181 | 0 | 0.45271 | 0.17654 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 207570.5751 | 38591.5207 | 246162.0959 | 3362.6433 | 4360.8418 | 7723.4852 | 14449.6952 | 1.8709
14 | Office | 1960-1979 | 2015 | economizers_enabled | 0.015037 | 0 | 6.0582 | 0.30062 | 0 | 0.68255 | 0.56765 | 0.17181 | 0 | 0.45215 | 0.17874 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 18999.9293 | -588.0544 | 18411.8749 | 307.7989 | -66.4501 | 241.3487 | 5646.2812 | 23.3947
14 | Office | 1960-1979 | 2015 | elec_reduce | 0.015037 | 0 | 5.364 | 0.30112 | 0 | 0.68255 | 0.39736 | 0.17181 | 0 | 0.21187 | 0.13984 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 121492.7599 | 65696.1384 | 187188.8983 | 1968.1827 | 7423.6636 | 9391.8464 | 123624.4621 | 13.163
14 | Office | 1960-1979 | 2015 | envelope_ecm_roof | 0.015037 | 0 | 5.118 | 0.25258 | 0 | 0.68255 | 0.56765 | 0.17181 | 0 | 0.4316 | 0.15383 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 157807.8247 | 13216.7931 | 171024.6178 | 2556.4868 | 1493.4976 | 4049.9844 | 682135.6152 | 168.4292
14 | Office | 1960-1979 | 2015 | envelope_ecm_wall | 0.015037 | 0 | 5.7693 | 0.28647 | 0 | 0.68255 | 0.56765 | 0.17181 | 0 | 0.44615 | 0.17119 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 61644.6962 | 3501.2687 | 65145.9648 | 998.6441 | 395.6434 | 1394.2874 | 316833.4857 | 227.2369
14 | Office | 1960-1979 | 2015 | envelope_ecm_windows | 0.015037 | 0 | 6.0283 | 0.3027 | 0 | 0.68255 | 0.56765 | 0.17181 | 0 | 0.45119 | 0.17759 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 23406.7296 | -582.6429 | 22824.0868 | 379.189 | -65.8386 | 313.3504 | 2493753.6637 | 7958.3554
14 | Office | 1960-1979 | 2015 | exhaust_fans_occ_control | 0.015037 | 0 | 6.0579 | 0.3027 | 0 | 0.68255 | 0.56765 | 0.17181 | 0 | 0.20981 | 0.17873 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 19037.8101 | 34884.6134 | 53922.4236 | 308.4125 | 3941.9613 | 4250.3738 | 4210.5707 | 0.99064
14 | Office | 1960-1979 | 2015 | fans_to_variable | 0.015037 | 0 | 6.059 | 0.30266 | 0 | 0.68255 | 0.56765 | 0.17181 | 0 | 0.45135 | 0.17874 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 18880.8754 | -770.243 | 18110.6323 | 305.8702 | -87.0375 | 218.8327 | 4149.9151 | 18.9639
14 | Office | 1960-1979 | 2015 | hrv_enabled | 0.015037 | 0 | 5.091 | 0.30787 | 0 | 0.68255 | 0.56765 | 0.17181 | 0 | 0.45218 | 0.17817 | 0.096317 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 161792.5246 | -15796.2956 | 145996.229 | 2621.0389 | -1784.9814 | 836.0575 | 250216.125 | 299.281
14 | Office | 1960-1979 | 2015 | infil_reduce | 0.015037 | 0 | 4.5462 | 0.27716 | 0 | 0.68254 | 0.56765 | 0.17181 | 0 | 0.41709 | 0.13867 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 242231.5114 | 13968.9977 | 256200.5091 | 3924.1505 | 1578.4967 | 5502.6472 | 43487.1492 | 7.903
14 | Office | 1960-1979 | 2015 | infil_reduce_plus_setback | 0.015037 | 0 | 4.0845 | 0.27244 | 0 | 0.68252 | 0.56765 | 0.17181 | 0 | 0.41993 | 0.14457 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 310397.1175 | 13373.7279 | 323770.8454 | 5028.4333 | 1511.2313 | 6539.6646 | 63461.0253 | 9.704
14 | Office | 1960-1979 | 2015 | lights_reduce_70p | 0.015037 | 0 | 6.2539 | 0.29954 | 0 | 0.68255 | 0.39736 | 0.17181 | 0 | 0.45401 | 0.17927 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | -9890.4977 | 24359.1613 | 14468.6635 | -160.2261 | 2752.5852 | 2592.3592 | 66379.5388 | 25.6058
14 | Office | 1960-1979 | 2015 | load_reduce | 0.015037 | 0 | 2.7922 | 0.27244 | 0 | 0.68252 | 0.56765 | 0.17181 | 0 | 0.41993 | 0.12596 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 501173.8692 | 16120.9882 | 517294.8574 | 8119.0167 | 1821.6717 | 9940.6883 | 64224.7729 | 6.4608
14 | Office | 1960-1979 | 2015 | occupancy_setback | 0.015037 | 0 | 5.7648 | 0.35075 | 0 | 0.68254 | 0.56765 | 0.17181 | 0 | 0.46485 | 0.19387 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 62310.316 | -12096.6036 | 50213.7124 | 1009.4271 | -1366.9162 | -357.4891 | 19973.8761 | -55.8727
14 | Office | 1960-1979 | 2015 | payback_less_than_20 | 0.015037 | 0 | 1.434 | 0.036093 | 0 | 0.68252 | 0.39736 | 0.17181 | 0 | 0.17666 | 0.093495 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 701698.6147 | 116862.2825 | 818560.8972 | 11367.5176 | 13205.4379 | 24572.9555 | 225633.4424 | 9.1822
14 | Office | 1960-1979 | 2015 | plug_loads_90_percent | 0.015037 | 0 | 6.0696 | 0.30304 | 0 | 0.68255 | 0.56765 | 0.17181 | 0 | 0.4522 | 0.17877 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 17318.7431 | -956.0394 | 16362.7038 | 280.5636 | -108.0324 | 172.5312 | 11548.7397 | 66.9371
14 | Office | 1960-1979 | 2015 | pumps_to_variable | 0.015037 | 0 | 6.1889 | 0.3027 | 0 | 0.68255 | 0.56765 | 0.17181 | 0 | 0.45216 | 0.041151 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | -297.6349 | 19416.6182 | 19118.9833 | -4.8217 | 2194.0779 | 2189.2562 | 2815.5576 | 1.2861
14 | Office | 1960-1979 | 2015 | pump_fan_eff_ | 0.015037 | 0 | 6.0579 | 0.3027 | 0 | 0.68255 | 0.56765 | 0.17181 | 0 | 0.45216 | 0.13979 | 0 | 0 | 913396.3937 | 43759.5448 | 0 | 100770.1559 | 83804.9669 | 25365.7084 | 0 | 66890.2857 | 26285.6708 | 0 | 1260272.7261 | 19037.8101 | 4854.1545 | 23891.9647 | 308.4125 | 548.5195 | 856.932 | 6604.7532 | 7.7074
15 | Office | 1980-2004 | 2015 | air_temp_reset_enabled | 0.076404 | 0 | 18.0054 | 0.19506 | 0 | 3.4678 | 2.8843 | 0.87299 | 0 | 2.1197 | 0.67272 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | 595413.9694 | 108473.9024 | 703887.8718 | 9645.7063 | 12257.551 | 21903.2573 | 115089.8695 | 5.2545
15 | Office | 1980-2004 | 2015 | baseline | 0.076404 | 0 | 20.578 | 0.7479 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.0692 | 0.63907 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Office | 1980-2004 | 2015 | boiler_eff_upgrade | 0.076404 | 0 | 22.0667 | 1.133 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.1016 | 0.67824 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | -344515.9876 | -105686.6262 | -450202.6138 | -5581.159 | -11942.5888 | -17523.7478 | 215553.5526 | -12.3007
15 | Office | 1980-2004 | 2015 | boiler_reset | 0.076404 | 0 | 15.4857 | 1.133 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.1016 | 0.59257 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | 1178500.7057 | -85859.6083 | 1092641.0974 | 19091.7114 | -9702.1357 | 9389.5757 | 6083.147 | 0.64786
15 | Office | 1980-2004 | 2015 | cooling_cop_3_0 | 0.076404 | 0 | 22.0667 | 0.97115 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.1016 | 0.67824 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | -344515.9876 | -68230.8032 | -412746.7908 | -5581.159 | -7710.0808 | -13291.2398 | 131578.5218 | -9.8996
15 | Office | 1980-2004 | 2015 | dcv_enabled | 0.076404 | 0 | 17.356 | 1.1442 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.1016 | 0.6739 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | 745653.9162 | -107281.4081 | 638372.5081 | 12079.5934 | -12122.7991 | -43.2057 | 277821.3344 | -6430.2055
15 | Office | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.076404 | 0 | 16.6663 | 0.16166 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.1064 | 0.67166 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | 905275.778 | 119508.0689 | 1024783.8469 | 14665.4676 | 13504.4118 | 28169.8794 | 115089.8695 | 4.0856
15 | Office | 1980-2004 | 2015 | economizers_enabled | 0.076404 | 0 | 22.069 | 1.1192 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.1016 | 0.67831 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | -345047.5816 | -102511.4298 | -447559.0114 | -5589.7708 | -11583.7916 | -17173.5624 | 44971.8669 | -2.6187
15 | Office | 1980-2004 | 2015 | elec_reduce | 0.076404 | 0 | 16.6282 | 0.85276 | 0 | 3.468 | 2.019 | 0.87299 | 0 | 0.85729 | 0.50932 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | 914082.9969 | 486465.9422 | 1400548.9391 | 14808.1445 | 54970.6515 | 69778.796 | 984652.135 | 14.1111
15 | Office | 1980-2004 | 2015 | envelope_ecm_roof | 0.076404 | 0 | 20.657 | 1.0964 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.0823 | 0.64813 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | -18289.7055 | -85802.1386 | -104091.8441 | -296.2932 | -9695.6417 | -9991.9349 | 5433117.9943 | -543.7503
15 | Office | 1980-2004 | 2015 | envelope_ecm_wall | 0.076404 | 0 | 21.6909 | 1.1357 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.0972 | 0.67024 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | -257564.4567 | -103459.6785 | -361024.1353 | -4172.5442 | -11690.9437 | -15863.4879 | 2523535.8986 | -159.0783
15 | Office | 1980-2004 | 2015 | envelope_ecm_windows | 0.076404 | 0 | 21.971 | 1.1342 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.1019 | 0.67737 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | -322375.8176 | -105830.3002 | -428206.1178 | -5222.4882 | -11958.8239 | -17181.3122 | 19862410.9375 | -1156.0474
15 | Office | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.076404 | 0 | 22.0667 | 1.133 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 0.87026 | 0.67824 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | -344530.355 | 179276.4708 | -165253.8842 | -5581.3918 | 20258.2412 | 14676.8494 | 33536.6269 | 2.285
15 | Office | 1980-2004 | 2015 | fans_to_variable | 0.076404 | 0 | 22.0708 | 1.1329 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.0984 | 0.67824 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | -345464.2363 | -104925.1538 | -450389.39 | -5596.5206 | -11856.5424 | -17453.063 | 33053.5132 | -1.8939
15 | Office | 1980-2004 | 2015 | hrv_enabled | 0.076404 | 0 | 17.0369 | 1.1711 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.1017 | 0.67533 | 0.48939 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | 819516.7417 | -227119.9274 | 592396.8144 | 13276.1712 | -25664.5518 | -12388.3806 | 1992937.6229 | -160.8715
15 | Office | 1980-2004 | 2015 | infil_reduce | 0.076404 | 0 | 18.5425 | 1.1291 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.0712 | 0.61722 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | 471078.4525 | -83618.2932 | 387460.1594 | 7631.4709 | -9448.8671 | -1817.3962 | 317193.168 | -174.5317
15 | Office | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.076404 | 0 | 16.7554 | 1.109 | 0 | 3.4679 | 2.8843 | 0.87299 | 0 | 2.0555 | 0.6269 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | 884672.9205 | -77583.9832 | 807088.9373 | 14331.7013 | -8766.9901 | 5564.7112 | 476282.3918 | 85.5898
15 | Office | 1980-2004 | 2015 | lights_reduce_70p | 0.076404 | 0 | 21.4056 | 0.85189 | 0 | 3.468 | 2.019 | 0.87299 | 0 | 2.0884 | 0.65484 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | -191517.4992 | 168084.2628 | -23433.2363 | -3102.5835 | 18993.5217 | 15890.9382 | 528704.0563 | 33.2708
15 | Office | 1980-2004 | 2015 | load_reduce | 0.076404 | 0 | 11.246 | 1.109 | 0 | 3.4679 | 2.8843 | 0.87299 | 0 | 2.0555 | 0.56612 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | 2159708.2155 | -63518.2944 | 2096189.9211 | 34987.2731 | -7177.5673 | 27809.7058 | 482365.5388 | 17.3452
15 | Office | 1980-2004 | 2015 | occupancy_setback | 0.076404 | 0 | 19.9232 | 1.1164 | 0 | 3.4679 | 2.8843 | 0.87299 | 0 | 2.1165 | 0.70581 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | 151576.1156 | -111677.8338 | 39898.2818 | 2455.5331 | -12619.5952 | -10164.0621 | 159089.2238 | -15.6521
15 | Office | 1980-2004 | 2015 | payback_less_than_20 | 0.076404 | 0 | 5.1181 | 0.16222 | 0 | 3.4679 | 2.019 | 0.87299 | 0 | 0.79396 | 0.011609 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | 3577857.2243 | 776112.813 | 4353970.0373 | 57961.287 | 87700.7479 | 145662.0349 | 1767963.7791 | 12.1374
15 | Office | 1980-2004 | 2015 | plug_loads_90_percent | 0.076404 | 0 | 22.0439 | 1.1246 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.101 | 0.67787 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | -339257.5176 | -103531.5155 | -442789.0332 | -5495.9718 | -11699.0613 | -17195.033 | 91984.1508 | -5.3495
15 | Office | 1980-2004 | 2015 | pumps_to_variable | 0.076404 | 0 | 22.6093 | 1.133 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.1016 | 0.13211 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | -470087.1012 | 20703.4295 | -449383.6717 | -7615.411 | 2339.4875 | -5275.9235 | 22425.536 | -4.2505
15 | Office | 1980-2004 | 2015 | pump_fan_eff_ | 0.076404 | 0 | 22.0667 | 1.133 | 0 | 3.468 | 2.8843 | 0.87299 | 0 | 2.1016 | 0.53049 | 0 | 0 | 4762306.0351 | 173084.1197 | 0 | 802591.9394 | 667495.2365 | 202034.4393 | 0 | 478865.5855 | 147898.0599 | 0 | 7234275.4153 | -344515.9876 | -71492.2039 | -416008.1915 | -5581.159 | -8078.619 | -13659.778 | 52605.9665 | -3.8512
19 | Recreation Center | 1980-2004 | 2015 | air_temp_reset_enabled | 0.068406 | 0.59492 | 28.4613 | 0.10668 | 0 | 1.6002 | 3.6431 | 0.45204 | 0.34782 | 1.1393 | 0.28679 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | -1009163.4534 | 52988.7169 | -956174.7365 | -16348.4479 | 5987.725 | -10360.7229 | 40364.2663 | -3.8959
19 | Recreation Center | 1980-2004 | 2015 | baseline | 0.068406 | 0.84031 | 24.1006 | 0.092065 | 0 | 1.6003 | 3.6431 | 0.45204 | 0.34782 | 1.1393 | 0.28498 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | Recreation Center | 1980-2004 | 2015 | boiler_eff_upgrade | 0.068406 | 0.83324 | 23.6952 | 0.10025 | 0 | 1.6003 | 3.6431 | 0.45204 | 0.34782 | 1.1393 | 0.28664 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | 93812.8309 | -641.5268 | 93171.3042 | 1519.7679 | -72.4925 | 1447.2753 | 83341.7829 | 57.5853
19 | Recreation Center | 1980-2004 | 2015 | boiler_reset | 0.068406 | 0.83324 | 21.8879 | 0.10025 | 0 | 1.6003 | 3.6431 | 0.45204 | 0.34782 | 1.1393 | 0.28664 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | 512070.8545 | -641.5268 | 511429.3277 | 8295.5478 | -72.4925 | 8223.0553 | 1185.2584 | 0.14414
19 | Recreation Center | 1980-2004 | 2015 | cooling_cop_3_0 | 0.068406 | 0.83324 | 23.6952 | 0.085933 | 0 | 1.6003 | 3.6431 | 0.45204 | 0.34782 | 1.1393 | 0.28664 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | 93812.8309 | 2670.7039 | 96483.5348 | 1519.7679 | 301.7895 | 1821.5574 | 55330.4166 | 30.3753
19 | Recreation Center | 1980-2004 | 2015 | dcv_enabled | 0.068406 | 0.80887 | 17.2448 | 0.16763 | 0 | 1.6003 | 3.6431 | 0.45204 | 0.34782 | 1.1393 | 0.28641 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | 1586635.1731 | -10543.3531 | 1576091.8201 | 25703.4898 | -1191.3989 | 24512.0909 | 33964.8811 | 1.3856
19 | Recreation Center | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.068406 | 0.84638 | 23.5835 | 0.09547 | 0 | 1.6003 | 3.6431 | 0.45204 | 0.34782 | 1.1393 | 0.28659 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | 119665.6626 | -2566.1071 | 117099.5555 | 1938.5837 | -289.9701 | 1648.6136 | 40364.2663 | 24.4838
19 | Recreation Center | 1980-2004 | 2015 | economizers_enabled | 0.068406 | 0.83347 | 23.7019 | 0.098167 | 0 | 1.6003 | 3.6431 | 0.45204 | 0.34782 | 1.1393 | 0.2854 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | 92261.3124 | 73.2177 | 92334.5301 | 1494.6333 | 8.2736 | 1502.9069 | 10514.9476 | 6.9964
19 | Recreation Center | 1980-2004 | 2015 | elec_reduce | 0.068406 | 0.88172 | 18.0207 | 0.14838 | 0 | 1.6003 | 2.5502 | 0.45204 | 0.34782 | 1.1366 | 0.22362 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | 1407046.0287 | 245143.4183 | 1652189.447 | 22794.1457 | 27701.2063 | 50495.3519 | 384274.8182 | 7.6101
19 | Recreation Center | 1980-2004 | 2015 | envelope_ecm_roof | 0.068406 | 0.79885 | 24.1426 | 0.10602 | 0 | 1.6001 | 3.6431 | 0.45204 | 0.34782 | 1.0045 | 0.29629 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | -9689.1462 | 34945.7764 | 25256.6301 | -156.9642 | 3948.8727 | 3791.9086 | 1839061.5143 | 484.9963
19 | Recreation Center | 1980-2004 | 2015 | envelope_ecm_wall | 0.068406 | 0.90453 | 24.8973 | 0.11399 | 0 | 1.6001 | 3.6431 | 0.45204 | 0.34782 | 1.0948 | 0.31972 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | -184351.7834 | -17662.9056 | -202014.689 | -2986.4989 | -1995.9083 | -4982.4072 | 1688513.2585 | -338.8951
19 | Recreation Center | 1980-2004 | 2015 | envelope_ecm_windows | 0.068406 | 0.95732 | 25.0191 | 0.1138 | 0 | 1.6001 | 3.6431 | 0.45204 | 0.34782 | 1.1148 | 0.32186 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | -212519.6899 | -34956.236 | -247475.926 | -3442.819 | -3950.0547 | -7392.8736 | 301414.8156 | -40.771
19 | Recreation Center | 1980-2004 | 2015 | fans_to_variable | 0.068406 | 0.83327 | 23.7046 | 0.10016 | 0 | 1.6003 | 3.6431 | 0.45204 | 0.34782 | 1.1278 | 0.28664 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | 91651.1646 | 2053.583 | 93704.7476 | 1484.7489 | 232.0549 | 1716.8037 | 14754.3644 | 8.5941
19 | Recreation Center | 1980-2004 | 2015 | hrv_enabled | 0.068406 | 0.77968 | 15.1885 | 0.21744 | 0 | 1.6003 | 3.6431 | 0.45204 | 0.34782 | 1.1393 | 0.28668 | 0.213 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | 2062508.5767 | -64672.1746 | 1997836.4021 | 33412.6389 | -7307.9557 | 26104.6832 | 986217.6838 | 37.7793
19 | Recreation Center | 1980-2004 | 2015 | infil_reduce | 0.068406 | 0.57098 | 21.5282 | 0.095515 | 0 | 1.6002 | 3.6431 | 0.45204 | 0.34782 | 0.97428 | 0.22678 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | 595336.8458 | 113198.0965 | 708534.9423 | 9644.4569 | 12791.3849 | 22435.8418 | 139765.8013 | 6.2296
19 | Recreation Center | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.068406 | 0.66535 | 26.8295 | 0.24441 | 0 | 1.5999 | 3.6431 | 0.45204 | 0.34782 | 0.742 | 0.23656 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | -631433.1865 | 108393.6188 | -523039.5677 | -10229.2176 | 12248.4789 | 2019.2613 | 159215.3521 | 78.8483
19 | Recreation Center | 1980-2004 | 2015 | lights_reduce_70p | 0.068406 | 0.89876 | 24.4298 | 0.089609 | 0 | 1.6004 | 2.5502 | 0.45204 | 0.34782 | 1.1373 | 0.28615 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | -76198.7371 | 240178.5589 | 163979.8218 | -1234.4195 | 27140.1772 | 25905.7576 | 287755.3033 | 11.1078
19 | Recreation Center | 1980-2004 | 2015 | load_reduce | 0.068406 | 0.66535 | 24.7875 | 0.24441 | 0 | 1.5999 | 3.6431 | 0.45204 | 0.34782 | 0.742 | 0.23656 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | -158858.0673 | 108393.6188 | -50464.4485 | -2573.5007 | 12248.4789 | 9674.9782 | 160400.5977 | 16.5789
19 | Recreation Center | 1980-2004 | 2015 | occupancy_setback | 0.068406 | 1.0952 | 29.3629 | 0.24397 | 0 | 1.5999 | 3.6431 | 0.45204 | 0.34782 | 0.85587 | 0.28329 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | -1217743.3322 | -28157.4469 | -1245900.779 | -19727.442 | -3181.7915 | -22909.2335 | 19449.5507 | -0.84898
19 | Recreation Center | 1980-2004 | 2015 | payback_less_than_20 | 0.068406 | 0.73947 | 18.7474 | 0.34019 | 0 | 1.5999 | 2.5502 | 0.45204 | 0.34782 | 0.74283 | 0.18082 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | 1238972.9872 | 334716.5941 | 1573689.5812 | 20071.3624 | 37822.9751 | 57894.3375 | 620931.6973 | 10.7253
19 | Recreation Center | 1980-2004 | 2015 | plug_loads_90_percent | 0.068406 | 0.83306 | 23.7181 | 0.099447 | 0 | 1.6003 | 3.6431 | 0.45204 | 0.34782 | 1.1387 | 0.2865 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | 88527.2082 | -233.5994 | 88293.6088 | 1434.1408 | -26.3967 | 1407.744 | 11245.6612 | 7.9884
19 | Recreation Center | 1980-2004 | 2015 | pumps_to_variable | 0.068406 | 0.83324 | 23.915 | 0.099703 | 0 | 1.6034 | 3.6431 | 0.45204 | 0.34782 | 1.1393 | 0.031954 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | 42236.1703 | 58424.2616 | 100660.4319 | 684.226 | 6601.9416 | 7286.1675 | 17477.845 | 2.3988
19 | Recreation Center | 1980-2004 | 2015 | pump_fan_eff_ | 0.068406 | 0.83324 | 23.6952 | 0.10025 | 0 | 1.6003 | 3.6431 | 0.45204 | 0.34782 | 1.1393 | 0.22419 | 0 | 194469.7763 | 5577524.4191 | 21306.3593 | 0 | 370359.6821 | 843116.1024 | 104614.1893 | 80494.1773 | 263674.477 | 65951.7416 | 0 | 7521510.9244 | 93812.8309 | 13810.2584 | 107623.0894 | 1519.7679 | 1560.5592 | 3080.3271 | 43840.759 | 14.2325
20 | Storage Building | 1959-pre | 2015 | baseline | 0.0014259 | 0 | 0.56681 | 0 | 0 | 0 | 0.049717 | 0.0046058 | 0 | 0.023487 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | Storage Building | 1959-pre | 2015 | dcv_enabled | 0.0014259 | 0 | 0.56191 | 0 | 0 | 0 | 0.049717 | 0.0046058 | 0 | 0.023168 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | 1133.8822 | 73.7484 | 1207.6306 | 18.3689 | 8.3336 | 26.7025 | 284.4855 | 10.6539
20 | Storage Building | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.0014259 | 0 | 0.56191 | 0 | 0 | 0 | 0.049717 | 0.0046058 | 0 | 0.023168 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | 1133.8822 | 73.7484 | 1207.6306 | 18.3689 | 8.3336 | 26.7025 | 0 | 0
20 | Storage Building | 1959-pre | 2015 | elec_reduce | 0.0014259 | 0 | 0.57728 | 0 | 0 | 0 | 0.034805 | 0.0046058 | 0 | 0.023721 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | -2424.4798 | 3397.0373 | 972.5575 | -39.2766 | 383.8652 | 344.5886 | 15390.7444 | 44.6641
20 | Storage Building | 1959-pre | 2015 | envelope_ecm_roof | 0.0014259 | 0 | 0.52407 | 0 | 0 | 0 | 0.049717 | 0.0046058 | 0 | 0.02161 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | 9889.2043 | 434.4244 | 10323.6287 | 160.2051 | 49.09 | 209.2951 | 95647.7522 | 456.9996
20 | Storage Building | 1959-pre | 2015 | envelope_ecm_wall | 0.0014259 | 0 | 0.54472 | 0 | 0 | 0 | 0.049717 | 0.0046058 | 0 | 0.022426 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | 5110.5361 | 245.444 | 5355.9801 | 82.7907 | 27.7352 | 110.5259 | 53416.1483 | 483.291
20 | Storage Building | 1959-pre | 2015 | envelope_ecm_windows | 0.0014259 | 0 | 0.56191 | 0 | 0 | 0 | 0.049717 | 0.0046058 | 0 | 0.023168 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | 1133.8822 | 73.7484 | 1207.6306 | 18.3689 | 8.3336 | 26.7025 | 0 | 0
20 | Storage Building | 1959-pre | 2015 | exhaust_fans_occ_control | 0.0014259 | 0 | 0.56191 | 0 | 0 | 0 | 0.049717 | 0.0046058 | 0 | 0.023168 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | 1133.8822 | 73.7484 | 1207.6306 | 18.3689 | 8.3336 | 26.7025 | 250.2942 | 9.3734
20 | Storage Building | 1959-pre | 2015 | hrv_enabled | 0.0014259 | 0 | 0.56191 | 0 | 0 | 0 | 0.049717 | 0.0046058 | 0 | 0.023168 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | 1133.8822 | 73.7484 | 1207.6306 | 18.3689 | 8.3336 | 26.7025 | 0 | 0
20 | Storage Building | 1959-pre | 2015 | infil_reduce | 0.0014259 | 0 | 0.29226 | 0 | 0 | 0 | 0.049717 | 0.0046058 | 0 | 0.012323 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | 63536.5819 | 2583.4999 | 66120.0818 | 1029.2926 | 291.9355 | 1321.2281 | 12401.4923 | 9.3863
20 | Storage Building | 1959-pre | 2015 | infil_reduce_plus_setback | 0.0014259 | 0 | 0.25349 | 0 | 0 | 0 | 0.049717 | 0.0046058 | 0 | 0.012677 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | 72509.6924 | 2501.6852 | 75011.3776 | 1174.657 | 282.6904 | 1457.3474 | 12564.4824 | 8.6215
20 | Storage Building | 1959-pre | 2015 | lights_reduce_70p | 0.0014259 | 0 | 0.57705 | 0 | 0 | 0 | 0.034805 | 0.0046058 | 0 | 0.023696 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | -2371.4731 | 3402.7989 | 1031.3258 | -38.4179 | 384.5163 | 346.0984 | 8111.6431 | 23.4374
20 | Storage Building | 1959-pre | 2015 | load_reduce | 0.0014259 | 0 | 0.25349 | 0 | 0 | 0 | 0.049717 | 0.0046058 | 0 | 0.012677 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | 72509.6924 | 2501.6852 | 75011.3776 | 1174.657 | 282.6904 | 1457.3474 | 12564.4824 | 8.6215
20 | Storage Building | 1959-pre | 2015 | occupancy_setback | 0.0014259 | 0 | 0.49484 | 0 | 0 | 0 | 0.049717 | 0.0046058 | 0 | 0.024821 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | 16655.6233 | -308.8216 | 16346.8017 | 269.8211 | -34.8968 | 234.9243 | 162.9901 | 0.6938
20 | Storage Building | 1959-pre | 2015 | payback_less_than_20 | 0.0014259 | 0 | 0.26912 | 0 | 0 | 0 | 0.034805 | 0.0046058 | 0 | 0.01308 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | 68892.5621 | 5859.5437 | 74752.1057 | 1116.0595 | 662.1284 | 1778.1879 | 21708.8369 | 12.2084
20 | Storage Building | 1959-pre | 2015 | plug_loads_90_percent | 0.0014259 | 0 | 0.56211 | 0 | 0 | 0 | 0.049717 | 0.0046058 | 0 | 0.023188 | 0 | 0 | 0 | 131174.2683 | 0 | 0 | 0 | 11505.9083 | 1065.8954 | 0 | 5435.4902 | 0 | 0 | 149181.5621 | 1087.7894 | 69.1392 | 1156.9286 | 17.6222 | 7.8127 | 25.4349 | 94.2757 | 3.7065
21 | Storage Building | 1960-1979 | 2015 | baseline | 0.0035951 | 0 | 1.3041 | 0 | 0 | 0 | 0.12535 | 0.011612 | 0 | 0.05398 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | Storage Building | 1960-1979 | 2015 | dcv_enabled | 0.0035951 | 0 | 1.2863 | 0 | 0 | 0 | 0.12535 | 0.011612 | 0 | 0.053114 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | 4128.348 | 200.4617 | 4328.8097 | 66.8792 | 22.6522 | 89.5314 | 717.2484 | 8.0111
21 | Storage Building | 1960-1979 | 2015 | ecm_cold_deck_reset_control | 0.0035951 | 0 | 1.2863 | 0 | 0 | 0 | 0.12535 | 0.011612 | 0 | 0.053114 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | 4128.348 | 200.4617 | 4328.8097 | 66.8792 | 22.6522 | 89.5314 | 0 | 0
21 | Storage Building | 1960-1979 | 2015 | elec_reduce | 0.0035951 | 0 | 1.3242 | 0 | 0 | 0 | 0.08775 | 0.011612 | 0 | 0.05442 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | -4636.7653 | 8599.5146 | 3962.7493 | -75.1156 | 971.7451 | 896.6295 | 38803.3314 | 43.2769
21 | Storage Building | 1960-1979 | 2015 | envelope_ecm_roof | 0.0035951 | 0 | 1.0108 | 0 | 0 | 0 | 0.12535 | 0.011612 | 0 | 0.042017 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | 67878.0601 | 2768.6951 | 70646.7552 | 1099.6246 | 312.8625 | 1412.4871 | 157992.7706 | 111.8543
21 | Storage Building | 1960-1979 | 2015 | envelope_ecm_wall | 0.0035951 | 0 | 1.2711 | 0 | 0 | 0 | 0.12535 | 0.011612 | 0 | 0.052449 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | 7637.8796 | 354.4395 | 7992.3191 | 123.7337 | 40.0517 | 163.7853 | 134673.4404 | 822.2559
21 | Storage Building | 1960-1979 | 2015 | envelope_ecm_windows | 0.0035951 | 0 | 1.2863 | 0 | 0 | 0 | 0.12535 | 0.011612 | 0 | 0.053114 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | 4128.348 | 200.4617 | 4328.8097 | 66.8792 | 22.6522 | 89.5314 | 0 | 0
21 | Storage Building | 1960-1979 | 2015 | exhaust_fans_occ_control | 0.0035951 | 0 | 1.2863 | 0 | 0 | 0 | 0.12535 | 0.011612 | 0 | 0.053114 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | 4128.348 | 200.4617 | 4328.8097 | 66.8792 | 22.6522 | 89.5314 | 631.0448 | 7.0483
21 | Storage Building | 1960-1979 | 2015 | hrv_enabled | 0.0035951 | 0 | 1.2863 | 0 | 0 | 0 | 0.12535 | 0.011612 | 0 | 0.053114 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | 4128.348 | 200.4617 | 4328.8097 | 66.8792 | 22.6522 | 89.5314 | 0 | 0
21 | Storage Building | 1960-1979 | 2015 | infil_reduce | 0.0035951 | 0 | 0.9475 | 0 | 0 | 0 | 0.12535 | 0.011612 | 0 | 0.039343 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | 82532.0978 | 3387.5115 | 85919.6093 | 1337.02 | 382.7888 | 1719.8088 | 31266.7927 | 18.1804
21 | Storage Building | 1960-1979 | 2015 | infil_reduce_plus_setback | 0.0035951 | 0 | 0.82241 | 0 | 0 | 0 | 0.12535 | 0.011612 | 0 | 0.041251 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | 111479.9231 | 2945.9148 | 114425.8379 | 1805.9748 | 332.8884 | 2138.8631 | 31677.7252 | 14.8105
21 | Storage Building | 1960-1979 | 2015 | lights_reduce_70p | 0.0035951 | 0 | 1.3234 | 0 | 0 | 0 | 0.08775 | 0.011612 | 0 | 0.05437 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | -4453.7351 | 8611.1355 | 4157.4004 | -72.1505 | 973.0583 | 900.9078 | 20451.1729 | 22.7006
21 | Storage Building | 1960-1979 | 2015 | load_reduce | 0.0035951 | 0 | 0.82241 | 0 | 0 | 0 | 0.12535 | 0.011612 | 0 | 0.041251 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | 111479.9231 | 2945.9148 | 114425.8379 | 1805.9748 | 332.8884 | 2138.8631 | 31677.7252 | 14.8105
21 | Storage Building | 1960-1979 | 2015 | occupancy_setback | 0.0035951 | 0 | 1.1254 | 0 | 0 | 0 | 0.12535 | 0.011612 | 0 | 0.056767 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | 41350.3009 | -644.9636 | 40705.3373 | 669.8749 | -72.8809 | 596.994 | 410.9325 | 0.68834
21 | Storage Building | 1960-1979 | 2015 | payback_less_than_20 | 0.0035951 | 0 | 0.86194 | 0 | 0 | 0 | 0.08775 | 0.011612 | 0 | 0.042393 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | 102331.3179 | 11382.7358 | 113714.0538 | 1657.7674 | 1286.2491 | 2944.0165 | 54732.5827 | 18.5911
21 | Storage Building | 1960-1979 | 2015 | plug_loads_90_percent | 0.0035951 | 0 | 1.287 | 0 | 0 | 0 | 0.12535 | 0.011612 | 0 | 0.053177 | 0 | 0 | 0 | 301808.0979 | 0 | 0 | 0 | 29008.8354 | 2687.3483 | 0 | 12492.538 | 0 | 0 | 345996.8197 | 3965.6545 | 185.9354 | 4151.59 | 64.2436 | 21.0107 | 85.2543 | 237.6892 | 2.788
22 | Storage Building | 1980-2004 | 2015 | baseline | 0.043746 | 0 | 9.6216 | 0 | 0 | 0 | 1.5253 | 0.1413 | 0 | 0.40602 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | Storage Building | 1980-2004 | 2015 | dcv_enabled | 0.043746 | 0 | 9.489 | 0 | 0 | 0 | 1.5253 | 0.1413 | 0 | 0.39808 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | 26745.0937 | 1602.2406 | 28347.3343 | 433.2705 | 181.0532 | 614.3237 | 7606.9706 | 12.3827
22 | Storage Building | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.043746 | 0 | 9.489 | 0 | 0 | 0 | 1.5253 | 0.1413 | 0 | 0.39808 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | 26745.0937 | 1602.2406 | 28347.3343 | 433.2705 | 181.0532 | 614.3237 | 0 | 0
22 | Storage Building | 1980-2004 | 2015 | elec_reduce | 0.043746 | 0 | 9.9328 | 0 | 0 | 0 | 1.0678 | 0.1413 | 0 | 0.41473 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | -62764.6956 | 90526.5958 | 27761.9002 | -1016.7881 | 10229.5053 | 9212.7173 | 411539.1777 | 44.6708
22 | Storage Building | 1980-2004 | 2015 | envelope_ecm_roof | 0.043746 | 0 | 8.316 | 0 | 0 | 0 | 1.5253 | 0.1413 | 0 | 0.35164 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | 263352.898 | 10969.1859 | 274322.0839 | 4266.3169 | 1239.518 | 5505.835 | 1453142.402 | 263.9277
22 | Storage Building | 1980-2004 | 2015 | envelope_ecm_wall | 0.043746 | 0 | 9.3616 | 0 | 0 | 0 | 1.5253 | 0.1413 | 0 | 0.39243 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | 52442.5684 | 2742.2965 | 55184.8649 | 849.5696 | 309.8795 | 1159.4491 | 1428315.4309 | 1231.8914
22 | Storage Building | 1980-2004 | 2015 | envelope_ecm_windows | 0.043746 | 0 | 9.489 | 0 | 0 | 0 | 1.5253 | 0.1413 | 0 | 0.39808 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | 26745.0937 | 1602.2406 | 28347.3343 | 433.2705 | 181.0532 | 614.3237 | 0 | 0
22 | Storage Building | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.043746 | 0 | 9.489 | 0 | 0 | 0 | 1.5253 | 0.1413 | 0 | 0.39808 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | 26745.0937 | 1602.2406 | 28347.3343 | 433.2705 | 181.0532 | 614.3237 | 6692.7152 | 10.8944
22 | Storage Building | 1980-2004 | 2015 | hrv_enabled | 0.043746 | 0 | 9.489 | 0 | 0 | 0 | 1.5253 | 0.1413 | 0 | 0.39808 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | 26745.0937 | 1602.2406 | 28347.3343 | 433.2705 | 181.0532 | 614.3237 | 0 | 0
22 | Storage Building | 1980-2004 | 2015 | infil_reduce | 0.043746 | 0 | 8.4608 | 0 | 0 | 0 | 1.5253 | 0.1413 | 0 | 0.35714 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | 234142.8188 | 9859.9424 | 244002.7611 | 3793.1137 | 1114.1735 | 4907.2872 | 297576.7849 | 60.6398
22 | Storage Building | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.043746 | 0 | 7.3168 | 0 | 0 | 0 | 1.5253 | 0.1413 | 0 | 0.36646 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | 464896.2824 | 7980.3908 | 472876.6732 | 7531.3198 | 901.7842 | 8433.1039 | 301935.0404 | 35.8035
22 | Storage Building | 1980-2004 | 2015 | lights_reduce_70p | 0.043746 | 0 | 9.9271 | 0 | 0 | 0 | 1.0678 | 0.1413 | 0 | 0.41412 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | -61624.6398 | 90649.8451 | 29025.2053 | -998.3192 | 10243.4325 | 9245.1133 | 216900.4198 | 23.4611
22 | Storage Building | 1980-2004 | 2015 | load_reduce | 0.043746 | 0 | 7.3168 | 0 | 0 | 0 | 1.5253 | 0.1413 | 0 | 0.36646 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | 464896.2824 | 7980.3908 | 472876.6732 | 7531.3198 | 901.7842 | 8433.1039 | 301935.0404 | 35.8035
22 | Storage Building | 1980-2004 | 2015 | occupancy_setback | 0.043746 | 0 | 8.2309 | 0 | 0 | 0 | 1.5253 | 0.1413 | 0 | 0.41168 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | 280515.3602 | -1140.0558 | 279375.3044 | 4544.3488 | -128.8263 | 4415.5225 | 4358.2555 | 0.98703
22 | Storage Building | 1980-2004 | 2015 | payback_less_than_20 | 0.043746 | 0 | 7.7953 | 0 | 0 | 0 | 1.0678 | 0.1413 | 0 | 0.37883 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | 368392.0965 | 97767.491 | 466159.5875 | 5967.952 | 11047.7265 | 17015.6784 | 546449.5389 | 32.1145
22 | Storage Building | 1980-2004 | 2015 | plug_loads_90_percent | 0.043746 | 0 | 9.4939 | 0 | 0 | 0 | 1.5253 | 0.1413 | 0 | 0.39854 | 0 | 0 | 0 | 1940775.5924 | 0 | 0 | 0 | 307661.014 | 28501.3959 | 0 | 81899.1462 | 0 | 0 | 2358837.1486 | 25759.0994 | 1509.8037 | 27268.9031 | 417.2974 | 170.6078 | 587.9052 | 2520.8764 | 4.2879
23 | Storage Building | 2005-2014 | 2015 | baseline | 0.0021648 | 0 | 0.28571 | 0 | 0 | 0 | 0.07548 | 0.0069924 | 0 | 0.011581 | 0 | 0 | 0 | 66121.4646 | 0 | 0 | 0 | 17468.0607 | 1618.223 | 0 | 2680.1271 | 0 | 0 | 87887.8754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | Storage Building | 2005-2014 | 2015 | dcv_enabled | 0.0021648 | 0 | 0.28044 | 0 | 0 | 0 | 0.07548 | 0.0069924 | 0 | 0.011256 | 0 | 0 | 0 | 66121.4646 | 0 | 0 | 0 | 17468.0607 | 1618.223 | 0 | 2680.1271 | 0 | 0 | 87887.8754 | 1221.1023 | 75.2255 | 1296.3278 | 19.7819 | 8.5005 | 28.2823 | 431.9008 | 15.271
23 | Storage Building | 2005-2014 | 2015 | ecm_cold_deck_reset_control | 0.0021648 | 0 | 0.28044 | 0 | 0 | 0 | 0.07548 | 0.0069924 | 0 | 0.011256 | 0 | 0 | 0 | 66121.4646 | 0 | 0 | 0 | 17468.0607 | 1618.223 | 0 | 2680.1271 | 0 | 0 | 87887.8754 | 1221.1023 | 75.2255 | 1296.3278 | 19.7819 | 8.5005 | 28.2823 | 0 | 0
23 | Storage Building | 2005-2014 | 2015 | elec_reduce | 0.0021648 | 0 | 0.30113 | 0 | 0 | 0 | 0.05284 | 0.0069924 | 0 | 0.012042 | 0 | 0 | 0 | 66121.4646 | 0 | 0 | 0 | 17468.0607 | 1618.223 | 0 | 2680.1271 | 0 | 0 | 87887.8754 | -3567.0882 | 5132.8283 | 1565.74 | -57.7868 | 580.0096 | 522.2228 | 14957.7535 | 28.6425
23 | Storage Building | 2005-2014 | 2015 | envelope_ecm_roof | 0.0021648 | 0 | 0.24144 | 0 | 0 | 0 | 0.07548 | 0.0069924 | 0 | 0.0097742 | 0 | 0 | 0 | 66121.4646 | 0 | 0 | 0 | 17468.0607 | 1618.223 | 0 | 2680.1271 | 0 | 0 | 87887.8754 | 10244.6634 | 418.1138 | 10662.7772 | 165.9635 | 47.2469 | 213.2104 | 0 | 0
23 | Storage Building | 2005-2014 | 2015 | envelope_ecm_wall | 0.0021648 | 0 | 0.27824 | 0 | 0 | 0 | 0.07548 | 0.0069924 | 0 | 0.011165 | 0 | 0 | 0 | 66121.4646 | 0 | 0 | 0 | 17468.0607 | 1618.223 | 0 | 2680.1271 | 0 | 0 | 87887.8754 | 1728.4371 | 96.2187 | 1824.6557 | 28.0007 | 10.8727 | 38.8734 | 0 | 0
23 | Storage Building | 2005-2014 | 2015 | envelope_ecm_windows | 0.0021648 | 0 | 0.28044 | 0 | 0 | 0 | 0.07548 | 0.0069924 | 0 | 0.011256 | 0 | 0 | 0 | 66121.4646 | 0 | 0 | 0 | 17468.0607 | 1618.223 | 0 | 2680.1271 | 0 | 0 | 87887.8754 | 1221.1023 | 75.2255 | 1296.3278 | 19.7819 | 8.5005 | 28.2823 | 0 | 0
23 | Storage Building | 2005-2014 | 2015 | exhaust_fans_occ_control | 0.0021648 | 0 | 0.28044 | 0 | 0 | 0 | 0.07548 | 0.0069924 | 0 | 0.011256 | 0 | 0 | 0 | 66121.4646 | 0 | 0 | 0 | 17468.0607 | 1618.223 | 0 | 2680.1271 | 0 | 0 | 87887.8754 | 1221.1023 | 75.2255 | 1296.3278 | 19.7819 | 8.5005 | 28.2823 | 379.9921 | 13.4357
23 | Storage Building | 2005-2014 | 2015 | hrv_enabled | 0.0021648 | 0 | 0.28044 | 0 | 0 | 0 | 0.07548 | 0.0069924 | 0 | 0.011256 | 0 | 0 | 0 | 66121.4646 | 0 | 0 | 0 | 17468.0607 | 1618.223 | 0 | 2680.1271 | 0 | 0 | 87887.8754 | 1221.1023 | 75.2255 | 1296.3278 | 19.7819 | 8.5005 | 28.2823 | 0 | 0
23 | Storage Building | 2005-2014 | 2015 | lights_reduce_70p | 0.0021648 | 0 | 0.30089 | 0 | 0 | 0 | 0.05284 | 0.0069924 | 0 | 0.012019 | 0 | 0 | 0 | 66121.4646 | 0 | 0 | 0 | 17468.0607 | 1618.223 | 0 | 2680.1271 | 0 | 0 | 87887.8754 | -3512.8559 | 5138.0766 | 1625.2207 | -56.9083 | 580.6027 | 523.6944 | 12314.949 | 23.5155
23 | Storage Building | 2005-2014 | 2015 | load_reduce | 0.0021648 | 0 | 0.32833 | 0 | 0 | 0 | 0.07548 | 0.0069924 | 0 | 0.015459 | 0 | 0 | 0 | 66121.4646 | 0 | 0 | 0 | 17468.0607 | 1618.223 | 0 | 2680.1271 | 0 | 0 | 87887.8754 | -9863.2876 | -897.4577 | -10760.7453 | -159.7853 | -101.4127 | -261.198 | 247.4485 | -0.94736
23 | Storage Building | 2005-2014 | 2015 | occupancy_setback | 0.0021648 | 0 | 0.23859 | 0 | 0 | 0 | 0.07548 | 0.0069924 | 0 | 0.011369 | 0 | 0 | 0 | 66121.4646 | 0 | 0 | 0 | 17468.0607 | 1618.223 | 0 | 2680.1271 | 0 | 0 | 87887.8754 | 10905.948 | 48.984 | 10954.932 | 176.6764 | 5.5352 | 182.2116 | 247.4485 | 1.358
23 | Storage Building | 2005-2014 | 2015 | payback_less_than_20 | 0.0021648 | 0 | 0.35205 | 0 | 0 | 0 | 0.05284 | 0.0069924 | 0 | 0.016033 | 0 | 0 | 0 | 66121.4646 | 0 | 0 | 0 | 17468.0607 | 1618.223 | 0 | 2680.1271 | 0 | 0 | 87887.8754 | -15352.9996 | 4209.1291 | -11143.8705 | -248.7186 | 475.6316 | 226.913 | 14130.2414 | 62.2716
23 | Storage Building | 2005-2014 | 2015 | plug_loads_90_percent | 0.0021648 | 0 | 0.28062 | 0 | 0 | 0 | 0.07548 | 0.0069924 | 0 | 0.011279 | 0 | 0 | 0 | 66121.4646 | 0 | 0 | 0 | 17468.0607 | 1618.223 | 0 | 2680.1271 | 0 | 0 | 87887.8754 | 1177.3665 | 69.9772 | 1247.3437 | 19.0733 | 7.9074 | 26.9808 | 143.1277 | 5.3048
24 | Training Building | 1959-pre | 2015 | air_temp_reset_enabled | 0.029521 | 0 | 15.9769 | 0.41814 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.80731 | 0.01598 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | -170292.1525 | -84233.0641 | -254525.2166 | -2758.7329 | -9518.3362 | -12277.0691 | 26453.8066 | -2.1547
24 | Training Building | 1959-pre | 2015 | baseline | 0.029521 | 0 | 15.2411 | 0.056628 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.79854 | 0.022297 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | Training Building | 1959-pre | 2015 | boiler_eff_upgrade | 0.029521 | 0 | 15.1442 | 0.090073 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.80731 | 0.021986 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 22414.961 | -9699.4717 | 12715.4893 | 363.1224 | -1096.0403 | -732.9179 | 122894.6622 | -167.6786
24 | Training Building | 1959-pre | 2015 | boiler_reset | 0.029521 | 0 | 9.4994 | 0.090073 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.80731 | 0.021986 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 1328776.3297 | -9699.4717 | 1319076.858 | 21526.1765 | -1096.0403 | 20430.1362 | 1747.766 | 0.085548
24 | Training Building | 1959-pre | 2015 | cooling_cop_3_0 | 0.029521 | 0 | 15.1442 | 0.064341 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.80731 | 0.021986 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 22414.961 | -3744.3756 | 18670.5854 | 363.1224 | -423.1144 | -59.9921 | 37164.9845 | -619.4982
24 | Training Building | 1959-pre | 2015 | dcv_enabled | 0.029521 | 0 | 12.9148 | 0.093043 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.80381 | 0.017953 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 538354.0195 | -8642.8397 | 529711.1799 | 8721.3351 | -976.6409 | 7744.6942 | 64170.3232 | 8.2857
24 | Training Building | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.029521 | 0 | 14.5107 | 0.22068 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.80731 | 0.012323 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 169030.3492 | -37689.9619 | 131340.3872 | 2738.2917 | -4258.9657 | -1520.674 | 26453.8066 | -17.3961
24 | Training Building | 1959-pre | 2015 | economizers_enabled | 0.029521 | 0 | 15.1369 | 0.075423 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.80731 | 0.021986 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 24102.4947 | -6309.0165 | 17793.4782 | 390.4604 | -712.9189 | -322.4584 | 10336.8057 | -32.0562
24 | Training Building | 1959-pre | 2015 | elec_reduce | 0.029521 | 0 | 13.3531 | 0.056407 | 0.22764 | 0 | 0.7844 | 0.27352 | 0 | 0.80281 | 0.014584 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 436922.4739 | 78647.2763 | 515569.7502 | 7078.1441 | 8887.1422 | 15965.2863 | 387054.6318 | 24.2435
24 | Training Building | 1959-pre | 2015 | envelope_ecm_roof | 0.029521 | 0 | 13.7743 | 0.086261 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.72582 | 0.022142 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 339435.3459 | 10007.2286 | 349442.5745 | 5498.8526 | 1130.8168 | 6629.6694 | 955346.5376 | 144.1017
24 | Training Building | 1959-pre | 2015 | envelope_ecm_wall | 0.029521 | 0 | 14.5122 | 0.093686 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.77096 | 0.022053 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 168676.4288 | -2138.9105 | 166537.5183 | 2732.5581 | -241.6969 | 2490.8613 | 831843.7229 | 333.9583
24 | Training Building | 1959-pre | 2015 | envelope_ecm_windows | 0.029521 | 0 | 14.9043 | 0.090938 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.79621 | 0.021898 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 77934.3062 | -7309.2264 | 70625.0797 | 1262.5358 | -825.9426 | 436.5932 | 301998.8503 | 691.7168
24 | Training Building | 1959-pre | 2015 | exhaust_fans_occ_control | 0.029521 | 0 | 15.1445 | 0.089874 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.80671 | 0.021964 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 22348.2804 | -9509.6883 | 12838.5921 | 362.0421 | -1074.5948 | -712.5526 | 2754.0487 | -3.865
24 | Training Building | 1959-pre | 2015 | fans_to_variable | 0.029521 | 0 | 15.1442 | 0.090073 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.80731 | 0.021986 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 22414.961 | -9699.4717 | 12715.4893 | 363.1224 | -1096.0403 | -732.9179 | 13814.0536 | -18.848
24 | Training Building | 1959-pre | 2015 | hrv_enabled | 0.029521 | 0 | 12.9243 | 0.10306 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.80707 | 0.018063 | 0.034952 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 536163.8163 | -19829.8031 | 516334.0132 | 8685.8538 | -2240.7677 | 6445.0861 | 464390.6762 | 72.0534
24 | Training Building | 1959-pre | 2015 | infil_reduce | 0.029521 | 0 | 8.3732 | 0.14808 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.48887 | 0.019305 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 1589410.5208 | 51195.3607 | 1640605.8815 | 25748.4504 | 5785.0758 | 31533.5262 | 212660.4373 | 6.7439
24 | Training Building | 1959-pre | 2015 | infil_reduce_plus_setback | 0.029521 | 0 | 7.1205 | 0.12749 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.61821 | 0.010882 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 1879307.264 | 27975.1024 | 1907282.3664 | 30444.7777 | 3161.1866 | 33605.9642 | 249407.2017 | 7.4215
24 | Training Building | 1959-pre | 2015 | lights_reduce_70p | 0.029521 | 0 | 15.5812 | 0.057138 | 0.22764 | 0 | 0.7844 | 0.27352 | 0 | 0.80445 | 0.022696 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | -78719.0863 | 76221.1261 | -2497.9602 | -1275.2492 | 8612.9872 | 7337.738 | 292766.9521 | 39.8988
24 | Training Building | 1959-pre | 2015 | load_reduce | 0.029521 | 0 | 4.4 | 0.12749 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.61821 | 0.010882 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 2508916.3343 | 27975.1024 | 2536891.4367 | 40644.4446 | 3161.1866 | 43805.6312 | 249407.2017 | 5.6935
24 | Training Building | 1959-pre | 2015 | occupancy_setback | 0.029521 | 0 | 13.5836 | 0.071633 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.81115 | 0.017775 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 383572.8149 | -5344.7115 | 378228.1034 | 6213.8796 | -603.9524 | 5609.9272 | 36746.7644 | 6.5503
24 | Training Building | 1959-pre | 2015 | payback_less_than_20 | 0.029521 | 0 | 3.2959 | 0.2434 | 0.22764 | 0 | 0.7844 | 0.27352 | 0 | 0.65241 | 0.0040116 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 2764441.7609 | 72625.4996 | 2837067.2605 | 44783.9565 | 8206.6815 | 52990.638 | 730574.159 | 13.7869
24 | Training Building | 1959-pre | 2015 | plug_loads_90_percent | 0.029521 | 0 | 15.152 | 0.086106 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.80627 | 0.022009 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 20604.3246 | -8545.3833 | 12058.9413 | 333.7901 | -965.6283 | -631.8383 | 21247.058 | -33.6274
24 | Training Building | 1959-pre | 2015 | pumps_to_variable | 0.029521 | 0 | 15.1442 | 0.090073 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.80731 | 0.021986 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 22414.961 | -9699.4717 | 12715.4893 | 363.1224 | -1096.0403 | -732.9179 | 15178.2866 | -20.7094
24 | Training Building | 1959-pre | 2015 | pump_fan_eff_ | 0.029521 | 0 | 15.1442 | 0.090073 | 0.22764 | 0 | 1.1206 | 0.27352 | 0 | 0.80731 | 0.017199 | 0 | 0 | 3527191.5963 | 13105.3147 | 52682.8524 | 0 | 259331.3535 | 63300.4655 | 0 | 184802.8904 | 5160.0574 | 0 | 4105574.5302 | 22414.961 | -8591.5469 | 13823.4142 | 363.1224 | -970.8448 | -607.7224 | 36586.0451 | -60.2019
25 | Training Building | 1980-2004 | 2015 | air_temp_reset_enabled | 0.020875 | 0 | 6.6966 | 0.19222 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.3456 | 0.0095131 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | -92448.2146 | -40520.6738 | -132968.8884 | -1497.6611 | -4578.8361 | -6076.4972 | 18705.846 | -3.0784
25 | Training Building | 1980-2004 | 2015 | baseline | 0.020875 | 0 | 6.2971 | 0.038742 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.31796 | 0.015547 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | Training Building | 1980-2004 | 2015 | boiler_eff_upgrade | 0.020875 | 0 | 6.2792 | 0.077123 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.3456 | 0.014654 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 4138.3896 | -15073.7487 | -10935.3591 | 67.0419 | -1703.3336 | -1636.2917 | 86900.4849 | -53.1082
25 | Training Building | 1980-2004 | 2015 | boiler_reset | 0.020875 | 0 | 4.0299 | 0.077123 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.3456 | 0.014654 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 524686.8698 | -15073.7487 | 509613.1211 | 8499.9273 | -1703.3336 | 6796.5937 | 1235.8691 | 0.18184
25 | Training Building | 1980-2004 | 2015 | cooling_cop_3_0 | 0.020875 | 0 | 6.2792 | 0.066106 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.3456 | 0.014654 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 4138.3896 | -12523.9784 | -8385.5888 | 67.0419 | -1415.2096 | -1348.1676 | 26279.8653 | -19.493
25 | Training Building | 1980-2004 | 2015 | dcv_enabled | 0.020875 | 0 | 4.7111 | 0.081684 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.34311 | 0.0084473 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 367050.858 | -14116.2247 | 352934.6333 | 5946.2239 | -1595.1334 | 4351.0905 | 45375.7071 | 10.4286
25 | Training Building | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.020875 | 0 | 5.9722 | 0.1232 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.3456 | 0.0055323 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 75191.0211 | -23626.1787 | 51564.8424 | 1218.0945 | -2669.7582 | -1451.6637 | 18705.846 | -12.8858
25 | Training Building | 1980-2004 | 2015 | economizers_enabled | 0.020875 | 0 | 6.2718 | 0.053866 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.3456 | 0.014638 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 5853.9534 | -9687.6763 | -3833.7229 | 94.834 | -1094.7074 | -999.8734 | 7309.2957 | -7.3102
25 | Training Building | 1980-2004 | 2015 | elec_reduce | 0.020875 | 0 | 4.9751 | 0.045669 | 0.16097 | 0 | 0.55466 | 0.19341 | 0 | 0.32609 | 0.0098579 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 305943.4187 | 52845.168 | 358788.5867 | 4956.2834 | 5971.504 | 10927.7874 | 282538.9193 | 25.8551
25 | Training Building | 1980-2004 | 2015 | envelope_ecm_roof | 0.020875 | 0 | 5.7552 | 0.079505 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.3205 | 0.014371 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 125417.5061 | -9749.335 | 115668.1711 | 2031.7636 | -1101.6749 | 930.0887 | 675538.5134 | 726.3162
25 | Training Building | 1980-2004 | 2015 | envelope_ecm_wall | 0.020875 | 0 | 6.1188 | 0.07949 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.3388 | 0.014575 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 41256.9517 | -14029.1771 | 27227.7746 | 668.3626 | -1585.297 | -916.9344 | 588207.9955 | -641.4941
25 | Training Building | 1980-2004 | 2015 | envelope_ecm_windows | 0.020875 | 0 | 6.1604 | 0.078941 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.34271 | 0.014465 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 31638.1881 | -14779.9629 | 16858.2252 | 512.5386 | -1670.1358 | -1157.5972 | 213547.4891 | -184.4748
25 | Training Building | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.020875 | 0 | 6.2755 | 0.076982 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.34518 | 0.014638 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 4997.985 | -14939.5502 | -9941.5652 | 80.9674 | -1688.1692 | -1607.2018 | 1947.4252 | -1.2117
25 | Training Building | 1980-2004 | 2015 | fans_to_variable | 0.020875 | 0 | 6.3302 | 0.076716 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.31644 | 0.0099049 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | -7649.3109 | -7130.652 | -14779.9629 | -123.9188 | -805.7637 | -929.6825 | 9768.1049 | -10.5069
25 | Training Building | 1980-2004 | 2015 | hrv_enabled | 0.020875 | 0 | 4.7533 | 0.092842 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.34543 | 0.0089332 | 0.024699 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 357276.1341 | -23063.9961 | 334212.138 | 5787.8734 | -2606.2316 | 3181.6418 | 328376.955 | 103.2099
25 | Training Building | 1980-2004 | 2015 | infil_reduce | 0.020875 | 0 | 4.8762 | 0.091416 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.31418 | 0.010877 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 328829.6926 | -10235.351 | 318594.3416 | 5327.041 | -1156.5947 | 4170.4464 | 134050.5666 | 32.143
25 | Training Building | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.020875 | 0 | 4.1189 | 0.08532 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.37477 | 0.0069428 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 504096.4773 | -21936.0038 | 482160.4734 | 8166.3629 | -2478.7684 | 5687.5945 | 160034.7028 | 28.1375
25 | Training Building | 1980-2004 | 2015 | lights_reduce_70p | 0.020875 | 0 | 6.512 | 0.044776 | 0.16097 | 0 | 0.55466 | 0.19341 | 0 | 0.32895 | 0.015735 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | -49729.5881 | 51031.6756 | 1302.0875 | -805.6193 | 5766.5793 | 4960.96 | 207019.4886 | 41.7297
25 | Training Building | 1980-2004 | 2015 | load_reduce | 0.020875 | 0 | 2.5606 | 0.08532 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.37477 | 0.0069428 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 864716.6913 | -21936.0038 | 842780.6874 | 14008.4104 | -2478.7684 | 11529.642 | 160034.7028 | 13.8803
25 | Training Building | 1980-2004 | 2015 | occupancy_setback | 0.020875 | 0 | 5.3779 | 0.065604 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.44362 | 0.0082123 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 212726.2833 | -33600.3868 | 179125.8965 | 3446.1658 | -3796.8437 | -350.6779 | 25984.1362 | -74.0969
25 | Training Building | 1980-2004 | 2015 | payback_less_than_20 | 0.020875 | 0 | 1.7622 | 0.13257 | 0.16097 | 0 | 0.55466 | 0.19341 | 0 | 0.38226 | 0.0024292 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 1049500.684 | 21453.6149 | 1070954.2989 | 17001.9111 | 2424.2585 | 19426.1696 | 500274.4074 | 25.7526
25 | Training Building | 1980-2004 | 2015 | plug_loads_90_percent | 0.020875 | 0 | 6.2704 | 0.072907 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.34155 | 0.014748 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 6173.1281 | -13180.4626 | -7007.3346 | 100.0047 | -1489.3923 | -1389.3876 | 15024.0833 | -10.8135
25 | Training Building | 1980-2004 | 2015 | pumps_to_variable | 0.020875 | 0 | 6.2792 | 0.077123 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.3456 | 0.014654 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 4138.3896 | -15073.7487 | -10935.3591 | 67.0419 | -1703.3336 | -1636.2917 | 10732.7726 | -6.5592
25 | Training Building | 1980-2004 | 2015 | pump_fan_eff_ | 0.020875 | 0 | 6.2792 | 0.077123 | 0.16097 | 0 | 0.79237 | 0.19341 | 0 | 0.3456 | 0.011456 | 0 | 0 | 1457318.8507 | 8965.9063 | 37252.7605 | 0 | 183376.7226 | 44760.619 | 0 | 73584.2669 | 3597.9689 | 0 | 1808857.0949 | 4138.3896 | -14333.8438 | -10195.4542 | 67.0419 | -1619.7243 | -1552.6824 | 25870.4894 | -16.6618
26 | Training Building | 2005-2014 | 2015 | air_temp_reset_enabled | 0.008076 | 0 | 1.9008 | 0.059965 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10914 | 0.0029892 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | -50174.0397 | -17454.3413 | -67628.381 | -812.8194 | -1972.3406 | -2785.16 | 7236.8508 | -2.5984
26 | Training Building | 2005-2014 | 2015 | baseline | 0.008076 | 0 | 1.684 | 0.014267 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.076657 | 0.005754 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | Training Building | 2005-2014 | 2015 | boiler_eff_upgrade | 0.008076 | 0 | 1.6984 | 0.030844 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10914 | 0.0036986 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | -3341.007 | -10878.97 | -14219.977 | -54.1243 | -1229.3236 | -1283.4479 | 16942.2702 | -13.2006
26 | Training Building | 2005-2014 | 2015 | boiler_reset | 0.008076 | 0 | 1.0706 | 0.030844 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10914 | 0.0036986 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | 141966.84 | -10878.97 | 131087.87 | 2299.8628 | -1229.3236 | 1070.5392 | 478.1286 | 0.44662
26 | Training Building | 2005-2014 | 2015 | cooling_cop_3_0 | 0.008076 | 0 | 1.6984 | 0.030844 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10914 | 0.0036986 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | -3341.007 | -10878.97 | -14219.977 | -54.1243 | -1229.3236 | -1283.4479 | 10167.0603 | -7.9217
26 | Training Building | 2005-2014 | 2015 | dcv_enabled | 0.008076 | 0 | 1.0704 | 0.033554 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10824 | 0.001819 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | 142011.7422 | -10862.1317 | 131149.6106 | 2300.5902 | -1227.4209 | 1073.1693 | 17554.7913 | 16.3579
26 | Training Building | 2005-2014 | 2015 | ecm_cold_deck_reset_control | 0.008076 | 0 | 1.6208 | 0.042618 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10914 | 0.001534 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | 14632.5163 | -13103.0339 | 1529.4824 | 237.0468 | -1480.6428 | -1243.5961 | 7236.8508 | -5.8193
26 | Training Building | 2005-2014 | 2015 | economizers_enabled | 0.008076 | 0 | 1.6951 | 0.019275 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10914 | 0.0036986 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | -2570.653 | -8201.6741 | -10772.3272 | -41.6446 | -926.7892 | -968.4338 | 2827.7942 | -2.92
26 | Training Building | 2005-2014 | 2015 | elec_reduce | 0.008076 | 0 | 1.1946 | 0.020294 | 0.062275 | 0 | 0.21458 | 0.074826 | 0 | 0.088159 | 0.003256 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | 113268.698 | 17805.14 | 131073.838 | 1834.9529 | 2011.9808 | 3846.9337 | 109307.6465 | 28.4142
26 | Training Building | 2005-2014 | 2015 | envelope_ecm_roof | 0.008076 | 0 | 1.5816 | 0.031238 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10519 | 0.0034197 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | 23690.1394 | -9990.7476 | 13699.3917 | 383.7803 | -1128.9545 | -745.1742 | 0 | 0
26 | Training Building | 2005-2014 | 2015 | envelope_ecm_wall | 0.008076 | 0 | 1.6634 | 0.031062 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10874 | 0.0035834 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | 4768.0562 | -10810.2134 | -6042.1572 | 77.2425 | -1221.5541 | -1144.3116 | 0 | 0
26 | Training Building | 2005-2014 | 2015 | envelope_ecm_windows | 0.008076 | 0 | 1.6495 | 0.031395 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10904 | 0.0035227 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | 7985.5821 | -10942.1138 | -2956.5316 | 129.3664 | -1236.4589 | -1107.0924 | 82616.4887 | -74.6247
26 | Training Building | 2005-2014 | 2015 | exhaust_fans_occ_control | 0.008076 | 0 | 1.6977 | 0.030941 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10898 | 0.0036986 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | -3171.2205 | -10863.5349 | -14034.7553 | -51.3738 | -1227.5794 | -1278.9532 | 753.4129 | -0.58909
26 | Training Building | 2005-2014 | 2015 | fans_to_variable | 0.008076 | 0 | 1.705 | 0.030668 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10281 | 0.0023707 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | -4849.4415 | -9064.639 | -13914.0805 | -78.561 | -1024.3042 | -1102.8652 | 3779.0495 | -3.4266
26 | Training Building | 2005-2014 | 2015 | hrv_enabled | 0.008076 | 0 | 1.1076 | 0.03966 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10908 | 0.0019463 | 0.0095496 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | 133394.7224 | -14709.692 | 118685.0303 | 2160.9945 | -1662.1952 | 498.7993 | 127041.3018 | 254.6942
26 | Training Building | 2005-2014 | 2015 | lights_reduce_70p | 0.008076 | 0 | 1.7786 | 0.018996 | 0.062275 | 0 | 0.21458 | 0.074826 | 0 | 0.090348 | 0.0052508 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | -21901.0659 | 17137.2192 | -4763.8467 | -354.7973 | 1936.5058 | 1581.7085 | 80090.9592 | 50.6357
26 | Training Building | 2005-2014 | 2015 | load_reduce | 0.008076 | 0 | 0.87307 | 0.028388 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.12659 | 0.0023828 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | 187671.704 | -14043.1745 | 173628.5295 | 3040.2816 | -1586.8787 | 1453.4029 | 10052.6497 | 6.9166
26 | Training Building | 2005-2014 | 2015 | occupancy_setback | 0.008076 | 0 | 1.3987 | 0.028388 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.12659 | 0.0023828 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | 66037.158 | -14043.1745 | 51993.9835 | 1069.802 | -1586.8787 | -517.0768 | 10052.6497 | -19.4413
26 | Training Building | 2005-2014 | 2015 | payback_less_than_20 | 0.008076 | 0 | 0.57992 | 0.040963 | 0.062275 | 0 | 0.21458 | 0.074826 | 0 | 0.12254 | 0.0008731 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | 255516.177 | 5615.586 | 261131.763 | 4139.3621 | 634.5612 | 4773.9233 | 141683.3696 | 29.6786
26 | Training Building | 2005-2014 | 2015 | plug_loads_90_percent | 0.008076 | 0 | 1.6961 | 0.029485 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10669 | 0.0038016 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | -2796.5674 | -10021.6179 | -12818.1853 | -45.3044 | -1132.4428 | -1177.7472 | 5812.4636 | -4.9352
26 | Training Building | 2005-2014 | 2015 | pumps_to_variable | 0.008076 | 0 | 1.6984 | 0.030844 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10914 | 0.0036986 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | -3341.007 | -10878.97 | -14219.977 | -54.1243 | -1229.3236 | -1283.4479 | 4152.2567 | -3.2352
26 | Training Building | 2005-2014 | 2015 | pump_fan_eff_ | 0.008076 | 0 | 1.6984 | 0.030844 | 0.062275 | 0 | 0.30655 | 0.074826 | 0 | 0.10914 | 0.0028922 | 0 | 0 | 389724.7524 | 3301.7176 | 14412.2147 | 0 | 70944.1305 | 17316.8282 | 0 | 17740.593 | 1331.632 | 0 | 514771.8684 | -3341.007 | -10692.3451 | -14033.3521 | -54.1243 | -1208.235 | -1262.3593 | 10008.6824 | -7.9286
27 | Vehicle Garage | 1959-pre | 2015 | air_temp_reset_enabled | 0.02256 | 0 | 2.6619 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.18869 | 0.17157 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 5788.7371 | -2223.5466 | 3565.1904 | 93.7775 | -251.2608 | -157.4832 | 8505.8774 | -54.0113
27 | Vehicle Garage | 1959-pre | 2015 | baseline | 0.02256 | 0 | 2.7353 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.16133 | 0.17072 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | Vehicle Garage | 1959-pre | 2015 | boiler_eff_upgrade | 0.02256 | 0 | 2.6589 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.16117 | 0.17146 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 6023.005 | -46.3739 | 5976.6312 | 97.5727 | -5.2402 | 92.3324 | 61446.8568 | 665.4959
27 | Vehicle Garage | 1959-pre | 2015 | boiler_reset | 0.02256 | 0 | 1.6435 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.16117 | 0.17146 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 86045.8983 | -46.3739 | 85999.5245 | 1393.9436 | -5.2402 | 1388.7033 | 873.8762 | 0.62927
27 | Vehicle Garage | 1959-pre | 2015 | dcv_enabled | 0.02256 | 0 | 2.3044 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.1608 | 0.17146 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 33959.2581 | -16.7905 | 33942.4676 | 550.14 | -1.8973 | 548.2427 | 7989.9582 | 14.5738
27 | Vehicle Garage | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.02256 | 0 | 2.6589 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.16117 | 0.17146 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 6023.005 | -46.3739 | 5976.6312 | 97.5727 | -5.2402 | 92.3324 | 8505.8774 | 92.1223
27 | Vehicle Garage | 1959-pre | 2015 | economizers_enabled | 0.02256 | 0 | 2.6633 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.16119 | 0.16829 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 5676.0006 | 202.286 | 5878.2866 | 91.9512 | 22.8583 | 114.8095 | 3308.3016 | 28.8156
27 | Vehicle Garage | 1959-pre | 2015 | elec_reduce | 0.02256 | 0 | 2.4101 | 0 | 0.016891 | 0 | 0.16337 | 0.050329 | 0 | 0.16036 | 0.13448 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 25627.1547 | 8449.6372 | 34076.7919 | 415.1599 | 954.809 | 1369.9689 | 44471.6322 | 32.4618
27 | Vehicle Garage | 1959-pre | 2015 | envelope_ecm_roof | 0.02256 | 0 | 2.6062 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.15714 | 0.1674 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 10179.0624 | 591.6665 | 10770.7289 | 164.9008 | 66.8583 | 231.7591 | 325986.4743 | 1406.5745
27 | Vehicle Garage | 1959-pre | 2015 | envelope_ecm_wall | 0.02256 | 0 | 2.5064 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.15142 | 0.16028 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 18041.0308 | 1603.0964 | 19644.1272 | 292.2647 | 181.1499 | 473.4146 | 347237.9205 | 733.4753
27 | Vehicle Garage | 1959-pre | 2015 | envelope_ecm_windows | 0.02256 | 0 | 2.6562 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.16103 | 0.17131 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 6234.086 | -23.1869 | 6210.8991 | 100.9922 | -2.6201 | 98.3721 | 4076.2457 | 41.437
27 | Vehicle Garage | 1959-pre | 2015 | exhaust_fans_occ_control | 0.02256 | 0 | 2.6589 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.15968 | 0.17146 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 6023.005 | 71.1599 | 6094.1649 | 97.5727 | 8.0411 | 105.6137 | 688.5069 | 6.5191
27 | Vehicle Garage | 1959-pre | 2015 | fans_to_variable | 0.02256 | 0 | 2.6615 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.15967 | 0.17146 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 5820.719 | 71.9594 | 5892.6785 | 94.2956 | 8.1314 | 102.4271 | 2848.9929 | 27.8148
27 | Vehicle Garage | 1959-pre | 2015 | hrv_enabled | 0.02256 | 0 | 2.3665 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.16063 | 0.17149 | 0.047986 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 29067.6154 | -3787.4651 | 25280.1503 | 470.8954 | -427.9836 | 42.9118 | 149644.0821 | 3487.2468
27 | Vehicle Garage | 1959-pre | 2015 | infil_reduce | 0.02256 | 0 | 1.6758 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.10093 | 0.11029 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 83499.3337 | 9522.6324 | 93021.9661 | 1352.6892 | 1076.0575 | 2428.7467 | 61406.6773 | 25.2833
27 | Vehicle Garage | 1959-pre | 2015 | infil_reduce_plus_setback | 0.02256 | 0 | 1.5294 | 0 | 0.016902 | 0 | 0.23338 | 0.050329 | 0 | 0.11918 | 0.0015826 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 95044.0263 | 16650.6145 | 111694.6408 | 1539.7132 | 1881.5194 | 3421.2327 | 65888.3581 | 19.2587
27 | Vehicle Garage | 1959-pre | 2015 | lights_reduce_70p | 0.02256 | 0 | 2.7639 | 0 | 0.016891 | 0 | 0.16337 | 0.050329 | 0 | 0.16176 | 0.17189 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | -2253.9295 | 5391.361 | 3137.4315 | -36.5137 | 609.2238 | 572.7101 | 23887.6814 | 41.7099
27 | Vehicle Garage | 1959-pre | 2015 | load_reduce | 0.02256 | 0 | 0.96133 | 0 | 0.016902 | 0 | 0.23338 | 0.050329 | 0 | 0.11918 | 0.0015826 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 139810.7925 | 16650.6145 | 156461.407 | 2264.9348 | 1881.5194 | 4146.4543 | 66762.2343 | 16.101
27 | Vehicle Garage | 1959-pre | 2015 | occupancy_setback | 0.02256 | 0 | 2.2537 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.18774 | 0.19443 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 37959.4034 | -3950.5732 | 34008.8302 | 614.9423 | -446.4148 | 168.5276 | 4481.6807 | 26.5932
27 | Vehicle Garage | 1959-pre | 2015 | payback_less_than_20 | 0.02256 | 0 | 0.73846 | 0 | 0.016891 | 0 | 0.16337 | 0.050329 | 0 | 0.11752 | 0.095921 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 157376.0914 | 14865.2209 | 172241.3123 | 2549.4927 | 1679.77 | 4229.2626 | 122461.7933 | 28.9558
27 | Vehicle Garage | 1959-pre | 2015 | plug_loads_90_percent | 0.02256 | 0 | 2.6612 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.16147 | 0.17152 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 5843.906 | -74.3581 | 5769.5479 | 94.6713 | -8.4025 | 86.2688 | 2591.4847 | 30.0396
27 | Vehicle Garage | 1959-pre | 2015 | pump_fan_eff_ | 0.02256 | 0 | 2.6589 | 0 | 0.016891 | 0 | 0.23338 | 0.050329 | 0 | 0.16117 | 0.1341 | 0 | 0 | 215575.2861 | 0 | 1331.2496 | 0 | 18392.8325 | 3966.5642 | 0 | 12714.4332 | 13454.8159 | 0 | 265435.1815 | 6023.005 | 2898.3663 | 8921.3713 | 97.5727 | 327.5154 | 425.0881 | 3058.1013 | 7.194
28 | Vehicle Garage | 1980-2004 | 2015 | air_temp_reset_enabled | 0.051036 | 0 | 4.2363 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.28851 | 0.27017 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | -926.8728 | -9716.3656 | -10643.2384 | -15.0153 | -1097.9493 | -1112.9647 | 56024.9329 | -50.3385
28 | Vehicle Garage | 1980-2004 | 2015 | baseline | 0.051036 | 0 | 4.2322 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.2483 | 0.26804 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | Vehicle Garage | 1980-2004 | 2015 | boiler_eff_upgrade | 0.051036 | 0 | 4.1668 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.24894 | 0.2698 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 15003.7539 | -552.9639 | 14450.79 | 243.0608 | -62.4849 | 180.5759 | 203957.198 | 1129.4819
28 | Vehicle Garage | 1980-2004 | 2015 | boiler_reset | 0.051036 | 0 | 2.5885 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.24894 | 0.2698 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 377184.5757 | -552.9639 | 376631.6118 | 6110.3901 | -62.4849 | 6047.9052 | 5755.8857 | 0.95172
28 | Vehicle Garage | 1980-2004 | 2015 | dcv_enabled | 0.051036 | 0 | 3.3813 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.24697 | 0.2698 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 195264.7189 | -100.0601 | 195164.6588 | 3163.2884 | -11.3068 | 3151.9817 | 52626.7716 | 16.6964
28 | Vehicle Garage | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.051036 | 0 | 4.1668 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.24894 | 0.2698 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 15003.7539 | -552.9639 | 14450.79 | 243.0608 | -62.4849 | 180.5759 | 56024.9329 | 310.257
28 | Vehicle Garage | 1980-2004 | 2015 | economizers_enabled | 0.051036 | 0 | 4.1782 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.24896 | 0.26182 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 12402.1904 | 1274.4502 | 13676.6405 | 200.9155 | 144.0129 | 344.9284 | 21790.506 | 63.174
28 | Vehicle Garage | 1980-2004 | 2015 | elec_reduce | 0.051036 | 0 | 3.6077 | 0 | 0.038212 | 0 | 0.36957 | 0.11386 | 0 | 0.24612 | 0.21206 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 143317.7103 | 49687.7562 | 193005.4665 | 2321.7469 | 5614.7164 | 7936.4634 | 268378.3533 | 33.8159
28 | Vehicle Garage | 1980-2004 | 2015 | envelope_ecm_roof | 0.051036 | 0 | 4.0561 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.24118 | 0.26166 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 40403.229 | 3096.5979 | 43499.8269 | 654.5323 | 349.9156 | 1004.4479 | 2147147.1317 | 2137.6392
28 | Vehicle Garage | 1980-2004 | 2015 | envelope_ecm_wall | 0.051036 | 0 | 3.964 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.23554 | 0.2547 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 61547.5153 | 5987.8091 | 67535.3244 | 997.0697 | 676.6224 | 1673.6922 | 2287122.2084 | 1366.5131
28 | Vehicle Garage | 1980-2004 | 2015 | envelope_ecm_windows | 0.051036 | 0 | 4.1621 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.24873 | 0.26955 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 16083.3501 | -447.6374 | 15635.7126 | 260.5503 | -50.583 | 209.9672 | 26848.6579 | 127.8707
28 | Vehicle Garage | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.051036 | 0 | 4.1668 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.24557 | 0.2698 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 15003.7539 | 221.1856 | 15224.9395 | 243.0608 | 24.994 | 268.0548 | 4534.929 | 16.9179
28 | Vehicle Garage | 1980-2004 | 2015 | fans_to_variable | 0.051036 | 0 | 4.1707 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.2466 | 0.2698 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 14119.0116 | -15.7989 | 14103.2127 | 228.728 | -1.7853 | 226.9427 | 18765.217 | 82.687
28 | Vehicle Garage | 1980-2004 | 2015 | hrv_enabled | 0.051036 | 0 | 3.5154 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.24722 | 0.27017 | 0.10855 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 164488.3282 | -25151.9579 | 139336.3702 | 2664.7109 | -2842.1712 | -177.4603 | 985647.8323 | -5554.1868
28 | Vehicle Garage | 1980-2004 | 2015 | infil_reduce | 0.051036 | 0 | 3.448 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.20522 | 0.22473 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 179955.5184 | 19822.4393 | 199777.9576 | 2915.2794 | 2239.9356 | 5155.215 | 373740.1218 | 72.4975
28 | Vehicle Garage | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.051036 | 0 | 3.124 | 0 | 0.038235 | 0 | 0.52795 | 0.11386 | 0 | 0.24327 | 0.0032819 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 254305.4644 | 61900.3589 | 316205.8233 | 4119.7485 | 6994.7406 | 11114.4891 | 403259.2237 | 36.2823
28 | Vehicle Garage | 1980-2004 | 2015 | lights_reduce_70p | 0.051036 | 0 | 4.3952 | 0 | 0.038212 | 0 | 0.36957 | 0.11386 | 0 | 0.25068 | 0.271 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | -37406.6912 | 35115.8408 | -2290.8504 | -605.9884 | 3968.09 | 3362.1016 | 157338.9409 | 46.7978
28 | Vehicle Garage | 1980-2004 | 2015 | load_reduce | 0.051036 | 0 | 1.9697 | 0 | 0.038235 | 0 | 0.52795 | 0.11386 | 0 | 0.24327 | 0.0032819 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 519164.6398 | 61900.3589 | 581064.9987 | 8410.4672 | 6994.7406 | 15405.2077 | 409015.0474 | 26.5504
28 | Vehicle Garage | 1980-2004 | 2015 | occupancy_setback | 0.051036 | 0 | 3.4897 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.29278 | 0.3073 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 170381.3434 | -19216.8121 | 151164.5314 | 2760.1778 | -2171.4998 | 588.678 | 29519.1019 | 50.1447
28 | Vehicle Garage | 1980-2004 | 2015 | payback_less_than_20 | 0.051036 | 0 | 1.4872 | 0 | 0.038212 | 0 | 0.36957 | 0.11386 | 0 | 0.23923 | 0.19588 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 629889.0779 | 54980.4106 | 684869.4885 | 10204.2031 | 6212.7864 | 16416.9895 | 775886.614 | 47.2612
28 | Vehicle Garage | 1980-2004 | 2015 | plug_loads_90_percent | 0.051036 | 0 | 4.1727 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.24889 | 0.26999 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 13660.8415 | -584.5618 | 13076.2797 | 221.3056 | -66.0555 | 155.2501 | 17069.1099 | 109.9459
28 | Vehicle Garage | 1980-2004 | 2015 | pump_fan_eff_ | 0.051036 | 0 | 4.1668 | 0 | 0.038212 | 0 | 0.52795 | 0.11386 | 0 | 0.24894 | 0.211 | 0 | 0 | 971157.3318 | 0 | 8768.4276 | 0 | 121146.491 | 26126.2277 | 0 | 56976.347 | 61505.3847 | 0 | 1245680.2097 | 15003.7539 | 12939.3553 | 27943.1092 | 243.0608 | 1462.1471 | 1705.208 | 20142.5334 | 11.8124
[17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## base_energy_ecm
year | measure_id | Electricity-Heating KWh/m2 | Natural Gas-Heating KWh/m2 | Electricity-Cooling KWh/m2 | Electricity-Water Systems KWh/m2 | Natural Gas-Water Systems KWh/m2 | Electricity-Interior Lighting KWh/m2 | Electricity-Interior Equipment KWh/m2 | District Heating-Interior Equipment KWh/m2 | Electricity-Fans KWh/m2 | Electricity-Pumps KWh/m2 | Electricity-Heat Recovery KWh/m2 | Savings Electricity-Heating KWh/m2 | Savings Natural Gas-Heating KWh/m2 | Savings Electricity-Cooling KWh/m2 | Savings Electricity-Water Systems KWh/m2 | Savings Natural Gas-Water Systems KWh/m2 | Savings Electricity-Interior Lighting KWh/m2 | Savings Electricity-Interior Equipment KWh/m2 | Savings District Heating-Interior Equipment KWh/m2 | Savings Electricity-Fans KWh/m2 | Savings Electricity-Pumps KWh/m2 | Savings Electricity-Heat Recovery KWh/m2 | Electrical Energy Savings Intensity KWh/M2 | Natural Gas Energy Savings Intensity Kwh/M2 | Electrical Cost Savings Intensity $/M2 | Gas Cost Savings Intensity $/M2 | % Energy Savings | Net Cost Savings Intensity $/M2 | Base Total Elec Savings $ | Base Total Gas Savings $ | Base Total Energy Cost Savings $ | GHG Savings (tonnes) at bldg and des level | GHG Savings % | Capital Cost $ | Base ECM Payback (yrs) | 2015 EUI kWh/m2 | 2018 EUI kWh/m2 | 2020 EUI kWh/m2 | 2023 EUI kWh/m2 | 2025 EUI kWh/m2 | 2028 EUI kWh/m2 | Elec Savings 2023 kWh | Gas Savings 2023 m3 | Gas+Elec Savings 2023 kWh | 2015 Baseline Gas $/m2 | 2015 Baseline Elec $/m2
2015 | air_temp_reset_enabled | 0.67421 | 331.9765 | 3.7336 | 3.0948 | 12.9795 | 40.1063 | 6.5602 | 0.34782 | 15.4484 | 8.9454 | 0 | 0.175 | 12.5698 | -0.60861 | -0.0001839 | 0.00068956 | 1.7758 | 0.16451 | 0 | 0.17199 | -0.48697 | 0 | 1.1915 | 12.5705 | 0.13464 | 0.20364 | 3.1447 | 0.33829 | 27312.8509 | 41309.0897 | 68621.9406 | 666.7247 |  | 631774.464 | 9.2066 | 423.8667 | 424.8851 | 410.795 | 371.5306 | 360.9388 | 360.9388 | 241706.6454 | 242244.6619 | 2791650.455
2015 | baseline | 0.84922 | 344.5463 | 3.1249 | 3.0946 | 12.9802 | 41.8821 | 6.7247 | 0.34782 | 15.6204 | 8.4584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | #DIV/0! | 437.6287 | 438.6801 | 424.1326 | 383.5934 | 372.6577 | 372.6577 | 0 | 0 | 0
2015 | boiler_eff_upgrade | 0.83324 | 330.0681 | 3.7322 | 3.0222 | 12.9802 | 39.7721 | 6.4802 | 0.34782 | 15.0951 | 8.5369 | 0 | 0.015977 | 14.4783 | -0.60727 | 0.072338 | 4.235e-05 | 2.11 | 0.24453 | 0 | 0.52524 | -0.078513 | 0 | 2.2823 | 14.4783 | 0.2579 | 0.23455 | 3.8299 | 0.49244 | 52314.7261 | 47578.6332 | 99893.3593 | 928.4916 |  | 3284997.9457 | 32.885 | 420.8682 | 421.8793 | 407.889 | 368.9023 | 358.3854 | 358.3854 | 462962.1781 | 279010.5032 | 3399914.8435
2015 | boiler_reset | 0.85001 | 252.7119 | 3.7661 | 3.0946 | 12.9802 | 40.1063 | 6.5602 | 0.34782 | 15.2685 | 4.636 | 0 | -0.0007958 | 91.8344 | -0.64113 | 1.2157e-05 | 4.235e-05 | 1.7758 | 0.16451 | 0 | 0.35189 | 3.8224 | 0 | 5.4727 | 91.8345 | 0.61842 | 1.4877 | 22.2351 | 2.1061 | 125447.4772 | 301786.6252 | 427234.1024 | 4300.3905 |  | 52574.359 | 0.12306 | 340.3215 | 341.1391 | 329.8263 | 298.301 | 289.7969 | 289.7969 | 1110154.6655 | 1769736.3826 | 19738958.6929
2015 | cooling_cop_3_0 | 0.85001 | 324.2446 | 2.8976 | 3.0395 | 12.9802 | 39.345 | 6.3961 | 0.34782 | 14.8583 | 8.0958 | 0 | -0.0007958 | 20.3017 | 0.22731 | 0.055116 | 4.235e-05 | 2.5371 | 0.32869 | 0 | 0.76201 | 0.36258 | 0 | 4.272 | 20.3018 | 0.48274 | 0.32889 | 5.6152 | 0.81163 | 97924.9065 | 66715.7694 | 164640.6758 | 1491.1032 |  | 792658.5621 | 4.8145 | 413.0549 | 414.0473 | 400.3167 | 362.0537 | 351.7321 | 351.7321 | 866592.0925 | 391234.4501 | 4984849.462
2015 | dcv_enabled | 0.82564 | 284.7384 | 3.9971 | 3.0946 | 12.9801 | 41.8821 | 6.7247 | 0.34782 | 15.7269 | 8.4197 | 0 | 0.02358 | 59.808 | -0.87211 | 2.8305e-05 | 7.2481e-05 | -4.2748e-10 | -1.5987e-14 | 0 | -0.10654 | 0.03867 | 0 | -0.91638 | 59.808 | -0.10355 | 0.96889 | 13.457 | 0.86534 | -21005.4332 | 196541.2949 | 175535.8617 | 2009.9367 |  | 1624430.1321 | 9.2541 | 378.7371 | 379.647 | 367.0572 | 331.9732 | 322.5092 | 322.5092 | -185888.789 | 1152556.9761 | 11946289.9069
2015 | ecm_cold_deck_reset_control | 0.99155 | 324.2737 | 2.2204 | 3.0951 | 12.9801 | 41.8821 | 6.7247 | 0.34782 | 15.7979 | 8.47 | 0 | -0.14233 | 20.2726 | 0.90458 | -0.00057058 | 0.00010882 | -4.2748e-10 | -1.5987e-14 | 0 | -0.17759 | -0.011633 | 0 | 0.57246 | 20.2728 | 0.064688 | 0.32842 | 4.7632 | 0.39311 | 13122.0105 | 66620.3881 | 79742.3986 | 837.142 |  | 631774.464 | 7.9227 | 416.7835 | 417.7848 | 403.9303 | 365.322 | 354.9072 | 354.9072 | 116123.9866 | 390675.1153 | 4228493.6216
2015 | economizers_enabled | 0.85024 | 331.1065 | 3.635 | 3.0946 | 12.9802 | 40.1063 | 6.5602 | 0.34782 | 15.2688 | 8.5108 | 0 | -0.0010218 | 13.4398 | -0.51008 | 1.2157e-05 | 4.235e-05 | 1.7758 | 0.16451 | 0 | 0.35156 | -0.052357 | 0 | 1.7284 | 13.4399 | 0.19531 | 0.21773 | 3.466 | 0.41304 | 39619.4878 | 44166.1502 | 83785.638 | 793.0437 |  | 238982.7874 | 2.8523 | 422.4604 | 423.4754 | 409.4321 | 370.2979 | 359.7413 | 359.7413 | 350614.9362 | 258999.0289 | 3076920.5032
2015 | envelope_ecm_roof | 0.81581 | 321.7447 | 3.5356 | 3.0943 | 12.98 | 41.8821 | 6.7247 | 0.34782 | 15.0332 | 8.1075 | 0 | 0.033406 | 22.8016 | -0.41069 | 0.00024652 | 0.00020807 | -4.2748e-10 | -1.5987e-14 | 0 | 0.58711 | 0.3509 | 0 | 0.56098 | 22.8018 | 0.063391 | 0.36939 | 5.3385 | 0.43278 | 12859.0195 | 74931.3946 | 87790.4142 | 926.9487 |  | 28452014.9522 | 324.0902 | 414.2659 | 415.2612 | 401.4903 | 363.1152 | 352.7634 | 352.7634 | 113796.633 | 439412.4994 | 4739191.3632
2015 | envelope_ecm_wall | 0.92097 | 331.6036 | 3.6876 | 3.0943 | 12.98 | 41.8821 | 6.7247 | 0.34782 | 15.22 | 8.1044 | 0 | -0.071753 | 12.9427 | -0.56266 | 0.00031245 | 0.000193 | -4.2748e-10 | -1.5987e-14 | 0 | 0.40037 | 0.35405 | 0 | 0.12032 | 12.9429 | 0.013596 | 0.20967 | 2.985 | 0.22327 | 2758.0531 | 42532.96 | 45291.0131 | 491.1975 |  | 24844217.7396 | 548.5463 | 424.5655 | 425.5855 | 411.4723 | 372.1431 | 361.5339 | 361.5339 | 24407.5497 | 249421.6792 | 2649898.9099
2015 | envelope_ecm_windows | 0.97411 | 339.7773 | 3.795 | 3.0945 | 12.98 | 41.8821 | 6.7247 | 0.34782 | 15.586 | 8.4364 | 0 | -0.12489 | 4.7691 | -0.67009 | 3.8445e-05 | 0.000193 | -4.2748e-10 | -1.5987e-14 | 0 | 0.03433 | 0.021978 | 0 | -0.73863 | 4.7693 | -0.083466 | 0.077262 | 0.92101 | -0.0062038 | -16931.1753 | 15672.7316 | -1258.4438 | 42.8189 |  | 39931393.2437 | -31730.7723 | 433.5981 | 434.6398 | 420.2263 | 380.0604 | 369.2255 | 369.2255 | -149833.4101 | 91907.9937 | 817619.1549
2015 | exhaust_fans_occ_control | 0.016773 | 308.5603 | 3.5642 | 2.9628 | 9.4497 | 36.8227 | 5.8759 | 0 | 10.371 | 7.8153 | 0 | 0.83245 | 35.9861 | -0.43926 | 0.13176 | 3.5306 | 5.0594 | 0.84881 | 0.34782 | 5.2494 | 0.64308 | 0 | 12.3256 | 39.8644 | 1.3928 | 0.6458 | 11.9256 | 2.0386 | 282531.8373 | 131002.5506 | 413534.3879 | 3622.7424 |  | 138358.5111 | 0.33458 | 385.4387 | 386.3647 | 373.5521 | 337.8474 | 328.2159 | 328.2159 | 2500281.7463 | 768224.8338 | 10586858.9438
2015 | fans_to_variable | 0.85007 | 331.2372 | 3.7634 | 3.0946 | 12.9802 | 40.1063 | 6.5602 | 0.34782 | 15.1527 | 8.5315 | 0 | -0.00085221 | 13.3092 | -0.63845 | 1.2157e-05 | 4.235e-05 | 1.7758 | 0.16451 | 0 | 0.46762 | -0.073043 | 0 | 1.6956 | 13.3092 | 0.1916 | 0.21561 | 3.4287 | 0.40721 | 38867.0321 | 43736.7513 | 82603.7834 | 782.5059 |  | 213728.331 | 2.5874 | 422.6239 | 423.6393 | 409.5906 | 370.4412 | 359.8805 | 359.8805 | 343956.0362 | 256480.9488 | 3043755.4974
2015 | hrv_enabled | 0.79646 | 285.2588 | 4.1671 | 3.0946 | 12.9801 | 41.8821 | 6.7247 | 0.34782 | 15.7329 | 8.4089 | 3.0425 | 0.052762 | 59.2875 | -1.0421 | 1.2157e-05 | 0.00012237 | -4.2748e-10 | -1.5987e-14 | 0 | -0.1125 | 0.049522 | -3.0425 | -4.0948 | 59.2877 | -0.46271 | 0.96046 | 12.6118 | 0.49775 | -93862.2763 | 194831.2898 | 100969.0136 | 1430.109 |  | 11751069.8348 | 116.3829 | 382.4359 | 383.3547 | 370.6419 | 335.2153 | 325.6589 | 325.6589 | -830639.613 | 1142529.1688 | 11195983.216
2015 | infil_reduce | 0.58751 | 223.5534 | 3.6623 | 3.0252 | 12.9798 | 41.4722 | 6.6363 | 0.34782 | 12.6352 | 5.8257 | 0 | 0.26171 | 120.9929 | -0.5374 | 0.06939 | 0.00039772 | 0.40991 | 0.088495 | 0 | 2.9851 | 2.6327 | 0 | 5.9099 | 120.9933 | 0.66782 | 1.9601 | 28.9979 | 2.6279 | 135468.5386 | 397608.415 | 533076.9537 | 5436.3154 |  | 3868326.8868 | 7.2566 | 310.7255 | 311.472 | 301.143 | 272.3593 | 264.5948 | 264.5948 | 1198836.6252 | 2331654.2855 | 25742565.9467
2015 | lights_reduce_70p | 0.91226 | 354.2104 | 3.2156 | 3.0947 | 12.9802 | 29.3177 | 6.7247 | 0.34782 | 15.7375 | 8.5933 | 0 | -0.063045 | -9.6641 | -0.090613 | -8.4647e-05 | -1.7912e-05 | 12.5644 | -1.5987e-14 | 0 | -0.11717 | -0.13492 | 0 | 12.1586 | -9.6641 | 1.3739 | -0.15656 | 0.57 | 1.2174 | 278701.97 | -31758.1746 | 246943.7953 | 1794.8503 |  | 4187706.7433 | 16.9581 | 435.1343 | 436.1797 | 421.7151 | 381.4069 | 370.5336 | 370.5336 | 2466389.1146 | -186236.2093 | 506007.9643
2015 | occupancy_setback | 1.1104 | 316.6597 | 3.9725 | 3.0948 | 12.9795 | 41.8821 | 6.7247 | 0.34782 | 15.5442 | 8.3073 | 0 | -0.26123 | 27.8867 | -0.84751 | -0.00021181 | 0.00067132 | -4.2748e-10 | -1.5987e-14 | 0 | 0.076187 | 0.15109 | 0 | -0.88167 | 27.8873 | -0.099629 | 0.45177 | 6.1709 | 0.35215 | -20209.8986 | 91643.4341 | 71433.5355 | 857.005 |  | 929500.2525 | 13.0121 | 410.6231 | 411.6096 | 397.9598 | 359.9222 | 349.6613 | 349.6613 | -178848.6601 | 537415.2 | 5478153.4454
2015 | plug_loads_90_percent | 0.84969 | 342.8585 | 3.738 | 3.0945 | 12.9802 | 41.8821 | 6.7247 | 0.34782 | 15.749 | 8.5388 | 0 | -0.00047526 | 1.6878 | -0.6131 | 3.8445e-05 | 4.235e-05 | -4.2748e-10 | -1.5987e-14 | 0 | -0.12866 | -0.080416 | 0 | -0.82261 | 1.6879 | -0.092955 | 0.027344 | 0.19772 | -0.065611 | -18856.108 | 5546.7168 | -13309.3912 | -83.8875 |  | 537436.1594 | -40.3802 | 436.7635 | 437.8128 | 423.2941 | 382.8349 | 371.9209 | 371.9209 | -166868.2126 | 32527.0429 | 175521.7127
2015 | pump_fan_eff_ | 0.85001 | 331.0703 | 3.7661 | 3.0946 | 12.9802 | 40.1063 | 6.5602 | 0.34782 | 15.2685 | 6.677 | 0 | -0.0007958 | 13.476 | -0.64113 | 1.2157e-05 | 4.235e-05 | 1.7758 | 0.16451 | 0 | 0.35189 | 1.7814 | 0 | 3.4317 | 13.4761 | 0.38778 | 0.21831 | 3.8635 | 0.6061 | 78662.8038 | 44285.0564 | 122947.8603 | 1094.9565 |  | 411358.5382 | 3.3458 | 420.7209 | 421.7317 | 407.7463 | 368.7732 | 358.2601 | 358.2601 | 696131.0075 | 259696.3185 | 3429776.4652
2015 | pumps_to_variable | 0.83324 | 249.0251 | 3.3957 | 0.45089 | 10.9087 | 30.7133 | 4.9355 | 0.34782 | 10.508 | 3.3029 | 0 | 0.015977 | 95.5212 | -0.27075 | 2.6437 | 2.0715 | 11.1689 | 1.7893 | 0 | 5.1124 | 5.1555 | 0 | 25.6149 | 97.5928 | 2.8945 | 1.581 | 28.1535 | 4.4755 | 587152.4449 | 320709.5512 | 907861.9961 | 8064.1968 |  | 106381.596 | 0.11718 | 314.421 | 315.1764 | 304.7246 | 275.5985 | 267.7416 | 267.7416 | 5196039.3354 | 1880704.1581 | 24992925.2099
2015 | load_reduce | 0.68038 | 158.7644 | 3.564 | 3.0936 | 12.9793 | 41.8821 | 6.7247 | 0.34782 | 12.4541 | 3.2831 | 0 | 0.16884 | 185.7819 | -0.43906 | 0.00099689 | 0.00090379 | 0 | 0 | 0 | 3.1662 | 5.1753 | 0 | 8.0723 | 185.7828 | 0.91216 | 3.0097 | 44.2967 | 3.9218 | 185034.3533 | 610519.8503 | 795554.2035 | 8170.4683 |  | 5031050.0514 | 6.324 | 243.7737 | 244.3593 | 236.2559 | 213.6742 | 207.5827 | 207.5827 | 1637472.1527 | 3580208.9986 | 39323882.6638
2015 | infil_reduce_plus_setback | 0.6789 | 204.9685 | 3.5332 | 3.0254 | 12.9793 | 41.4722 | 6.6363 | 0.34782 | 12.3014 | 5.1704 | 0 | 0.17032 | 139.5778 | -0.40827 | 0.069173 | 0.00090379 | 0.40991 | 0.088495 | 0 | 3.3189 | 3.288 | 0 | 6.9365 | 139.5787 | 0.78383 | 2.2612 | 33.4794 | 3.045 | 159000.9782 | 458683.9757 | 617684.9539 | 6292.3416 |  | 4957410.9406 | 8.0258 | 291.1135 | 291.8129 | 282.1358 | 255.1688 | 247.8943 | 247.8943 | 1407088.3025 | 2689813.4376 | 29720913.9615
2015 | elec_reduce | 0.89502 | 296.3263 | 3.3643 | 3.0946 | 12.9802 | 29.3177 | 6.7247 | 0.34782 | 12.2056 | 6.6409 | 0 | -0.0458 | 48.22 | -0.23936 | -6.6107e-05 | -2.8463e-06 | 12.5644 | -1.5987e-14 | 0 | 3.4147 | 1.8175 | 0 | 17.5114 | 48.22 | 1.9788 | 0.78116 | 15.0199 | 2.7599 | 401400.3042 | 158460.5892 | 559860.8934 | 4841.3188 |  | 7107146.5156 | 12.6945 | 371.8974 | 372.7909 | 360.4284 | 325.9781 | 316.6849 | 316.6849 | 3552215.0815 | 929244.1957 | 13333732.9312
2015 | retro-commissioning | 0.75823 | 307.6306 | 2.7901 | 3.0946 | 12.9802 | 41.8821 | 6.7247 | 0.34782 | 13.9467 | 7.5521 | 0 | 0.090988 | 36.9157 | 0.33482 | 0 | 0 | 0 | 0 | 0 | 1.6736 | 0.90626 | 0 | 3.0057 | 36.9157 | 0.33964 | 0.59803 | 9.1222 | 0.93767 | 68896.8196 | 121312.3871 | 190209.2067 | 1870.8715 |  | 1694143.6657 | 40.9216 | 397.7074 | 398.6629 | 385.4424 | 348.6012 | 338.6631 | 338.6631 | 609706.3684 | 711399.8009 | 8098125.3256
2015 | solar_dhw | 0.84922 | 344.5463 | 3.1249 | 1.9939 | 10.1154 | 41.8821 | 6.7247 | 0.34782 | 15.6204 | 8.5851 | 0 | 0 | 0 | 0 | 1.1006 | 2.8648 | 0 | 0 | 0 | 0 | -0.12667 | 0 | 0.97398 | 2.8648 | 0.11006 | 0.04641 | 0.87718 | 0.15647 | 22325.8454 | 9414.2803 | 31740.1256 | 275.9112 |  | 3638984.6328 | 101.1674 | 433.79 | 434.8321 | 420.4123 | 380.2286 | 369.3888 | 369.3888 | 197573.8528 | 55207.1991 | 778702.2643
2015 | payback_less_than_20 | 0.81878 | 120.5325 | 2.4608 | 3.094 | 12.9793 | 29.3177 | 6.7247 | 0.34782 | 8.9052 | 2.3 | 0 | 0.030442 | 224.0138 | 0.66414 | 0.00055078 | 0.00090547 | 12.5644 | 0 | 0 | 6.7152 | 6.1584 | 0 | 26.1331 | 224.0147 | 2.953 | 3.629 | 57.1598 | 6.5821 | 599029.7391 | 736157.6224 | 1335187.3615 | 12746.0862 |  | 13497657.4456 | 10.1092 | 187.4809 | 187.9314 | 181.6992 | 164.3321 | 159.6472 | 159.6472 | 5301148.1336 | 4316973.7113 | 50742976.6739
[26 empty] | 599029.7391 | 736157.6224 | [8 empty] | 13497657.4456
Note on A1: Lopez, Phylroy: You must add the evaluation year manually and it must match what is in base_build_arch_areas.
Note on B1: You must add the ecm names manually…Sorry. Phylroy
Note on B25: Lubun, Mike: 12% savings on heating/cooling/fan/pump

## base_scenario_arch_ghg
baseline_id | building_name | vintage_name | year | measure_id | Percent of Total Base Area | GHG Savings tonnes | GHG Savings %
1 | Barracks | 1959-pre | 2015 | air_temp_reset_enabled | 0.08671 | -46.4264
1 | Barracks | 1959-pre | 2015 | baseline | 0.08671 | 0
1 | Barracks | 1959-pre | 2015 | boiler_eff_upgrade | 0.08671 | -2.3226
1 | Barracks | 1959-pre | 2015 | boiler_reset | 0.08671 | 144.3046
1 | Barracks | 1959-pre | 2015 | cooling_cop_3_0 | 0.08671 | 2.2534
1 | Barracks | 1959-pre | 2015 | dcv_enabled | 0.08671 | 5.2528
1 | Barracks | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.08671 | -19.1627
1 | Barracks | 1959-pre | 2015 | economizers_enabled | 0.08671 | 1.5101
1 | Barracks | 1959-pre | 2015 | elec_reduce | 0.08671 | 58.5356
1 | Barracks | 1959-pre | 2015 | envelope_ecm_roof | 0.08671 | -0.34816
1 | Barracks | 1959-pre | 2015 | envelope_ecm_wall | 0.08671 | 14.7385
1 | Barracks | 1959-pre | 2015 | envelope_ecm_windows | 0.08671 | 28.1975
1 | Barracks | 1959-pre | 2015 | fans_to_variable | 0.08671 | -1.7581
1 | Barracks | 1959-pre | 2015 | hrv_enabled | 0.08671 | -9.6107
1 | Barracks | 1959-pre | 2015 | infil_reduce | 0.08671 | 154.8971
1 | Barracks | 1959-pre | 2015 | infil_reduce_plus_setback | 0.08671 | 184.3577
1 | Barracks | 1959-pre | 2015 | lights_reduce_70p | 0.08671 | 37.5525
1 | Barracks | 1959-pre | 2015 | load_reduce | 0.08671 | 248.1398
1 | Barracks | 1959-pre | 2015 | occupancy_setback | 0.08671 | 1.0419
1 | Barracks | 1959-pre | 2015 | payback_less_than_20 | 0.08671 | 281.6082
1 | Barracks | 1959-pre | 2015 | plug_loads_90_percent | 0.08671 | -2.5062
1 | Barracks | 1959-pre | 2015 | pump_fan_eff_ | 0.08671 | 10.7289
2 | Fire Hall | 1959-pre | 2015 | air_temp_reset_enabled | 0.0055698 | -0.3386
2 | Fire Hall | 1959-pre | 2015 | baseline | 0.0055698 | 0
2 | Fire Hall | 1959-pre | 2015 | boiler_eff_upgrade | 0.0055698 | 1.3737
2 | Fire Hall | 1959-pre | 2015 | boiler_reset | 0.0055698 | 29.1568
2 | Fire Hall | 1959-pre | 2015 | cooling_cop_3_0 | 0.0055698 | 1.7927
2 | Fire Hall | 1959-pre | 2015 | dcv_enabled | 0.0055698 | 1.3737
2 | Fire Hall | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.0055698 | 11.6384
2 | Fire Hall | 1959-pre | 2015 | economizers_enabled | 0.0055698 | 1.9317
2 | Fire Hall | 1959-pre | 2015 | elec_reduce | 0.0055698 | 24.5119
2 | Fire Hall | 1959-pre | 2015 | envelope_ecm_roof | 0.0055698 | 3.4175
2 | Fire Hall | 1959-pre | 2015 | envelope_ecm_wall | 0.0055698 | 4.8743
2 | Fire Hall | 1959-pre | 2015 | envelope_ecm_windows | 0.0055698 | 4.0754
2 | Fire Hall | 1959-pre | 2015 | fans_to_variable | 0.0055698 | 1.4649
2 | Fire Hall | 1959-pre | 2015 | hrv_enabled | 0.0055698 | 10.1622
2 | Fire Hall | 1959-pre | 2015 | infil_reduce | 0.0055698 | 74.911
2 | Fire Hall | 1959-pre | 2015 | infil_reduce_plus_setback | 0.0055698 | 63.865
2 | Fire Hall | 1959-pre | 2015 | lights_reduce_70p | 0.0055698 | 21.3501
2 | Fire Hall | 1959-pre | 2015 | load_reduce | 0.0055698 | 79.2145
2 | Fire Hall | 1959-pre | 2015 | occupancy_setback | 0.0055698 | -21.4727
2 | Fire Hall | 1959-pre | 2015 | payback_less_than_20 | 0.0055698 | 111.5167
2 | Fire Hall | 1959-pre | 2015 | plug_loads_90_percent | 0.0055698 | 1.2741
2 | Fire Hall | 1959-pre | 2015 | pump_fan_eff_ | 0.0055698 | 4.5712
3 | Food Service | 1959-pre | 2015 | air_temp_reset_enabled | 0.043262 | -100.2149
3 | Food Service | 1959-pre | 2015 | baseline | 0.043262 | 0
3 | Food Service | 1959-pre | 2015 | boiler_eff_upgrade | 0.043262 | 2.2989
3 | Food Service | 1959-pre | 2015 | boiler_reset | 0.043262 | 275.2752
3 | Food Service | 1959-pre | 2015 | cooling_cop_3_0 | 0.043262 | 10.7873
3 | Food Service | 1959-pre | 2015 | dcv_enabled | 0.043262 | 259.0852
3 | Food Service | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.043262 | 22.6202
3 | Food Service | 1959-pre | 2015 | economizers_enabled | 0.043262 | 5.1472
3 | Food Service | 1959-pre | 2015 | elec_reduce | 0.043262 | 510.7153
3 | Food Service | 1959-pre | 2015 | envelope_ecm_roof | 0.043262 | 45.218
3 | Food Service | 1959-pre | 2015 | envelope_ecm_wall | 0.043262 | 20.1673
3 | Food Service | 1959-pre | 2015 | envelope_ecm_windows | 0.043262 | 43.0777
3 | Food Service | 1959-pre | 2015 | exhaust_fans_occ_control | 0.043262 | 87.6884
3 | Food Service | 1959-pre | 2015 | fans_to_variable | 0.043262 | 3.3636
3 | Food Service | 1959-pre | 2015 | hrv_enabled | 0.043262 | 277.2825
3 | Food Service | 1959-pre | 2015 | infil_reduce | 0.043262 | 474.5247
3 | Food Service | 1959-pre | 2015 | infil_reduce_plus_setback | 0.043262 | 539.5407
3 | Food Service | 1959-pre | 2015 | lights_reduce_70p | 0.043262 | 138.2881
3 | Food Service | 1959-pre | 2015 | load_reduce | 0.043262 | 692.1223
3 | Food Service | 1959-pre | 2015 | occupancy_setback | 0.043262 | 47.3045
3 | Food Service | 1959-pre | 2015 | payback_less_than_20 | 0.043262 | 1066.5296
3 | Food Service | 1959-pre | 2015 | plug_loads_90_percent | 0.043262 | 2.0207
3 | Food Service | 1959-pre | 2015 | pump_fan_eff_ | 0.043262 | 24.6282
4 | Food Service | 2005-2014 | 2015 | air_temp_reset_enabled | 0 | 0
4 | Food Service | 2005-2014 | 2015 | baseline | 0 | 0
4 | Food Service | 2005-2014 | 2015 | boiler_eff_upgrade | 0 | 0
4 | Food Service | 2005-2014 | 2015 | boiler_reset | 0 | 0
4 | Food Service | 2005-2014 | 2015 | cooling_cop_3_0 | 0 | 0
4 | Food Service | 2005-2014 | 2015 | dcv_enabled | 0 | 0
4 | Food Service | 2005-2014 | 2015 | ecm_cold_deck_reset_control | 0 | 0
4 | Food Service | 2005-2014 | 2015 | economizers_enabled | 0 | 0
4 | Food Service | 2005-2014 | 2015 | elec_reduce | 0 | 0
4 | Food Service | 2005-2014 | 2015 | envelope_ecm_roof | 0 | 0
4 | Food Service | 2005-2014 | 2015 | envelope_ecm_wall | 0 | 0
4 | Food Service | 2005-2014 | 2015 | envelope_ecm_windows | 0 | 0
4 | Food Service | 2005-2014 | 2015 | exhaust_fans_occ_control | 0 | 0
4 | Food Service | 2005-2014 | 2015 | fans_to_variable | 0 | 0
4 | Food Service | 2005-2014 | 2015 | hrv_enabled | 0 | 0
4 | Food Service | 2005-2014 | 2015 | lights_reduce_70p | 0 | 0
4 | Food Service | 2005-2014 | 2015 | load_reduce | 0 | 0
4 | Food Service | 2005-2014 | 2015 | occupancy_setback | 0 | 0
4 | Food Service | 2005-2014 | 2015 | payback_less_than_20 | 0 | 0
4 | Food Service | 2005-2014 | 2015 | plug_loads_90_percent | 0 | 0
4 | Food Service | 2005-2014 | 2015 | pump_fan_eff_ | 0 | 0
5 | Hangar | 1959-pre | 2015 | air_temp_reset_enabled | 0.26866 | -300.9946
5 | Hangar | 1959-pre | 2015 | baseline | 0.26866 | 0
5 | Hangar | 1959-pre | 2015 | boiler_eff_upgrade | 0.26866 | 29.0574
5 | Hangar | 1959-pre | 2015 | boiler_reset | 0.26866 | 1179.3036
5 | Hangar | 1959-pre | 2015 | cooling_cop_3_0 | 0.26866 | 34.8567
5 | Hangar | 1959-pre | 2015 | dcv_enabled | 0.26866 | 639.6481
5 | Hangar | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.26866 | 13.8796
5 | Hangar | 1959-pre | 2015 | economizers_enabled | 0.26866 | 29.6894
5 | Hangar | 1959-pre | 2015 | elec_reduce | 0.26866 | 1399.2939
5 | Hangar | 1959-pre | 2015 | envelope_ecm_roof | 0.26866 | 384.8617
5 | Hangar | 1959-pre | 2015 | envelope_ecm_wall | 0.26866 | 265.7032
5 | Hangar | 1959-pre | 2015 | envelope_ecm_windows | 0.26866 | 96.5086
5 | Hangar | 1959-pre | 2015 | exhaust_fans_occ_control | 0.26866 | 68.8983
5 | Hangar | 1959-pre | 2015 | fans_to_variable | 0.26866 | 32.1727
5 | Hangar | 1959-pre | 2015 | hrv_enabled | 0.26866 | 465.7004
5 | Hangar | 1959-pre | 2015 | infil_reduce | 0.26866 | 2161.618
5 | Hangar | 1959-pre | 2015 | infil_reduce_plus_setback | 0.26866 | 2602.6362
5 | Hangar | 1959-pre | 2015 | lights_reduce_70p | 0.26866 | 659.0473
5 | Hangar | 1959-pre | 2015 | load_reduce | 0.26866 | 3188.2906
5 | Hangar | 1959-pre | 2015 | occupancy_setback | 0.26866 | 686.5711
5 | Hangar | 1959-pre | 2015 | payback_less_than_20 | 0.26866 | 4220.5453
5 | Hangar | 1959-pre | 2015 | plug_loads_90_percent | 0.26866 | 27.6771
5 | Hangar | 1959-pre | 2015 | pumps_to_variable | 0.26866 | 29.6538
5 | Hangar | 1959-pre | 2015 | pump_fan_eff_ | 0.26866 | 120.5539
6 | Hangar | 1960-1979 | 2015 | air_temp_reset_enabled | 0.026924 | -26.7588
6 | Hangar | 1960-1979 | 2015 | baseline | 0.026924 | 0
6 | Hangar | 1960-1979 | 2015 | boiler_eff_upgrade | 0.026924 | 4.172
6 | Hangar | 1960-1979 | 2015 | boiler_reset | 0.026924 | 113.8315
6 | Hangar | 1960-1979 | 2015 | cooling_cop_3_0 | 0.026924 | 4.6612
6 | Hangar | 1960-1979 | 2015 | dcv_enabled | 0.026924 | 65.2204
6 | Hangar | 1960-1979 | 2015 | ecm_cold_deck_reset_control | 0.026924 | 3.3794
6 | Hangar | 1960-1979 | 2015 | economizers_enabled | 0.026924 | 4.2399
6 | Hangar | 1960-1979 | 2015 | elec_reduce | 0.026924 | 141.0738
6 | Hangar | 1960-1979 | 2015 | envelope_ecm_roof | 0.026924 | 48.4877
6 | Hangar | 1960-1979 | 2015 | envelope_ecm_wall | 0.026924 | 17.7079
6 | Hangar | 1960-1979 | 2015 | envelope_ecm_windows | 0.026924 | 10.8541
6 | Hangar | 1960-1979 | 2015 | exhaust_fans_occ_control | 0.026924 | 8.1667
6 | Hangar | 1960-1979 | 2015 | fans_to_variable | 0.026924 | 4.4598
6 | Hangar | 1960-1979 | 2015 | hrv_enabled | 0.026924 | 47.6918
6 | Hangar | 1960-1979 | 2015 | infil_reduce | 0.026924 | 197.0095
6 | Hangar | 1960-1979 | 2015 | infil_reduce_plus_setback | 0.026924 | 243.8831
6 | Hangar | 1960-1979 | 2015 | lights_reduce_70p | 0.026924 | 67.5526
6 | Hangar | 1960-1979 | 2015 | load_reduce | 0.026924 | 300.5736
6 | Hangar | 1960-1979 | 2015 | occupancy_setback | 0.026924 | 70.541
6 | Hangar | 1960-1979 | 2015 | payback_less_than_20 | 0.026924 | 404.9995
6 | Hangar | 1960-1979 | 2015 | plug_loads_90_percent | 0.026924 | 3.982
6 | Hangar | 1960-1979 | 2015 | pumps_to_variable | 0.026924 | 4.2317
6 | Hangar | 1960-1979 | 2015 | pump_fan_eff_ | 0.026924 | 12.8124
7 | Hangar | 1980-2004 | 2015 | air_temp_reset_enabled | 0.031409 | -21.4906
7 | Hangar | 1980-2004 | 2015 | baseline | 0.031409 | 0
7 | Hangar | 1980-2004 | 2015 | boiler_eff_upgrade | 0.031409 | 1.2385
7 | Hangar | 1980-2004 | 2015 | boiler_reset | 0.031409 | 86.2554
7 | Hangar | 1980-2004 | 2015 | cooling_cop_3_0 | 0.031409 | 1.4849
7 | Hangar | 1980-2004 | 2015 | dcv_enabled | 0.031409 | 71.1255
7 | Hangar | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.031409 | 3.403
7 | Hangar | 1980-2004 | 2015 | economizers_enabled | 0.031409 | 1.3246
7 | Hangar | 1980-2004 | 2015 | elec_reduce | 0.031409 | 157.6152
7 | Hangar | 1980-2004 | 2015 | envelope_ecm_roof | 0.031409 | 24.6787
7 | Hangar | 1980-2004 | 2015 | envelope_ecm_wall | 0.031409 | 9.2392
7 | Hangar | 1980-2004 | 2015 | envelope_ecm_windows | 0.031409 | 6.7667
7 | Hangar | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.031409 | 5.8988
7 | Hangar | 1980-2004 | 2015 | fans_to_variable | 0.031409 | 1.4637
7 | Hangar | 1980-2004 | 2015 | hrv_enabled | 0.031409 | 50.4027
7 | Hangar | 1980-2004 | 2015 | infil_reduce | 0.031409 | 73.5324
7 | Hangar | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.031409 | 121.1817
7 | Hangar | 1980-2004 | 2015 | lights_reduce_70p | 0.031409 | 76.609
7 | Hangar | 1980-2004 | 2015 | load_reduce | 0.031409 | 176.3017
7 | Hangar | 1980-2004 | 2015 | occupancy_setback | 0.031409 | 54.6926
7 | Hangar | 1980-2004 | 2015 | payback_less_than_20 | 0.031409 | 299.7232
7 | Hangar | 1980-2004 | 2015 | plug_loads_90_percent | 0.031409 | 1.1833
7 | Hangar | 1980-2004 | 2015 | pumps_to_variable | 0.031409 | 1.3083
7 | Hangar | 1980-2004 | 2015 | pump_fan_eff_ | 0.031409 | 7.5942
10 | Maintenance Shop-Small | 1959-pre | 2015 | air_temp_reset_enabled | 0.0067581 | -14.1937
10 | Maintenance Shop-Small | 1959-pre | 2015 | baseline | 0.0067581 | 0
10 | Maintenance Shop-Small | 1959-pre | 2015 | boiler_eff_upgrade | 0.0067581 | 0.71806
10 | Maintenance Shop-Small | 1959-pre | 2015 | boiler_reset | 0.0067581 | 68.5437
10 | Maintenance Shop-Small | 1959-pre | 2015 | cooling_cop_3_0 | 0.0067581 | 1.1202
10 | Maintenance Shop-Small | 1959-pre | 2015 | dcv_enabled | 0.0067581 | 0.71806
10 | Maintenance Shop-Small | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.0067581 | -4.1613
10 | Maintenance Shop-Small | 1959-pre | 2015 | economizers_enabled | 0.0067581 | 0.87944
10 | Maintenance Shop-Small | 1959-pre | 2015 | elec_reduce | 0.0067581 | 24.5127
10 | Maintenance Shop-Small | 1959-pre | 2015 | envelope_ecm_roof | 0.0067581 | 17.5555
10 | Maintenance Shop-Small | 1959-pre | 2015 | envelope_ecm_wall | 0.0067581 | 32.8207
10 | Maintenance Shop-Small | 1959-pre | 2015 | envelope_ecm_windows | 0.0067581 | 1.1049
10 | Maintenance Shop-Small | 1959-pre | 2015 | exhaust_fans_occ_control | 0.0067581 | 0.71806
10 | Maintenance Shop-Small | 1959-pre | 2015 | fans_to_variable | 0.0067581 | 0.79624
10 | Maintenance Shop-Small | 1959-pre | 2015 | hrv_enabled | 0.0067581 | 1.1698
10 | Maintenance Shop-Small | 1959-pre | 2015 | infil_reduce | 0.0067581 | 112.7299
10 | Maintenance Shop-Small | 1959-pre | 2015 | infil_reduce_plus_setback | 0.0067581 | 124.342
10 | Maintenance Shop-Small | 1959-pre | 2015 | lights_reduce_70p | 0.0067581 | 14.1541
10 | Maintenance Shop-Small | 1959-pre | 2015 | load_reduce | 0.0067581 | 157.6296
10 | Maintenance Shop-Small | 1959-pre | 2015 | occupancy_setback | 0.0067581 | 18.6452
10 | Maintenance Shop-Small | 1959-pre | 2015 | payback_less_than_20 | 0.0067581 | 169.7731
10 | Maintenance Shop-Small | 1959-pre | 2015 | plug_loads_90_percent | 0.0067581 | 0.69803
10 | Maintenance Shop-Small | 1959-pre | 2015 | pump_fan_eff_ | 0.0067581 | 11.0054
11 | Maintenance Shop-Small | 1960-1979 | 2015 | air_temp_reset_enabled | 0.0031284 | -5.5114
11 | Maintenance Shop-Small | 1960-1979 | 2015 | baseline | 0.0031284 | 0
11 | Maintenance Shop-Small | 1960-1979 | 2015 | boiler_eff_upgrade | 0.0031284 | 0.38406
11 | Maintenance Shop-Small | 1960-1979 | 2015 | boiler_reset | 0.0031284 | 29.5406
11 | Maintenance Shop-Small | 1960-1979 | 2015 | cooling_cop_3_0 | 0.0031284 | 0.57183
11 | Maintenance Shop-Small | 1960-1979 | 2015 | dcv_enabled | 0.0031284 | 0.38406
11 | Maintenance Shop-Small | 1960-1979 | 2015 | ecm_cold_deck_reset_control | 0.0031284 | -1.6083
11 | Maintenance Shop-Small | 1960-1979 | 2015 | economizers_enabled | 0.0031284 | 0.47449
11 | Maintenance Shop-Small | 1960-1979 | 2015 | elec_reduce | 0.0031284 | 11.1362
11 | Maintenance Shop-Small | 1960-1979 | 2015 | envelope_ecm_roof | 0.0031284 | 12.6863
11 | Maintenance Shop-Small | 1960-1979 | 2015 | envelope_ecm_wall | 0.0031284 | 6.7011
11 | Maintenance Shop-Small | 1960-1979 | 2015 | envelope_ecm_windows | 0.0031284 | 0.56403
11 | Maintenance Shop-Small | 1960-1979 | 2015 | exhaust_fans_occ_control | 0.0031284 | 0.38406
11 | Maintenance Shop-Small | 1960-1979 | 2015 | fans_to_variable | 0.0031284 | 0.4193
11 | Maintenance Shop-Small | 1960-1979 | 2015 | hrv_enabled | 0.0031284 | 0.58071
11 | Maintenance Shop-Small | 1960-1979 | 2015 | infil_reduce | 0.0031284 | 47.0851
11 | Maintenance Shop-Small | 1960-1979 | 2015 | infil_reduce_plus_setback | 0.0031284 | 52.8379
11 | Maintenance Shop-Small | 1960-1979 | 2015 | lights_reduce_70p | 0.0031284 | 6.6488
11 | Maintenance Shop-Small | 1960-1979 | 2015 | load_reduce | 0.0031284 | 67.3011
11 | Maintenance Shop-Small | 1960-1979 | 2015 | occupancy_setback | 0.0031284 | 8.7839
11 | Maintenance Shop-Small | 1960-1979 | 2015 | payback_less_than_20 | 0.0031284 | 73.0595
11 | Maintenance Shop-Small | 1960-1979 | 2015 | plug_loads_90_percent | 0.0031284 | 0.36785
11 | Maintenance Shop-Small | 1960-1979 | 2015 | pump_fan_eff_ | 0.0031284 | 4.8403
12 | Maintenance Shop-Small | 1980-2004 | 2015 | air_temp_reset_enabled | 0.021039 | -17.4977
12 | Maintenance Shop-Small | 1980-2004 | 2015 | baseline | 0.021039 | 0
12 | Maintenance Shop-Small | 1980-2004 | 2015 | boiler_eff_upgrade | 0.021039 | -0.87946
12 | Maintenance Shop-Small | 1980-2004 | 2015 | boiler_reset | 0.021039 | 104.2535
12 | Maintenance Shop-Small | 1980-2004 | 2015 | cooling_cop_3_0 | 0.021039 | -0.32429
12 | Maintenance Shop-Small | 1980-2004 | 2015 | dcv_enabled | 0.021039 | -0.87946
12 | Maintenance Shop-Small | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.021039 | -7.1456
12 | Maintenance Shop-Small | 1980-2004 | 2015 | economizers_enabled | 0.021039 | 0.51668
12 | Maintenance Shop-Small | 1980-2004 | 2015 | elec_reduce | 0.021039 | 58.8994
12 | Maintenance Shop-Small | 1980-2004 | 2015 | envelope_ecm_roof | 0.021039 | 18.0615
12 | Maintenance Shop-Small | 1980-2004 | 2015 | envelope_ecm_wall | 0.021039 | 11.1074
12 | Maintenance Shop-Small | 1980-2004 | 2015 | envelope_ecm_windows | 0.021039 | 0.037675
12 | Maintenance Shop-Small | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.021039 | -0.87946
12 | Maintenance Shop-Small | 1980-2004 | 2015 | fans_to_variable | 0.021039 | -0.75232
12 | Maintenance Shop-Small | 1980-2004 | 2015 | hrv_enabled | 0.021039 | 0.52716
12 | Maintenance Shop-Small | 1980-2004 | 2015 | infil_reduce | 0.021039 | 103.0336
12 | Maintenance Shop-Small | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.021039 | 132.3876
12 | Maintenance Shop-Small | 1980-2004 | 2015 | lights_reduce_70p | 0.021039 | 41.5531
12 | Maintenance Shop-Small | 1980-2004 | 2015 | load_reduce | 0.021039 | 198.5649
12 | Maintenance Shop-Small | 1980-2004 | 2015 | occupancy_setback | 0.021039 | 35.6037
12 | Maintenance Shop-Small | 1980-2004 | 2015 | payback_less_than_20 | 0.021039 | 246.5596
12 | Maintenance Shop-Small | 1980-2004 | 2015 | plug_loads_90_percent | 0.021039 | -0.83238
12 | Maintenance Shop-Small | 1980-2004 | 2015 | pump_fan_eff_ | 0.021039 | 15.9718
8 | Maintenance Shop | 1959-pre | 2015 | air_temp_reset_enabled | 0.017211 | -8.1812
8 | Maintenance Shop | 1959-pre | 2015 | baseline | 0.017211 | 0
8 | Maintenance Shop | 1959-pre | 2015 | boiler_eff_upgrade | 0.017211 | -0.051466
8 | Maintenance Shop | 1959-pre | 2015 | boiler_reset | 0.017211 | 124.764
8 | Maintenance Shop | 1959-pre | 2015 | cooling_cop_3_0 | 0.017211 | 0.30844
8 | Maintenance Shop | 1959-pre | 2015 | dcv_enabled | 0.017211 | 78.9289
8 | Maintenance Shop | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.017211 | -0.8997
8 | Maintenance Shop | 1959-pre | 2015 | economizers_enabled | 0.017211 | 0.19163
8 | Maintenance Shop | 1959-pre | 2015 | elec_reduce | 0.017211 | 120.4335
8 | Maintenance Shop | 1959-pre | 2015 | envelope_ecm_roof | 0.017211 | 29.2037
8 | Maintenance Shop | 1959-pre | 2015 | envelope_ecm_wall | 0.017211 | 58.7498
8 | Maintenance Shop | 1959-pre | 2015 | envelope_ecm_windows | 0.017211 | 2.8591
8 | Maintenance Shop | 1959-pre | 2015 | exhaust_fans_occ_control | 0.017211 | 2.8987
8 | Maintenance Shop | 1959-pre | 2015 | fans_to_variable | 0.017211 | 0.42561
8 | Maintenance Shop | 1959-pre | 2015 | hrv_enabled | 0.017211 | 19.8771
8 | Maintenance Shop | 1959-pre | 2015 | infil_reduce | 0.017211 | 184.3604
8 | Maintenance Shop | 1959-pre | 2015 | infil_reduce_plus_setback | 0.017211 | 199.1955
8 | Maintenance Shop | 1959-pre | 2015 | lights_reduce_70p | 0.017211 | 19.1983
8 | Maintenance Shop | 1959-pre | 2015 | load_reduce | 0.017211 | 270.1956
8 | Maintenance Shop | 1959-pre | 2015 | occupancy_setback | 0.017211 | 19.9848
8 | Maintenance Shop | 1959-pre | 2015 | payback_less_than_20 | 0.017211 | 349.7715
8 | Maintenance Shop | 1959-pre | 2015 | plug_loads_90_percent | 0.017211 | -0.19438
8 | Maintenance Shop | 1959-pre | 2015 | pump_fan_eff_ | 0.017211 | 18.5945
9 | Maintenance Shop | 1980-2004 | 2015 | air_temp_reset_enabled | 0.047471 | -25.7344
9 | Maintenance Shop | 1980-2004 | 2015 | baseline | 0.047471 | 0
9 | Maintenance Shop | 1980-2004 | 2015 | boiler_eff_upgrade | 0.047471 | -3.4424
9 | Maintenance Shop | 1980-2004 | 2015 | boiler_reset | 0.047471 | 193.0011
9 | Maintenance Shop | 1980-2004 | 2015 | cooling_cop_3_0 | 0.047471 | -2.9843
9 | Maintenance Shop | 1980-2004 | 2015 | dcv_enabled | 0.047471 | 177.164
9 | Maintenance Shop | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.047471 | -5.7303
9 | Maintenance Shop | 1980-2004 | 2015 | economizers_enabled | 0.047471 | -2.9072
9 | Maintenance Shop | 1980-2004 | 2015 | elec_reduce | 0.047471 | 270.4795
9 | Maintenance Shop | 1980-2004 | 2015 | envelope_ecm_roof | 0.047471 | 26.2216
9 | Maintenance Shop | 1980-2004 | 2015 | envelope_ecm_wall | 0.047471 | 28.3021
9 | Maintenance Shop | 1980-2004 | 2015 | envelope_ecm_windows | 0.047471 | 2.2618
9 | Maintenance Shop | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.047471 | 6.0019
9 | Maintenance Shop | 1980-2004 | 2015 | fans_to_variable | 0.047471 | -2.7134
9 | Maintenance Shop | 1980-2004 | 2015 | hrv_enabled | 0.047471 | 57.5009
9 | Maintenance Shop | 1980-2004 | 2015 | infil_reduce | 0.047471 | 149.3823
9 | Maintenance Shop | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.047471 | 186.4153
9 | Maintenance Shop | 1980-2004 | 2015 | lights_reduce_70p | 0.047471 | 49.8239
9 | Maintenance Shop | 1980-2004 | 2015 | load_reduce | 0.047471 | 328.2953
9 | Maintenance Shop | 1980-2004 | 2015 | occupancy_setback | 0.047471 | 38.5322
9 | Maintenance Shop | 1980-2004 | 2015 | payback_less_than_20 | 0.047471 | 523.7179
9 | Maintenance Shop | 1980-2004 | 2015 | plug_loads_90_percent | 0.047471 | -3.7492
9 | Maintenance Shop | 1980-2004 | 2015 | pump_fan_eff_ | 0.047471 | 25.4758
16 | Office-Small | 1960-1979 | 2015 | air_temp_reset_enabled | 0.0049605 | -4.0553
16 | Office-Small | 1960-1979 | 2015 | baseline | 0.0049605 | 0
16 | Office-Small | 1960-1979 | 2015 | boiler_reset | 0.0049605 | -0.27891
16 | Office-Small | 1960-1979 | 2015 | cooling_cop_3_0 | 0.0049605 | 0.063272
16 | Office-Small | 1960-1979 | 2015 | dcv_enabled | 0.0049605 | -0.27891
16 | Office-Small | 1960-1979 | 2015 | ecm_cold_deck_reset_control | 0.0049605 | -2.8763
16 | Office-Small | 1960-1979 | 2015 | economizers_enabled | 0.0049605 | -0.27891
16 | Office-Small | 1960-1979 | 2015 | elec_reduce | 0.0049605 | 3.7654
16 | Office-Small | 1960-1979 | 2015 | envelope_ecm_roof | 0.0049605 | 2.9701
16 | Office-Small | 1960-1979 | 2015 | envelope_ecm_wall | 0.0049605 | 0.95385
16 | Office-Small | 1960-1979 | 2015 | envelope_ecm_windows | 0.0049605 | 0.15192
16 | Office-Small | 1960-1979 | 2015 | exhaust_fans_occ_control | 0.0049605 | 0.57279
16 | Office-Small | 1960-1979 | 2015 | fans_to_variable | 0.0049605 | -0.22435
16 | Office-Small | 1960-1979 | 2015 | hrv_enabled | 0.0049605 | -0.27891
16 | Office-Small | 1960-1979 | 2015 | infil_reduce | 0.0049605 | 6.0316
16 | Office-Small | 1960-1979 | 2015 | infil_reduce_plus_setback | 0.0049605 | 6.6764
16 | Office-Small | 1960-1979 | 2015 | lights_reduce_70p | 0.0049605 | 2.9028
16 | Office-Small | 1960-1979 | 2015 | load_reduce | 0.0049605 | 6.6764
16 | Office-Small | 1960-1979 | 2015 | occupancy_setback | 0.0049605 | 0.53445
16 | Office-Small | 1960-1979 | 2015 | payback_less_than_20 | 0.0049605 | 8.4175
16 | Office-Small | 1960-1979 | 2015 | plug_loads_90_percent | 0.0049605 | -0.2611
16 | Office-Small | 1960-1979 | 2015 | pump_fan_eff_ | 0.0049605 | -0.27703
17 | Office-Small | 1980-2004 | 2015 | air_temp_reset_enabled | 0.018822 | -9.3381
17 | Office-Small | 1980-2004 | 2015 | baseline | 0.018822 | 0
17 | Office-Small | 1980-2004 | 2015 | boiler_reset | 0.018822 | -1.3892
17 | Office-Small | 1980-2004 | 2015 | cooling_cop_3_0 | 0.018822 | -0.80069
17 | Office-Small | 1980-2004 | 2015 | dcv_enabled | 0.018822 | -1.3892
17 | Office-Small | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.018822 | -8.2305
17 | Office-Small | 1980-2004 | 2015 | economizers_enabled | 0.018822 | -1.3892
17 | Office-Small | 1980-2004 | 2015 | elec_reduce | 0.018822 | 14.254
17 | Office-Small | 1980-2004 | 2015 | envelope_ecm_roof | 0.018822 | 2.7316
17 | Office-Small | 1980-2004 | 2015 | envelope_ecm_wall | 0.018822 | 0.32543
17 | Office-Small | 1980-2004 | 2015 | envelope_ecm_windows | 0.018822 | -0.23717
17 | Office-Small | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.018822 | 1.846
17 | Office-Small | 1980-2004 | 2015 | fans_to_variable | 0.018822 | -1.2552
17 | Office-Small | 1980-2004 | 2015 | hrv_enabled | 0.018822 | -1.3892
17 | Office-Small | 1980-2004 | 2015 | infil_reduce | 0.018822 | 9.6259
17 | Office-Small | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.018822 | 11.687
17 | Office-Small | 1980-2004 | 2015 | lights_reduce_70p | 0.018822 | 10.9189
17 | Office-Small | 1980-2004 | 2015 | load_reduce | 0.018822 | 11.687
17 | Office-Small | 1980-2004 | 2015 | occupancy_setback | 0.018822 | 0.56855
17 | Office-Small | 1980-2004 | 2015 | payback_less_than_20 | 0.018822 | 20.9357
17 | Office-Small | 1980-2004 | 2015 | plug_loads_90_percent | 0.018822 | -1.2709
17 | Office-Small | 1980-2004 | 2015 | pump_fan_eff_ | 0.018822 | -1.3821
18 | Office-Small | 2005-2014 | 2015 | air_temp_reset_enabled | 0.0021648 | -0.57329
18 | Office-Small | 2005-2014 | 2015 | baseline | 0.0021648 | 0
18 | Office-Small | 2005-2014 | 2015 | boiler_reset | 0.0021648 | -0.19973
18 | Office-Small | 2005-2014 | 2015 | cooling_cop_3_0 | 0.0021648 | -0.19973
18 | Office-Small | 2005-2014 | 2015 | dcv_enabled | 0.0021648 | -0.19973
18 | Office-Small | 2005-2014 | 2015 | ecm_cold_deck_reset_control | 0.0021648 | -0.68543
18 | Office-Small | 2005-2014 | 2015 | economizers_enabled | 0.0021648 | -0.19973
18 | Office-Small | 2005-2014 | 2015 | elec_reduce | 0.0021648 | 1.7506
18 | Office-Small | 2005-2014 | 2015 | envelope_ecm_roof | 0.0021648 | 0.027743
18 | Office-Small | 2005-2014 | 2015 | envelope_ecm_wall | 0.0021648 | -0.11165
18 | Office-Small | 2005-2014 | 2015 | envelope_ecm_windows | 0.0021648 | -0.10083
18 | Office-Small | 2005-2014 | 2015 | exhaust_fans_occ_control | 0.0021648 | 0.17237
18 | Office-Small | 2005-2014 | 2015 | fans_to_variable | 0.0021648 | -0.18911
18 | Office-Small | 2005-2014 | 2015 | hrv_enabled | 0.0021648 | -0.19973
18 | Office-Small | 2005-2014 | 2015 | lights_reduce_70p | 0.0021648 | 1.3662
18 | Office-Small | 2005-2014 | 2015 | load_reduce | 0.0021648 | 0.081523
18 | Office-Small | 2005-2014 | 2015 | occupancy_setback | 0.0021648 | 0.081523
18 | Office-Small | 2005-2014 | 2015 | payback_less_than_20 | 0.0021648 | 1.2894
18 | Office-Small | 2005-2014 | 2015 | plug_loads_90_percent | 0.0021648 | -0.18253
18 | Office-Small | 2005-2014 | 2015 | pump_fan_eff_ | 0.0021648 | -0.19891
13 | Office | 1959-pre | 2015 | air_temp_reset_enabled | 0.071353 | 419.1001
13 | Office | 1959-pre | 2015 | baseline | 0.071353 | 0
13 | Office | 1959-pre | 2015 | boiler_eff_upgrade | 0.071353 | 12.9794
13 | Office | 1959-pre | 2015 | boiler_reset | 0.071353 | 360.0585
13 | Office | 1959-pre | 2015 | cooling_cop_3_0 | 0.071353 | 87.6305
13 | Office | 1959-pre | 2015 | dcv_enabled | 0.071353 | 165.7387
13 | Office | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.071353 | 475.4829
13 | Office | 1959-pre | 2015 | economizers_enabled | 0.071353 | 14.7532
13 | Office | 1959-pre | 2015 | elec_reduce | 0.071353 | 498.0463
13 | Office | 1959-pre | 2015 | envelope_ecm_roof | 0.071353 | 120.5344
13 | Office | 1959-pre | 2015 | envelope_ecm_wall | 0.071353 | 91.7496
13 | Office | 1959-pre | 2015 | envelope_ecm_windows | 0.071353 | 20.7806
13 | Office | 1959-pre | 2015 | exhaust_fans_occ_control | 0.071353 | 210.1339
13 | Office | 1959-pre | 2015 | fans_to_variable | 0.071353 | 13.5286
13 | Office | 1959-pre | 2015 | hrv_enabled | 0.071353 | 94.0938
13 | Office | 1959-pre | 2015 | infil_reduce | 0.071353 | 585.8359
13 | Office | 1959-pre | 2015 | infil_reduce_plus_setback | 0.071353 | 651.9114
13 | Office | 1959-pre | 2015 | lights_reduce_70p | 0.071353 | 116.4767
13 | Office | 1959-pre | 2015 | load_reduce | 0.071353 | 856.0103
13 | Office | 1959-pre | 2015 | occupancy_setback | 0.071353 | -3.4264
13 | Office | 1959-pre | 2015 | payback_less_than_20 | 0.071353 | 1621.7287
13 | Office | 1959-pre | 2015 | plug_loads_90_percent | 0.071353 | 11.1292
13 | Office | 1959-pre | 2015 | pumps_to_variable | 0.071353 | 108.9
13 | Office | 1959-pre | 2015 | pump_fan_eff_ | 0.071353 | 46.9452
14 | Office | 1960-1979 | 2015 | air_temp_reset_enabled | 0.015037 | 83.0426
14 | Office | 1960-1979 | 2015 | baseline | 0.015037 | 0
14 | Office | 1960-1979 | 2015 | boiler_eff_upgrade | 0.015037 | 3.5098
14 | Office | 1960-1979 | 2015 | boiler_reset | 0.015037 | 71.0157
14 | Office | 1960-1979 | 2015 | cooling_cop_3_0 | 0.015037 | 18.337
14 | Office | 1960-1979 | 2015 | dcv_enabled | 0.015037 | 35.3964
14 | Office | 1960-1979 | 2015 | ecm_cold_deck_reset_control | 0.015037 | 94.4132
14 | Office | 1960-1979 | 2015 | economizers_enabled | 0.015037 | 3.8569
14 | Office | 1960-1979 | 2015 | elec_reduce | 0.015037 | 105.323
14 | Office | 1960-1979 | 2015 | envelope_ecm_roof | 0.015037 | 53.055
14 | Office | 1960-1979 | 2015 | envelope_ecm_wall | 0.015037 | 18.7953
14 | Office | 1960-1979 | 2015 | envelope_ecm_windows | 0.015037 | 4.9161
14 | Office | 1960-1979 | 2015 | exhaust_fans_occ_control | 0.015037 | 45.0608
14 | Office | 1960-1979 | 2015 | fans_to_variable | 0.015037 | 3.6168
14 | Office | 1960-1979 | 2015 | hrv_enabled | 0.015037 | 20.3138
14 | Office | 1960-1979 | 2015 | infil_reduce | 0.015037 | 74.1005
14 | Office | 1960-1979 | 2015 | infil_reduce_plus_setback | 0.015037 | 89.6965
14 | Office | 1960-1979 | 2015 | lights_reduce_70p | 0.015037 | 25.9254
14 | Office | 1960-1979 | 2015 | load_reduce | 0.015037 | 138.4706
14 | Office | 1960-1979 | 2015 | occupancy_setback | 0.015037 | 0.84029
14 | Office | 1960-1979 | 2015 | payback_less_than_20 | 0.015037 | 303.3757
14 | Office | 1960-1979 | 2015 | plug_loads_90_percent | 0.015037 | 3.0278
14 | Office | 1960-1979 | 2015 | pumps_to_variable | 0.015037 | 22.4777
14 | Office | 1960-1979 | 2015 | pump_fan_eff_ | 0.015037 | 10.186
15 | Office | 1980-2004 | 2015 | air_temp_reset_enabled | 0.076404 | 171.1178
15 | Office | 1980-2004 | 2015 | baseline | 0.076404 | 0
15 | Office | 1980-2004 | 2015 | boiler_eff_upgrade | 0.076404 | -130.8097
15 | Office | 1980-2004 | 2015 | boiler_reset | 0.076404 | 116.0253
15 | Office | 1980-2004 | 2015 | cooling_cop_3_0 | 0.076404 | -103.061
15 | Office | 1980-2004 | 2015 | dcv_enabled | 0.076404 | 34.1784
15 | Office | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.076404 | 226.5232
15 | Office | 1980-2004 | 2015 | economizers_enabled | 0.076404 | -128.5384
15 | Office | 1980-2004 | 2015 | elec_reduce | 0.076404 | 499.7222
15 | Office | 1980-2004 | 2015 | envelope_ecm_roof | 0.076404 | -66.3533
15 | Office | 1980-2004 | 2015 | envelope_ecm_wall | 0.076404 | -115.9063
15 | Office | 1980-2004 | 2015 | envelope_ecm_windows | 0.076404 | -127.5414
15 | Office | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.076404 | 80.2997
15 | Office | 1980-2004 | 2015 | fans_to_variable | 0.076404 | -130.3901
15 | Office | 1980-2004 | 2015 | hrv_enabled | 0.076404 | -43.344
15 | Office | 1980-2004 | 2015 | infil_reduce | 0.076404 | 9.8567
15 | Office | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.076404 | 77.3694
15 | Office | 1980-2004 | 2015 | lights_reduce_70p | 0.076404 | 95.3312
15 | Office | 1980-2004 | 2015 | load_reduce | 0.076404 | 282.1376
15 | Office | 1980-2004 | 2015 | occupancy_setback | 0.076404 | -59.6312
15 | Office | 1980-2004 | 2015 | payback_less_than_20 | 0.076404 | 1120.3305
15 | Office | 1980-2004 | 2015 | plug_loads_90_percent | 0.076404 | -128.4116
15 | Office | 1980-2004 | 2015 | pumps_to_variable | 0.076404 | -56.3153
15 | Office | 1980-2004 | 2015 | pump_fan_eff_ | 0.076404 | -105.4772
19 | Recreation Center | 1980-2004 | 2015 | air_temp_reset_enabled | 0.068406 | -114.5661
19 | Recreation Center | 1980-2004 | 2015 | baseline | 0.068406 | 0
19 | Recreation Center | 1980-2004 | 2015 | boiler_eff_upgrade | 0.068406 | 13.8242
19 | Recreation Center | 1980-2004 | 2015 | boiler_reset | 0.068406 | 77.5773
19 | Recreation Center | 1980-2004 | 2015 | cooling_cop_3_0 | 0.068406 | 16.278
19 | Recreation Center | 1980-2004 | 2015 | dcv_enabled | 0.068406 | 234.0326
19 | Recreation Center | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.068406 | 16.339
19 | Recreation Center | 1980-2004 | 2015 | economizers_enabled | 0.068406 | 14.1172
19 | Recreation Center | 1980-2004 | 2015 | elec_reduce | 0.068406 | 396.0812
19 | Recreation Center | 1980-2004 | 2015 | envelope_ecm_roof | 0.068406 | 24.4123
19 | Recreation Center | 1980-2004 | 2015 | envelope_ecm_wall | 0.068406 | -41.1853
19 | Recreation Center | 1980-2004 | 2015 | envelope_ecm_windows | 0.068406 | -58.2903
19 | Recreation Center | 1980-2004 | 2015 | fans_to_variable | 0.068406 | 15.4913
19 | Recreation Center | 1980-2004 | 2015 | hrv_enabled | 0.068406 | 266.467
19 | Recreation Center | 1980-2004 | 2015 | infil_reduce | 0.068406 | 174.606
19 | Recreation Center | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.068406 | -15.9443
19 | Recreation Center | 1980-2004 | 2015 | lights_reduce_70p | 0.068406 | 166.3189
19 | Recreation Center | 1980-2004 | 2015 | load_reduce | 0.068406 | 56.0882
19 | Recreation Center | 1980-2004 | 2015 | occupancy_setback | 0.068406 | -206.4751
19 | Recreation Center | 1980-2004 | 2015 | payback_less_than_20 | 0.068406 | 436.8219
19 | Recreation Center | 1980-2004 | 2015 | plug_loads_90_percent | 0.068406 | 13.3207
19 | Recreation Center | 1980-2004 | 2015 | pumps_to_variable | 0.068406 | 49.7208
19 | Recreation Center | 1980-2004 | 2015 | pump_fan_eff_ | 0.068406 | 24.5306
20 | Storage Building | 1959-pre | 2015 | baseline | 0.0014259 | 0
20 | Storage Building | 1959-pre | 2015 | dcv_enabled | 0.0014259 | 0.22747
20 | Storage Building | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.0014259 | 0.22747
20 | Storage Building | 1959-pre | 2015 | elec_reduce | 0.0014259 | 2.1471
20 | Storage Building | 1959-pre | 2015 | envelope_ecm_roof | 0.0014259 | 1.8292
20 | Storage Building | 1959-pre | 2015 | envelope_ecm_wall | 0.0014259 | 0.96081
20 | Storage Building | 1959-pre | 2015 | envelope_ecm_windows | 0.0014259 | 0.22747
20 | Storage Building | 1959-pre | 2015 | exhaust_fans_occ_control | 0.0014259 | 0.22747
20 | Storage Building | 1959-pre | 2015 | hrv_enabled | 0.0014259 | 0.22747
20 | Storage Building | 1959-pre | 2015 | infil_reduce | 0.0014259 | 11.5985
20 | Storage Building | 1959-pre | 2015 | infil_reduce_plus_setback | 0.0014259 | 12.9057
20 | Storage Building | 1959-pre | 2015 | lights_reduce_70p | 0.0014259 | 2.1595
20 | Storage Building | 1959-pre | 2015 | load_reduce | 0.0014259 | 12.9057
20 | Storage Building | 1959-pre | 2015 | occupancy_setback | 0.0014259 | 2.31
20 | Storage Building | 1959-pre | 2015 | payback_less_than_20 | 0.0014259 | 14.842
20 | Storage Building | 1959-pre | 2015 | plug_loads_90_percent | 0.0014259 | 0.21703
21 | Storage Building | 1960-1979 | 2015 | baseline | 0.0035951 | 0
21 | Storage Building | 1960-1979 | 2015 | dcv_enabled | 0.0035951 | 0.77777
21 | Storage Building | 1960-1979 | 2015 | ecm_cold_deck_reset_control | 0.0035951 | 0.77777
21 | Storage Building | 1960-1979 | 2015 | elec_reduce | 0.0035951 | 5.6641
21 | Storage Building | 1960-1979 | 2015 | envelope_ecm_roof | 0.0035951 | 12.3975
21 | Storage Building | 1960-1979 | 2015 | envelope_ecm_wall | 0.0035951 | 1.4268
21 | Storage Building | 1960-1979 | 2015 | envelope_ecm_windows | 0.0035951 | 0.77777
21 | Storage Building | 1960-1979 | 2015 | exhaust_fans_occ_control | 0.0035951 | 0.77777
21 | Storage Building | 1960-1979 | 2015 | hrv_enabled | 0.0035951 | 0.77777
21 | Storage Building | 1960-1979 | 2015 | infil_reduce | 0.0035951 | 15.0896
21 | Storage Building | 1960-1979 | 2015 | infil_reduce_plus_setback | 0.0035951 | 19.1748
21 | Storage Building | 1960-1979 | 2015 | lights_reduce_70p | 0.0035951 | 5.7006
21 | Storage Building | 1960-1979 | 2015 | load_reduce | 0.0035951 | 19.1748
21 | Storage Building | 1960-1979 | 2015 | occupancy_setback | 0.0035951 | 5.825
21 | Storage Building | 1960-1979 | 2015 | payback_less_than_20 | 0.0035951 | 24.0307
21 | Storage Building | 1960-1979 | 2015 | plug_loads_90_percent | 0.0035951 | 0.74221
22 | Storage Building | 1980-2004 | 2015 | baseline | 0.043746 | 0
22 | Storage Building | 1980-2004 | 2015 | dcv_enabled | 0.043746 | 6.0391
22 | Storage Building | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.043746 | 6.0391
22 | Storage Building | 1980-2004 | 2015 | elec_reduce | 0.043746 | 65.9697
22 | Storage Building | 1980-2004 | 2015 | envelope_ecm_roof | 0.043746 | 55.3792
22 | Storage Building | 1980-2004 | 2015 | envelope_ecm_wall | 0.043746 | 11.5021
22 | Storage Building | 1980-2004 | 2015 | envelope_ecm_windows | 0.043746 | 6.0391
22 | Storage Building | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.043746 | 6.0391
22 | Storage Building | 1980-2004 | 2015 | hrv_enabled | 0.043746 | 6.0391
22 | Storage Building | 1980-2004 | 2015 | infil_reduce | 0.043746 | 49.328
22 | Storage Building | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.043746 | 88.085
22 | Storage Building | 1980-2004 | 2015 | lights_reduce_70p | 0.043746 | 66.2738
22 | Storage Building | 1980-2004 | 2015 | load_reduce | 0.043746 | 88.085
22 | Storage Building | 1980-2004 | 2015 | occupancy_setback | 0.043746 | 48.0879
22 | Storage Building | 1980-2004 | 2015 | payback_less_than_20 | 0.043746 | 147.5257
22 | Storage Building | 1980-2004 | 2015 | plug_loads_90_percent | 0.043746 | 5.7881
23 | Storage Building | 2005-2014 | 2015 | baseline | 0.0021648 | 0
23 | Storage Building | 2005-2014 | 2015 | dcv_enabled | 0.0021648 | 0.24186
23 | Storage Building | 2005-2014 | 2015 | ecm_cold_deck_reset_control | 0.0021648 | 0.24186
23 | Storage Building | 2005-2014 | 2015 | elec_reduce | 0.0021648 | 3.2589
23 | Storage Building | 2005-2014 | 2015 | envelope_ecm_roof | 0.0021648 | 1.8713
23 | Storage Building | 2005-2014 | 2015 | envelope_ecm_wall | 0.0021648 | 0.33474
23 | Storage Building | 2005-2014 | 2015 | envelope_ecm_windows | 0.0021648 | 0.24186
23 | Storage Building | 2005-2014 | 2015 | exhaust_fans_occ_control | 0.0021648 | 0.24186
23 | Storage Building | 2005-2014 | 2015 | hrv_enabled | 0.0021648 | 0.24186
23 | Storage Building | 2005-2014 | 2015 | lights_reduce_70p | 0.0021648 | 3.271
23 | Storage Building | 2005-2014 | 2015 | load_reduce | 0.0021648 | -2.1683
23 | Storage Building | 2005-2014 | 2015 | occupancy_setback | 0.0021648 | 1.6986
23 | Storage Building | 2005-2014 | 2015 | payback_less_than_20 | 0.0021648 | 0.7781
23 | Storage Building | 2005-2014 | 2015 | plug_loads_90_percent | 0.0021648 | 0.2313
24 | Training Building | 1959-pre | 2015 | air_temp_reset_enabled | 0.029521 | -88.3599
24 | Training Building | 1959-pre | 2015 | baseline | 0.029521 | 0
24 | Training Building | 1959-pre | 2015 | boiler_eff_upgrade | 0.029521 | -3.7691
24 | Training Building | 1959-pre | 2015 | boiler_reset | 0.029521 | 195.3535
24 | Training Building | 1959-pre | 2015 | cooling_cop_3_0 | 0.029521 | 0.64263
24 | Training Building | 1959-pre | 2015 | dcv_enabled | 0.029521 | 75.6559
24 | Training Building | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.029521 | -2.1577
24 | Training Building | 1959-pre | 2015 | economizers_enabled | 0.029521 | -1.0001
24 | Training Building | 1959-pre | 2015 | elec_reduce | 0.029521 | 124.863
24 | Training Building | 1959-pre | 2015 | envelope_ecm_roof | 0.029521 | 59.1523
24 | Training Building | 1959-pre | 2015 | envelope_ecm_wall | 0.029521 | 24.126
24 | Training Building | 1959-pre | 2015 | envelope_ecm_windows | 0.029521 | 6.4642
24 | Training Building | 1959-pre | 2015 | exhaust_fans_occ_control | 0.029521 | -3.6387
24 | Training Building | 1959-pre | 2015 | fans_to_variable | 0.029521 | -3.7691
24 | Training Building | 1959-pre | 2015 | hrv_enabled | 0.029521 | 67.0343
24 | Training Building | 1959-pre | 2015 | infil_reduce | 0.029521 | 280.194
24 | Training Building | 1959-pre | 2015 | infil_reduce_plus_setback | 0.029521 | 307.1792
24 | Training Building | 1959-pre | 2015 | lights_reduce_70p | 0.029521 | 44.4688
24 | Training Building | 1959-pre | 2015 | load_reduce | 0.029521 | 403.1476
24 | Training Building | 1959-pre | 2015 | occupancy_setback | 0.029521 | 54.5067
24 | Training Building | 1959-pre | 2015 | payback_less_than_20 | 0.029521 | 475.1749
24 | Training Building | 1959-pre | 2015 | plug_loads_90_percent | 0.029521 | -3.1901
24 | Training Building | 1959-pre | 2015 | pumps_to_variable | 0.029521 | -3.7691
24 | Training Building | 1959-pre | 2015 | pump_fan_eff_ | 0.029521 | -2.9483
25 | Training Building | 1980-2004 | 2015 | air_temp_reset_enabled | 0.020875 | -44.1107
25 | Training Building | 1980-2004 | 2015 | baseline | 0.020875 | 0
25 | Training Building | 1980-2004 | 2015 | boiler_eff_upgrade | 0.020875 | -10.5364
25 | Training Building | 1980-2004 | 2015 | boiler_reset | 0.020875 | 68.8084
25 | Training Building | 1980-2004 | 2015 | cooling_cop_3_0 | 0.020875 | -8.6474
25 | Training Building | 1980-2004 | 2015 | dcv_enabled | 0.020875 | 45.49
25 | Training Building | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.020875 | -6.0422
25 | Training Building | 1980-2004 | 2015 | economizers_enabled | 0.020875 | -6.2847
25 | Training Building | 1980-2004 | 2015 | elec_reduce | 0.020875 | 85.7833
25 | Training Building | 1980-2004 | 2015 | envelope_ecm_roof | 0.020875 | 11.8941
25 | Training Building | 1980-2004 | 2015 | envelope_ecm_wall | 0.020875 | -4.1047
25 | Training Building | 1980-2004 | 2015 | envelope_ecm_windows | 0.020875 | -6.1271
25 | Training Building | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.020875 | -10.306
25 | Training Building | 1980-2004 | 2015 | fans_to_variable | 0.020875 | -6.4486
25 | Training Building | 1980-2004 | 2015 | hrv_enabled | 0.020875 | 37.3713
25 | Training Building | 1980-2004 | 2015 | infil_reduce | 0.020875 | 42.5393
25 | Training Building | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.020875 | 60.5861
25 | Training Building | 1980-2004 | 2015 | lights_reduce_70p | 0.020875 | 30.2262
25 | Training Building | 1980-2004 | 2015 | load_reduce | 0.020875 | 115.5537
25 | Training Building | 1980-2004 | 2015 | occupancy_setback | 0.020875 | 7.5324
25 | Training Building | 1980-2004 | 2015 | payback_less_than_20 | 0.020875 | 175.8642
25 | Training Building | 1980-2004 | 2015 | plug_loads_90_percent | 0.020875 | -8.8237
25 | Training Building | 1980-2004 | 2015 | pumps_to_variable | 0.020875 | -10.5364
25 | Training Building | 1980-2004 | 2015 | pump_fan_eff_ | 0.020875 | -9.9883
26 | Training Building | 2005-2014 | 2015 | air_temp_reset_enabled | 0.008076 | -20.5786
26 | Training Building | 2005-2014 | 2015 | baseline | 0.008076 | 0
26 | Training Building | 2005-2014 | 2015 | boiler_eff_upgrade | 0.008076 | -8.5688
26 | Training Building | 2005-2014 | 2015 | boiler_reset | 0.008076 | 13.5798
26 | Training Building | 2005-2014 | 2015 | cooling_cop_3_0 | 0.008076 | -8.5688
26 | Training Building | 2005-2014 | 2015 | dcv_enabled | 0.008076 | 13.5991
26 | Training Building | 2005-2014 | 2015 | ecm_cold_deck_reset_control | 0.008076 | -7.4769
26 | Training Building | 2005-2014 | 2015 | economizers_enabled | 0.008076 | -6.4679
26 | Training Building | 2005-2014 | 2015 | elec_reduce | 0.008076 | 30.4558
26 | Training Building | 2005-2014 | 2015 | envelope_ecm_roof | 0.008076 | -3.7906
26 | Training Building | 2005-2014 | 2015 | envelope_ecm_wall | 0.008076 | -7.2818
26 | Training Building | 2005-2014 | 2015 | envelope_ecm_windows | 0.008076 | -6.8891
26 | Training Building | 2005-2014 | 2015 | exhaust_fans_occ_control | 0.008076 | -8.5315
26 | Training Building | 2005-2014 | 2015 | fans_to_variable | 0.008076 | -7.4546
26 | Training Building | 2005-2014 | 2015 | hrv_enabled | 0.008076 | 9.4352
26 | Training Building | 2005-2014 | 2015 | lights_reduce_70p | 0.008076 | 9.3576
26 | Training Building | 2005-2014 | 2015 | load_reduce | 0.008076 | 18.2022
26 | Training Building | 2005-2014 | 2015 | occupancy_setback | 0.008076 | -0.33798
26 | Training Building | 2005-2014 | 2015 | payback_less_than_20 | 0.008076 | 43.1074
26 | Training Building | 2005-2014 | 2015 | plug_loads_90_percent | 0.008076 | -7.8507
26 | Training Building | 2005-2014 | 2015 | pumps_to_variable | 0.008076 | -8.5688
26 | Training Building | 2005-2014 | 2015 | pump_fan_eff_ | 0.008076 | -8.4306
27 | Vehicle Garage | 1959-pre | 2015 | air_temp_reset_enabled | 0.02256 | -2.2462
27 | Vehicle Garage | 1959-pre | 2015 | baseline | 0.02256 | 0
27 | Vehicle Garage | 1959-pre | 2015 | boiler_eff_upgrade | 0.02256 | 2.5949
27 | Vehicle Garage | 1959-pre | 2015 | boiler_reset | 0.02256 | 38.4123
27 | Vehicle Garage | 1959-pre | 2015 | dcv_enabled | 0.02256 | 15.1633
27 | Vehicle Garage | 1959-pre | 2015 | ecm_cold_deck_reset_control | 0.02256 | 2.5949
27 | Vehicle Garage | 1959-pre | 2015 | economizers_enabled | 0.02256 | 2.9806
27 | Vehicle Garage | 1959-pre | 2015 | elec_reduce | 0.02256 | 29.852
27 | Vehicle Garage | 1959-pre | 2015 | envelope_ecm_roof | 0.02256 | 5.8432
27 | Vehicle Garage | 1959-pre | 2015 | envelope_ecm_wall | 0.02256 | 11.5624
27 | Vehicle Garage | 1959-pre | 2015 | envelope_ecm_windows | 0.02256 | 2.7399
27 | Vehicle Garage | 1959-pre | 2015 | exhaust_fans_occ_control | 0.02256 | 2.8506
27 | Vehicle Garage | 1959-pre | 2015 | fans_to_variable | 0.02256 | 2.7618
27 | Vehicle Garage | 1959-pre | 2015 | hrv_enabled | 0.02256 | 4.771
27 | Vehicle Garage | 1959-pre | 2015 | infil_reduce | 0.02256 | 58.0892
27 | Vehicle Garage | 1959-pre | 2015 | infil_reduce_plus_setback | 0.02256 | 78.7629
27 | Vehicle Garage | 1959-pre | 2015 | lights_reduce_70p | 0.02256 | 10.7197
27 | Vehicle Garage | 1959-pre | 2015 | load_reduce | 0.02256 | 98.8
27 | Vehicle Garage | 1959-pre | 2015 | occupancy_setback | 0.02256 | 8.396
27 | Vehicle Garage | 1959-pre | 2015 | payback_less_than_20 | 0.02256 | 102.7781
27 | Vehicle Garage | 1959-pre | 2015 | plug_loads_90_percent | 0.02256 | 2.4539
27 | Vehicle Garage | 1959-pre | 2015 | pump_fan_eff_ | 0.02256 | 9.001
28 | Vehicle Garage | 1980-2004 | 2015 | air_temp_reset_enabled | 0.051036 | -7.4022
28 | Vehicle Garage | 1980-2004 | 2015 | baseline | 0.051036 | 0
28 | Vehicle Garage | 1980-2004 | 2015 | boiler_eff_upgrade | 0.051036 | 1.8933
28 | Vehicle Garage | 1980-2004 | 2015 | boiler_reset | 0.051036 | 57.5703
28 | Vehicle Garage | 1980-2004 | 2015 | dcv_enabled | 0.051036 | 29.9427
28 | Vehicle Garage | 1980-2004 | 2015 | ecm_cold_deck_reset_control | 0.051036 | 1.8933
28 | Vehicle Garage | 1980-2004 | 2015 | economizers_enabled | 0.051036 | 2.8588
28 | Vehicle Garage | 1980-2004 | 2015 | elec_reduce | 0.051036 | 59.1567
28 | Vehicle Garage | 1980-2004 | 2015 | envelope_ecm_roof | 0.051036 | 8.5247
28 | Vehicle Garage | 1980-2004 | 2015 | envelope_ecm_wall | 0.051036 | 13.9354
28 | Vehicle Garage | 1980-2004 | 2015 | envelope_ecm_windows | 0.051036 | 2.138
28 | Vehicle Garage | 1980-2004 | 2015 | exhaust_fans_occ_control | 0.051036 | 2.4717
28 | Vehicle Garage | 1980-2004 | 2015 | fans_to_variable | 0.051036 | 2.1587
28 | Vehicle Garage | 1980-2004 | 2015 | hrv_enabled | 0.051036 | 6.4936
28 | Vehicle Garage | 1980-2004 | 2015 | infil_reduce | 0.051036 | 42.4746
28 | Vehicle Garage | 1980-2004 | 2015 | infil_reduce_plus_setback | 0.051036 | 85.3434
28 | Vehicle Garage | 1980-2004 | 2015 | lights_reduce_70p | 0.051036 | 20.4869
28 | Vehicle Garage | 1980-2004 | 2015 | load_reduce | 0.051036 | 126.0593
28 | Vehicle Garage | 1980-2004 | 2015 | occupancy_setback | 0.051036 | 11.8341
28 | Vehicle Garage | 1980-2004 | 2015 | payback_less_than_20 | 0.051036 | 137.9103
28 | Vehicle Garage | 1980-2004 | 2015 | plug_loads_90_percent | 0.051036 | 1.6633
28 | Vehicle Garage | 1980-2004 | 2015 | pump_fan_eff_ | 0.051036 | 11.9743

## ChartsAfterThis!
Year | 20 Year Payback ECM Package | Business as Usual
2015 | 424 | 424
2018 | 409 | 409
2020 | 388 | 388
2023 | 164.3321 | 336
2025 | 159.6472 | 336
2030 | 159.6472 | 336
2033 | 159.6472 | 336
2035 | 159.6472 | 336
Archetype | 2015 | 2023
Barracks: pre 1960 | 133.4423 | 72.2348
Firehall: pre 1960 | 736.4335 | 340.1063
Food Services: pre 1960 | 784.9417 | 283.8909
Food Services: 2005-2014 | 486.9522 | 268.6647
Hanger: pre 1960 | 543.9877 | 214.0157
Hanger: 1960-1979 | 529.6298 | 215.6583
Hanger: 1980-2004 | 361.5386 | 183.5138
Small Main. Shop: pre 1960 | 892.5013 | 344.7148
Small Main. Shop: 1960-1979 | 834.6611 | 326.2425
Small Main. Shop: 1980-2004 | 478.0106 | 241.3441
Large Main. Shop: pre 1960 | 653.2778 | 199.7001
Large Main. Shop: 1980-2004 | 393.2228 | 144.9586
Small Office: 1960-1979 | 93.6986 | 50.8086
Small Office: 1980-2004 | 62.1083 | 38.01
Small Office: post 2005 | 43.3719 | 34.0573
Large Office: pre 1960 | 599.95 | 175.4437
Large Office: 1960-1979 | 567.6904 | 198.9693
Large Office: 1980-2004 | 409.1322 | 162.8948
Recreation Centre: 1980-2004 | 475.1128 | 375.7072
Storage: pre 1960 | 452.0653 | 225.5438
Storage: 1960-1979 | 415.8616 | 279.186
Storage: 1980-2004 | 267.3206 | 214.492
Storage: post 2005 | 175.4249 | 197.6682
Training Bldg: pre 1960 | 600.933 | 185.6714
Training Bldg: 1980-2004 | 374.4271 | 152.7433
Training Bldg post 2005 | 275.4264 | 135.709
Vehicle Garage: pre 1960 | 149.2886 | 52.415
Vehicle Garage: 1980-2004 | 106.3684 | 47.8875
Year | Business As Usual | 12% Savings | 15% Savings | 20% Savings | 30% Savings
2015 | 437.6287 | 437.6287 | 437.6287 | 437.6287 | 437.6287
2018 | 438.6801 | 391.6787 | 381.461 | 365.5668 | 337.4462
2020 | 424.1326 | 378.6899 | 368.811 | 353.4439 | 326.2559
2023 | 383.5934 | 342.4941 | 333.5594 | 319.6611 | 295.0718
2025 | 372.6577 | 332.7301 | 324.0502 | 310.5481 | 286.6598
| Cost Savings $/m2 | GHG (tonnes)
supply air temperature reset | 0.33829 | 666.7247
boiler/rooftop efficiency upgrade | 0.49244 | 928.4916
hot water loop temperature reset | 2.1061 | 4300.3905
cooling DX upgrade to COP 3.5 | 0.81163 | 1491.1032
demand control ventilation (DCV) | 0.86534 | 2009.9367
cold deck reset | 0.39311 | 837.142
economizer control for free cooling | 0.41304 | 793.0437
additional RSI 2.68 roof insulation | 0.43278 | 926.9487
additional RSI 1.32 exterior wall insulation | 0.22327 | 491.1975
upgrade windows to triple glazing | -0.0062038 | 42.8189
exhaust fan operational controls | 2.0386 | 3622.7424
convert 1 hp+ fans to variable frequency drives (VFD) | 0.40721 | 782.5059
heat recovery ventilation | 0.49775 | 1430.109
envelope air sealing to 0.27 air changes per hour (ACH) | 2.6279 | 5436.3154
reduce lighting power by 30% | 1.2174 | 1794.8503
2 °C night temperature setback | 0.35215 | 857.005
reduce plug loads by 10% (unoccupied hours) | -0.065611 | -83.8875
convert motors to high efficiency | 0.6061 | 1094.9565
convert 10 hp+ pumps to variable speed (VSP) | 4.4755 | 8064.1968
air sealing+hot water loop+ setback+VSP | 3.9218 | 8170.4683
air sealing+setback+VSP | 3.045 | 6292.3416
lighting+DCV+VSP+motor upgrades+VFD+exhaust fan control | 2.7599 | 4841.3188
retro-commissioning | 0.93767 | 1870.8715
solar hot water preheating | 0.15647 | 275.9112
measures with less than 20 yr payback | 6.5821 | 12746.0862
| 2015 | 2018 | 2020 | 2023 | 2025 | 2030 | 2033 | 2035
Natural Gas Cost: BAU | 5.7919 | 6.1464 | 6.3948 | 6.7862 | 7.0603 | 7.7952 | 8.2723 | 8.6065
Electricity Cost: BAU | 9.0515 | 10.1818 | 11.0126 | 12.3877 | 13.3985 | 16.3013 | 18.3368 | 19.8331
Natural Gas Cost: ECMs | 5.7919 | 6.1464 | 6.3948 | 2.2953 | 2.388 | 2.6366 | 2.7979 | 2.911
Electricity Cost: ECMs | 9.0515 | 10.1818 | 11.0126 | 6.86 | 7.4198 | 9.0273 | 10.1545 | 10.9831
Total: BAU | 14.8435 | 16.3282 | 17.4073 | 19.1738 | 20.4588 | 24.0965 | 26.6091 | 28.4396
Total: ECM | 14.8435 | 16.3282 | 17.4073 | 14.6829 | 15.7865 | 18.9379 | 21.1347 | 22.744
| 2015 | 2018 | 2020 | 2023 | 2025 | 2030 | 2033 | 2035
Total: BAU | 3435181.3976 | 3787865.2959 | 3904294.512 | 3889451.082 | 4031801.4451 | 4748673.24 | 5243824.0338 | 5604555.2459
Total: ECM | 3435181.3976 | 3787865.2959 | 3904294.512 | 2978464.8933 | 3111031.4573 | 3732068.7723 | 4164995.2399 | 4482141.7687
Note on A81: Lubun, Mike: 12% savings on heating/cooling/fan/pump

## ECM Base Cost Savings Intensity
Row Labels | Sum of Net Cost Savings Intensity $/M2
air_temp_reset_enabled | 0.33639
baseline | 0
boiler_eff_upgrade | 0.50569
boiler_reset | 2.0559
cooling_cop_3_0 | 0.82849
dcv_enabled | 0.86133
ecm_cold_deck_reset_control | 0.3816
economizers_enabled | 0.42553
envelope_ecm_roof | 0.43205
envelope_ecm_wall | 0.22272
envelope_ecm_windows | -0.0052808
exhaust_fans_occ_control | 2.0305
fans_to_variable | 0.42046
hrv_enabled | 0.49416
infil_reduce | 2.6122
lights_reduce_70p | 1.2166
occupancy_setback | 0.34945
plug_loads_90_percent | -0.065157
pump_fan_eff_ | 0.61996
pumps_to_variable | 4.482
Grand Total | 18.2046

## ECMBaseEnergySavingIntensity
Row Labels | Sum of Savings Electricity-Heating KWh/m2 | Sum of Savings Natural Gas-Heating KWh/m2 | Sum of Savings Electricity-Cooling KWh/m2 | Sum of Savings Electricity-Water Systems KWh/m2 | Sum of Savings Natural Gas-Water Systems KWh/m2 | Sum of Savings Electricity-Interior Lighting KWh/m2 | Sum of Savings Electricity-Interior Equipment KWh/m2 | Sum of Savings District Heating-Interior Equipment KWh/m2 | Sum of Savings Electricity-Fans KWh/m2 | Sum of Savings Electricity-Pumps KWh/m2
2013 | 0.70516 | 632.93 | -9.0049 | 2.8296 | 5.2641 | 43.1618 | 4.1682 | 0.34804 | 16.826 | 13.8981
air_temp_reset_enabled | 0.17253 | 12.5403 | -0.66882 | -0.00015498 | 0.00066345 | 1.8264 | 0.16919 | 0 | 0.18431 | -0.50445
baseline | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
boiler_eff_upgrade | 0.013897 | 14.7736 | -0.60583 | 0.070142 | 3.015e-05 | 2.161 | 0.24932 | 0 | 0.53866 | -0.069993
boiler_reset | -0.0028973 | 92.1885 | -0.63974 | 1.7642e-05 | 3.015e-05 | 1.8264 | 0.16919 | 0 | 0.36508 | 3.2598
cooling_cop_3_0 | -0.0028973 | 20.7183 | 0.20775 | 0.055295 | 3.015e-05 | 2.6032 | 0.33671 | 0 | 0.78252 | 0.37903
dcv_enabled | 0.022459 | 59.653 | -0.87054 | 1.7642e-05 | 4.5225e-05 | 0 | 0 | 0 | -0.1134 | 0.031798
ecm_cold_deck_reset_control | -0.14447 | 19.9224 | 0.84436 | -0.00059223 | 9.3813e-05 | 0 | 0 | 0 | -0.17756 | -0.00089302
economizers_enabled | -0.0030933 | 13.7126 | -0.51407 | 1.7642e-05 | 3.015e-05 | 1.8264 | 0.16919 | 0 | 0.36474 | -0.043268
envelope_ecm_roof | 0.030392 | 22.7575 | -0.41506 | 0.00022599 | 0.0001809 | 0 | 0 | 0 | 0.58719 | 0.35806
envelope_ecm_wall | -0.072105 | 12.875 | -0.56494 | 0.00031285 | 0.00016582 | 0 | 0 | 0 | 0.39943 | 0.36244
envelope_ecm_windows | -0.12529 | 4.7455 | -0.66857 | 1.7642e-05 | 0.00016582 | 0 | 0 | 0 | 0.034048 | 0.032714
exhaust_fans_occ_control | 0.83274 | 36.0329 | -0.43363 | 0.12406 | 3.2813 | 5.0626 | 0.84934 | 0.34804 | 5.1948 | 0.65326
fans_to_variable | -0.0029538 | 13.5953 | -0.63698 | 1.7642e-05 | 3.015e-05 | 1.8264 | 0.16919 | 0 | 0.48074 | -0.06458
hrv_enabled | 0.052443 | 59.0859 | -1.0489 | 1.7642e-05 | 7.5515e-05 | 0 | 0 | 0 | -0.11296 | 0.036759
infil_reduce | 0.25076 | 120.539 | -0.54896 | 0.065444 | 0.00037716 | 0.41017 | 0.088551 | 0 | 2.9655 | 2.6041
lights_reduce_70p | -0.063315 | -9.6715 | -0.089955 | -6.3021e-05 | -4.5225e-05 | 12.552 | 0 | 0 | -0.11725 | -0.12891
occupancy_setback | -0.26162 | 28.0937 | -0.83046 | -0.00022744 | 0.00047378 | 0 | 0 | 0 | 0.077783 | 0.079365
plug_loads_90_percent | -0.0024408 | 1.6696 | -0.6116 | 1.7642e-05 | 1.5075e-05 | 0 | 0 | 0 | -0.12868 | -0.073276
pump_fan_eff_ | -0.0028973 | 13.77 | -0.63974 | 1.7642e-05 | 3.015e-05 | 1.8264 | 0.16919 | 0 | 0.36508 | 1.7942
pumps_to_variable | 0.013912 | 95.9284 | -0.26919 | 2.515 | 1.9805 | 11.241 | 1.7983 | 0 | 5.1359 | 5.192
Grand Total | 0.70516 | 632.93 | -9.0049 | 2.8296 | 5.2641 | 43.1618 | 4.1682 | 0.34804 | 16.826 | 13.8981